## ReadMe
Tab Name | Content
DC_raw | Raw data of a weekly typical data center energy consumption profile from Rahmani 2017 | Variables are marked with grey background
DC_load | Data center energy consumption with server utilization rate
Basic characteristics of the data center
Linear models of server and non-server energy consumption
Key assumptions on PUE and DR
DC_201X | The hourly data center energy consumption profile given the assumed PUE and DR value for the year 201X
201X | Wind, solar and total curtailment by hour from CAISO
Hourly GHG intensity of CAISO excess VRE and PJM grid mix
Absorption by existing and additional datacenters by hour
Total GHG emissions reduction by hour
Summary | Yearly total curtailment, absorption and GHG reduction
Cost change breakdown and abatement cost
EmbodiedGHG | Normalized embodied GHG emissions of datacenters with reference

## DC_raw
Hour | Server | Power_loss | Chiller | CRAH | Pumps | Miscellenous | Total (W) | Source: Rahmani, R., Moser, I. & Seyedmahmoudian, M. A Complete Model for Modular Simulation of Data Centre Power Load. (2018).
1 | 5135241.9616 | 636748.2682 | 869572.1217 | 874191.3056 | 375787.6829 | 473492.4804 | 8365033.8204
2 | 5084363.56 | 630147.2199 | 831220.3254 | 853938.0193 | 369983.4562 | 466179.1549 | 8235831.7357
3 | 5080449.8372 | 629640.6041 | 822007.7094 | 852380.0744 | 369223.9113 | 465222.1282 | 8218924.2645
4 | 5143069.4072 | 637766.2934 | 855223.1737 | 877307.1955 | 375668.3035 | 473342.0624 | 8362376.4358
5 | 5150896.8528 | 638784.9798 | 860121.2724 | 880423.0854 | 376511.3095 | 474404.25 | 8381141.75
6 | 5350496.7416 | 664984.8798 | 962914.539 | 959878.2878 | 396913.7224 | 500111.2902 | 8835299.4608
7 | 5687076.944 | 710138.8473 | 1127809.7595 | 1093861.5694 | 430944.356 | 542989.8886 | 9592821.3648
8 | 6000174.8044 | 753240.087 | 1334955.8095 | 1218497.1793 | 465343.394 | 586332.6764 | 10358543.9506
9 | 5988433.636 | 751604.6993 | 1416015.4726 | 1213823.3445 | 468493.8576 | 590302.2606 | 10428673.2705
10 | 6696817.5512 | 852935.817 | 1929404.3564 | 1495811.4142 | 548748.4569 | 691423.0557 | 12215140.6516
11 | 7667420.9252 | 1000569.1995 | 2735078.6374 | 1882181.8075 | 664262.5285 | 836970.7859 | 14786483.884
12 | 8117499.0992 | 1072478.317 | 3192135.6568 | 2061345.4966 | 722172.9285 | 909937.8899 | 16075569.3879
13 | 8293616.6512 | 1101211.725 | 3445828.7756 | 2131453.0293 | 748605.5091 | 943242.9414 | 16663958.6317
14 | 8191859.8428 | 1084569.3728 | 3382240.6513 | 2090946.4546 | 737480.8161 | 929225.8283 | 16416322.9658
15 | 8148808.8868 | 1077562.0151 | 3392607.9715 | 2073809.0582 | 734639.3966 | 925645.6397 | 16353072.9678
16 | 8700643.8692 | 1168898.516 | 3947001.127 | 2293479.322 | 805501.1417 | 1014931.4386 | 17930455.4144
17 | 9319012.1496 | 1275151.6187 | 4534554.2556 | 2539634.6539 | 883417.6339 | 1113106.2187 | 19664876.5303
18 | 9205514.1728 | 1255340.2851 | 4306870.7686 | 2494454.2444 | 863108.9735 | 1087517.3067 | 19212805.7511
19 | 9452078.7404 | 1298555.7284 | 4488175.9434 | 2592604.7881 | 891570.76 | 1123379.1576 | 19846365.118
20 | 9420768.9528 | 1293031.6882 | 4309793.5817 | 2580141.2265 | 880186.7725 | 1109035.3333 | 19592957.555
21 | 9686902.1396 | 1340323.2269 | 4456241.1094 | 2686081.4971 | 908477.3987 | 1144681.5223 | 20222706.894
22 | 7839624.7492 | 1027824.0648 | 2762169.2891 | 1950731.3933 | 679017.4748 | 855562.0183 | 15114928.9894
23 | 6078449.2708 | 764180.6906 | 1503714.7766 | 1249656.0823 | 479800.041 | 604548.0517 | 10680348.913
24 | 5298083.1492 | 658063.3365 | 1024430.9926 | 939013.8844 | 395979.5681 | 498934.2558 | 8814505.1866
25 | 5252653.6612 | 652088.0715 | 978155.2683 | 920929.6601 | 390191.3331 | 491641.0796 | 8685659.0738
26 | 5201775.2596 | 645422.5587 | 944530.2522 | 900676.3738 | 384620.2222 | 484621.48 | 8561646.1465
27 | 5154810.5756 | 639294.5709 | 869117.6383 | 881981.0304 | 377260.1908 | 475347.8404 | 8397811.8463
28 | 5193947.8088 | 644399.574 | 865917.1514 | 897560.4818 | 380091.2508 | 478914.976 | 8460831.2429
29 | 5307445.7856 | 659297.5564 | 897068.4449 | 942740.8914 | 390327.6339 | 491812.8187 | 8688693.1309
30 | 5420943.7624 | 674334.5508 | 945397.9612 | 987921.3009 | 401429.8788 | 505801.6472 | 8935829.1013
31 | 5816229.812 | 727789.9236 | 1154662.8473 | 1145273.7587 | 442197.8171 | 557169.2495 | 9843323.4082
32 | 5980606.1904 | 750515.2673 | 1305313.9312 | 1210707.4546 | 462357.1422 | 582569.9991 | 10292069.9848
33 | 6289790.328 | 794050.5768 | 1577483.8084 | 1333785.1195 | 499755.4916 | 629691.9195 | 11124557.2438
34 | 6708558.7196 | 854660.9591 | 1986141.4007 | 1500485.249 | 552492.3164 | 696140.3187 | 12298478.9636
35 | 7722213.0496 | 1009206.4902 | 2898728.48 | 1903993.0388 | 676707.0529 | 852650.8867 | 15063498.9983
36 | 8203601.0164 | 1086483.9421 | 3404291.6454 | 2095620.2915 | 739499.8448 | 931769.8044 | 16461266.5447
37 | 8238824.5216 | 1092236.5735 | 3530885.3483 | 2109641.796 | 748579.412 | 943210.0591 | 16663377.7104
38 | 8274048.032 | 1098002.5944 | 3621548.6705 | 2123663.3025 | 755863.13 | 952387.5438 | 16825513.2732
39 | 8121412.8272 | 1073113.2015 | 3526134.181 | 2062903.4436 | 739178.1827 | 931364.5102 | 16454106.346
40 | 8614541.9572 | 1154431.0615 | 4042298.7257 | 2259204.5291 | 803523.8137 | 1012440.0052 | 17886440.0923
41 | 8872847.6932 | 1198073.4312 | 4296744.8048 | 2362028.9077 | 836484.7418 | 1053970.7747 | 18620150.3535
42 | 8880675.144 | 1199407.1679 | 4211992.1646 | 2365144.7997 | 832860.9638 | 1049404.8144 | 18539485.0544
43 | 9052878.968 | 1228916.6373 | 4307469.1643 | 2433694.3854 | 851147.9578 | 1072446.4268 | 18946553.5395
44 | 9592972.7768 | 1323544.8201 | 4697473.1383 | 2648690.8123 | 913134.0774 | 1150548.9375 | 20326364.5623
45 | 9405114.0616 | 1290273.6357 | 4342125.6625 | 2573909.4468 | 880571.1403 | 1109519.6368 | 19601513.5837
46 | 8121412.8272 | 1073113.2015 | 3102786.7262 | 2062903.4436 | 718010.8099 | 904693.6205 | 15982920.6289
47 | 6438511.8152 | 815359.0597 | 1758335.717 | 1392987.0356 | 520259.6814 | 655527.1985 | 11580980.5074
48 | 5737955.3456 | 717070.8133 | 1306394.0934 | 1114114.8557 | 443776.7554 | 559158.7118 | 9878470.5753
49 | 5428771.208 | 675376.7088 | 1144253.4311 | 991037.1908 | 411971.9269 | 519084.6279 | 9170495.0936
50 | 5283963.4436 | 656203.8097 | 1047891.3244 | 933393.2197 | 396072.5899 | 499051.4632 | 8816575.8505
51 | 5233085.042 | 649521.1064 | 958389.8584 | 913139.9333 | 387706.797 | 488510.5642 | 8630353.3014
52 | 5248739.9384 | 651574.348 | 919078.2267 | 919371.7152 | 386938.2114 | 487542.1464 | 8613244.5861
53 | 5260481.1068 | 653116.0143 | 895552.5347 | 924045.55 | 386659.7603 | 487191.298 | 8607046.264
54 | 5530528.0112 | 688984.9317 | 1023264.9456 | 1031543.7634 | 413716.0826 | 521282.2641 | 9209319.9986
55 | 6062794.3796 | 761987.2808 | 1308403.432 | 1243424.3025 | 468830.4697 | 590726.3919 | 10436166.2565
56 | 6176292.3564 | 777949.4232 | 1455788.0561 | 1288604.712 | 484931.7274 | 611013.9765 | 10794580.2517
57 | 6618543.0848 | 841472.8857 | 1868208.0063 | 1464652.5112 | 539643.8244 | 679951.2187 | 12012471.5312
58 | 7135154.5568 | 918350.0814 | 2385498.8975 | 1670301.2684 | 605465.2402 | 762886.2027 | 13477656.2471
59 | 7698730.7128 | 1005500.8275 | 3033615.0554 | 1894645.3691 | 681624.5982 | 858846.9938 | 15172963.5569
60 | 7992259.9592 | 1052249.3142 | 3389738.8834 | 2011491.2543 | 722286.9706 | 910081.5829 | 16078107.9646
61 | 8309271.5424 | 1103782.0041 | 3819430.8399 | 2137684.8091 | 768508.4598 | 968320.6593 | 17106998.3147
62 | 8215342.1848 | 1088399.9983 | 3841946.5228 | 2100294.1263 | 762299.1416 | 960496.9184 | 16968778.8922
63 | 8493216.5348 | 1134180.8914 | 4177770.629 | 2210908.2297 | 800803.8142 | 1009012.8059 | 17825892.905
64 | 8935467.2684 | 1208761.8327 | 4681313.4275 | 2386956.0309 | 860624.928 | 1084387.4092 | 19157510.8967
65 | 9225082.792 | 1258746.1151 | 4974981.7525 | 2502243.9711 | 898052.7315 | 1131546.4417 | 19990653.804
66 | 9178118.1132 | 1250579.0667 | 4810664.4748 | 2483548.6298 | 886145.5142 | 1116543.3479 | 19725599.1466
67 | 9522525.7612 | 1311023.4972 | 5057679.4198 | 2620647.8012 | 925593.824 | 1166248.2182 | 20603718.5216
68 | 9636023.7328 | 1331223.1044 | 4986421.7826 | 2665828.2087 | 930974.8414 | 1173028.3002 | 20723499.9701
69 | 9397286.616 | 1288895.6012 | 4587625.7669 | 2570793.5569 | 892230.077 | 1124209.8971 | 19861041.515
70 | 8324926.4336 | 1106354.9279 | 3509658.9141 | 2143916.5889 | 754242.8432 | 950345.9825 | 16789445.6902
71 | 6215429.5844 | 783485.8417 | 1715829.0585 | 1304184.1615 | 500946.4323 | 631192.5047 | 11151067.5831
72 | 5708890.268 | 713107.3991 | 1320772.8397 | 1102544.8512 | 442265.7679 | 557254.8676 | 9844835.9935
73 | 5373979.0836 | 668095.4864 | 1099927.3742 | 969225.9595 | 405561.3952 | 511007.3579 | 9027796.6569
74 | 5268308.5524 | 654144.6182 | 1053566.561 | 927161.4399 | 395159.0586 | 497900.4138 | 8796240.6439
75 | 5221343.8736 | 647982.9113 | 1014970.3897 | 908466.0985 | 389638.1637 | 490944.0862 | 8673345.523
76 | 5193947.8088 | 644399.574 | 970390.0251 | 897560.4818 | 385314.8945 | 485496.7671 | 8577109.5512
77 | 5276135.998 | 655173.8834 | 961701.3486 | 930277.3298 | 391164.428 | 492867.1793 | 8707320.1671
78 | 5463994.7184 | 680074.6028 | 1031576.8817 | 1005058.6974 | 409035.245 | 515384.4087 | 9105124.5539
79 | 5984519.9132 | 751059.9006 | 1323628.895 | 1212265.3995 | 463573.7054 | 584102.8688 | 10319150.6826
80 | 6066708.1024 | 762535.3853 | 1447391.0974 | 1244982.2474 | 476080.8416 | 599861.8605 | 10597559.5346
81 | 6618543.0848 | 841472.8857 | 1934826.9943 | 1464652.5112 | 542974.7738 | 684148.215 | 12086618.4647
82 | 7127327.1112 | 917163.7874 | 2508575.8358 | 1667185.3786 | 611012.6056 | 769875.8831 | 13601140.6017
83 | 7471734.7592 | 969986.2012 | 2956071.4457 | 1804284.55 | 660103.8478 | 831730.8482 | 14693911.6522
84 | 8050965.8064 | 1061710.5844 | 3687951.4231 | 2034860.4305 | 741774.4122 | 934635.7594 | 16511898.4159
85 | 7910071.77 | 1039066.0165 | 3698338.0546 | 1978774.4064 | 731312.5124 | 921453.7656 | 16279016.5253
86 | 7671334.648 | 1001185.0744 | 3597601.4474 | 1883739.7525 | 707693.0461 | 891693.2381 | 15753247.2064
87 | 7878761.9824 | 1034062.9817 | 3904250.3133 | 1966310.8447 | 739169.3061 | 931353.3257 | 16453908.7539
88 | 8187946.12 | 1083931.5139 | 4168929.1833 | 2089388.5097 | 776509.7663 | 978402.3056 | 17285107.3988
89 | 8818055.5688 | 1188755.7922 | 4855081.0092 | 2340217.6764 | 860105.5023 | 1083732.9329 | 19145948.4819
90 | 8544094.9416 | 1142653.5595 | 4428838.9876 | 2231161.5181 | 817337.4503 | 1029845.1874 | 18193931.6446
91 | 8865020.2476 | 1196740.3565 | 4632423.6018 | 2358913.0178 | 852654.8612 | 1074345.1251 | 18980097.21
92 | 8583232.1696 | 1149190.0039 | 4131542.6234 | 2246740.9675 | 805535.2882 | 1014974.4632 | 17931215.5158
93 | 7456079.868 | 967557.4134 | 2890248.8091 | 1798052.7703 | 655596.943 | 826052.1482 | 14593587.9521
94 | 7033397.7536 | 902979.8292 | 2428427.6841 | 1629794.6958 | 599729.9981 | 755659.7977 | 13349989.7585
95 | 6164551.1828 | 776291.7201 | 1732981.5268 | 1283930.8751 | 497887.7652 | 627338.5842 | 11082981.6544
96 | 5702731.8352 | 712268.7844 | 1403188.7728 | 1100093.3492 | 445914.1371 | 561851.8127 | 9926048.6914
97 | 5679249.4984 | 709074.8705 | 1349864.6788 | 1090745.6795 | 441446.7364 | 556222.8878 | 9826604.3515
98 | 5542269.1848 | 690562.302 | 1237009.7069 | 1036217.6003 | 425302.9397 | 535881.704 | 9467243.4379
99 | 5514873.12 | 686884.0862 | 1183008.1158 | 1025311.9837 | 420503.8653 | 529834.8703 | 9360416.0413
100 | 5350496.7416 | 664984.8798 | 1032127.0706 | 959878.2878 | 400374.349 | 504471.6797 | 8912333.0085
101 | 5323100.6768 | 661363.3596 | 987719.6093 | 948972.6712 | 396057.8158 | 499032.848 | 8816246.9807
102 | 5432684.9308 | 675898.0358 | 1033768.2211 | 992595.1357 | 406747.3162 | 512501.6184 | 9054195.258
103 | 5781006.3016 | 722958.1419 | 1223468.2642 | 1131252.2522 | 442934.248 | 558097.1525 | 9859716.3604
104 | 5898418.0012 | 739116.1482 | 1369042.3658 | 1177990.6066 | 459228.3561 | 578627.7287 | 10222423.2066
105 | 6125413.9496 | 770776.7891 | 1648480.6946 | 1268351.4237 | 490651.1428 | 618220.44 | 10921894.4397
106 | 6806401.8 | 869094.9975 | 2295249.2615 | 1539433.8767 | 575508.9968 | 725141.3359 | 12810830.2684
107 | 6970778.1784 | 893576.7505 | 2591346.1741 | 1604867.5726 | 603028.4338 | 759815.8266 | 13423412.9359
108 | 7706558.1584 | 1006735.3873 | 3366981.6681 | 1897761.259 | 698901.8236 | 880616.2978 | 15557554.5942
109 | 7397374.0156 | 958473.0117 | 3209235.3942 | 1774683.592 | 666988.3007 | 840405.2589 | 14847159.5731
110 | 7186032.9584 | 926077.1094 | 3171202.531 | 1690554.5548 | 648693.3577 | 817353.6307 | 14439914.142
111 | 7111672.22 | 914793.1829 | 3117575.5496 | 1660953.5988 | 640249.7276 | 806714.6567 | 14251958.9356
112 | 7142982.0024 | 919537.0366 | 3143987.8625 | 1673417.1583 | 643996.203 | 811435.2158 | 14335355.4786
113 | 6982519.352 | 895336.6051 | 2943542.0707 | 1609541.4095 | 621546.9719 | 783149.1845 | 13835635.5936
114 | 7060793.8132 | 907106.9816 | 2921347.8253 | 1640700.3104 | 626497.4465 | 789386.7826 | 13945833.1597
115 | 6849452.756 | 875478.7026 | 2656514.6888 | 1556571.2732 | 596900.871 | 752095.0975 | 13287013.3891
116 | 7166464.3444 | 923101.87 | 2832876.2123 | 1682764.8301 | 630260.3628 | 794128.0572 | 14029595.6768
117 | 6970778.1784 | 893576.7505 | 2525947.841 | 1604867.5726 | 599758.5171 | 755695.7316 | 13350624.5913
118 | 6610715.6392 | 840330.2292 | 2135467.2035 | 1461536.6213 | 552402.4847 | 696027.1307 | 12296479.3085
119 | 5867108.2136 | 734792.8005 | 1562926.8698 | 1165527.045 | 466517.7465 | 587812.3605 | 10384685.036
120 | 5718911.9264 | 714472.9573 | 1443978.5976 | 1106534.1966 | 449194.8839 | 565985.5537 | 9999078.1154
121 | 5377892.8064 | 668614.4993 | 1174847.2446 | 970783.9045 | 409606.9227 | 516104.7227 | 9117850.1002
122 | 5186120.3632 | 643377.2512 | 1005440.9912 | 894444.592 | 386469.1599 | 486951.1414 | 8602803.4988
123 | 5146983.13 | 638275.554 | 951134.113 | 878865.1405 | 380762.8969 | 479761.2501 | 8475782.0844
124 | 5131328.2388 | 636239.5036 | 915722.0973 | 872633.3607 | 377796.16 | 476023.1616 | 8409742.522
125 | 5111759.6196 | 633698.159 | 881578.2959 | 864843.6339 | 374593.9854 | 471988.4216 | 8338462.1156
126 | 5178292.9176 | 642355.5895 | 905158.0685 | 891328.7021 | 380856.7639 | 479879.5225 | 8477871.5641
127 | 5882763.11 | 736953.1524 | 1290379.625 | 1171758.8269 | 454092.7357 | 572156.847 | 10108104.297
128 | 6610715.6392 | 840330.2292 | 1846520.0042 | 1461536.6213 | 537955.1247 | 677823.4571 | 11974881.0757
129 | 6927727.2224 | 887136.6803 | 2243099.0271 | 1587730.1762 | 582284.6553 | 733678.6657 | 12961656.427
130 | 7131240.834 | 917756.8518 | 2594410.8146 | 1668743.3235 | 615607.5912 | 775665.5649 | 13703424.9799
131 | 7205601.5776 | 929056.482 | 2777054.6122 | 1698344.2815 | 630502.8477 | 794433.5881 | 14034993.389
132 | 7088189.878 | 911242.2342 | 2830836.5591 | 1651605.9271 | 624093.7299 | 786358.0997 | 13892326.428
133 | 7385632.8472 | 956660.5947 | 3189640.5036 | 1770009.7572 | 665097.1851 | 838022.4533 | 14805063.341
134 | 7526526.8888 | 978507.7873 | 3454029.2418 | 1826095.7834 | 689257.9851 | 868465.0612 | 15342882.7475
135 | 7557836.6712 | 983391.8099 | 3449068.7608 | 1838559.3429 | 691442.8292 | 871217.9648 | 15391517.3789
136 | 7178205.5128 | 924886.5178 | 3001105.4543 | 1687438.6649 | 639581.8075 | 805873.0774 | 14237091.0348
137 | 7131240.834 | 917756.8518 | 2917258.1437 | 1668743.3235 | 631749.9577 | 796004.9466 | 14062754.0573
138 | 7107758.4972 | 914200.945 | 2864454.5557 | 1659395.6539 | 627290.4826 | 790386.0081 | 13963486.1424
139 | 6951209.5644 | 890646.9669 | 2644788.4118 | 1597077.8479 | 604186.1395 | 761274.5358 | 13449183.4663
140 | 6955123.2872 | 891232.593 | 2517585.0018 | 1598635.7928 | 598128.8337 | 753642.3305 | 13314347.8391
141 | 6649852.8724 | 846050.1243 | 2161272.9266 | 1477116.0728 | 556714.5998 | 701460.3958 | 12392466.9917
142 | 6352409.9032 | 802993.4782 | 1857846.724 | 1358712.2427 | 518598.1174 | 653433.6279 | 11543994.0935
143 | 5941468.9572 | 745078.0242 | 1546889.2989 | 1195128.0031 | 471428.2142 | 593999.5498 | 10493992.0473
144 | 5655767.1564 | 705886.9065 | 1299909.4295 | 1081398.0078 | 437148.075 | 550806.5745 | 9730916.1497
145 | 5436598.6536 | 676419.528 | 1128555.4829 | 994153.0807 | 411786.3373 | 518850.7849 | 9166363.8674
146 | 5338755.5732 | 663431.8083 | 1033761.8022 | 955204.453 | 399557.6818 | 503442.6791 | 8894153.9976
147 | 5307445.7856 | 659297.5564 | 996406.8457 | 942740.8914 | 395294.554 | 498071.138 | 8799256.771
148 | 5303532.0628 | 658781.5189 | 970798.9711 | 941182.9464 | 393714.775 | 496080.6165 | 8764090.8906
149 | 5303532.0628 | 658781.5189 | 958346.9361 | 941182.9464 | 393092.1732 | 495296.1382 | 8750231.7757
150 | 5307445.7856 | 659297.5564 | 952921.8953 | 942740.8914 | 393120.3064 | 495331.5861 | 8750858.0212
151 | 5812316.0892 | 727252.3979 | 1200980.7285 | 1143715.8138 | 444213.2515 | 559708.6968 | 9888186.9777
152 | 6524613.7272 | 827804.6434 | 1701988.753 | 1427261.8285 | 524083.4476 | 660345.144 | 11666097.5437
153 | 6810315.528 | 869674.5086 | 2030537.5234 | 1540991.8237 | 562575.9692 | 708845.7212 | 12522941.0741
154 | 7072534.9868 | 908878.2414 | 2306115.2885 | 1645374.1473 | 596645.1332 | 751772.8678 | 13281320.6651
155 | 7002087.966 | 898273.0005 | 2337129.8639 | 1617331.1342 | 592741.0982 | 746853.7838 | 13194416.8466
156 | 7080362.4324 | 910059.9072 | 2495780.0906 | 1648490.0372 | 606734.6234 | 764485.6254 | 13505912.7162
157 | 7413028.912 | 960891.8828 | 2881024.927 | 1780915.3738 | 651793.0548 | 821259.249 | 14508913.3994
158 | 7565664.1168 | 984614.4685 | 3114048.7581 | 1841675.2328 | 675300.1288 | 850878.1623 | 15032180.8674
159 | 7690903.262 | 1004266.9281 | 3296498.4902 | 1891529.4772 | 694159.9079 | 874641.4839 | 15451999.5493
160 | 7632197.4148 | 995033.7631 | 3249282.8893 | 1868160.301 | 687233.7184 | 865914.4852 | 15297822.5718
161 | 7988346.2312 | 1051619.8845 | 3566155.1819 | 2009933.3073 | 730802.7302 | 920811.4401 | 16267668.7752
162 | 7757436.56 | 1014776.1424 | 3297507.299 | 1918014.5453 | 699386.7273 | 881227.2764 | 15568348.5505
163 | 7925726.6612 | 1041571.5005 | 3410061.2607 | 1985006.1861 | 718118.2804 | 904829.0333 | 15985312.9223
164 | 7295617.2124 | 942814.8182 | 2726939.399 | 1734177.0194 | 634977.4224 | 800071.5523 | 14134597.4237
165 | 8755435.9988 | 1178146.7325 | 3893415.9298 | 2315290.5553 | 807114.4608 | 1016964.2206 | 17966367.8978
166 | 7800487.516 | 1021601.6772 | 2946232.4108 | 1935151.9418 | 685173.6773 | 863318.8334 | 15251966.0564
167 | 6117586.504 | 769675.7865 | 1614453.6092 | 1265235.5338 | 488347.5717 | 615317.9403 | 10870616.9454
168 | 5816229.812 | 727789.9236 | 1355736.1516 | 1145273.7587 | 452251.4823 | 569836.8677 | 10067117.996

## DC_load
Hour | Server | Power_loss | Chiller | CRAH | Pumps | Miscellenous | Total (MW) | Server utilization rate | Non-Server | PUE (Total/IT) | Data center metrics: |  |  |  | Utilization | Power (W) | Hour-year | Hour-week | Total (MWh) | Server | Useful
1 | 5.1352 | 0.63675 | 0.86957 | 0.87419 | 0.37579 | 0.47349 | 8.365 | 6.447% | 3.2298 | 1.6289 | Minimum server power | 120 | W |  | 0% | 120 | 1 | 1 | 8.365 | 5.1352 | 0.33524
2 | 5.0844 | 0.63015 | 0.83122 | 0.85394 | 0.36998 | 0.46618 | 8.2358 | 5.469% | 3.1515 | 1.6198 | Maximum server power | 250 | W |  | 10% | 133 | 2 | 2 | 8.2358 | 5.0844 | 0.28436
3 | 5.0804 | 0.62964 | 0.82201 | 0.85238 | 0.36922 | 0.46522 | 8.2189 | 5.393% | 3.1385 | 1.6178 | Utilization slope | 130 |  |  | 20% | 146 | 3 | 3 | 8.2189 | 5.0804 | 0.28045
4 | 5.1431 | 0.63777 | 0.85522 | 0.87731 | 0.37567 | 0.47334 | 8.3624 | 6.597% | 3.2193 | 1.626 | Dynamic range | 0.48 |  |  | 30% | 159 | 4 | 4 | 8.3624 | 5.1431 | 0.34307
5 | 5.1509 | 0.63878 | 0.86012 | 0.88042 | 0.37651 | 0.4744 | 8.3811 | 6.748% | 3.2302 | 1.6271 | Number of servers | 40000 |  |  | 40% | 172 | 5 | 5 | 8.3811 | 5.1509 | 0.3509
6 | 5.3505 | 0.66498 | 0.96291 | 0.95988 | 0.39691 | 0.50011 | 8.8353 | 10.59% | 3.4848 | 1.6513 | Average server wattage | 171.6861 | W |  | 50% | 185 | 6 | 6 | 8.8353 | 5.3505 | 0.5505
7 | 5.6871 | 0.71014 | 1.1278 | 1.0939 | 0.43094 | 0.54299 | 9.5928 | 17.06% | 3.9057 | 1.6868 | Average utilization rate | 39.76% |  |  | 60% | 198 | 7 | 7 | 9.5928 | 5.6871 | 0.88708
8 | 6.0002 | 0.75324 | 1.335 | 1.2185 | 0.46534 | 0.58633 | 10.3585 | 23.08% | 4.3584 | 1.7264 | IT peak load | 10 | MW |  | 70% | 211 | 8 | 8 | 10.3585 | 6.0002 | 1.2002
9 | 5.9884 | 0.7516 | 1.416 | 1.2138 | 0.46849 | 0.5903 | 10.4287 | 22.85% | 4.4402 | 1.7415 | Total peak load | 20.7235 | MW |  | 80% | 224 | 9 | 9 | 10.4287 | 5.9884 | 1.1884
10 | 6.6968 | 0.85294 | 1.9294 | 1.4958 | 0.54875 | 0.69142 | 12.2151 | 36.48% | 5.5183 | 1.824 | Peak server power | 242.1726 | W |  | 90% | 237 | 10 | 10 | 12.2151 | 6.6968 | 1.8968
11 | 7.6674 | 1.0006 | 2.7351 | 1.8822 | 0.66426 | 0.83697 | 14.7865 | 55.14% | 7.1191 | 1.9285 | Lowest server power | 127.0112 | W |  | 100% | 250 | 11 | 11 | 14.7865 | 7.6674 | 2.8674
12 | 8.1175 | 1.0725 | 3.1921 | 2.0613 | 0.72217 | 0.90994 | 16.0756 | 63.8% | 7.9581 | 1.9804 | Total annual electricity use | 114234.4017 | MWh |  |  |  | 12 | 12 | 16.0756 | 8.1175 | 3.3175
13 | 8.2936 | 1.1012 | 3.4458 | 2.1315 | 0.74861 | 0.94324 | 16.664 | 67.18% | 8.3703 | 2.0093 | Annual average PUE | 1.8987 |  |  |  |  | 13 | 13 | 16.664 | 8.2936 | 3.4936
14 | 8.1919 | 1.0846 | 3.3822 | 2.0909 | 0.73748 | 0.92923 | 16.4163 | 65.23% | 8.2245 | 2.004 | [6 empty] | 14 | 14 | 16.4163 | 8.1919 | 3.3919
15 | 8.1488 | 1.0776 | 3.3926 | 2.0738 | 0.73464 | 0.92565 | 16.3531 | 64.4% | 8.2043 | 2.0068 |  | Assumptions of the past: |  |  |  |  | 15 | 15 | 16.3531 | 8.1488 | 3.3488
16 | 8.7006 | 1.1689 | 3.947 | 2.2935 | 0.8055 | 1.0149 | 17.9305 | 75.01% | 9.2298 | 2.0608 |  |  | PUE | DR |  |  | 16 | 16 | 17.9305 | 8.7006 | 3.9006
17 | 9.319 | 1.2752 | 4.5346 | 2.5396 | 0.88342 | 1.1131 | 19.6649 | 86.9% | 10.3459 | 2.1102 |  | 2012 | 1.59 | 0.25 |  |  | 17 | 17 | 19.6649 | 9.319 | 4.519
18 | 9.2055 | 1.2553 | 4.3069 | 2.4945 | 0.86311 | 1.0875 | 19.2128 | 84.72% | 10.0073 | 2.0871 |  | 2013 | 1.5486 | 0.23 |  |  | 18 | 18 | 19.2128 | 9.2055 | 4.4055
19 | 9.4521 | 1.2986 | 4.4882 | 2.5926 | 0.89157 | 1.1234 | 19.8464 | 89.46% | 10.3943 | 2.0997 |  | 2014 | 1.5071 | 0.21 |  |  | 19 | 19 | 19.8464 | 9.4521 | 4.6521
20 | 9.4208 | 1.293 | 4.3098 | 2.5801 | 0.88019 | 1.109 | 19.593 | 88.86% | 10.1722 | 2.0798 |  | 2015 | 1.4657 | 0.19 |  |  | 20 | 20 | 19.593 | 9.4208 | 4.6208
21 | 9.6869 | 1.3403 | 4.4562 | 2.6861 | 0.90848 | 1.1447 | 20.2227 | 93.98% | 10.5358 | 2.0876 |  | 2016 | 1.4243 | 0.17 |  |  | 21 | 21 | 20.2227 | 9.6869 | 4.8869
22 | 7.8396 | 1.0278 | 2.7622 | 1.9507 | 0.67902 | 0.85556 | 15.1149 | 58.45% | 7.2753 | 1.928 |  | 2017 | 1.3829 | 0.15 |  |  | 22 | 22 | 15.1149 | 7.8396 | 3.0396
23 | 6.0784 | 0.76418 | 1.5037 | 1.2497 | 0.4798 | 0.60455 | 10.6803 | 24.59% | 4.6019 | 1.7571 |  | 2018 | 1.3414 | 0.13 |  |  | 23 | 23 | 10.6803 | 6.0784 | 1.2784
24 | 5.2981 | 0.65806 | 1.0244 | 0.93901 | 0.39598 | 0.49893 | 8.8145 | 9.579% | 3.5164 | 1.6637 |  | 2019 | 1.3 | 0.11 |  |  | 24 | 24 | 8.8145 | 5.2981 | 0.49808
25 | 5.2527 | 0.65209 | 0.97816 | 0.92093 | 0.39019 | 0.49164 | 8.6857 | 8.705% | 3.433 | 1.6536 | PUE: Uptime datacenter industry survey (2012/2013) + CA colo list PUE (2019) | [5 empty] | 25 | 25 | 8.6857 | 5.2527 | 0.45265
26 | 5.2018 | 0.64542 | 0.94453 | 0.90068 | 0.38462 | 0.48462 | 8.5616 | 7.726% | 3.3599 | 1.6459 | DR: Barroso 2019 Fig 5.8 + Jiang 2017 Fig 10 + Malla 2020 Fig 13 | [5 empty] | 26 | 26 | 8.5616 | 5.2018 | 0.40178
27 | 5.1548 | 0.63929 | 0.86912 | 0.88198 | 0.37726 | 0.47535 | 8.3978 | 6.823% | 3.243 | 1.6291 | *Bold are values from references, others are interpolated | [5 empty] | 27 | 27 | 8.3978 | 5.1548 | 0.35481
28 | 5.1939 | 0.6444 | 0.86592 | 0.89756 | 0.38009 | 0.47891 | 8.4608 | 7.576% | 3.2669 | 1.629 | [6 empty] | 28 | 28 | 8.4608 | 5.1939 | 0.39395
29 | 5.3074 | 0.6593 | 0.89707 | 0.94274 | 0.39033 | 0.49181 | 8.6887 | 9.759% | 3.3812 | 1.6371 | Assumption of server max utilization rate: |  |  | 65% |  |  | 29 | 29 | 8.6887 | 5.3074 | 0.50745
30 | 5.4209 | 0.67433 | 0.9454 | 0.98792 | 0.40143 | 0.5058 | 8.9358 | 11.94% | 3.5149 | 1.6484 | [6 empty] | 30 | 30 | 8.9358 | 5.4209 | 0.62094
31 | 5.8162 | 0.72779 | 1.1547 | 1.1453 | 0.4422 | 0.55717 | 9.8433 | 19.54% | 4.0271 | 1.6924 | [6 empty] | 31 | 31 | 9.8433 | 5.8162 | 1.0162
32 | 5.9806 | 0.75052 | 1.3053 | 1.2107 | 0.46236 | 0.58257 | 10.2921 | 22.7% | 4.3115 | 1.7209 | [6 empty] | 32 | 32 | 10.2921 | 5.9806 | 1.1806
33 | 6.2898 | 0.79405 | 1.5775 | 1.3338 | 0.49976 | 0.62969 | 11.1246 | 28.65% | 4.8348 | 1.7687 | [6 empty] | 33 | 33 | 11.1246 | 6.2898 | 1.4898
34 | 6.7086 | 0.85466 | 1.9861 | 1.5005 | 0.55249 | 0.69614 | 12.2985 | 36.7% | 5.5899 | 1.8333 | [6 empty] | 34 | 34 | 12.2985 | 6.7086 | 1.9086
35 | 7.7222 | 1.0092 | 2.8987 | 1.904 | 0.67671 | 0.85265 | 15.0635 | 56.2% | 7.3413 | 1.9507 | [6 empty] | 35 | 35 | 15.0635 | 7.7222 | 2.9222
36 | 8.2036 | 1.0865 | 3.4043 | 2.0956 | 0.7395 | 0.93177 | 16.4613 | 65.45% | 8.2577 | 2.0066 | [6 empty] | 36 | 36 | 16.4613 | 8.2036 | 3.4036
37 | 8.2388 | 1.0922 | 3.5309 | 2.1096 | 0.74858 | 0.94321 | 16.6634 | 66.13% | 8.4246 | 2.0225 | [6 empty] | 37 | 37 | 16.6634 | 8.2388 | 3.4388
38 | 8.274 | 1.098 | 3.6215 | 2.1237 | 0.75586 | 0.95239 | 16.8255 | 66.81% | 8.5515 | 2.0335 | [6 empty] | 38 | 38 | 16.8255 | 8.274 | 3.474
39 | 8.1214 | 1.0731 | 3.5261 | 2.0629 | 0.73918 | 0.93136 | 16.4541 | 63.87% | 8.3327 | 2.026 | [6 empty] | 39 | 39 | 16.4541 | 8.1214 | 3.3214
40 | 8.6145 | 1.1544 | 4.0423 | 2.2592 | 0.80352 | 1.0124 | 17.8864 | 73.36% | 9.2719 | 2.0763 | [6 empty] | 40 | 40 | 17.8864 | 8.6145 | 3.8145
41 | 8.8728 | 1.1981 | 4.2967 | 2.362 | 0.83648 | 1.054 | 18.6202 | 78.32% | 9.7473 | 2.0986 | [6 empty] | 41 | 41 | 18.6202 | 8.8728 | 4.0728
42 | 8.8807 | 1.1994 | 4.212 | 2.3651 | 0.83286 | 1.0494 | 18.5395 | 78.47% | 9.6588 | 2.0876 | [6 empty] | 42 | 42 | 18.5395 | 8.8807 | 4.0807
43 | 9.0529 | 1.2289 | 4.3075 | 2.4337 | 0.85115 | 1.0724 | 18.9466 | 81.79% | 9.8937 | 2.0929 | [6 empty] | 43 | 43 | 18.9466 | 9.0529 | 4.2529
44 | 9.593 | 1.3235 | 4.6975 | 2.6487 | 0.91313 | 1.1505 | 20.3264 | 92.17% | 10.7334 | 2.1189 | [6 empty] | 44 | 44 | 20.3264 | 9.593 | 4.793
45 | 9.4051 | 1.2903 | 4.3421 | 2.5739 | 0.88057 | 1.1095 | 19.6015 | 88.56% | 10.1964 | 2.0841 | [6 empty] | 45 | 45 | 19.6015 | 9.4051 | 4.6051
46 | 8.1214 | 1.0731 | 3.1028 | 2.0629 | 0.71801 | 0.90469 | 15.9829 | 63.87% | 7.8615 | 1.968 | [6 empty] | 46 | 46 | 15.9829 | 8.1214 | 3.3214
47 | 6.4385 | 0.81536 | 1.7583 | 1.393 | 0.52026 | 0.65553 | 11.581 | 31.51% | 5.1425 | 1.7987 | [6 empty] | 47 | 47 | 11.581 | 6.4385 | 1.6385
48 | 5.738 | 0.71707 | 1.3064 | 1.1141 | 0.44378 | 0.55916 | 9.8785 | 18.04% | 4.1405 | 1.7216 | [6 empty] | 48 | 48 | 9.8785 | 5.738 | 0.93796
49 | 5.4288 | 0.67538 | 1.1443 | 0.99104 | 0.41197 | 0.51908 | 9.1705 | 12.09% | 3.7417 | 1.6892 | [6 empty] | 49 | 49 | 9.1705 | 5.4288 | 0.62877
50 | 5.284 | 0.6562 | 1.0479 | 0.93339 | 0.39607 | 0.49905 | 8.8166 | 9.307% | 3.5326 | 1.6686 | [6 empty] | 50 | 50 | 8.8166 | 5.284 | 0.48396
51 | 5.2331 | 0.64952 | 0.95839 | 0.91314 | 0.38771 | 0.48851 | 8.6304 | 8.329% | 3.3973 | 1.6492 | [6 empty] | 51 | 51 | 8.6304 | 5.2331 | 0.43309
52 | 5.2487 | 0.65157 | 0.91908 | 0.91937 | 0.38694 | 0.48754 | 8.6132 | 8.63% | 3.3645 | 1.641 | [6 empty] | 52 | 52 | 8.6132 | 5.2487 | 0.44874
53 | 5.2605 | 0.65312 | 0.89555 | 0.92405 | 0.38666 | 0.48719 | 8.607 | 8.855% | 3.3466 | 1.6362 | [6 empty] | 53 | 53 | 8.607 | 5.2605 | 0.46048
54 | 5.5305 | 0.68898 | 1.0233 | 1.0315 | 0.41372 | 0.52128 | 9.2093 | 14.05% | 3.6788 | 1.6652 | [6 empty] | 54 | 54 | 9.2093 | 5.5305 | 0.73053
55 | 6.0628 | 0.76199 | 1.3084 | 1.2434 | 0.46883 | 0.59073 | 10.4362 | 24.28% | 4.3734 | 1.7213 | [6 empty] | 55 | 55 | 10.4362 | 6.0628 | 1.2628
56 | 6.1763 | 0.77795 | 1.4558 | 1.2886 | 0.48493 | 0.61101 | 10.7946 | 26.47% | 4.6183 | 1.7477 | [6 empty] | 56 | 56 | 10.7946 | 6.1763 | 1.3763
57 | 6.6185 | 0.84147 | 1.8682 | 1.4647 | 0.53964 | 0.67995 | 12.0125 | 34.97% | 5.3939 | 1.815 | [6 empty] | 57 | 57 | 12.0125 | 6.6185 | 1.8185
58 | 7.1352 | 0.91835 | 2.3855 | 1.6703 | 0.60547 | 0.76289 | 13.4777 | 44.91% | 6.3425 | 1.8889 | [6 empty] | 58 | 58 | 13.4777 | 7.1352 | 2.3352
59 | 7.6987 | 1.0055 | 3.0336 | 1.8946 | 0.68162 | 0.85885 | 15.173 | 55.74% | 7.4742 | 1.9708 | [6 empty] | 59 | 59 | 15.173 | 7.6987 | 2.8987
60 | 7.9923 | 1.0522 | 3.3897 | 2.0115 | 0.72229 | 0.91008 | 16.0781 | 61.39% | 8.0858 | 2.0117 | [6 empty] | 60 | 60 | 16.0781 | 7.9923 | 3.1923
61 | 8.3093 | 1.1038 | 3.8194 | 2.1377 | 0.76851 | 0.96832 | 17.107 | 67.49% | 8.7977 | 2.0588 | [6 empty] | 61 | 61 | 17.107 | 8.3093 | 3.5093
62 | 8.2153 | 1.0884 | 3.8419 | 2.1003 | 0.7623 | 0.9605 | 16.9688 | 65.68% | 8.7534 | 2.0655 | [6 empty] | 62 | 62 | 16.9688 | 8.2153 | 3.4153
63 | 8.4932 | 1.1342 | 4.1778 | 2.2109 | 0.8008 | 1.009 | 17.8259 | 71.02% | 9.3327 | 2.0988 | [6 empty] | 63 | 63 | 17.8259 | 8.4932 | 3.6932
64 | 8.9355 | 1.2088 | 4.6813 | 2.387 | 0.86062 | 1.0844 | 19.1575 | 79.53% | 10.222 | 2.144 | [6 empty] | 64 | 64 | 19.1575 | 8.9355 | 4.1355
65 | 9.2251 | 1.2587 | 4.975 | 2.5022 | 0.89805 | 1.1315 | 19.9907 | 85.1% | 10.7656 | 2.167 | [6 empty] | 65 | 65 | 19.9907 | 9.2251 | 4.4251
66 | 9.1781 | 1.2506 | 4.8107 | 2.4835 | 0.88615 | 1.1165 | 19.7256 | 84.19% | 10.5475 | 2.1492 | [6 empty] | 66 | 66 | 19.7256 | 9.1781 | 4.3781
67 | 9.5225 | 1.311 | 5.0577 | 2.6206 | 0.92559 | 1.1662 | 20.6037 | 90.82% | 11.0812 | 2.1637 | [6 empty] | 67 | 67 | 20.6037 | 9.5225 | 4.7225
68 | 9.636 | 1.3312 | 4.9864 | 2.6658 | 0.93097 | 1.173 | 20.7235 | 93% | 11.0875 | 2.1506 | [6 empty] | 68 | 68 | 20.7235 | 9.636 | 4.836
69 | 9.3973 | 1.2889 | 4.5876 | 2.5708 | 0.89223 | 1.1242 | 19.861 | 88.41% | 10.4638 | 2.1135 | [6 empty] | 69 | 69 | 19.861 | 9.3973 | 4.5973
70 | 8.3249 | 1.1064 | 3.5097 | 2.1439 | 0.75424 | 0.95035 | 16.7894 | 67.79% | 8.4645 | 2.0168 | [6 empty] | 70 | 70 | 16.7894 | 8.3249 | 3.5249
71 | 6.2154 | 0.78349 | 1.7158 | 1.3042 | 0.50095 | 0.63119 | 11.1511 | 27.22% | 4.9356 | 1.7941 | [6 empty] | 71 | 71 | 11.1511 | 6.2154 | 1.4154
72 | 5.7089 | 0.71311 | 1.3208 | 1.1025 | 0.44227 | 0.55725 | 9.8448 | 17.48% | 4.1359 | 1.7245 | [6 empty] | 72 | 72 | 9.8448 | 5.7089 | 0.90889
73 | 5.374 | 0.6681 | 1.0999 | 0.96923 | 0.40556 | 0.51101 | 9.0278 | 11.04% | 3.6538 | 1.6799 | [6 empty] | 73 | 73 | 9.0278 | 5.374 | 0.57398
74 | 5.2683 | 0.65414 | 1.0536 | 0.92716 | 0.39516 | 0.4979 | 8.7962 | 9.006% | 3.5279 | 1.6697 | [6 empty] | 74 | 74 | 8.7962 | 5.2683 | 0.46831
75 | 5.2213 | 0.64798 | 1.015 | 0.90847 | 0.38964 | 0.49094 | 8.6733 | 8.103% | 3.452 | 1.6611 | [6 empty] | 75 | 75 | 8.6733 | 5.2213 | 0.42134
76 | 5.1939 | 0.6444 | 0.97039 | 0.89756 | 0.38531 | 0.4855 | 8.5771 | 7.576% | 3.3832 | 1.6514 | [6 empty] | 76 | 76 | 8.5771 | 5.1939 | 0.39395
77 | 5.2761 | 0.65517 | 0.9617 | 0.93028 | 0.39116 | 0.49287 | 8.7073 | 9.156% | 3.4312 | 1.6503 | [6 empty] | 77 | 77 | 8.7073 | 5.2761 | 0.47614
78 | 5.464 | 0.68007 | 1.0316 | 1.0051 | 0.40904 | 0.51538 | 9.1051 | 12.77% | 3.6411 | 1.6664 | [6 empty] | 78 | 78 | 9.1051 | 5.464 | 0.66399
79 | 5.9845 | 0.75106 | 1.3236 | 1.2123 | 0.46357 | 0.5841 | 10.3192 | 22.78% | 4.3346 | 1.7243 | [6 empty] | 79 | 79 | 10.3192 | 5.9845 | 1.1845
80 | 6.0667 | 0.76254 | 1.4474 | 1.245 | 0.47608 | 0.59986 | 10.5976 | 24.36% | 4.5309 | 1.7468 | [6 empty] | 80 | 80 | 10.5976 | 6.0667 | 1.2667
81 | 6.6185 | 0.84147 | 1.9348 | 1.4647 | 0.54297 | 0.68415 | 12.0866 | 34.97% | 5.4681 | 1.8262 | [6 empty] | 81 | 81 | 12.0866 | 6.6185 | 1.8185
82 | 7.1273 | 0.91716 | 2.5086 | 1.6672 | 0.61101 | 0.76988 | 13.6011 | 44.76% | 6.4738 | 1.9083 | [6 empty] | 82 | 82 | 13.6011 | 7.1273 | 2.3273
83 | 7.4717 | 0.96999 | 2.9561 | 1.8043 | 0.6601 | 0.83173 | 14.6939 | 51.38% | 7.2222 | 1.9666 | [6 empty] | 83 | 83 | 14.6939 | 7.4717 | 2.6717
84 | 8.051 | 1.0617 | 3.688 | 2.0349 | 0.74177 | 0.93464 | 16.5119 | 62.52% | 8.4609 | 2.0509 | [6 empty] | 84 | 84 | 16.5119 | 8.051 | 3.251
85 | 7.9101 | 1.0391 | 3.6983 | 1.9788 | 0.73131 | 0.92145 | 16.279 | 59.81% | 8.3689 | 2.058 | [6 empty] | 85 | 85 | 16.279 | 7.9101 | 3.1101
86 | 7.6713 | 1.0012 | 3.5976 | 1.8837 | 0.70769 | 0.89169 | 15.7532 | 55.22% | 8.0819 | 2.0535 | [6 empty] | 86 | 86 | 15.7532 | 7.6713 | 2.8713
87 | 7.8788 | 1.0341 | 3.9043 | 1.9663 | 0.73917 | 0.93135 | 16.4539 | 59.21% | 8.5751 | 2.0884 | [6 empty] | 87 | 87 | 16.4539 | 7.8788 | 3.0788
88 | 8.1879 | 1.0839 | 4.1689 | 2.0894 | 0.77651 | 0.9784 | 17.2851 | 65.15% | 9.0972 | 2.111 | [6 empty] | 88 | 88 | 17.2851 | 8.1879 | 3.3879
89 | 8.8181 | 1.1888 | 4.8551 | 2.3402 | 0.86011 | 1.0837 | 19.1459 | 77.27% | 10.3279 | 2.1712 | [6 empty] | 89 | 89 | 19.1459 | 8.8181 | 4.0181
90 | 8.5441 | 1.1427 | 4.4288 | 2.2312 | 0.81734 | 1.0298 | 18.1939 | 72% | 9.6498 | 2.1294 | [6 empty] | 90 | 90 | 18.1939 | 8.5441 | 3.7441
91 | 8.865 | 1.1967 | 4.6324 | 2.3589 | 0.85265 | 1.0743 | 18.9801 | 78.17% | 10.1151 | 2.141 | [6 empty] | 91 | 91 | 18.9801 | 8.865 | 4.065
92 | 8.5832 | 1.1492 | 4.1315 | 2.2467 | 0.80554 | 1.015 | 17.9312 | 72.75% | 9.348 | 2.0891 | [6 empty] | 92 | 92 | 17.9312 | 8.5832 | 3.7832
93 | 7.4561 | 0.96756 | 2.8902 | 1.7981 | 0.6556 | 0.82605 | 14.5936 | 51.08% | 7.1375 | 1.9573 | [6 empty] | 93 | 93 | 14.5936 | 7.4561 | 2.6561
94 | 7.0334 | 0.90298 | 2.4284 | 1.6298 | 0.59973 | 0.75566 | 13.35 | 42.95% | 6.3166 | 1.8981 | [6 empty] | 94 | 94 | 13.35 | 7.0334 | 2.2334
95 | 6.1646 | 0.77629 | 1.733 | 1.2839 | 0.49789 | 0.62734 | 11.083 | 26.24% | 4.9184 | 1.7979 | [6 empty] | 95 | 95 | 11.083 | 6.1646 | 1.3646
96 | 5.7027 | 0.71227 | 1.4032 | 1.1001 | 0.44591 | 0.56185 | 9.926 | 17.36% | 4.2233 | 1.7406 | [6 empty] | 96 | 96 | 9.926 | 5.7027 | 0.90273
97 | 5.6792 | 0.70907 | 1.3499 | 1.0907 | 0.44145 | 0.55622 | 9.8266 | 16.91% | 4.1474 | 1.7303 | [6 empty] | 97 | 97 | 9.8266 | 5.6792 | 0.87925
98 | 5.5423 | 0.69056 | 1.237 | 1.0362 | 0.4253 | 0.53588 | 9.4672 | 14.27% | 3.925 | 1.7082 | [6 empty] | 98 | 98 | 9.4672 | 5.5423 | 0.74227
99 | 5.5149 | 0.68688 | 1.183 | 1.0253 | 0.4205 | 0.52983 | 9.3604 | 13.75% | 3.8455 | 1.6973 | [6 empty] | 99 | 99 | 9.3604 | 5.5149 | 0.71487
100 | 5.3505 | 0.66498 | 1.0321 | 0.95988 | 0.40037 | 0.50447 | 8.9123 | 10.59% | 3.5618 | 1.6657 | [6 empty] | 100 | 100 | 8.9123 | 5.3505 | 0.5505
101 | 5.3231 | 0.66136 | 0.98772 | 0.94897 | 0.39606 | 0.49903 | 8.8162 | 10.06% | 3.4931 | 1.6562 | [6 empty] | 101 | 101 | 8.8162 | 5.3231 | 0.5231
102 | 5.4327 | 0.6759 | 1.0338 | 0.9926 | 0.40675 | 0.5125 | 9.0542 | 12.17% | 3.6215 | 1.6666 | [6 empty] | 102 | 102 | 9.0542 | 5.4327 | 0.63268
103 | 5.781 | 0.72296 | 1.2235 | 1.1313 | 0.44293 | 0.5581 | 9.8597 | 18.87% | 4.0787 | 1.7055 | [6 empty] | 103 | 103 | 9.8597 | 5.781 | 0.98101
104 | 5.8984 | 0.73912 | 1.369 | 1.178 | 0.45923 | 0.57863 | 10.2224 | 21.12% | 4.324 | 1.7331 | [6 empty] | 104 | 104 | 10.2224 | 5.8984 | 1.0984
105 | 6.1254 | 0.77078 | 1.6485 | 1.2684 | 0.49065 | 0.61822 | 10.9219 | 25.49% | 4.7965 | 1.783 | [6 empty] | 105 | 105 | 10.9219 | 6.1254 | 1.3254
106 | 6.8064 | 0.86909 | 2.2952 | 1.5394 | 0.57551 | 0.72514 | 12.8108 | 38.58% | 6.0044 | 1.8822 | [6 empty] | 106 | 106 | 12.8108 | 6.8064 | 2.0064
107 | 6.9708 | 0.89358 | 2.5913 | 1.6049 | 0.60303 | 0.75982 | 13.4234 | 41.75% | 6.4526 | 1.9257 | [6 empty] | 107 | 107 | 13.4234 | 6.9708 | 2.1708
108 | 7.7066 | 1.0067 | 3.367 | 1.8978 | 0.6989 | 0.88062 | 15.5576 | 55.9% | 7.851 | 2.0187 | [6 empty] | 108 | 108 | 15.5576 | 7.7066 | 2.9066
109 | 7.3974 | 0.95847 | 3.2092 | 1.7747 | 0.66699 | 0.84041 | 14.8472 | 49.95% | 7.4498 | 2.0071 | [6 empty] | 109 | 109 | 14.8472 | 7.3974 | 2.5974
110 | 7.186 | 0.92608 | 3.1712 | 1.6906 | 0.64869 | 0.81735 | 14.4399 | 45.89% | 7.2539 | 2.0094 | [6 empty] | 110 | 110 | 14.4399 | 7.186 | 2.386
111 | 7.1117 | 0.91479 | 3.1176 | 1.661 | 0.64025 | 0.80671 | 14.252 | 44.46% | 7.1403 | 2.004 | [6 empty] | 111 | 111 | 14.252 | 7.1117 | 2.3117
112 | 7.143 | 0.91954 | 3.144 | 1.6734 | 0.644 | 0.81144 | 14.3354 | 45.06% | 7.1924 | 2.0069 | [6 empty] | 112 | 112 | 14.3354 | 7.143 | 2.343
113 | 6.9825 | 0.89534 | 2.9435 | 1.6095 | 0.62155 | 0.78315 | 13.8356 | 41.97% | 6.8531 | 1.9815 | [6 empty] | 113 | 113 | 13.8356 | 6.9825 | 2.1825
114 | 7.0608 | 0.90711 | 2.9213 | 1.6407 | 0.6265 | 0.78939 | 13.9458 | 43.48% | 6.885 | 1.9751 | [6 empty] | 114 | 114 | 13.9458 | 7.0608 | 2.2608
115 | 6.8495 | 0.87548 | 2.6565 | 1.5566 | 0.5969 | 0.7521 | 13.287 | 39.41% | 6.4376 | 1.9399 | [6 empty] | 115 | 115 | 13.287 | 6.8495 | 2.0495
116 | 7.1665 | 0.9231 | 2.8329 | 1.6828 | 0.63026 | 0.79413 | 14.0296 | 45.51% | 6.8631 | 1.9577 | [6 empty] | 116 | 116 | 14.0296 | 7.1665 | 2.3665
117 | 6.9708 | 0.89358 | 2.5259 | 1.6049 | 0.59976 | 0.7557 | 13.3506 | 41.75% | 6.3798 | 1.9152 | [6 empty] | 117 | 117 | 13.3506 | 6.9708 | 2.1708
118 | 6.6107 | 0.84033 | 2.1355 | 1.4615 | 0.5524 | 0.69603 | 12.2965 | 34.82% | 5.6858 | 1.8601 | [6 empty] | 118 | 118 | 12.2965 | 6.6107 | 1.8107
119 | 5.8671 | 0.73479 | 1.5629 | 1.1655 | 0.46652 | 0.58781 | 10.3847 | 20.52% | 4.5176 | 1.77 | [6 empty] | 119 | 119 | 10.3847 | 5.8671 | 1.0671
120 | 5.7189 | 0.71447 | 1.444 | 1.1065 | 0.44919 | 0.56599 | 9.9991 | 17.67% | 4.2802 | 1.7484 | [6 empty] | 120 | 120 | 9.9991 | 5.7189 | 0.91891
121 | 5.3779 | 0.66861 | 1.1748 | 0.97078 | 0.40961 | 0.5161 | 9.1179 | 11.11% | 3.74 | 1.6954 | [6 empty] | 121 | 121 | 9.1179 | 5.3779 | 0.57789
122 | 5.1861 | 0.64338 | 1.0054 | 0.89444 | 0.38647 | 0.48695 | 8.6028 | 7.425% | 3.4167 | 1.6588 | [6 empty] | 122 | 122 | 8.6028 | 5.1861 | 0.38612
123 | 5.147 | 0.63828 | 0.95113 | 0.87887 | 0.38076 | 0.47976 | 8.4758 | 6.673% | 3.3288 | 1.6467 | [6 empty] | 123 | 123 | 8.4758 | 5.147 | 0.34698
124 | 5.1313 | 0.63624 | 0.91572 | 0.87263 | 0.3778 | 0.47602 | 8.4097 | 6.372% | 3.2784 | 1.6389 | [6 empty] | 124 | 124 | 8.4097 | 5.1313 | 0.33133
125 | 5.1118 | 0.6337 | 0.88158 | 0.86484 | 0.37459 | 0.47199 | 8.3385 | 5.995% | 3.2267 | 1.6312 | [6 empty] | 125 | 125 | 8.3385 | 5.1118 | 0.31176
126 | 5.1783 | 0.64236 | 0.90516 | 0.89133 | 0.38086 | 0.47988 | 8.4779 | 7.275% | 3.2996 | 1.6372 | [6 empty] | 126 | 126 | 8.4779 | 5.1783 | 0.37829
127 | 5.8828 | 0.73695 | 1.2904 | 1.1718 | 0.45409 | 0.57216 | 10.1081 | 20.82% | 4.2253 | 1.7183 | [6 empty] | 127 | 127 | 10.1081 | 5.8828 | 1.0828
128 | 6.6107 | 0.84033 | 1.8465 | 1.4615 | 0.53796 | 0.67782 | 11.9749 | 34.82% | 5.3642 | 1.8114 | [6 empty] | 128 | 128 | 11.9749 | 6.6107 | 1.8107
129 | 6.9277 | 0.88714 | 2.2431 | 1.5877 | 0.58228 | 0.73368 | 12.9617 | 40.92% | 6.0339 | 1.871 | [6 empty] | 129 | 129 | 12.9617 | 6.9277 | 2.1277
130 | 7.1312 | 0.91776 | 2.5944 | 1.6687 | 0.61561 | 0.77567 | 13.7034 | 44.83% | 6.5722 | 1.9216 | [6 empty] | 130 | 130 | 13.7034 | 7.1312 | 2.3312
131 | 7.2056 | 0.92906 | 2.7771 | 1.6983 | 0.6305 | 0.79443 | 14.035 | 46.26% | 6.8294 | 1.9478 | [6 empty] | 131 | 131 | 14.035 | 7.2056 | 2.4056
132 | 7.0882 | 0.91124 | 2.8308 | 1.6516 | 0.62409 | 0.78636 | 13.8923 | 44% | 6.8041 | 1.9599 | [6 empty] | 132 | 132 | 13.8923 | 7.0882 | 2.2882
133 | 7.3856 | 0.95666 | 3.1896 | 1.77 | 0.6651 | 0.83802 | 14.8051 | 49.72% | 7.4194 | 2.0046 | [6 empty] | 133 | 133 | 14.8051 | 7.3856 | 2.5856
134 | 7.5265 | 0.97851 | 3.454 | 1.8261 | 0.68926 | 0.86847 | 15.3429 | 52.43% | 7.8164 | 2.0385 | [6 empty] | 134 | 134 | 15.3429 | 7.5265 | 2.7265
135 | 7.5578 | 0.98339 | 3.4491 | 1.8386 | 0.69144 | 0.87122 | 15.3915 | 53.04% | 7.8337 | 2.0365 | [6 empty] | 135 | 135 | 15.3915 | 7.5578 | 2.7578
136 | 7.1782 | 0.92489 | 3.0011 | 1.6874 | 0.63958 | 0.80587 | 14.2371 | 45.73% | 7.0589 | 1.9834 | [6 empty] | 136 | 136 | 14.2371 | 7.1782 | 2.3782
137 | 7.1312 | 0.91776 | 2.9173 | 1.6687 | 0.63175 | 0.796 | 14.0628 | 44.83% | 6.9315 | 1.972 | [6 empty] | 137 | 137 | 14.0628 | 7.1312 | 2.3312
138 | 7.1078 | 0.9142 | 2.8645 | 1.6594 | 0.62729 | 0.79039 | 13.9635 | 44.38% | 6.8557 | 1.9645 | [6 empty] | 138 | 138 | 13.9635 | 7.1078 | 2.3078
139 | 6.9512 | 0.89065 | 2.6448 | 1.5971 | 0.60419 | 0.76127 | 13.4492 | 41.37% | 6.498 | 1.9348 | [6 empty] | 139 | 139 | 13.4492 | 6.9512 | 2.1512
140 | 6.9551 | 0.89123 | 2.5176 | 1.5986 | 0.59813 | 0.75364 | 13.3143 | 41.44% | 6.3592 | 1.9143 | [6 empty] | 140 | 140 | 13.3143 | 6.9551 | 2.1551
141 | 6.6499 | 0.84605 | 2.1613 | 1.4771 | 0.55671 | 0.70146 | 12.3925 | 35.57% | 5.7426 | 1.8636 | [6 empty] | 141 | 141 | 12.3925 | 6.6499 | 1.8499
142 | 6.3524 | 0.80299 | 1.8578 | 1.3587 | 0.5186 | 0.65343 | 11.544 | 29.85% | 5.1916 | 1.8173 | [6 empty] | 142 | 142 | 11.544 | 6.3524 | 1.5524
143 | 5.9415 | 0.74508 | 1.5469 | 1.1951 | 0.47143 | 0.594 | 10.494 | 21.95% | 4.5525 | 1.7662 | [6 empty] | 143 | 143 | 10.494 | 5.9415 | 1.1415
144 | 5.6558 | 0.70589 | 1.2999 | 1.0814 | 0.43715 | 0.55081 | 9.7309 | 16.46% | 4.0751 | 1.7205 | [6 empty] | 144 | 144 | 9.7309 | 5.6558 | 0.85577
145 | 5.4366 | 0.67642 | 1.1286 | 0.99415 | 0.41179 | 0.51885 | 9.1664 | 12.24% | 3.7298 | 1.686 | [6 empty] | 145 | 145 | 9.1664 | 5.4366 | 0.6366
146 | 5.3388 | 0.66343 | 1.0338 | 0.9552 | 0.39956 | 0.50344 | 8.8942 | 10.36% | 3.5554 | 1.666 | [6 empty] | 146 | 146 | 8.8942 | 5.3388 | 0.53876
147 | 5.3074 | 0.6593 | 0.99641 | 0.94274 | 0.39529 | 0.49807 | 8.7993 | 9.759% | 3.4918 | 1.6579 | [6 empty] | 147 | 147 | 8.7993 | 5.3074 | 0.50745
148 | 5.3035 | 0.65878 | 0.9708 | 0.94118 | 0.39371 | 0.49608 | 8.7641 | 9.683% | 3.4606 | 1.6525 | [6 empty] | 148 | 148 | 8.7641 | 5.3035 | 0.50353
149 | 5.3035 | 0.65878 | 0.95835 | 0.94118 | 0.39309 | 0.4953 | 8.7502 | 9.683% | 3.4467 | 1.6499 | [6 empty] | 149 | 149 | 8.7502 | 5.3035 | 0.50353
150 | 5.3074 | 0.6593 | 0.95292 | 0.94274 | 0.39312 | 0.49533 | 8.7509 | 9.759% | 3.4434 | 1.6488 | [6 empty] | 150 | 150 | 8.7509 | 5.3074 | 0.50745
151 | 5.8123 | 0.72725 | 1.201 | 1.1437 | 0.44421 | 0.55971 | 9.8882 | 19.47% | 4.0759 | 1.7012 | [6 empty] | 151 | 151 | 9.8882 | 5.8123 | 1.0123
152 | 6.5246 | 0.8278 | 1.702 | 1.4273 | 0.52408 | 0.66035 | 11.6661 | 33.17% | 5.1415 | 1.788 | [6 empty] | 152 | 152 | 11.6661 | 6.5246 | 1.7246
153 | 6.8103 | 0.86967 | 2.0305 | 1.541 | 0.56258 | 0.70885 | 12.5229 | 38.66% | 5.7126 | 1.8388 | [6 empty] | 153 | 153 | 12.5229 | 6.8103 | 2.0103
154 | 7.0725 | 0.90888 | 2.3061 | 1.6454 | 0.59665 | 0.75177 | 13.2813 | 43.7% | 6.2088 | 1.8779 | [6 empty] | 154 | 154 | 13.2813 | 7.0725 | 2.2725
155 | 7.0021 | 0.89827 | 2.3371 | 1.6173 | 0.59274 | 0.74685 | 13.1944 | 42.35% | 6.1923 | 1.8844 | [6 empty] | 155 | 155 | 13.1944 | 7.0021 | 2.2021
156 | 7.0804 | 0.91006 | 2.4958 | 1.6485 | 0.60673 | 0.76449 | 13.5059 | 43.85% | 6.4256 | 1.9075 | [6 empty] | 156 | 156 | 13.5059 | 7.0804 | 2.2804
157 | 7.413 | 0.96089 | 2.881 | 1.7809 | 0.65179 | 0.82126 | 14.5089 | 50.25% | 7.0959 | 1.9572 | [6 empty] | 157 | 157 | 14.5089 | 7.413 | 2.613
158 | 7.5657 | 0.98461 | 3.114 | 1.8417 | 0.6753 | 0.85088 | 15.0322 | 53.19% | 7.4665 | 1.9869 | [6 empty] | 158 | 158 | 15.0322 | 7.5657 | 2.7657
159 | 7.6909 | 1.0043 | 3.2965 | 1.8915 | 0.69416 | 0.87464 | 15.452 | 55.59% | 7.7611 | 2.0091 | [6 empty] | 159 | 159 | 15.452 | 7.6909 | 2.8909
160 | 7.6322 | 0.99503 | 3.2493 | 1.8682 | 0.68723 | 0.86591 | 15.2978 | 54.47% | 7.6656 | 2.0044 | [6 empty] | 160 | 160 | 15.2978 | 7.6322 | 2.8322
161 | 7.9883 | 1.0516 | 3.5662 | 2.0099 | 0.7308 | 0.92081 | 16.2677 | 61.31% | 8.2793 | 2.0364 | [6 empty] | 161 | 161 | 16.2677 | 7.9883 | 3.1883
162 | 7.7574 | 1.0148 | 3.2975 | 1.918 | 0.69939 | 0.88123 | 15.5683 | 56.87% | 7.8109 | 2.0069 | [6 empty] | 162 | 162 | 15.5683 | 7.7574 | 2.9574
163 | 7.9257 | 1.0416 | 3.4101 | 1.985 | 0.71812 | 0.90483 | 15.9853 | 60.11% | 8.0596 | 2.0169 | [6 empty] | 163 | 163 | 15.9853 | 7.9257 | 3.1257
164 | 7.2956 | 0.94281 | 2.7269 | 1.7342 | 0.63498 | 0.80007 | 14.1346 | 47.99% | 6.839 | 1.9374 | [6 empty] | 164 | 164 | 14.1346 | 7.2956 | 2.4956
165 | 8.7554 | 1.1781 | 3.8934 | 2.3153 | 0.80711 | 1.017 | 17.9664 | 76.07% | 9.2109 | 2.052 | [6 empty] | 165 | 165 | 17.9664 | 8.7554 | 3.9554
166 | 7.8005 | 1.0216 | 2.9462 | 1.9352 | 0.68517 | 0.86332 | 15.252 | 57.7% | 7.4515 | 1.9553 | [6 empty] | 166 | 166 | 15.252 | 7.8005 | 3.0005
167 | 6.1176 | 0.76968 | 1.6145 | 1.2652 | 0.48835 | 0.61532 | 10.8706 | 25.34% | 4.753 | 1.7769 | [6 empty] | 167 | 167 | 10.8706 | 6.1176 | 1.3176
168 | 5.8162 | 0.72779 | 1.3557 | 1.1453 | 0.45225 | 0.56984 | 10.0671 | 19.54% | 4.2509 | 1.7309 | [6 empty] | 168 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 169 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 170 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 171 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 172 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 173 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 174 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 175 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 176 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 177 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 178 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 179 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 180 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 181 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 182 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 183 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 184 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 185 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 186 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 187 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 188 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 189 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 190 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 191 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 192 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 193 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 194 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 195 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 196 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 197 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 198 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 199 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 200 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 201 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 202 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 203 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 204 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 205 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 206 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 207 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 208 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 209 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 210 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 211 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 212 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 213 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 214 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 215 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 216 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 217 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 218 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 219 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 220 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 221 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 222 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 223 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 224 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 225 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 226 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 227 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 228 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 229 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 230 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 231 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 232 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 233 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 234 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 235 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 236 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 237 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 238 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 239 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 240 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 241 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 242 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 243 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 244 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 245 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 246 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 247 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 248 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 249 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 250 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 251 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 252 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 253 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 254 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 255 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 256 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 257 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 258 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 259 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 260 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 261 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 262 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 263 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 264 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 265 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 266 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 267 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 268 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 269 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 270 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 271 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 272 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 273 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 274 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 275 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 276 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 277 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 278 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 279 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 280 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 281 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 282 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 283 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 284 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 285 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 286 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 287 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 288 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 289 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 290 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 291 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 292 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 293 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 294 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 295 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 296 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 297 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 298 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 299 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 300 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 301 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 302 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 303 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 304 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 305 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 306 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 307 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 308 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 309 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 310 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 311 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 312 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 313 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 314 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 315 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 316 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 317 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 318 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 319 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 320 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 321 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 322 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 323 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 324 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 325 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 326 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 327 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 328 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 329 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 330 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 331 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 332 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 333 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 334 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 335 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 336 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 337 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 338 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 339 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 340 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 341 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 342 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 343 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 344 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 345 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 346 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 347 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 348 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 349 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 350 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 351 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 352 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 353 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 354 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 355 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 356 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 357 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 358 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 359 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 360 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 361 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 362 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 363 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 364 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 365 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 366 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 367 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 368 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 369 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 370 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 371 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 372 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 373 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 374 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 375 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 376 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 377 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 378 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 379 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 380 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 381 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 382 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 383 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 384 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 385 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 386 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 387 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 388 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 389 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 390 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 391 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 392 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 393 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 394 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 395 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 396 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 397 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 398 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 399 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 400 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 401 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 402 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 403 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 404 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 405 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 406 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 407 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 408 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 409 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 410 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 411 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 412 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 413 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 414 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 415 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 416 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 417 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 418 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 419 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 420 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 421 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 422 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 423 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 424 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 425 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 426 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 427 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 428 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 429 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 430 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 431 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 432 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 433 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 434 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 435 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 436 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 437 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 438 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 439 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 440 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 441 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 442 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 443 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 444 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 445 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 446 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 447 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 448 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 449 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 450 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 451 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 452 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 453 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 454 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 455 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 456 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 457 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 458 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 459 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 460 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 461 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 462 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 463 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 464 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 465 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 466 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 467 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 468 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 469 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 470 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 471 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 472 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 473 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 474 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 475 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 476 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 477 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 478 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 479 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 480 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 481 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 482 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 483 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 484 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 485 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 486 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 487 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 488 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 489 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 490 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 491 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 492 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 493 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 494 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 495 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 496 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 497 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 498 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 499 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 500 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 501 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 502 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 503 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 504 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 505 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 506 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 507 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 508 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 509 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 510 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 511 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 512 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 513 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 514 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 515 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 516 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 517 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 518 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 519 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 520 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 521 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 522 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 523 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 524 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 525 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 526 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 527 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 528 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 529 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 530 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 531 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 532 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 533 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 534 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 535 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 536 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 537 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 538 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 539 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 540 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 541 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 542 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 543 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 544 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 545 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 546 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 547 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 548 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 549 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 550 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 551 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 552 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 553 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 554 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 555 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 556 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 557 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 558 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 559 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 560 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 561 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 562 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 563 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 564 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 565 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 566 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 567 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 568 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 569 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 570 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 571 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 572 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 573 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 574 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 575 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 576 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 577 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 578 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 579 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 580 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 581 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 582 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 583 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 584 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 585 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 586 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 587 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 588 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 589 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 590 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 591 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 592 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 593 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 594 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 595 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 596 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 597 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 598 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 599 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 600 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 601 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 602 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 603 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 604 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 605 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 606 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 607 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 608 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 609 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 610 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 611 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 612 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 613 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 614 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 615 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 616 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 617 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 618 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 619 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 620 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 621 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 622 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 623 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 624 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 625 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 626 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 627 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 628 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 629 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 630 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 631 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 632 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 633 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 634 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 635 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 636 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 637 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 638 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 639 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 640 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 641 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 642 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 643 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 644 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 645 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 646 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 647 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 648 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 649 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 650 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 651 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 652 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 653 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 654 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 655 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 656 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 657 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 658 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 659 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 660 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 661 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 662 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 663 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 664 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 665 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 666 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 667 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 668 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 669 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 670 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 671 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 672 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 673 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 674 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 675 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 676 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 677 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 678 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 679 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 680 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 681 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 682 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 683 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 684 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 685 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 686 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 687 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 688 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 689 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 690 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 691 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 692 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 693 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 694 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 695 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 696 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 697 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 698 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 699 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 700 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 701 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 702 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 703 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 704 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 705 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 706 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 707 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 708 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 709 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 710 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 711 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 712 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 713 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 714 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 715 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 716 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 717 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 718 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 719 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 720 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 721 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 722 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 723 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 724 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 725 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 726 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 727 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 728 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 729 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 730 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 731 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 732 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 733 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 734 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 735 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 736 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 737 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 738 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 739 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 740 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 741 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 742 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 743 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 744 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 745 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 746 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 747 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 748 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 749 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 750 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 751 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 752 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 753 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 754 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 755 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 756 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 757 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 758 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 759 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 760 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 761 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 762 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 763 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 764 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 765 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 766 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 767 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 768 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 769 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 770 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 771 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 772 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 773 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 774 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 775 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 776 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 777 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 778 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 779 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 780 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 781 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 782 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 783 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 784 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 785 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 786 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 787 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 788 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 789 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 790 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 791 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 792 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 793 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 794 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 795 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 796 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 797 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 798 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 799 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 800 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 801 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 802 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 803 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 804 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 805 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 806 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 807 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 808 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 809 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 810 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 811 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 812 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 813 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 814 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 815 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 816 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 817 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 818 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 819 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 820 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 821 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 822 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 823 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 824 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 825 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 826 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 827 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 828 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 829 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 830 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 831 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 832 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 833 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 834 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 835 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 836 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 837 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 838 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 839 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 840 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 841 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 842 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 843 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 844 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 845 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 846 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 847 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 848 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 849 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 850 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 851 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 852 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 853 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 854 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 855 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 856 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 857 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 858 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 859 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 860 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 861 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 862 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 863 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 864 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 865 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 866 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 867 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 868 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 869 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 870 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 871 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 872 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 873 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 874 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 875 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 876 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 877 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 878 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 879 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 880 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 881 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 882 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 883 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 884 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 885 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 886 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 887 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 888 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 889 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 890 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 891 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 892 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 893 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 894 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 895 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 896 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 897 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 898 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 899 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 900 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 901 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 902 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 903 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 904 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 905 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 906 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 907 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 908 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 909 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 910 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 911 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 912 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 913 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 914 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 915 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 916 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 917 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 918 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 919 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 920 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 921 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 922 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 923 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 924 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 925 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 926 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 927 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 928 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 929 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 930 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 931 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 932 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 933 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 934 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 935 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 936 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 937 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 938 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 939 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 940 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 941 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 942 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 943 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 944 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 945 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 946 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 947 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 948 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 949 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 950 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 951 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 952 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 953 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 954 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 955 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 956 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 957 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 958 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 959 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 960 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 961 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 962 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 963 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 964 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 965 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 966 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 967 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 968 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 969 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 970 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 971 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 972 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 973 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 974 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 975 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 976 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 977 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 978 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 979 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 980 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 981 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 982 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 983 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 984 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 985 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 986 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 987 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 988 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 989 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 990 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 991 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 992 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 993 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 994 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 995 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 996 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 997 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 998 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 999 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1000 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1001 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1002 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1003 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1004 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1005 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1006 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1007 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1008 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1009 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1010 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1011 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1012 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1013 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1014 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1015 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1016 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1017 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1018 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1019 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1020 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1021 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1022 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1023 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1024 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1025 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1026 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1027 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1028 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1029 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1030 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1031 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1032 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1033 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1034 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1035 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1036 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1037 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1038 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1039 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1040 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1041 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1042 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1043 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1044 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1045 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1046 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1047 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1048 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1049 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1050 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1051 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1052 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1053 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1054 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1055 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1056 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1057 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1058 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1059 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1060 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1061 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1062 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1063 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1064 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1065 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1066 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1067 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1068 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1069 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1070 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1071 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1072 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1073 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1074 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1075 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1076 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1077 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1078 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1079 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1080 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1081 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1082 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1083 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1084 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1085 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1086 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1087 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1088 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1089 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1090 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1091 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1092 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1093 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1094 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1095 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1096 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1097 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1098 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1099 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1100 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1101 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1102 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1103 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1104 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1105 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1106 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1107 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1108 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1109 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1110 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1111 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1112 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1113 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1114 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1115 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1116 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1117 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1118 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1119 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1120 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1121 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1122 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1123 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1124 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1125 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1126 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1127 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1128 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1129 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1130 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1131 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1132 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1133 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1134 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1135 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1136 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1137 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1138 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1139 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1140 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1141 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1142 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1143 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1144 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1145 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1146 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1147 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1148 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1149 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1150 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1151 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1152 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1153 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1154 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1155 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1156 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1157 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1158 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1159 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 1160 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 1161 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 1162 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 1163 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 1164 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 1165 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 1166 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 1167 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1168 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1169 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1170 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1171 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1172 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1173 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1174 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1175 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1176 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1177 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1178 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1179 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1180 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1181 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1182 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1183 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1184 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1185 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1186 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1187 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1188 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1189 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1190 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1191 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1192 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1193 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1194 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1195 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1196 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1197 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1198 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1199 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1200 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1201 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1202 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1203 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1204 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1205 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1206 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1207 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1208 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1209 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1210 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1211 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1212 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1213 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1214 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1215 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1216 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1217 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1218 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1219 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1220 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1221 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1222 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1223 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1224 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1225 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1226 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1227 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1228 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1229 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1230 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1231 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1232 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1233 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1234 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1235 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1236 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1237 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1238 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1239 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1240 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1241 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1242 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1243 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1244 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1245 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1246 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1247 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1248 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1249 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1250 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1251 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1252 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1253 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1254 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1255 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1256 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1257 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1258 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1259 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1260 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1261 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1262 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1263 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1264 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1265 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1266 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1267 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1268 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1269 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1270 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1271 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1272 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1273 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1274 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1275 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1276 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1277 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1278 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1279 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1280 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1281 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1282 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1283 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1284 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1285 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1286 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1287 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1288 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1289 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1290 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1291 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1292 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1293 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1294 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1295 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1296 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1297 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1298 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1299 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1300 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1301 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1302 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1303 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1304 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1305 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1306 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1307 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1308 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1309 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1310 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1311 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1312 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1313 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1314 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1315 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1316 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1317 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1318 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1319 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1320 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1321 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1322 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1323 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1324 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1325 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1326 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1327 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 1328 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 1329 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 1330 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 1331 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 1332 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 1333 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 1334 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 1335 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1336 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1337 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1338 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1339 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1340 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1341 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1342 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1343 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1344 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1345 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1346 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1347 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1348 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1349 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1350 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1351 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1352 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1353 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1354 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1355 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1356 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1357 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1358 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1359 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1360 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1361 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1362 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1363 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1364 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1365 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1366 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1367 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1368 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1369 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1370 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1371 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1372 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1373 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1374 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1375 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1376 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1377 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1378 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1379 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1380 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1381 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1382 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1383 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1384 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1385 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1386 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1387 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1388 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1389 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1390 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1391 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1392 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1393 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1394 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1395 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1396 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1397 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1398 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1399 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1400 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1401 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1402 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1403 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1404 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1405 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1406 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1407 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1408 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1409 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1410 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1411 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1412 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1413 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1414 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1415 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1416 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1417 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1418 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1419 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1420 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1421 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1422 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1423 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1424 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1425 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1426 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1427 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1428 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1429 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1430 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1431 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1432 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1433 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1434 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1435 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1436 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1437 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1438 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1439 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1440 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1441 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1442 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1443 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1444 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1445 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1446 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1447 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1448 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1449 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1450 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1451 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1452 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1453 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1454 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1455 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1456 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1457 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1458 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1459 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1460 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1461 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1462 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1463 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1464 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1465 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1466 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1467 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1468 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1469 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1470 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1471 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1472 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1473 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1474 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1475 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1476 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1477 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1478 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1479 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1480 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1481 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1482 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1483 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1484 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1485 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1486 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1487 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1488 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1489 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1490 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1491 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1492 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1493 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1494 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1495 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 1496 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 1497 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 1498 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 1499 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 1500 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 1501 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 1502 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 1503 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1504 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1505 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1506 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1507 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1508 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1509 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1510 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1511 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1512 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1513 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1514 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1515 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1516 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1517 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1518 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1519 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1520 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1521 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1522 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1523 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1524 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1525 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1526 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1527 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1528 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1529 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1530 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1531 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1532 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1533 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1534 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1535 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1536 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1537 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1538 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1539 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1540 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1541 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1542 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1543 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1544 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1545 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1546 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1547 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1548 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1549 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1550 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1551 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1552 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1553 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1554 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1555 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1556 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1557 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1558 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1559 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1560 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1561 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1562 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1563 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1564 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1565 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1566 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1567 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1568 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1569 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1570 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1571 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1572 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1573 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1574 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1575 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1576 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1577 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1578 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1579 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1580 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1581 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1582 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1583 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1584 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1585 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1586 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1587 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1588 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1589 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1590 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1591 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1592 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1593 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1594 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1595 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1596 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1597 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1598 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1599 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1600 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1601 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1602 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1603 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1604 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1605 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1606 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1607 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1608 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1609 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1610 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1611 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1612 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1613 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1614 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1615 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1616 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1617 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1618 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1619 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1620 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1621 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1622 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1623 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1624 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1625 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1626 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1627 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1628 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1629 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1630 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1631 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1632 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1633 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1634 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1635 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1636 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1637 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1638 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1639 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1640 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1641 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1642 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1643 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1644 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1645 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1646 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1647 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1648 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1649 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1650 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1651 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1652 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1653 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1654 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1655 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1656 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1657 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1658 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1659 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1660 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1661 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1662 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1663 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 1664 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 1665 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 1666 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 1667 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 1668 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 1669 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 1670 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 1671 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1672 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1673 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1674 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1675 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1676 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1677 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1678 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1679 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1680 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1681 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1682 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1683 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1684 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1685 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1686 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1687 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1688 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1689 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1690 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1691 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1692 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1693 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1694 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1695 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1696 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1697 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1698 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1699 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1700 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1701 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1702 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1703 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1704 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1705 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1706 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1707 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1708 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1709 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1710 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1711 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1712 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1713 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1714 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1715 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1716 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1717 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1718 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1719 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1720 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1721 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1722 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1723 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1724 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1725 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1726 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1727 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1728 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1729 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1730 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1731 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1732 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1733 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1734 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1735 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1736 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1737 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1738 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1739 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1740 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1741 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1742 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1743 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1744 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1745 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1746 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1747 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1748 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1749 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1750 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1751 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1752 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1753 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1754 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1755 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1756 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1757 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1758 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1759 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1760 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1761 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1762 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1763 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1764 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1765 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1766 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1767 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1768 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1769 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1770 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1771 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1772 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1773 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1774 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1775 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1776 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1777 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1778 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1779 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1780 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1781 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1782 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1783 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1784 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1785 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1786 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1787 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1788 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1789 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1790 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1791 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1792 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1793 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1794 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1795 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1796 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1797 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1798 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1799 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1800 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1801 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1802 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1803 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1804 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1805 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1806 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1807 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1808 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1809 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1810 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1811 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1812 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1813 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1814 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1815 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1816 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1817 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1818 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1819 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1820 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1821 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1822 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1823 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1824 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1825 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1826 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1827 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1828 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1829 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1830 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1831 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 1832 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 1833 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 1834 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 1835 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 1836 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 1837 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 1838 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 1839 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 1840 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 1841 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 1842 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 1843 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 1844 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 1845 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 1846 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 1847 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 1848 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 1849 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 1850 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 1851 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 1852 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 1853 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 1854 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 1855 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 1856 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 1857 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 1858 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 1859 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 1860 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 1861 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 1862 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 1863 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 1864 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 1865 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 1866 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 1867 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 1868 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 1869 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 1870 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 1871 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 1872 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 1873 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 1874 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 1875 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 1876 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 1877 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 1878 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 1879 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 1880 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 1881 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 1882 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 1883 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 1884 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 1885 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 1886 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 1887 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 1888 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 1889 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 1890 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 1891 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 1892 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 1893 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 1894 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 1895 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 1896 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 1897 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 1898 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 1899 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 1900 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 1901 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 1902 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 1903 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 1904 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 1905 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 1906 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 1907 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 1908 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 1909 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 1910 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 1911 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 1912 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 1913 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 1914 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 1915 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 1916 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 1917 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 1918 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 1919 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 1920 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 1921 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 1922 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 1923 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 1924 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 1925 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 1926 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 1927 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 1928 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 1929 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 1930 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 1931 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 1932 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 1933 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 1934 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 1935 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 1936 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 1937 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 1938 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 1939 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 1940 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 1941 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 1942 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 1943 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 1944 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 1945 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 1946 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 1947 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 1948 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 1949 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 1950 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 1951 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 1952 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 1953 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 1954 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 1955 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 1956 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 1957 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 1958 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 1959 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 1960 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 1961 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 1962 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 1963 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 1964 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 1965 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 1966 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 1967 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 1968 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 1969 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 1970 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 1971 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 1972 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 1973 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 1974 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 1975 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 1976 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 1977 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 1978 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 1979 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 1980 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 1981 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 1982 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 1983 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 1984 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 1985 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 1986 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 1987 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 1988 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 1989 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 1990 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 1991 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 1992 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 1993 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 1994 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 1995 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 1996 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 1997 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 1998 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 1999 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2000 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2001 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2002 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2003 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2004 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2005 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2006 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2007 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2008 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2009 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2010 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2011 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2012 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2013 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2014 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2015 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2016 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2017 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2018 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2019 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2020 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2021 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2022 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2023 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2024 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2025 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2026 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2027 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2028 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2029 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2030 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2031 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2032 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2033 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2034 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2035 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2036 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2037 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2038 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2039 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2040 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2041 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2042 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2043 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2044 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2045 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2046 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2047 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2048 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2049 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2050 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2051 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2052 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2053 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2054 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2055 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2056 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2057 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2058 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2059 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2060 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2061 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2062 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2063 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2064 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2065 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2066 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2067 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2068 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2069 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2070 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2071 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2072 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2073 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2074 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2075 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2076 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2077 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2078 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2079 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2080 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2081 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2082 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2083 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2084 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2085 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2086 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2087 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2088 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2089 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2090 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2091 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2092 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2093 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2094 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2095 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2096 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2097 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2098 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2099 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2100 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2101 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2102 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2103 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2104 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2105 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2106 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2107 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2108 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2109 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2110 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2111 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2112 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2113 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2114 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2115 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2116 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2117 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2118 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2119 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2120 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2121 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2122 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2123 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2124 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2125 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2126 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2127 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2128 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2129 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2130 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2131 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2132 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2133 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2134 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2135 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2136 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2137 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2138 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2139 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2140 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2141 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2142 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2143 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2144 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2145 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2146 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2147 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2148 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2149 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2150 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2151 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2152 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2153 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2154 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2155 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2156 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2157 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2158 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2159 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 2160 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 2161 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 2162 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 2163 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 2164 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 2165 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 2166 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 2167 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2168 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2169 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2170 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2171 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2172 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2173 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2174 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2175 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2176 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2177 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2178 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2179 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2180 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2181 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2182 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2183 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2184 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2185 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2186 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2187 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2188 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2189 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2190 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2191 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2192 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2193 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2194 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2195 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2196 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2197 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2198 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2199 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2200 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2201 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2202 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2203 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2204 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2205 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2206 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2207 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2208 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2209 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2210 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2211 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2212 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2213 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2214 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2215 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2216 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2217 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2218 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2219 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2220 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2221 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2222 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2223 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2224 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2225 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2226 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2227 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2228 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2229 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2230 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2231 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2232 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2233 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2234 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2235 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2236 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2237 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2238 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2239 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2240 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2241 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2242 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2243 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2244 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2245 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2246 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2247 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2248 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2249 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2250 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2251 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2252 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2253 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2254 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2255 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2256 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2257 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2258 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2259 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2260 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2261 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2262 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2263 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2264 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2265 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2266 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2267 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2268 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2269 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2270 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2271 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2272 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2273 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2274 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2275 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2276 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2277 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2278 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2279 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2280 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2281 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2282 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2283 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2284 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2285 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2286 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2287 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2288 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2289 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2290 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2291 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2292 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2293 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2294 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2295 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2296 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2297 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2298 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2299 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2300 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2301 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2302 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2303 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2304 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2305 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2306 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2307 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2308 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2309 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2310 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2311 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2312 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2313 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2314 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2315 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2316 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2317 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2318 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2319 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2320 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2321 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2322 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2323 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2324 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2325 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2326 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2327 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 2328 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 2329 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 2330 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 2331 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 2332 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 2333 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 2334 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 2335 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2336 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2337 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2338 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2339 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2340 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2341 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2342 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2343 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2344 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2345 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2346 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2347 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2348 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2349 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2350 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2351 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2352 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2353 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2354 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2355 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2356 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2357 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2358 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2359 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2360 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2361 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2362 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2363 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2364 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2365 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2366 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2367 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2368 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2369 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2370 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2371 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2372 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2373 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2374 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2375 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2376 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2377 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2378 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2379 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2380 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2381 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2382 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2383 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2384 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2385 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2386 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2387 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2388 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2389 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2390 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2391 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2392 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2393 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2394 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2395 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2396 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2397 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2398 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2399 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2400 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2401 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2402 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2403 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2404 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2405 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2406 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2407 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2408 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2409 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2410 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2411 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2412 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2413 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2414 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2415 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2416 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2417 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2418 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2419 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2420 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2421 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2422 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2423 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2424 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2425 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2426 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2427 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2428 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2429 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2430 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2431 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2432 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2433 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2434 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2435 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2436 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2437 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2438 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2439 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2440 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2441 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2442 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2443 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2444 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2445 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2446 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2447 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2448 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2449 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2450 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2451 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2452 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2453 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2454 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2455 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2456 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2457 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2458 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2459 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2460 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2461 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2462 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2463 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2464 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2465 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2466 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2467 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2468 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2469 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2470 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2471 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2472 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2473 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2474 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2475 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2476 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2477 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2478 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2479 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2480 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2481 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2482 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2483 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2484 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2485 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2486 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2487 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2488 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2489 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2490 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2491 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2492 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2493 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2494 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2495 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 2496 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 2497 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 2498 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 2499 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 2500 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 2501 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 2502 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 2503 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2504 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2505 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2506 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2507 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2508 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2509 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2510 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2511 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2512 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2513 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2514 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2515 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2516 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2517 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2518 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2519 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2520 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2521 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2522 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2523 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2524 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2525 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2526 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2527 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2528 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2529 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2530 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2531 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2532 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2533 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2534 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2535 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2536 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2537 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2538 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2539 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2540 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2541 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2542 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2543 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2544 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2545 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2546 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2547 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2548 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2549 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2550 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2551 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2552 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2553 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2554 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2555 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2556 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2557 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2558 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2559 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2560 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2561 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2562 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2563 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2564 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2565 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2566 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2567 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2568 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2569 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2570 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2571 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2572 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2573 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2574 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2575 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2576 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2577 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2578 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2579 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2580 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2581 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2582 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2583 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2584 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2585 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2586 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2587 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2588 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2589 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2590 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2591 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2592 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2593 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2594 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2595 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2596 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2597 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2598 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2599 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2600 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2601 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2602 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2603 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2604 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2605 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2606 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2607 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2608 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2609 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2610 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2611 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2612 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2613 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2614 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2615 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2616 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2617 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2618 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2619 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2620 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2621 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2622 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2623 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2624 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2625 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2626 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2627 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2628 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2629 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2630 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2631 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2632 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2633 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2634 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2635 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2636 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2637 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2638 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2639 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2640 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2641 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2642 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2643 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2644 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2645 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2646 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2647 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2648 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2649 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2650 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2651 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2652 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2653 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2654 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2655 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2656 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2657 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2658 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2659 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2660 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2661 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2662 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2663 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 2664 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 2665 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 2666 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 2667 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 2668 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 2669 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 2670 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 2671 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2672 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2673 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2674 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2675 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2676 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2677 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2678 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2679 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2680 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2681 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2682 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2683 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2684 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2685 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2686 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2687 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2688 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2689 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2690 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2691 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2692 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2693 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2694 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2695 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2696 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2697 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2698 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2699 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2700 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2701 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2702 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2703 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2704 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2705 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2706 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2707 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2708 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2709 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2710 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2711 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2712 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2713 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2714 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2715 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2716 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2717 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2718 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2719 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2720 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2721 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2722 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2723 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2724 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2725 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2726 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2727 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2728 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2729 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2730 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2731 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2732 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2733 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2734 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2735 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2736 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2737 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2738 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2739 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2740 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2741 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2742 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2743 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2744 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2745 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2746 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2747 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2748 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2749 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2750 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2751 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2752 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2753 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2754 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2755 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2756 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2757 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2758 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2759 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2760 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2761 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2762 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2763 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2764 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2765 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2766 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2767 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2768 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2769 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2770 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2771 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2772 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2773 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2774 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2775 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2776 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2777 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2778 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2779 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2780 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2781 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2782 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2783 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2784 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2785 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2786 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2787 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2788 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2789 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2790 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2791 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2792 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2793 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2794 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2795 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2796 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2797 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2798 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2799 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2800 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2801 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2802 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2803 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2804 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2805 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2806 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2807 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2808 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2809 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2810 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2811 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2812 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2813 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2814 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2815 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2816 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2817 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2818 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2819 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2820 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2821 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2822 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2823 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2824 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2825 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2826 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2827 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2828 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2829 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2830 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2831 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 2832 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 2833 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 2834 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 2835 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 2836 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 2837 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 2838 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 2839 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 2840 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 2841 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 2842 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 2843 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 2844 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 2845 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 2846 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 2847 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 2848 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 2849 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 2850 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 2851 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 2852 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 2853 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 2854 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 2855 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 2856 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 2857 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 2858 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 2859 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 2860 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 2861 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 2862 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 2863 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 2864 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 2865 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 2866 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 2867 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 2868 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 2869 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 2870 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 2871 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 2872 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 2873 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 2874 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 2875 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 2876 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 2877 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 2878 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 2879 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 2880 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 2881 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 2882 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 2883 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 2884 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 2885 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 2886 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 2887 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 2888 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 2889 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 2890 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 2891 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 2892 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 2893 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 2894 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 2895 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 2896 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 2897 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 2898 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 2899 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 2900 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 2901 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 2902 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 2903 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 2904 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 2905 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 2906 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 2907 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 2908 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 2909 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 2910 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 2911 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 2912 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 2913 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 2914 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 2915 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 2916 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 2917 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 2918 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 2919 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 2920 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 2921 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 2922 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 2923 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 2924 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 2925 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 2926 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 2927 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 2928 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 2929 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 2930 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 2931 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 2932 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 2933 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 2934 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 2935 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 2936 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 2937 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 2938 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 2939 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 2940 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 2941 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 2942 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 2943 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 2944 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 2945 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 2946 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 2947 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 2948 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 2949 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 2950 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 2951 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 2952 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 2953 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 2954 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 2955 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 2956 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 2957 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 2958 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 2959 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 2960 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 2961 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 2962 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 2963 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 2964 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 2965 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 2966 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 2967 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 2968 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 2969 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 2970 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 2971 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 2972 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 2973 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 2974 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 2975 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 2976 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 2977 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 2978 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 2979 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 2980 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 2981 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 2982 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 2983 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 2984 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 2985 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 2986 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 2987 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 2988 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 2989 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 2990 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 2991 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 2992 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 2993 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 2994 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 2995 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 2996 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 2997 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 2998 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 2999 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3000 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3001 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3002 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3003 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3004 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3005 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3006 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3007 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3008 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3009 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3010 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3011 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3012 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3013 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3014 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3015 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3016 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3017 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3018 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3019 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3020 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3021 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3022 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3023 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3024 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3025 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3026 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3027 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3028 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3029 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3030 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3031 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3032 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3033 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3034 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3035 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3036 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3037 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3038 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3039 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3040 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3041 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3042 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3043 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3044 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3045 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3046 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3047 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3048 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3049 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3050 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3051 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3052 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3053 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3054 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3055 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3056 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3057 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3058 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3059 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3060 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3061 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3062 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3063 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3064 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3065 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3066 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3067 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3068 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3069 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3070 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3071 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3072 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3073 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3074 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3075 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3076 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3077 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3078 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3079 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3080 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3081 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3082 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3083 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3084 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3085 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3086 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3087 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3088 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3089 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3090 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3091 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3092 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3093 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3094 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3095 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3096 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3097 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3098 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3099 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3100 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3101 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3102 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3103 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3104 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3105 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3106 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3107 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3108 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3109 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3110 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3111 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3112 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3113 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3114 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3115 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3116 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3117 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3118 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3119 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3120 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3121 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3122 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3123 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3124 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3125 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3126 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3127 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3128 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3129 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3130 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3131 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3132 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3133 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3134 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3135 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3136 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3137 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3138 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3139 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3140 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3141 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3142 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3143 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3144 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3145 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3146 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3147 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3148 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3149 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3150 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3151 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3152 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3153 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3154 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3155 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3156 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3157 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3158 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3159 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 3160 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 3161 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 3162 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 3163 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 3164 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 3165 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 3166 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 3167 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3168 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3169 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3170 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3171 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3172 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3173 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3174 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3175 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3176 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3177 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3178 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3179 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3180 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3181 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3182 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3183 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3184 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3185 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3186 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3187 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3188 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3189 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3190 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3191 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3192 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3193 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3194 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3195 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3196 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3197 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3198 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3199 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3200 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3201 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3202 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3203 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3204 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3205 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3206 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3207 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3208 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3209 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3210 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3211 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3212 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3213 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3214 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3215 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3216 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3217 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3218 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3219 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3220 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3221 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3222 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3223 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3224 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3225 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3226 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3227 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3228 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3229 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3230 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3231 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3232 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3233 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3234 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3235 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3236 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3237 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3238 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3239 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3240 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3241 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3242 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3243 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3244 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3245 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3246 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3247 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3248 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3249 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3250 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3251 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3252 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3253 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3254 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3255 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3256 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3257 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3258 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3259 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3260 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3261 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3262 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3263 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3264 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3265 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3266 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3267 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3268 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3269 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3270 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3271 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3272 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3273 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3274 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3275 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3276 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3277 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3278 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3279 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3280 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3281 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3282 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3283 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3284 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3285 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3286 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3287 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3288 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3289 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3290 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3291 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3292 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3293 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3294 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3295 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3296 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3297 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3298 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3299 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3300 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3301 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3302 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3303 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3304 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3305 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3306 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3307 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3308 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3309 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3310 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3311 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3312 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3313 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3314 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3315 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3316 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3317 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3318 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3319 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3320 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3321 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3322 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3323 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3324 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3325 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3326 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3327 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 3328 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 3329 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 3330 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 3331 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 3332 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 3333 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 3334 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 3335 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3336 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3337 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3338 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3339 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3340 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3341 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3342 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3343 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3344 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3345 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3346 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3347 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3348 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3349 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3350 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3351 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3352 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3353 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3354 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3355 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3356 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3357 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3358 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3359 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3360 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3361 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3362 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3363 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3364 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3365 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3366 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3367 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3368 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3369 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3370 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3371 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3372 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3373 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3374 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3375 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3376 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3377 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3378 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3379 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3380 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3381 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3382 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3383 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3384 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3385 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3386 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3387 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3388 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3389 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3390 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3391 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3392 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3393 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3394 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3395 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3396 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3397 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3398 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3399 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3400 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3401 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3402 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3403 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3404 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3405 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3406 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3407 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3408 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3409 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3410 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3411 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3412 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3413 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3414 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3415 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3416 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3417 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3418 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3419 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3420 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3421 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3422 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3423 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3424 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3425 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3426 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3427 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3428 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3429 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3430 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3431 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3432 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3433 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3434 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3435 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3436 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3437 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3438 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3439 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3440 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3441 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3442 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3443 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3444 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3445 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3446 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3447 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3448 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3449 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3450 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3451 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3452 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3453 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3454 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3455 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3456 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3457 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3458 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3459 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3460 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3461 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3462 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3463 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3464 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3465 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3466 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3467 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3468 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3469 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3470 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3471 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3472 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3473 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3474 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3475 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3476 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3477 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3478 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3479 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3480 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3481 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3482 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3483 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3484 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3485 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3486 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3487 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3488 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3489 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3490 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3491 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3492 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3493 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3494 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3495 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 3496 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 3497 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 3498 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 3499 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 3500 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 3501 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 3502 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 3503 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3504 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3505 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3506 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3507 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3508 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3509 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3510 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3511 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3512 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3513 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3514 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3515 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3516 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3517 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3518 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3519 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3520 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3521 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3522 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3523 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3524 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3525 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3526 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3527 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3528 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3529 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3530 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3531 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3532 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3533 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3534 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3535 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3536 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3537 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3538 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3539 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3540 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3541 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3542 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3543 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3544 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3545 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3546 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3547 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3548 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3549 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3550 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3551 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3552 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3553 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3554 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3555 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3556 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3557 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3558 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3559 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3560 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3561 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3562 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3563 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3564 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3565 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3566 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3567 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3568 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3569 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3570 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3571 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3572 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3573 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3574 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3575 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3576 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3577 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3578 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3579 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3580 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3581 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3582 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3583 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3584 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3585 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3586 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3587 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3588 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3589 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3590 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3591 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3592 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3593 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3594 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3595 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3596 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3597 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3598 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3599 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3600 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3601 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3602 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3603 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3604 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3605 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3606 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3607 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3608 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3609 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3610 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3611 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3612 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3613 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3614 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3615 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3616 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3617 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3618 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3619 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3620 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3621 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3622 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3623 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3624 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3625 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3626 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3627 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3628 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3629 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3630 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3631 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3632 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3633 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3634 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3635 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3636 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3637 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3638 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3639 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3640 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3641 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3642 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3643 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3644 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3645 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3646 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3647 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3648 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3649 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3650 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3651 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3652 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3653 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3654 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3655 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3656 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3657 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3658 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3659 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3660 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3661 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3662 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3663 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 3664 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 3665 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 3666 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 3667 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 3668 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 3669 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 3670 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 3671 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3672 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3673 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3674 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3675 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3676 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3677 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3678 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3679 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3680 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3681 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3682 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3683 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3684 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3685 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3686 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3687 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3688 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3689 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3690 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3691 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3692 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3693 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3694 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3695 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3696 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3697 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3698 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3699 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3700 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3701 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3702 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3703 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3704 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3705 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3706 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3707 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3708 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3709 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3710 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3711 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3712 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3713 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3714 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3715 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3716 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3717 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3718 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3719 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3720 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3721 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3722 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3723 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3724 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3725 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3726 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3727 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3728 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3729 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3730 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3731 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3732 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3733 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3734 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3735 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3736 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3737 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3738 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3739 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3740 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3741 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3742 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3743 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3744 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3745 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3746 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3747 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3748 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3749 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3750 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3751 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3752 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3753 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3754 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3755 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3756 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3757 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3758 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3759 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3760 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3761 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3762 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3763 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3764 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3765 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3766 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3767 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3768 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3769 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3770 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3771 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3772 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3773 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3774 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3775 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3776 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3777 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3778 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3779 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3780 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3781 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3782 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3783 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3784 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3785 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3786 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3787 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3788 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3789 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3790 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3791 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3792 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3793 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3794 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3795 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3796 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3797 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3798 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3799 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3800 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3801 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3802 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3803 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3804 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3805 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3806 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3807 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3808 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3809 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3810 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3811 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3812 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3813 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3814 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3815 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3816 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3817 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3818 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3819 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3820 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3821 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3822 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3823 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3824 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3825 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3826 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3827 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3828 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3829 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3830 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3831 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 3832 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 3833 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 3834 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 3835 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 3836 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 3837 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 3838 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 3839 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 3840 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 3841 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 3842 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 3843 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 3844 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 3845 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 3846 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 3847 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 3848 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 3849 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 3850 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 3851 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 3852 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 3853 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 3854 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 3855 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 3856 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 3857 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 3858 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 3859 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 3860 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 3861 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 3862 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 3863 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 3864 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 3865 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 3866 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 3867 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 3868 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 3869 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 3870 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 3871 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 3872 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 3873 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 3874 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 3875 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 3876 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 3877 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 3878 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 3879 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 3880 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 3881 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 3882 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 3883 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 3884 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 3885 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 3886 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 3887 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 3888 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 3889 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 3890 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 3891 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 3892 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 3893 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 3894 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 3895 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 3896 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 3897 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 3898 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 3899 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 3900 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 3901 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 3902 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 3903 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 3904 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 3905 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 3906 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 3907 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 3908 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 3909 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 3910 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 3911 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 3912 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 3913 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 3914 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 3915 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 3916 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 3917 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 3918 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 3919 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 3920 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 3921 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 3922 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 3923 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 3924 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 3925 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 3926 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 3927 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 3928 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 3929 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 3930 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 3931 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 3932 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 3933 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 3934 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 3935 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 3936 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 3937 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 3938 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 3939 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 3940 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 3941 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 3942 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 3943 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 3944 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 3945 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 3946 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 3947 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 3948 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 3949 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 3950 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 3951 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 3952 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 3953 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 3954 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 3955 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 3956 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 3957 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 3958 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 3959 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 3960 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 3961 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 3962 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 3963 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 3964 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 3965 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 3966 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 3967 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 3968 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 3969 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 3970 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 3971 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 3972 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 3973 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 3974 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 3975 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 3976 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 3977 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 3978 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 3979 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 3980 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 3981 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 3982 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 3983 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 3984 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 3985 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 3986 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 3987 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 3988 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 3989 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 3990 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 3991 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 3992 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 3993 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 3994 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 3995 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 3996 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 3997 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 3998 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 3999 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4000 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4001 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4002 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4003 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4004 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4005 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4006 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4007 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4008 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4009 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4010 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4011 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4012 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4013 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4014 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4015 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4016 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4017 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4018 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4019 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4020 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4021 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4022 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4023 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4024 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4025 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4026 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4027 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4028 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4029 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4030 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4031 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4032 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4033 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4034 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4035 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4036 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4037 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4038 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4039 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4040 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4041 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4042 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4043 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4044 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4045 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4046 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4047 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4048 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4049 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4050 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4051 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4052 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4053 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4054 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4055 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4056 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4057 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4058 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4059 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4060 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4061 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4062 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4063 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4064 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4065 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4066 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4067 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4068 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4069 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4070 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4071 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4072 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4073 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4074 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4075 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4076 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4077 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4078 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4079 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4080 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4081 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4082 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4083 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4084 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4085 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4086 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4087 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4088 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4089 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4090 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4091 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4092 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4093 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4094 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4095 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4096 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4097 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4098 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4099 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4100 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4101 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4102 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4103 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4104 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4105 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4106 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4107 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4108 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4109 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4110 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4111 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4112 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4113 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4114 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4115 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4116 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4117 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4118 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4119 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4120 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4121 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4122 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4123 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4124 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4125 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4126 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4127 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4128 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4129 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4130 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4131 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4132 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4133 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4134 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4135 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4136 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4137 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4138 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4139 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4140 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4141 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4142 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4143 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4144 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4145 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4146 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4147 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4148 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4149 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4150 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4151 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4152 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4153 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4154 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4155 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4156 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4157 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4158 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4159 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 4160 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 4161 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 4162 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 4163 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 4164 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 4165 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 4166 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 4167 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4168 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4169 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4170 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4171 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4172 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4173 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4174 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4175 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4176 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4177 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4178 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4179 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4180 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4181 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4182 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4183 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4184 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4185 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4186 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4187 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4188 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4189 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4190 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4191 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4192 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4193 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4194 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4195 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4196 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4197 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4198 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4199 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4200 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4201 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4202 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4203 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4204 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4205 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4206 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4207 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4208 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4209 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4210 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4211 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4212 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4213 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4214 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4215 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4216 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4217 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4218 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4219 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4220 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4221 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4222 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4223 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4224 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4225 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4226 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4227 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4228 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4229 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4230 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4231 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4232 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4233 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4234 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4235 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4236 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4237 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4238 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4239 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4240 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4241 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4242 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4243 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4244 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4245 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4246 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4247 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4248 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4249 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4250 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4251 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4252 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4253 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4254 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4255 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4256 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4257 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4258 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4259 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4260 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4261 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4262 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4263 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4264 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4265 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4266 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4267 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4268 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4269 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4270 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4271 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4272 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4273 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4274 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4275 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4276 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4277 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4278 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4279 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4280 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4281 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4282 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4283 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4284 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4285 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4286 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4287 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4288 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4289 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4290 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4291 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4292 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4293 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4294 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4295 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4296 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4297 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4298 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4299 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4300 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4301 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4302 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4303 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4304 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4305 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4306 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4307 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4308 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4309 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4310 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4311 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4312 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4313 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4314 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4315 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4316 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4317 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4318 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4319 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4320 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4321 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4322 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4323 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4324 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4325 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4326 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4327 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 4328 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 4329 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 4330 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 4331 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 4332 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 4333 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 4334 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 4335 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4336 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4337 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4338 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4339 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4340 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4341 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4342 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4343 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4344 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4345 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4346 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4347 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4348 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4349 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4350 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4351 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4352 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4353 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4354 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4355 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4356 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4357 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4358 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4359 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4360 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4361 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4362 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4363 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4364 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4365 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4366 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4367 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4368 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4369 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4370 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4371 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4372 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4373 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4374 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4375 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4376 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4377 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4378 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4379 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4380 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4381 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4382 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4383 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4384 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4385 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4386 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4387 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4388 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4389 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4390 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4391 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4392 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4393 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4394 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4395 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4396 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4397 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4398 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4399 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4400 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4401 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4402 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4403 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4404 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4405 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4406 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4407 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4408 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4409 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4410 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4411 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4412 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4413 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4414 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4415 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4416 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4417 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4418 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4419 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4420 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4421 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4422 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4423 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4424 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4425 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4426 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4427 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4428 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4429 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4430 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4431 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4432 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4433 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4434 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4435 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4436 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4437 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4438 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4439 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4440 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4441 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4442 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4443 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4444 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4445 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4446 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4447 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4448 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4449 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4450 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4451 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4452 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4453 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4454 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4455 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4456 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4457 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4458 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4459 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4460 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4461 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4462 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4463 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4464 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4465 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4466 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4467 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4468 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4469 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4470 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4471 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4472 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4473 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4474 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4475 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4476 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4477 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4478 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4479 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4480 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4481 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4482 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4483 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4484 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4485 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4486 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4487 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4488 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4489 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4490 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4491 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4492 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4493 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4494 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4495 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 4496 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 4497 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 4498 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 4499 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 4500 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 4501 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 4502 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 4503 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4504 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4505 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4506 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4507 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4508 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4509 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4510 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4511 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4512 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4513 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4514 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4515 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4516 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4517 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4518 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4519 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4520 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4521 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4522 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4523 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4524 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4525 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4526 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4527 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4528 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4529 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4530 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4531 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4532 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4533 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4534 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4535 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4536 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4537 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4538 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4539 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4540 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4541 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4542 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4543 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4544 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4545 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4546 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4547 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4548 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4549 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4550 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4551 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4552 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4553 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4554 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4555 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4556 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4557 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4558 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4559 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4560 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4561 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4562 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4563 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4564 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4565 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4566 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4567 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4568 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4569 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4570 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4571 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4572 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4573 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4574 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4575 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4576 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4577 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4578 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4579 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4580 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4581 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4582 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4583 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4584 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4585 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4586 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4587 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4588 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4589 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4590 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4591 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4592 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4593 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4594 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4595 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4596 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4597 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4598 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4599 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4600 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4601 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4602 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4603 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4604 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4605 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4606 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4607 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4608 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4609 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4610 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4611 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4612 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4613 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4614 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4615 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4616 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4617 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4618 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4619 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4620 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4621 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4622 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4623 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4624 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4625 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4626 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4627 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4628 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4629 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4630 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4631 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4632 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4633 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4634 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4635 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4636 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4637 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4638 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4639 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4640 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4641 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4642 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4643 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4644 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4645 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4646 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4647 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4648 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4649 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4650 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4651 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4652 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4653 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4654 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4655 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4656 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4657 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4658 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4659 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4660 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4661 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4662 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4663 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 4664 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 4665 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 4666 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 4667 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 4668 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 4669 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 4670 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 4671 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4672 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4673 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4674 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4675 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4676 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4677 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4678 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4679 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4680 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4681 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4682 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4683 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4684 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4685 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4686 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4687 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4688 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4689 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4690 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4691 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4692 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4693 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4694 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4695 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4696 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4697 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4698 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4699 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4700 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4701 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4702 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4703 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4704 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4705 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4706 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4707 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4708 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4709 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4710 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4711 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4712 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4713 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4714 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4715 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4716 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4717 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4718 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4719 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4720 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4721 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4722 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4723 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4724 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4725 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4726 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4727 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4728 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4729 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4730 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4731 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4732 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4733 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4734 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4735 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4736 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4737 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4738 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4739 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4740 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4741 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4742 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4743 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4744 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4745 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4746 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4747 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4748 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4749 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4750 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4751 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4752 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4753 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4754 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4755 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4756 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4757 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4758 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4759 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4760 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4761 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4762 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4763 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4764 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4765 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4766 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4767 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4768 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4769 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4770 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4771 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4772 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4773 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4774 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4775 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4776 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4777 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4778 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4779 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4780 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4781 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4782 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4783 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4784 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4785 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4786 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4787 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4788 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4789 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4790 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4791 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4792 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4793 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4794 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4795 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4796 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4797 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4798 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4799 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4800 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4801 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4802 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4803 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4804 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4805 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4806 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4807 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4808 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4809 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4810 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4811 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4812 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4813 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4814 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4815 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4816 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4817 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4818 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4819 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4820 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4821 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4822 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4823 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4824 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4825 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4826 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4827 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4828 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4829 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4830 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4831 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 4832 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 4833 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 4834 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 4835 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 4836 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 4837 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 4838 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 4839 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 4840 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 4841 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 4842 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 4843 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 4844 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 4845 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 4846 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 4847 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 4848 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 4849 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 4850 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 4851 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 4852 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 4853 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 4854 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 4855 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 4856 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 4857 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 4858 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 4859 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 4860 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 4861 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 4862 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 4863 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 4864 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 4865 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 4866 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 4867 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 4868 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 4869 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 4870 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 4871 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 4872 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 4873 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 4874 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 4875 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 4876 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 4877 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 4878 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 4879 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 4880 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 4881 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 4882 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 4883 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 4884 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 4885 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 4886 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 4887 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 4888 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 4889 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 4890 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 4891 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 4892 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 4893 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 4894 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 4895 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 4896 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 4897 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 4898 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 4899 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 4900 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 4901 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 4902 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 4903 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 4904 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 4905 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 4906 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 4907 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 4908 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 4909 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 4910 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 4911 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 4912 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 4913 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 4914 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 4915 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 4916 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 4917 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 4918 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 4919 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 4920 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 4921 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 4922 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 4923 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 4924 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 4925 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 4926 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 4927 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 4928 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 4929 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 4930 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 4931 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 4932 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 4933 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 4934 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 4935 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 4936 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 4937 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 4938 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 4939 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 4940 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 4941 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 4942 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 4943 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 4944 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 4945 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 4946 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 4947 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 4948 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 4949 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 4950 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 4951 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 4952 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 4953 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 4954 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 4955 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 4956 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 4957 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 4958 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 4959 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 4960 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 4961 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 4962 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 4963 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 4964 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 4965 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 4966 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 4967 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 4968 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 4969 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 4970 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 4971 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 4972 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 4973 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 4974 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 4975 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 4976 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 4977 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 4978 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 4979 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 4980 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 4981 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 4982 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 4983 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 4984 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 4985 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 4986 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 4987 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 4988 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 4989 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 4990 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 4991 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 4992 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 4993 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 4994 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 4995 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 4996 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 4997 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 4998 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 4999 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5000 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5001 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5002 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5003 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5004 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5005 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5006 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5007 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5008 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5009 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5010 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5011 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5012 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5013 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5014 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5015 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5016 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5017 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5018 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5019 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5020 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5021 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5022 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5023 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5024 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5025 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5026 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5027 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5028 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5029 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5030 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5031 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5032 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5033 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5034 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5035 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5036 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5037 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5038 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5039 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5040 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5041 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5042 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5043 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5044 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5045 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5046 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5047 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5048 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5049 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5050 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5051 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5052 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5053 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5054 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5055 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5056 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5057 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5058 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5059 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5060 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5061 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5062 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5063 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5064 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5065 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5066 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5067 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5068 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5069 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5070 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5071 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5072 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5073 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5074 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5075 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5076 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5077 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5078 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5079 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5080 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5081 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5082 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5083 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5084 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5085 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5086 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5087 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5088 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5089 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5090 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5091 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5092 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5093 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5094 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5095 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5096 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5097 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5098 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5099 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5100 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5101 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5102 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5103 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5104 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5105 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5106 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5107 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5108 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5109 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5110 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5111 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5112 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5113 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5114 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5115 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5116 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5117 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5118 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5119 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5120 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5121 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5122 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5123 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5124 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5125 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5126 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5127 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5128 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5129 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5130 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5131 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5132 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5133 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5134 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5135 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5136 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5137 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5138 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5139 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5140 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5141 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5142 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5143 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5144 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5145 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5146 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5147 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5148 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5149 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5150 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5151 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5152 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5153 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5154 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5155 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5156 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5157 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5158 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5159 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 5160 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 5161 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 5162 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 5163 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 5164 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 5165 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 5166 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 5167 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5168 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5169 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5170 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5171 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5172 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5173 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5174 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5175 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5176 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5177 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5178 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5179 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5180 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5181 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5182 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5183 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5184 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5185 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5186 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5187 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5188 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5189 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5190 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5191 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5192 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5193 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5194 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5195 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5196 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5197 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5198 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5199 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5200 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5201 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5202 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5203 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5204 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5205 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5206 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5207 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5208 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5209 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5210 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5211 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5212 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5213 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5214 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5215 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5216 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5217 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5218 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5219 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5220 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5221 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5222 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5223 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5224 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5225 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5226 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5227 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5228 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5229 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5230 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5231 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5232 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5233 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5234 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5235 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5236 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5237 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5238 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5239 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5240 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5241 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5242 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5243 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5244 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5245 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5246 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5247 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5248 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5249 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5250 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5251 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5252 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5253 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5254 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5255 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5256 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5257 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5258 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5259 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5260 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5261 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5262 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5263 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5264 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5265 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5266 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5267 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5268 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5269 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5270 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5271 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5272 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5273 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5274 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5275 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5276 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5277 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5278 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5279 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5280 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5281 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5282 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5283 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5284 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5285 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5286 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5287 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5288 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5289 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5290 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5291 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5292 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5293 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5294 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5295 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5296 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5297 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5298 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5299 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5300 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5301 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5302 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5303 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5304 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5305 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5306 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5307 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5308 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5309 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5310 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5311 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5312 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5313 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5314 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5315 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5316 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5317 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5318 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5319 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5320 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5321 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5322 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5323 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5324 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5325 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5326 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5327 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 5328 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 5329 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 5330 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 5331 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 5332 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 5333 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 5334 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 5335 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5336 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5337 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5338 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5339 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5340 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5341 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5342 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5343 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5344 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5345 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5346 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5347 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5348 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5349 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5350 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5351 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5352 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5353 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5354 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5355 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5356 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5357 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5358 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5359 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5360 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5361 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5362 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5363 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5364 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5365 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5366 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5367 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5368 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5369 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5370 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5371 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5372 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5373 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5374 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5375 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5376 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5377 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5378 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5379 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5380 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5381 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5382 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5383 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5384 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5385 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5386 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5387 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5388 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5389 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5390 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5391 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5392 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5393 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5394 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5395 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5396 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5397 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5398 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5399 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5400 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5401 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5402 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5403 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5404 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5405 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5406 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5407 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5408 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5409 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5410 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5411 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5412 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5413 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5414 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5415 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5416 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5417 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5418 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5419 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5420 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5421 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5422 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5423 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5424 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5425 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5426 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5427 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5428 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5429 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5430 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5431 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5432 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5433 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5434 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5435 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5436 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5437 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5438 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5439 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5440 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5441 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5442 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5443 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5444 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5445 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5446 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5447 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5448 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5449 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5450 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5451 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5452 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5453 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5454 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5455 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5456 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5457 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5458 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5459 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5460 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5461 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5462 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5463 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5464 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5465 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5466 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5467 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5468 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5469 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5470 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5471 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5472 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5473 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5474 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5475 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5476 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5477 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5478 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5479 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5480 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5481 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5482 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5483 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5484 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5485 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5486 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5487 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5488 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5489 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5490 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5491 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5492 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5493 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5494 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5495 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 5496 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 5497 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 5498 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 5499 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 5500 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 5501 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 5502 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 5503 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5504 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5505 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5506 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5507 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5508 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5509 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5510 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5511 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5512 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5513 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5514 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5515 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5516 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5517 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5518 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5519 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5520 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5521 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5522 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5523 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5524 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5525 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5526 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5527 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5528 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5529 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5530 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5531 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5532 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5533 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5534 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5535 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5536 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5537 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5538 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5539 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5540 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5541 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5542 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5543 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5544 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5545 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5546 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5547 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5548 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5549 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5550 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5551 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5552 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5553 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5554 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5555 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5556 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5557 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5558 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5559 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5560 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5561 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5562 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5563 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5564 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5565 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5566 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5567 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5568 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5569 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5570 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5571 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5572 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5573 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5574 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5575 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5576 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5577 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5578 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5579 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5580 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5581 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5582 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5583 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5584 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5585 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5586 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5587 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5588 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5589 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5590 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5591 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5592 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5593 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5594 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5595 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5596 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5597 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5598 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5599 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5600 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5601 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5602 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5603 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5604 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5605 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5606 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5607 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5608 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5609 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5610 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5611 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5612 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5613 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5614 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5615 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5616 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5617 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5618 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5619 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5620 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5621 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5622 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5623 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5624 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5625 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5626 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5627 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5628 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5629 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5630 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5631 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5632 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5633 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5634 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5635 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5636 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5637 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5638 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5639 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5640 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5641 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5642 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5643 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5644 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5645 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5646 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5647 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5648 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5649 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5650 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5651 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5652 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5653 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5654 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5655 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5656 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5657 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5658 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5659 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5660 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5661 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5662 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5663 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 5664 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 5665 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 5666 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 5667 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 5668 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 5669 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 5670 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 5671 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5672 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5673 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5674 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5675 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5676 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5677 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5678 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5679 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5680 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5681 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5682 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5683 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5684 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5685 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5686 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5687 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5688 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5689 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5690 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5691 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5692 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5693 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5694 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5695 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5696 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5697 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5698 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5699 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5700 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5701 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5702 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5703 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5704 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5705 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5706 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5707 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5708 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5709 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5710 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5711 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5712 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5713 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5714 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5715 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5716 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5717 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5718 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5719 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5720 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5721 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5722 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5723 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5724 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5725 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5726 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5727 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5728 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5729 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5730 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5731 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5732 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5733 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5734 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5735 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5736 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5737 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5738 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5739 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5740 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5741 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5742 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5743 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5744 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5745 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5746 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5747 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5748 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5749 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5750 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5751 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5752 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5753 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5754 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5755 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5756 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5757 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5758 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5759 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5760 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5761 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5762 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5763 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5764 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5765 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5766 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5767 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5768 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5769 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5770 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5771 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5772 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5773 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5774 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5775 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5776 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5777 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5778 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5779 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5780 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5781 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5782 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5783 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5784 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5785 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5786 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5787 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5788 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5789 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5790 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5791 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5792 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5793 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5794 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5795 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5796 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5797 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5798 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5799 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5800 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5801 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5802 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5803 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5804 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5805 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5806 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5807 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5808 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5809 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5810 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5811 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5812 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5813 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5814 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5815 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5816 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5817 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5818 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5819 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5820 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5821 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5822 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5823 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5824 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5825 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5826 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5827 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5828 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5829 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5830 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5831 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 5832 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 5833 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 5834 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 5835 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 5836 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 5837 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 5838 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 5839 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 5840 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 5841 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 5842 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 5843 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 5844 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 5845 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 5846 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 5847 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 5848 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 5849 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 5850 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 5851 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 5852 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 5853 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 5854 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 5855 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 5856 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 5857 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 5858 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 5859 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 5860 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 5861 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 5862 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 5863 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 5864 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 5865 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 5866 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 5867 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 5868 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 5869 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 5870 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 5871 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 5872 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 5873 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 5874 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 5875 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 5876 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 5877 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 5878 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 5879 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 5880 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 5881 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 5882 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 5883 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 5884 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 5885 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 5886 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 5887 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 5888 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 5889 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 5890 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 5891 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 5892 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 5893 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 5894 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 5895 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 5896 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 5897 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 5898 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 5899 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 5900 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 5901 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 5902 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 5903 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 5904 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 5905 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 5906 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 5907 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 5908 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 5909 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 5910 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 5911 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 5912 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 5913 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 5914 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 5915 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 5916 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 5917 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 5918 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 5919 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 5920 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 5921 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 5922 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 5923 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 5924 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 5925 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 5926 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 5927 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 5928 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 5929 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 5930 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 5931 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 5932 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 5933 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 5934 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 5935 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 5936 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 5937 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 5938 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 5939 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 5940 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 5941 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 5942 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 5943 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 5944 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 5945 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 5946 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 5947 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 5948 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 5949 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 5950 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 5951 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 5952 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 5953 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 5954 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 5955 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 5956 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 5957 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 5958 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 5959 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 5960 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 5961 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 5962 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 5963 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 5964 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 5965 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 5966 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 5967 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 5968 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 5969 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 5970 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 5971 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 5972 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 5973 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 5974 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 5975 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 5976 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 5977 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 5978 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 5979 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 5980 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 5981 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 5982 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 5983 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 5984 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 5985 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 5986 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 5987 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 5988 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 5989 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 5990 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 5991 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 5992 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 5993 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 5994 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 5995 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 5996 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 5997 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 5998 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 5999 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6000 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6001 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6002 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6003 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6004 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6005 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6006 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6007 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6008 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6009 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6010 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6011 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6012 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6013 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6014 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6015 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6016 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6017 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6018 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6019 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6020 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6021 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6022 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6023 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6024 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6025 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6026 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6027 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6028 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6029 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6030 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6031 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6032 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6033 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6034 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6035 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6036 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6037 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6038 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6039 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6040 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6041 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6042 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6043 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6044 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6045 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6046 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6047 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6048 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6049 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6050 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6051 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6052 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6053 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6054 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6055 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6056 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6057 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6058 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6059 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6060 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6061 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6062 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6063 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6064 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6065 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6066 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6067 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6068 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6069 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6070 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6071 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6072 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6073 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6074 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6075 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6076 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6077 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6078 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6079 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6080 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6081 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6082 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6083 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6084 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6085 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6086 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6087 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6088 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6089 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6090 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6091 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6092 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6093 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6094 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6095 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6096 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6097 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6098 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6099 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6100 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6101 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6102 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6103 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6104 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6105 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6106 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6107 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6108 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6109 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6110 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6111 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6112 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6113 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6114 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6115 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6116 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6117 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6118 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6119 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6120 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6121 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6122 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6123 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6124 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6125 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6126 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6127 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6128 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6129 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6130 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6131 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6132 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6133 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6134 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6135 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6136 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6137 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6138 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6139 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6140 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6141 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6142 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6143 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6144 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6145 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6146 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6147 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6148 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6149 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6150 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6151 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6152 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6153 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6154 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6155 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6156 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6157 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6158 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6159 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 6160 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 6161 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 6162 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 6163 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 6164 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 6165 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 6166 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 6167 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6168 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6169 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6170 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6171 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6172 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6173 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6174 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6175 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6176 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6177 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6178 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6179 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6180 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6181 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6182 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6183 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6184 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6185 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6186 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6187 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6188 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6189 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6190 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6191 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6192 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6193 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6194 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6195 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6196 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6197 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6198 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6199 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6200 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6201 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6202 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6203 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6204 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6205 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6206 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6207 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6208 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6209 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6210 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6211 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6212 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6213 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6214 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6215 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6216 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6217 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6218 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6219 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6220 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6221 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6222 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6223 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6224 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6225 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6226 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6227 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6228 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6229 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6230 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6231 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6232 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6233 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6234 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6235 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6236 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6237 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6238 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6239 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6240 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6241 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6242 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6243 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6244 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6245 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6246 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6247 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6248 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6249 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6250 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6251 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6252 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6253 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6254 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6255 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6256 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6257 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6258 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6259 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6260 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6261 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6262 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6263 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6264 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6265 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6266 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6267 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6268 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6269 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6270 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6271 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6272 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6273 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6274 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6275 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6276 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6277 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6278 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6279 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6280 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6281 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6282 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6283 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6284 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6285 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6286 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6287 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6288 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6289 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6290 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6291 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6292 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6293 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6294 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6295 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6296 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6297 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6298 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6299 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6300 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6301 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6302 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6303 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6304 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6305 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6306 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6307 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6308 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6309 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6310 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6311 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6312 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6313 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6314 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6315 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6316 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6317 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6318 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6319 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6320 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6321 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6322 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6323 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6324 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6325 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6326 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6327 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 6328 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 6329 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 6330 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 6331 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 6332 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 6333 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 6334 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 6335 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6336 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6337 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6338 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6339 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6340 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6341 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6342 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6343 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6344 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6345 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6346 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6347 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6348 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6349 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6350 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6351 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6352 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6353 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6354 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6355 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6356 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6357 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6358 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6359 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6360 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6361 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6362 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6363 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6364 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6365 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6366 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6367 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6368 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6369 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6370 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6371 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6372 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6373 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6374 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6375 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6376 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6377 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6378 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6379 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6380 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6381 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6382 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6383 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6384 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6385 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6386 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6387 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6388 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6389 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6390 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6391 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6392 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6393 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6394 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6395 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6396 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6397 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6398 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6399 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6400 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6401 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6402 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6403 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6404 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6405 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6406 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6407 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6408 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6409 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6410 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6411 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6412 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6413 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6414 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6415 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6416 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6417 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6418 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6419 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6420 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6421 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6422 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6423 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6424 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6425 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6426 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6427 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6428 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6429 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6430 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6431 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6432 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6433 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6434 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6435 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6436 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6437 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6438 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6439 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6440 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6441 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6442 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6443 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6444 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6445 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6446 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6447 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6448 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6449 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6450 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6451 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6452 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6453 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6454 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6455 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6456 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6457 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6458 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6459 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6460 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6461 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6462 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6463 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6464 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6465 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6466 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6467 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6468 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6469 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6470 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6471 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6472 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6473 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6474 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6475 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6476 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6477 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6478 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6479 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6480 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6481 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6482 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6483 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6484 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6485 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6486 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6487 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6488 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6489 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6490 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6491 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6492 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6493 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6494 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6495 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 6496 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 6497 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 6498 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 6499 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 6500 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 6501 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 6502 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 6503 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6504 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6505 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6506 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6507 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6508 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6509 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6510 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6511 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6512 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6513 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6514 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6515 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6516 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6517 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6518 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6519 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6520 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6521 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6522 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6523 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6524 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6525 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6526 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6527 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6528 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6529 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6530 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6531 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6532 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6533 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6534 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6535 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6536 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6537 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6538 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6539 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6540 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6541 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6542 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6543 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6544 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6545 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6546 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6547 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6548 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6549 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6550 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6551 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6552 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6553 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6554 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6555 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6556 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6557 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6558 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6559 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6560 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6561 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6562 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6563 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6564 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6565 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6566 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6567 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6568 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6569 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6570 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6571 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6572 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6573 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6574 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6575 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6576 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6577 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6578 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6579 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6580 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6581 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6582 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6583 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6584 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6585 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6586 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6587 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6588 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6589 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6590 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6591 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6592 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6593 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6594 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6595 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6596 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6597 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6598 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6599 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6600 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6601 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6602 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6603 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6604 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6605 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6606 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6607 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6608 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6609 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6610 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6611 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6612 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6613 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6614 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6615 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6616 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6617 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6618 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6619 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6620 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6621 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6622 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6623 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6624 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6625 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6626 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6627 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6628 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6629 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6630 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6631 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6632 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6633 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6634 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6635 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6636 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6637 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6638 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6639 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6640 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6641 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6642 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6643 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6644 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6645 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6646 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6647 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6648 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6649 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6650 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6651 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6652 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6653 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6654 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6655 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6656 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6657 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6658 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6659 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6660 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6661 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6662 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6663 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 6664 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 6665 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 6666 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 6667 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 6668 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 6669 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 6670 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 6671 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6672 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6673 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6674 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6675 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6676 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6677 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6678 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6679 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6680 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6681 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6682 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6683 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6684 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6685 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6686 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6687 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6688 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6689 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6690 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6691 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6692 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6693 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6694 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6695 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6696 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6697 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6698 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6699 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6700 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6701 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6702 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6703 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6704 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6705 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6706 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6707 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6708 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6709 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6710 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6711 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6712 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6713 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6714 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6715 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6716 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6717 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6718 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6719 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6720 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6721 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6722 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6723 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6724 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6725 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6726 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6727 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6728 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6729 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6730 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6731 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6732 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6733 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6734 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6735 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6736 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6737 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6738 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6739 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6740 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6741 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6742 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6743 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6744 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6745 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6746 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6747 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6748 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6749 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6750 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6751 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6752 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6753 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6754 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6755 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6756 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6757 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6758 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6759 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6760 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6761 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6762 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6763 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6764 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6765 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6766 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6767 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6768 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6769 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6770 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6771 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6772 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6773 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6774 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6775 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6776 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6777 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6778 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6779 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6780 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6781 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6782 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6783 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6784 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6785 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6786 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6787 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6788 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6789 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6790 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6791 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6792 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6793 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6794 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6795 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6796 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6797 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6798 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6799 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6800 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6801 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6802 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6803 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6804 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6805 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6806 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6807 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6808 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6809 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6810 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6811 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6812 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6813 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6814 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6815 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6816 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6817 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6818 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6819 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6820 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6821 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6822 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6823 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6824 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6825 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6826 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6827 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6828 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6829 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6830 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6831 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 6832 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 6833 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 6834 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 6835 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 6836 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 6837 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 6838 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 6839 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 6840 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 6841 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 6842 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 6843 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 6844 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 6845 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 6846 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 6847 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 6848 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 6849 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 6850 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 6851 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 6852 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 6853 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 6854 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 6855 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 6856 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 6857 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 6858 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 6859 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 6860 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 6861 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 6862 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 6863 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 6864 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 6865 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 6866 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 6867 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 6868 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 6869 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 6870 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 6871 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 6872 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 6873 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 6874 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 6875 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 6876 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 6877 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 6878 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 6879 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 6880 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 6881 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 6882 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 6883 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 6884 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 6885 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 6886 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 6887 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 6888 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 6889 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 6890 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 6891 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 6892 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 6893 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 6894 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 6895 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 6896 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 6897 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 6898 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 6899 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 6900 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 6901 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 6902 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 6903 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 6904 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 6905 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 6906 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 6907 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 6908 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 6909 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 6910 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 6911 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 6912 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 6913 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 6914 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 6915 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 6916 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 6917 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 6918 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 6919 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 6920 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 6921 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 6922 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 6923 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 6924 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 6925 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 6926 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 6927 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 6928 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 6929 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 6930 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 6931 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 6932 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 6933 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 6934 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 6935 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 6936 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 6937 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 6938 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 6939 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 6940 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 6941 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 6942 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 6943 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 6944 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 6945 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 6946 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 6947 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 6948 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 6949 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 6950 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 6951 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 6952 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 6953 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 6954 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 6955 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 6956 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 6957 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 6958 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 6959 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 6960 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 6961 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 6962 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 6963 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 6964 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 6965 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 6966 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 6967 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 6968 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 6969 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 6970 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 6971 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 6972 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 6973 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 6974 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 6975 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 6976 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 6977 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 6978 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 6979 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 6980 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 6981 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 6982 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 6983 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 6984 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 6985 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 6986 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 6987 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 6988 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 6989 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 6990 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 6991 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 6992 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 6993 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 6994 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 6995 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 6996 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 6997 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 6998 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 6999 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7000 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7001 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7002 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7003 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7004 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7005 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7006 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7007 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7008 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7009 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7010 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7011 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7012 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7013 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7014 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7015 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7016 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7017 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7018 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7019 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7020 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7021 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7022 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7023 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7024 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7025 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7026 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7027 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7028 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7029 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7030 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7031 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7032 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7033 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7034 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7035 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7036 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7037 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7038 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7039 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7040 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7041 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7042 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7043 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7044 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7045 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7046 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7047 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7048 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7049 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7050 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7051 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7052 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7053 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7054 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7055 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7056 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7057 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7058 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7059 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7060 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7061 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7062 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7063 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7064 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7065 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7066 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7067 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7068 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7069 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7070 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7071 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7072 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7073 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7074 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7075 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7076 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7077 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7078 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7079 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7080 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7081 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7082 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7083 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7084 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7085 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7086 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7087 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7088 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7089 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7090 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7091 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7092 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7093 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7094 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7095 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7096 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7097 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7098 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7099 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7100 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7101 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7102 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7103 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7104 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7105 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7106 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7107 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7108 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7109 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7110 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7111 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7112 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7113 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7114 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7115 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7116 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7117 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7118 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7119 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7120 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7121 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7122 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7123 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7124 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7125 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7126 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7127 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7128 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7129 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7130 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7131 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7132 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7133 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7134 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7135 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7136 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7137 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7138 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7139 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7140 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7141 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7142 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7143 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7144 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7145 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7146 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7147 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7148 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7149 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7150 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7151 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7152 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7153 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7154 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7155 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7156 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7157 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7158 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7159 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 7160 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 7161 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 7162 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 7163 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 7164 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 7165 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 7166 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 7167 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7168 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7169 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7170 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7171 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7172 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7173 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7174 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7175 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7176 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7177 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7178 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7179 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7180 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7181 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7182 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7183 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7184 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7185 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7186 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7187 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7188 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7189 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7190 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7191 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7192 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7193 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7194 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7195 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7196 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7197 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7198 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7199 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7200 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7201 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7202 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7203 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7204 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7205 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7206 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7207 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7208 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7209 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7210 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7211 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7212 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7213 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7214 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7215 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7216 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7217 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7218 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7219 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7220 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7221 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7222 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7223 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7224 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7225 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7226 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7227 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7228 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7229 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7230 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7231 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7232 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7233 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7234 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7235 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7236 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7237 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7238 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7239 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7240 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7241 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7242 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7243 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7244 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7245 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7246 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7247 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7248 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7249 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7250 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7251 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7252 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7253 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7254 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7255 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7256 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7257 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7258 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7259 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7260 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7261 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7262 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7263 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7264 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7265 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7266 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7267 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7268 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7269 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7270 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7271 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7272 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7273 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7274 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7275 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7276 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7277 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7278 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7279 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7280 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7281 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7282 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7283 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7284 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7285 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7286 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7287 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7288 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7289 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7290 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7291 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7292 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7293 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7294 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7295 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7296 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7297 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7298 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7299 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7300 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7301 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7302 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7303 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7304 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7305 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7306 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7307 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7308 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7309 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7310 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7311 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7312 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7313 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7314 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7315 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7316 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7317 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7318 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7319 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7320 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7321 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7322 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7323 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7324 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7325 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7326 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7327 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 7328 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 7329 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 7330 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 7331 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 7332 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 7333 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 7334 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 7335 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7336 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7337 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7338 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7339 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7340 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7341 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7342 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7343 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7344 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7345 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7346 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7347 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7348 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7349 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7350 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7351 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7352 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7353 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7354 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7355 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7356 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7357 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7358 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7359 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7360 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7361 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7362 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7363 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7364 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7365 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7366 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7367 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7368 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7369 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7370 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7371 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7372 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7373 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7374 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7375 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7376 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7377 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7378 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7379 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7380 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7381 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7382 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7383 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7384 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7385 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7386 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7387 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7388 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7389 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7390 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7391 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7392 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7393 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7394 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7395 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7396 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7397 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7398 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7399 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7400 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7401 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7402 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7403 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7404 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7405 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7406 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7407 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7408 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7409 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7410 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7411 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7412 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7413 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7414 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7415 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7416 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7417 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7418 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7419 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7420 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7421 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7422 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7423 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7424 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7425 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7426 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7427 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7428 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7429 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7430 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7431 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7432 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7433 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7434 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7435 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7436 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7437 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7438 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7439 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7440 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7441 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7442 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7443 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7444 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7445 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7446 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7447 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7448 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7449 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7450 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7451 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7452 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7453 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7454 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7455 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7456 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7457 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7458 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7459 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7460 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7461 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7462 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7463 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7464 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7465 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7466 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7467 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7468 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7469 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7470 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7471 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7472 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7473 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7474 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7475 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7476 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7477 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7478 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7479 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7480 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7481 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7482 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7483 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7484 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7485 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7486 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7487 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7488 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7489 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7490 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7491 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7492 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7493 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7494 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7495 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 7496 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 7497 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 7498 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 7499 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 7500 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 7501 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 7502 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 7503 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7504 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7505 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7506 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7507 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7508 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7509 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7510 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7511 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7512 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7513 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7514 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7515 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7516 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7517 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7518 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7519 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7520 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7521 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7522 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7523 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7524 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7525 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7526 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7527 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7528 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7529 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7530 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7531 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7532 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7533 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7534 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7535 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7536 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7537 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7538 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7539 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7540 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7541 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7542 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7543 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7544 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7545 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7546 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7547 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7548 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7549 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7550 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7551 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7552 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7553 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7554 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7555 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7556 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7557 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7558 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7559 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7560 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7561 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7562 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7563 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7564 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7565 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7566 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7567 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7568 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7569 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7570 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7571 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7572 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7573 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7574 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7575 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7576 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7577 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7578 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7579 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7580 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7581 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7582 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7583 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7584 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7585 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7586 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7587 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7588 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7589 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7590 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7591 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7592 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7593 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7594 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7595 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7596 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7597 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7598 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7599 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7600 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7601 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7602 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7603 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7604 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7605 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7606 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7607 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7608 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7609 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7610 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7611 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7612 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7613 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7614 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7615 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7616 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7617 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7618 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7619 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7620 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7621 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7622 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7623 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7624 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7625 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7626 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7627 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7628 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7629 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7630 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7631 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7632 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7633 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7634 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7635 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7636 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7637 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7638 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7639 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7640 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7641 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7642 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7643 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7644 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7645 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7646 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7647 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7648 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7649 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7650 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7651 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7652 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7653 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7654 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7655 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7656 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7657 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7658 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7659 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7660 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7661 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7662 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7663 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 7664 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 7665 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 7666 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 7667 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 7668 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 7669 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 7670 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 7671 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7672 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7673 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7674 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7675 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7676 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7677 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7678 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7679 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7680 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7681 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7682 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7683 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7684 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7685 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7686 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7687 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7688 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7689 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7690 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7691 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7692 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7693 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7694 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7695 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7696 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7697 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7698 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7699 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7700 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7701 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7702 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7703 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7704 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7705 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7706 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7707 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7708 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7709 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7710 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7711 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7712 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7713 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7714 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7715 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7716 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7717 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7718 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7719 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7720 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7721 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7722 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7723 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7724 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7725 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7726 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7727 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7728 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7729 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7730 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7731 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7732 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7733 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7734 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7735 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7736 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7737 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7738 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7739 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7740 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7741 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7742 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7743 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7744 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7745 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7746 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7747 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7748 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7749 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7750 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7751 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7752 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7753 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7754 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7755 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7756 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7757 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7758 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7759 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7760 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7761 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7762 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7763 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7764 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7765 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7766 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7767 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7768 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7769 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7770 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7771 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7772 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7773 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7774 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7775 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7776 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7777 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7778 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7779 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7780 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7781 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7782 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7783 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7784 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7785 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7786 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7787 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7788 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7789 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7790 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7791 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7792 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7793 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7794 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7795 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7796 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7797 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7798 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7799 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7800 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7801 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7802 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7803 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7804 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7805 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7806 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7807 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7808 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7809 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7810 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7811 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7812 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7813 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7814 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7815 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7816 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7817 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7818 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7819 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7820 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7821 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7822 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7823 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7824 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7825 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7826 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7827 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7828 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7829 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7830 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7831 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 7832 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 7833 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 7834 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 7835 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 7836 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 7837 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 7838 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 7839 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 7840 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 7841 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 7842 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 7843 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 7844 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 7845 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 7846 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 7847 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 7848 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 7849 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 7850 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 7851 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 7852 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 7853 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 7854 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 7855 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 7856 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 7857 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 7858 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 7859 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 7860 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 7861 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 7862 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 7863 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 7864 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 7865 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 7866 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 7867 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 7868 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 7869 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 7870 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 7871 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 7872 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 7873 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 7874 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 7875 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 7876 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 7877 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 7878 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 7879 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 7880 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 7881 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 7882 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 7883 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 7884 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 7885 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 7886 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 7887 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 7888 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 7889 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 7890 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 7891 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 7892 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 7893 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 7894 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 7895 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 7896 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 7897 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 7898 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 7899 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 7900 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 7901 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 7902 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 7903 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 7904 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 7905 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 7906 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 7907 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 7908 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 7909 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 7910 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 7911 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 7912 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 7913 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 7914 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 7915 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 7916 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 7917 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 7918 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 7919 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 7920 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 7921 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 7922 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 7923 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 7924 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 7925 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 7926 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 7927 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 7928 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 7929 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 7930 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 7931 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 7932 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 7933 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 7934 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 7935 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 7936 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 7937 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 7938 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 7939 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 7940 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 7941 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 7942 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 7943 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 7944 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 7945 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 7946 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 7947 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 7948 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 7949 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 7950 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 7951 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 7952 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 7953 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 7954 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 7955 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 7956 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 7957 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 7958 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 7959 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 7960 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 7961 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 7962 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 7963 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 7964 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 7965 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 7966 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 7967 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 7968 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 7969 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 7970 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 7971 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 7972 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 7973 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 7974 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 7975 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 7976 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 7977 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 7978 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 7979 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 7980 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 7981 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 7982 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 7983 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 7984 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 7985 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 7986 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 7987 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 7988 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 7989 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 7990 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 7991 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 7992 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 7993 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 7994 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 7995 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 7996 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 7997 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 7998 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 7999 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 8000 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 8001 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 8002 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 8003 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 8004 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 8005 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 8006 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 8007 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 8008 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 8009 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 8010 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 8011 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 8012 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 8013 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 8014 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 8015 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 8016 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 8017 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 8018 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 8019 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 8020 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 8021 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 8022 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 8023 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 8024 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 8025 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 8026 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 8027 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 8028 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 8029 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 8030 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 8031 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 8032 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 8033 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 8034 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 8035 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 8036 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 8037 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 8038 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 8039 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 8040 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 8041 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 8042 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 8043 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 8044 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 8045 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 8046 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 8047 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 8048 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 8049 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 8050 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 8051 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 8052 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 8053 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 8054 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 8055 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 8056 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 8057 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 8058 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 8059 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 8060 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 8061 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 8062 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 8063 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 8064 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 8065 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 8066 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 8067 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 8068 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 8069 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 8070 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 8071 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 8072 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 8073 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 8074 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 8075 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 8076 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 8077 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 8078 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 8079 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 8080 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 8081 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 8082 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 8083 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 8084 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 8085 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 8086 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 8087 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 8088 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 8089 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 8090 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 8091 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 8092 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 8093 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 8094 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 8095 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 8096 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 8097 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 8098 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 8099 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 8100 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 8101 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 8102 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 8103 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 8104 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 8105 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 8106 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 8107 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 8108 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 8109 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 8110 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 8111 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 8112 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 8113 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 8114 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 8115 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 8116 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 8117 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 8118 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 8119 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 8120 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 8121 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 8122 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 8123 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 8124 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 8125 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 8126 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 8127 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 8128 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 8129 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 8130 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 8131 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 8132 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 8133 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 8134 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 8135 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 8136 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 8137 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 8138 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 8139 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 8140 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 8141 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 8142 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 8143 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 8144 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 8145 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 8146 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 8147 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 8148 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 8149 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 8150 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 8151 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 8152 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 8153 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 8154 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 8155 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 8156 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 8157 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 8158 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 8159 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 8160 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 8161 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 8162 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 8163 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 8164 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 8165 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 8166 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 8167 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 8168 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 8169 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 8170 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 8171 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 8172 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 8173 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 8174 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 8175 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 8176 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 8177 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 8178 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 8179 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 8180 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 8181 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 8182 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 8183 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 8184 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 8185 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 8186 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 8187 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 8188 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 8189 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 8190 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 8191 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 8192 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 8193 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 8194 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 8195 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 8196 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 8197 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 8198 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 8199 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 8200 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 8201 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 8202 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 8203 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 8204 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 8205 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 8206 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 8207 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 8208 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 8209 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 8210 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 8211 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 8212 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 8213 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 8214 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 8215 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 8216 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 8217 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 8218 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 8219 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 8220 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 8221 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 8222 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 8223 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 8224 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 8225 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 8226 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 8227 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 8228 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 8229 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 8230 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 8231 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 8232 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 8233 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 8234 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 8235 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 8236 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 8237 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 8238 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 8239 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 8240 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 8241 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 8242 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 8243 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 8244 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 8245 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 8246 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 8247 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 8248 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 8249 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 8250 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 8251 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 8252 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 8253 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 8254 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 8255 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 8256 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 8257 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 8258 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 8259 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 8260 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 8261 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 8262 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 8263 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 8264 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 8265 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 8266 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 8267 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 8268 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 8269 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 8270 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 8271 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 8272 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 8273 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 8274 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 8275 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 8276 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 8277 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 8278 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 8279 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 8280 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 8281 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 8282 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 8283 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 8284 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 8285 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 8286 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 8287 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 8288 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 8289 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 8290 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 8291 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 8292 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 8293 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 8294 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 8295 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 8296 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 8297 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 8298 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 8299 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 8300 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 8301 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 8302 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 8303 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 8304 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 8305 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 8306 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 8307 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 8308 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 8309 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 8310 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 8311 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 8312 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 8313 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 8314 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 8315 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 8316 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 8317 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 8318 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 8319 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 8320 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 8321 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 8322 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 8323 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 8324 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 8325 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 8326 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 8327 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 8328 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 8329 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 8330 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 8331 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 8332 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 8333 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 8334 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 8335 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 8336 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 8337 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 8338 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 8339 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 8340 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 8341 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 8342 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 8343 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 8344 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 8345 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 8346 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 8347 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 8348 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 8349 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 8350 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 8351 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 8352 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 8353 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 8354 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 8355 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 8356 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 8357 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 8358 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 8359 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 8360 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 8361 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 8362 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 8363 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 8364 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 8365 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 8366 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 8367 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 8368 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 8369 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 8370 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 8371 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 8372 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 8373 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 8374 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 8375 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 8376 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 8377 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 8378 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 8379 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 8380 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 8381 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 8382 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 8383 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 8384 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 8385 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 8386 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 8387 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 8388 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 8389 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 8390 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 8391 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 8392 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 8393 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 8394 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 8395 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 8396 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 8397 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 8398 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 8399 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 8400 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 8401 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 8402 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 8403 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 8404 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 8405 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 8406 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 8407 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 8408 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 8409 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 8410 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 8411 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 8412 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 8413 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 8414 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 8415 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 8416 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 8417 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 8418 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 8419 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 8420 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 8421 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 8422 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 8423 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 8424 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 8425 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 8426 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 8427 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 8428 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 8429 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 8430 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 8431 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 8432 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 8433 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 8434 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 8435 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 8436 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 8437 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 8438 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 8439 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 8440 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 8441 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 8442 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 8443 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 8444 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 8445 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 8446 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 8447 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 8448 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 8449 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 8450 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 8451 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 8452 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 8453 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 8454 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 8455 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 8456 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 8457 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 8458 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 8459 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 8460 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 8461 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 8462 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 8463 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 8464 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 8465 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 8466 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 8467 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 8468 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 8469 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 8470 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 8471 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 8472 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 8473 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 8474 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 8475 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 8476 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 8477 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 8478 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 8479 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 8480 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 8481 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 8482 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 8483 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 8484 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 8485 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 8486 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 8487 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 8488 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 8489 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 8490 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 8491 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 8492 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 8493 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 8494 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 8495 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 8496 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 8497 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 8498 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 8499 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 8500 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 8501 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 8502 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 8503 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 8504 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 8505 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 8506 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 8507 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 8508 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 8509 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 8510 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 8511 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 8512 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 8513 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 8514 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 8515 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 8516 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 8517 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 8518 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 8519 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 8520 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 8521 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 8522 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 8523 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 8524 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 8525 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 8526 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 8527 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 8528 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 8529 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 8530 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 8531 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 8532 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 8533 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 8534 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 8535 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 8536 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 8537 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 8538 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 8539 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 8540 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 8541 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 8542 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 8543 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 8544 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 8545 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 8546 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 8547 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 8548 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 8549 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 8550 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 8551 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 8552 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 8553 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 8554 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 8555 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 8556 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 8557 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 8558 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 8559 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 8560 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 8561 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 8562 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 8563 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 8564 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 8565 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 8566 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 8567 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 8568 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 8569 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 8570 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 8571 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 8572 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 8573 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 8574 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 8575 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 8576 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 8577 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 8578 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 8579 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 8580 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 8581 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 8582 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 8583 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 8584 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 8585 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 8586 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 8587 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 8588 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 8589 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 8590 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 8591 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 8592 | 24 | 8.8145 | 5.2981 | 0.49808
[17 empty] | 8593 | 25 | 8.6857 | 5.2527 | 0.45265
[17 empty] | 8594 | 26 | 8.5616 | 5.2018 | 0.40178
[17 empty] | 8595 | 27 | 8.3978 | 5.1548 | 0.35481
[17 empty] | 8596 | 28 | 8.4608 | 5.1939 | 0.39395
[17 empty] | 8597 | 29 | 8.6887 | 5.3074 | 0.50745
[17 empty] | 8598 | 30 | 8.9358 | 5.4209 | 0.62094
[17 empty] | 8599 | 31 | 9.8433 | 5.8162 | 1.0162
[17 empty] | 8600 | 32 | 10.2921 | 5.9806 | 1.1806
[17 empty] | 8601 | 33 | 11.1246 | 6.2898 | 1.4898
[17 empty] | 8602 | 34 | 12.2985 | 6.7086 | 1.9086
[17 empty] | 8603 | 35 | 15.0635 | 7.7222 | 2.9222
[17 empty] | 8604 | 36 | 16.4613 | 8.2036 | 3.4036
[17 empty] | 8605 | 37 | 16.6634 | 8.2388 | 3.4388
[17 empty] | 8606 | 38 | 16.8255 | 8.274 | 3.474
[17 empty] | 8607 | 39 | 16.4541 | 8.1214 | 3.3214
[17 empty] | 8608 | 40 | 17.8864 | 8.6145 | 3.8145
[17 empty] | 8609 | 41 | 18.6202 | 8.8728 | 4.0728
[17 empty] | 8610 | 42 | 18.5395 | 8.8807 | 4.0807
[17 empty] | 8611 | 43 | 18.9466 | 9.0529 | 4.2529
[17 empty] | 8612 | 44 | 20.3264 | 9.593 | 4.793
[17 empty] | 8613 | 45 | 19.6015 | 9.4051 | 4.6051
[17 empty] | 8614 | 46 | 15.9829 | 8.1214 | 3.3214
[17 empty] | 8615 | 47 | 11.581 | 6.4385 | 1.6385
[17 empty] | 8616 | 48 | 9.8785 | 5.738 | 0.93796
[17 empty] | 8617 | 49 | 9.1705 | 5.4288 | 0.62877
[17 empty] | 8618 | 50 | 8.8166 | 5.284 | 0.48396
[17 empty] | 8619 | 51 | 8.6304 | 5.2331 | 0.43309
[17 empty] | 8620 | 52 | 8.6132 | 5.2487 | 0.44874
[17 empty] | 8621 | 53 | 8.607 | 5.2605 | 0.46048
[17 empty] | 8622 | 54 | 9.2093 | 5.5305 | 0.73053
[17 empty] | 8623 | 55 | 10.4362 | 6.0628 | 1.2628
[17 empty] | 8624 | 56 | 10.7946 | 6.1763 | 1.3763
[17 empty] | 8625 | 57 | 12.0125 | 6.6185 | 1.8185
[17 empty] | 8626 | 58 | 13.4777 | 7.1352 | 2.3352
[17 empty] | 8627 | 59 | 15.173 | 7.6987 | 2.8987
[17 empty] | 8628 | 60 | 16.0781 | 7.9923 | 3.1923
[17 empty] | 8629 | 61 | 17.107 | 8.3093 | 3.5093
[17 empty] | 8630 | 62 | 16.9688 | 8.2153 | 3.4153
[17 empty] | 8631 | 63 | 17.8259 | 8.4932 | 3.6932
[17 empty] | 8632 | 64 | 19.1575 | 8.9355 | 4.1355
[17 empty] | 8633 | 65 | 19.9907 | 9.2251 | 4.4251
[17 empty] | 8634 | 66 | 19.7256 | 9.1781 | 4.3781
[17 empty] | 8635 | 67 | 20.6037 | 9.5225 | 4.7225
[17 empty] | 8636 | 68 | 20.7235 | 9.636 | 4.836
[17 empty] | 8637 | 69 | 19.861 | 9.3973 | 4.5973
[17 empty] | 8638 | 70 | 16.7894 | 8.3249 | 3.5249
[17 empty] | 8639 | 71 | 11.1511 | 6.2154 | 1.4154
[17 empty] | 8640 | 72 | 9.8448 | 5.7089 | 0.90889
[17 empty] | 8641 | 73 | 9.0278 | 5.374 | 0.57398
[17 empty] | 8642 | 74 | 8.7962 | 5.2683 | 0.46831
[17 empty] | 8643 | 75 | 8.6733 | 5.2213 | 0.42134
[17 empty] | 8644 | 76 | 8.5771 | 5.1939 | 0.39395
[17 empty] | 8645 | 77 | 8.7073 | 5.2761 | 0.47614
[17 empty] | 8646 | 78 | 9.1051 | 5.464 | 0.66399
[17 empty] | 8647 | 79 | 10.3192 | 5.9845 | 1.1845
[17 empty] | 8648 | 80 | 10.5976 | 6.0667 | 1.2667
[17 empty] | 8649 | 81 | 12.0866 | 6.6185 | 1.8185
[17 empty] | 8650 | 82 | 13.6011 | 7.1273 | 2.3273
[17 empty] | 8651 | 83 | 14.6939 | 7.4717 | 2.6717
[17 empty] | 8652 | 84 | 16.5119 | 8.051 | 3.251
[17 empty] | 8653 | 85 | 16.279 | 7.9101 | 3.1101
[17 empty] | 8654 | 86 | 15.7532 | 7.6713 | 2.8713
[17 empty] | 8655 | 87 | 16.4539 | 7.8788 | 3.0788
[17 empty] | 8656 | 88 | 17.2851 | 8.1879 | 3.3879
[17 empty] | 8657 | 89 | 19.1459 | 8.8181 | 4.0181
[17 empty] | 8658 | 90 | 18.1939 | 8.5441 | 3.7441
[17 empty] | 8659 | 91 | 18.9801 | 8.865 | 4.065
[17 empty] | 8660 | 92 | 17.9312 | 8.5832 | 3.7832
[17 empty] | 8661 | 93 | 14.5936 | 7.4561 | 2.6561
[17 empty] | 8662 | 94 | 13.35 | 7.0334 | 2.2334
[17 empty] | 8663 | 95 | 11.083 | 6.1646 | 1.3646
[17 empty] | 8664 | 96 | 9.926 | 5.7027 | 0.90273
[17 empty] | 8665 | 97 | 9.8266 | 5.6792 | 0.87925
[17 empty] | 8666 | 98 | 9.4672 | 5.5423 | 0.74227
[17 empty] | 8667 | 99 | 9.3604 | 5.5149 | 0.71487
[17 empty] | 8668 | 100 | 8.9123 | 5.3505 | 0.5505
[17 empty] | 8669 | 101 | 8.8162 | 5.3231 | 0.5231
[17 empty] | 8670 | 102 | 9.0542 | 5.4327 | 0.63268
[17 empty] | 8671 | 103 | 9.8597 | 5.781 | 0.98101
[17 empty] | 8672 | 104 | 10.2224 | 5.8984 | 1.0984
[17 empty] | 8673 | 105 | 10.9219 | 6.1254 | 1.3254
[17 empty] | 8674 | 106 | 12.8108 | 6.8064 | 2.0064
[17 empty] | 8675 | 107 | 13.4234 | 6.9708 | 2.1708
[17 empty] | 8676 | 108 | 15.5576 | 7.7066 | 2.9066
[17 empty] | 8677 | 109 | 14.8472 | 7.3974 | 2.5974
[17 empty] | 8678 | 110 | 14.4399 | 7.186 | 2.386
[17 empty] | 8679 | 111 | 14.252 | 7.1117 | 2.3117
[17 empty] | 8680 | 112 | 14.3354 | 7.143 | 2.343
[17 empty] | 8681 | 113 | 13.8356 | 6.9825 | 2.1825
[17 empty] | 8682 | 114 | 13.9458 | 7.0608 | 2.2608
[17 empty] | 8683 | 115 | 13.287 | 6.8495 | 2.0495
[17 empty] | 8684 | 116 | 14.0296 | 7.1665 | 2.3665
[17 empty] | 8685 | 117 | 13.3506 | 6.9708 | 2.1708
[17 empty] | 8686 | 118 | 12.2965 | 6.6107 | 1.8107
[17 empty] | 8687 | 119 | 10.3847 | 5.8671 | 1.0671
[17 empty] | 8688 | 120 | 9.9991 | 5.7189 | 0.91891
[17 empty] | 8689 | 121 | 9.1179 | 5.3779 | 0.57789
[17 empty] | 8690 | 122 | 8.6028 | 5.1861 | 0.38612
[17 empty] | 8691 | 123 | 8.4758 | 5.147 | 0.34698
[17 empty] | 8692 | 124 | 8.4097 | 5.1313 | 0.33133
[17 empty] | 8693 | 125 | 8.3385 | 5.1118 | 0.31176
[17 empty] | 8694 | 126 | 8.4779 | 5.1783 | 0.37829
[17 empty] | 8695 | 127 | 10.1081 | 5.8828 | 1.0828
[17 empty] | 8696 | 128 | 11.9749 | 6.6107 | 1.8107
[17 empty] | 8697 | 129 | 12.9617 | 6.9277 | 2.1277
[17 empty] | 8698 | 130 | 13.7034 | 7.1312 | 2.3312
[17 empty] | 8699 | 131 | 14.035 | 7.2056 | 2.4056
[17 empty] | 8700 | 132 | 13.8923 | 7.0882 | 2.2882
[17 empty] | 8701 | 133 | 14.8051 | 7.3856 | 2.5856
[17 empty] | 8702 | 134 | 15.3429 | 7.5265 | 2.7265
[17 empty] | 8703 | 135 | 15.3915 | 7.5578 | 2.7578
[17 empty] | 8704 | 136 | 14.2371 | 7.1782 | 2.3782
[17 empty] | 8705 | 137 | 14.0628 | 7.1312 | 2.3312
[17 empty] | 8706 | 138 | 13.9635 | 7.1078 | 2.3078
[17 empty] | 8707 | 139 | 13.4492 | 6.9512 | 2.1512
[17 empty] | 8708 | 140 | 13.3143 | 6.9551 | 2.1551
[17 empty] | 8709 | 141 | 12.3925 | 6.6499 | 1.8499
[17 empty] | 8710 | 142 | 11.544 | 6.3524 | 1.5524
[17 empty] | 8711 | 143 | 10.494 | 5.9415 | 1.1415
[17 empty] | 8712 | 144 | 9.7309 | 5.6558 | 0.85577
[17 empty] | 8713 | 145 | 9.1664 | 5.4366 | 0.6366
[17 empty] | 8714 | 146 | 8.8942 | 5.3388 | 0.53876
[17 empty] | 8715 | 147 | 8.7993 | 5.3074 | 0.50745
[17 empty] | 8716 | 148 | 8.7641 | 5.3035 | 0.50353
[17 empty] | 8717 | 149 | 8.7502 | 5.3035 | 0.50353
[17 empty] | 8718 | 150 | 8.7509 | 5.3074 | 0.50745
[17 empty] | 8719 | 151 | 9.8882 | 5.8123 | 1.0123
[17 empty] | 8720 | 152 | 11.6661 | 6.5246 | 1.7246
[17 empty] | 8721 | 153 | 12.5229 | 6.8103 | 2.0103
[17 empty] | 8722 | 154 | 13.2813 | 7.0725 | 2.2725
[17 empty] | 8723 | 155 | 13.1944 | 7.0021 | 2.2021
[17 empty] | 8724 | 156 | 13.5059 | 7.0804 | 2.2804
[17 empty] | 8725 | 157 | 14.5089 | 7.413 | 2.613
[17 empty] | 8726 | 158 | 15.0322 | 7.5657 | 2.7657
[17 empty] | 8727 | 159 | 15.452 | 7.6909 | 2.8909
[17 empty] | 8728 | 160 | 15.2978 | 7.6322 | 2.8322
[17 empty] | 8729 | 161 | 16.2677 | 7.9883 | 3.1883
[17 empty] | 8730 | 162 | 15.5683 | 7.7574 | 2.9574
[17 empty] | 8731 | 163 | 15.9853 | 7.9257 | 3.1257
[17 empty] | 8732 | 164 | 14.1346 | 7.2956 | 2.4956
[17 empty] | 8733 | 165 | 17.9664 | 8.7554 | 3.9554
[17 empty] | 8734 | 166 | 15.252 | 7.8005 | 3.0005
[17 empty] | 8735 | 167 | 10.8706 | 6.1176 | 1.3176
[17 empty] | 8736 | 168 | 10.0671 | 5.8162 | 1.0162
[17 empty] | 8737 | 1 | 8.365 | 5.1352 | 0.33524
[17 empty] | 8738 | 2 | 8.2358 | 5.0844 | 0.28436
[17 empty] | 8739 | 3 | 8.2189 | 5.0804 | 0.28045
[17 empty] | 8740 | 4 | 8.3624 | 5.1431 | 0.34307
[17 empty] | 8741 | 5 | 8.3811 | 5.1509 | 0.3509
[17 empty] | 8742 | 6 | 8.8353 | 5.3505 | 0.5505
[17 empty] | 8743 | 7 | 9.5928 | 5.6871 | 0.88708
[17 empty] | 8744 | 8 | 10.3585 | 6.0002 | 1.2002
[17 empty] | 8745 | 9 | 10.4287 | 5.9884 | 1.1884
[17 empty] | 8746 | 10 | 12.2151 | 6.6968 | 1.8968
[17 empty] | 8747 | 11 | 14.7865 | 7.6674 | 2.8674
[17 empty] | 8748 | 12 | 16.0756 | 8.1175 | 3.3175
[17 empty] | 8749 | 13 | 16.664 | 8.2936 | 3.4936
[17 empty] | 8750 | 14 | 16.4163 | 8.1919 | 3.3919
[17 empty] | 8751 | 15 | 16.3531 | 8.1488 | 3.3488
[17 empty] | 8752 | 16 | 17.9305 | 8.7006 | 3.9006
[17 empty] | 8753 | 17 | 19.6649 | 9.319 | 4.519
[17 empty] | 8754 | 18 | 19.2128 | 9.2055 | 4.4055
[17 empty] | 8755 | 19 | 19.8464 | 9.4521 | 4.6521
[17 empty] | 8756 | 20 | 19.593 | 9.4208 | 4.6208
[17 empty] | 8757 | 21 | 20.2227 | 9.6869 | 4.8869
[17 empty] | 8758 | 22 | 15.1149 | 7.8396 | 3.0396
[17 empty] | 8759 | 23 | 10.6803 | 6.0784 | 1.2784
[17 empty] | 8760 | 24 | 8.8145 | 5.2981 | 0.49808

## DC_2016
Hour | Server | Non-server | Total | Unit: MW | PUE | PUE-Max | Hour-year | Hour-week | Total (MWh) | Server (MWh)
1 | 2.2351 | 1.0774 | 3.3125 |  | 1.424 | 1.4018 | 1 | 1 | 3.3125 | 2.2351
2 | 2.1539 | 1.0468 | 3.2007 |  |  |  | 2 | 2 | 3.2007 | 2.1539
3 | 2.1476 | 1.0444 | 3.1921 |  | Server-Max | Total-Max | 3 | 3 | 3.1921 | 2.1476
4 | 2.2476 | 1.0821 | 3.3297 |  | 9.5002 | 13.3172 | 4 | 4 | 3.3297 | 2.2476
5 | 2.2601 | 1.0868 | 3.3469 |  |  |  | 5 | 5 | 3.3469 | 2.2601
6 | 2.5787 | 1.207 | 3.7857 |  | Assumed max utilization rate (UR) |  | 6 | 6 | 3.7857 | 2.5787
7 | 3.1159 | 1.4096 | 4.5255 |  | 65% |  | 7 | 7 | 4.5255 | 3.1159
8 | 3.6157 | 1.598 | 5.2137 |  |  |  | 8 | 8 | 5.2137 | 3.6157
9 | 3.5969 | 1.5909 | 5.1879 |  | Servers energy at max UR | Total energy at max UR | 9 | 9 | 5.1879 | 3.5969
10 | 4.7276 | 2.0173 | 6.7449 |  | 7.095 | 10.005 | 10 | 10 | 6.7449 | 4.7276
11 | 6.2768 | 2.6015 | 8.8783 |  |  |  | 11 | 11 | 8.8783 | 6.2768
12 | 6.9952 | 2.8724 | 9.8676 |  | Non-server power linear model scaling factor |  | 12 | 12 | 9.8676 | 6.9952
13 | 7.2763 | 2.9784 | 10.2547 |  | 0.3435 | (Goal Seek function) | 13 | 13 | 10.2547 | 7.2763
14 | 7.1139 | 2.9171 | 10.031 |  |  |  | 14 | 14 | 10.031 | 7.1139
15 | 7.0452 | 2.8912 | 9.9364 |  |  |  | 15 | 15 | 9.9364 | 7.0452
16 | 7.926 | 3.2233 | 11.1494 |  |  |  | 16 | 16 | 11.1494 | 7.926
17 | 8.913 | 3.5955 | 12.5086 |  |  |  | 17 | 17 | 12.5086 | 8.913
18 | 8.7319 | 3.5272 | 12.2591 |  |  |  | 18 | 18 | 12.2591 | 8.7319
19 | 9.1254 | 3.6756 | 12.801 |  |  |  | 19 | 19 | 12.801 | 9.1254
20 | 9.0755 | 3.6568 | 12.7322 |  |  |  | 20 | 20 | 12.7322 | 9.0755
21 | 9.5002 | 3.8169 | 13.3172 |  |  |  | 21 | 21 | 13.3172 | 9.5002
22 | 6.5517 | 2.7051 | 9.2568 |  |  |  | 22 | 22 | 9.2568 | 6.5517
23 | 3.7406 | 1.6451 | 5.3857 |  |  |  | 23 | 23 | 5.3857 | 3.7406
24 | 2.495 | 1.1754 | 3.6704 |  |  |  | 24 | 24 | 3.6704 | 2.495
25 | 2.4225 | 1.1481 | 3.5706 |  |  |  | 25 | 25 | 3.5706 | 2.4225
26 | 2.3413 | 1.1175 | 3.4588 |  |  |  | 26 | 26 | 3.4588 | 2.3413
27 | 2.2663 | 1.0892 | 3.3555 |  |  |  | 27 | 27 | 3.3555 | 2.2663
28 | 2.3288 | 1.1127 | 3.4416 |  |  |  | 28 | 28 | 3.4416 | 2.3288
29 | 2.51 | 1.1811 | 3.691 |  |  |  | 29 | 29 | 3.691 | 2.51
30 | 2.6911 | 1.2494 | 3.9405 |  |  |  | 30 | 30 | 3.9405 | 2.6911
31 | 3.3221 | 1.4873 | 4.8093 |  |  |  | 31 | 31 | 4.8093 | 3.3221
32 | 3.5844 | 1.5862 | 5.1706 |  |  |  | 32 | 32 | 5.1706 | 3.5844
33 | 4.0779 | 1.7723 | 5.8502 |  |  |  | 33 | 33 | 5.8502 | 4.0779
34 | 4.7464 | 2.0244 | 6.7707 |  |  |  | 34 | 34 | 6.7707 | 4.7464
35 | 6.3643 | 2.6344 | 8.9987 |  |  |  | 35 | 35 | 8.9987 | 6.3643
36 | 7.1327 | 2.9242 | 10.0569 |  |  |  | 36 | 36 | 10.0569 | 7.1327
37 | 7.1889 | 2.9454 | 10.1343 |  |  |  | 37 | 37 | 10.1343 | 7.1889
38 | 7.2451 | 2.9666 | 10.2117 |  |  |  | 38 | 38 | 10.2117 | 7.2451
39 | 7.0015 | 2.8747 | 9.8762 |  |  |  | 39 | 39 | 9.8762 | 7.0015
40 | 7.7886 | 3.1715 | 10.9601 |  |  |  | 40 | 40 | 10.9601 | 7.7886
41 | 8.2009 | 3.327 | 11.5279 |  |  |  | 41 | 41 | 11.5279 | 8.2009
42 | 8.2134 | 3.3317 | 11.5451 |  |  |  | 42 | 42 | 11.5451 | 8.2134
43 | 8.4882 | 3.4353 | 11.9236 |  |  |  | 43 | 43 | 11.9236 | 8.4882
44 | 9.3503 | 3.7604 | 13.1107 |  |  |  | 44 | 44 | 13.1107 | 9.3503
45 | 9.0505 | 3.6473 | 12.6978 |  |  |  | 45 | 45 | 12.6978 | 9.0505
46 | 7.0015 | 2.8747 | 9.8762 |  |  |  | 46 | 46 | 9.8762 | 7.0015
47 | 4.3153 | 1.8618 | 6.1771 |  |  |  | 47 | 47 | 6.1771 | 4.3153
48 | 3.1971 | 1.4402 | 4.6373 |  |  |  | 48 | 48 | 4.6373 | 3.1971
49 | 2.7036 | 1.2541 | 3.9577 |  |  |  | 49 | 49 | 3.9577 | 2.7036
50 | 2.4725 | 1.1669 | 3.6394 |  |  |  | 50 | 50 | 3.6394 | 2.4725
51 | 2.3913 | 1.1363 | 3.5276 |  |  |  | 51 | 51 | 3.5276 | 2.3913
52 | 2.4163 | 1.1457 | 3.562 |  |  |  | 52 | 52 | 3.562 | 2.4163
53 | 2.435 | 1.1528 | 3.5878 |  |  |  | 53 | 53 | 3.5878 | 2.435
54 | 2.866 | 1.3153 | 4.1814 |  |  |  | 54 | 54 | 4.1814 | 2.866
55 | 3.7156 | 1.6357 | 5.3513 |  |  |  | 55 | 55 | 5.3513 | 3.7156
56 | 3.8968 | 1.704 | 5.6008 |  |  |  | 56 | 56 | 5.6008 | 3.8968
57 | 4.6027 | 1.9702 | 6.5729 |  |  |  | 57 | 57 | 6.5729 | 4.6027
58 | 5.4273 | 2.2811 | 7.7084 |  |  |  | 58 | 58 | 7.7084 | 5.4273
59 | 6.3268 | 2.6203 | 8.9471 |  |  |  | 59 | 59 | 8.9471 | 6.3268
60 | 6.7953 | 2.797 | 9.5923 |  |  |  | 60 | 60 | 9.5923 | 6.7953
61 | 7.3013 | 2.9878 | 10.2891 |  |  |  | 61 | 61 | 10.2891 | 7.3013
62 | 7.1514 | 2.9312 | 10.0827 |  |  |  | 62 | 62 | 10.0827 | 7.1514
63 | 7.5949 | 3.0985 | 10.6934 |  |  |  | 63 | 63 | 10.6934 | 7.5949
64 | 8.3008 | 3.3647 | 11.6655 |  |  |  | 64 | 64 | 11.6655 | 8.3008
65 | 8.7631 | 3.539 | 12.3021 |  |  |  | 65 | 65 | 12.3021 | 8.7631
66 | 8.6882 | 3.5107 | 12.1989 |  |  |  | 66 | 66 | 12.1989 | 8.6882
67 | 9.2379 | 3.718 | 12.9559 |  |  |  | 67 | 67 | 12.9559 | 9.2379
68 | 9.419 | 3.7863 | 13.2054 |  |  |  | 68 | 68 | 13.2054 | 9.419
69 | 9.038 | 3.6426 | 12.6806 |  |  |  | 69 | 69 | 12.6806 | 9.038
70 | 7.3263 | 2.9972 | 10.3235 |  |  |  | 70 | 70 | 10.3235 | 7.3263
71 | 3.9592 | 1.7276 | 5.6868 |  |  |  | 71 | 71 | 5.6868 | 3.9592
72 | 3.1507 | 1.4227 | 4.5734 |  |  |  | 72 | 72 | 4.5734 | 3.1507
73 | 2.6162 | 1.2211 | 3.8373 |  |  |  | 73 | 73 | 3.8373 | 2.6162
74 | 2.4475 | 1.1575 | 3.605 |  |  |  | 74 | 74 | 3.605 | 2.4475
75 | 2.3725 | 1.1292 | 3.5018 |  |  |  | 75 | 75 | 3.5018 | 2.3725
76 | 2.3288 | 1.1127 | 3.4416 |  |  |  | 76 | 76 | 3.4416 | 2.3288
77 | 2.46 | 1.1622 | 3.6222 |  |  |  | 77 | 77 | 3.6222 | 2.46
78 | 2.7598 | 1.2753 | 4.0351 |  |  |  | 78 | 78 | 4.0351 | 2.7598
79 | 3.5907 | 1.5886 | 5.1793 |  |  |  | 79 | 79 | 5.1793 | 3.5907
80 | 3.7219 | 1.638 | 5.3599 |  |  |  | 80 | 80 | 5.3599 | 3.7219
81 | 4.6027 | 1.9702 | 6.5729 |  |  |  | 81 | 81 | 6.5729 | 4.6027
82 | 5.4148 | 2.2764 | 7.6912 |  |  |  | 82 | 82 | 7.6912 | 5.4148
83 | 5.9645 | 2.4837 | 8.4482 |  |  |  | 83 | 83 | 8.4482 | 5.9645
84 | 6.889 | 2.8323 | 9.7214 |  |  |  | 84 | 84 | 9.7214 | 6.889
85 | 6.6642 | 2.7475 | 9.4117 |  |  |  | 85 | 85 | 9.4117 | 6.6642
86 | 6.2831 | 2.6038 | 8.8869 |  |  |  | 86 | 86 | 8.8869 | 6.2831
87 | 6.6142 | 2.7287 | 9.3428 |  |  |  | 87 | 87 | 9.3428 | 6.6142
88 | 7.1077 | 2.9148 | 10.0224 |  |  |  | 88 | 88 | 10.0224 | 7.1077
89 | 8.1134 | 3.294 | 11.4074 |  |  |  | 89 | 89 | 11.4074 | 8.1134
90 | 7.6762 | 3.1291 | 10.8053 |  |  |  | 90 | 90 | 10.8053 | 7.6762
91 | 8.1884 | 3.3223 | 11.5107 |  |  |  | 91 | 91 | 11.5107 | 8.1884
92 | 7.7386 | 3.1527 | 10.8913 |  |  |  | 92 | 92 | 10.8913 | 7.7386
93 | 5.9395 | 2.4743 | 8.4138 |  |  |  | 93 | 93 | 8.4138 | 5.9395
94 | 5.2648 | 2.2199 | 7.4847 |  |  |  | 94 | 94 | 7.4847 | 5.2648
95 | 3.878 | 1.6969 | 5.575 |  |  |  | 95 | 95 | 5.575 | 3.878
96 | 3.1409 | 1.419 | 4.5599 |  |  |  | 96 | 96 | 4.5599 | 3.1409
97 | 3.1034 | 1.4048 | 4.5083 |  |  |  | 97 | 97 | 4.5083 | 3.1034
98 | 2.8848 | 1.3224 | 4.2072 |  |  |  | 98 | 98 | 4.2072 | 2.8848
99 | 2.841 | 1.3059 | 4.147 |  |  |  | 99 | 99 | 4.147 | 2.841
100 | 2.5787 | 1.207 | 3.7857 |  |  |  | 100 | 100 | 3.7857 | 2.5787
101 | 2.5349 | 1.1905 | 3.7254 |  |  |  | 101 | 101 | 3.7254 | 2.5349
102 | 2.7099 | 1.2564 | 3.9663 |  |  |  | 102 | 102 | 3.9663 | 2.7099
103 | 3.2658 | 1.4661 | 4.7319 |  |  |  | 103 | 103 | 4.7319 | 3.2658
104 | 3.4532 | 1.5368 | 4.99 |  |  |  | 104 | 104 | 4.99 | 3.4532
105 | 3.8156 | 1.6734 | 5.4889 |  |  |  | 105 | 105 | 5.4889 | 3.8156
106 | 4.9025 | 2.0832 | 6.9858 |  |  |  | 106 | 106 | 6.9858 | 4.9025
107 | 5.1649 | 2.1822 | 7.3471 |  |  |  | 107 | 107 | 7.3471 | 5.1649
108 | 6.3393 | 2.625 | 8.9643 |  |  |  | 108 | 108 | 8.9643 | 6.3393
109 | 5.8458 | 2.4389 | 8.2847 |  |  |  | 109 | 109 | 8.2847 | 5.8458
110 | 5.5085 | 2.3117 | 7.8202 |  |  |  | 110 | 110 | 7.8202 | 5.5085
111 | 5.3898 | 2.267 | 7.6568 |  |  |  | 111 | 111 | 7.6568 | 5.3898
112 | 5.4398 | 2.2858 | 7.7256 |  |  |  | 112 | 112 | 7.7256 | 5.4398
113 | 5.1836 | 2.1892 | 7.3729 |  |  |  | 113 | 113 | 7.3729 | 5.1836
114 | 5.3086 | 2.2364 | 7.5449 |  |  |  | 114 | 114 | 7.5449 | 5.3086
115 | 4.9712 | 2.1092 | 7.0804 |  |  |  | 115 | 115 | 7.0804 | 4.9712
116 | 5.4772 | 2.3 | 7.7772 |  |  |  | 116 | 116 | 7.7772 | 5.4772
117 | 5.1649 | 2.1822 | 7.3471 |  |  |  | 117 | 117 | 7.3471 | 5.1649
118 | 4.5902 | 1.9655 | 6.5556 |  |  |  | 118 | 118 | 6.5556 | 4.5902
119 | 3.4033 | 1.5179 | 4.9212 |  |  |  | 119 | 119 | 4.9212 | 3.4033
120 | 3.1667 | 1.4287 | 4.5954 |  |  |  | 120 | 120 | 4.5954 | 3.1667
121 | 2.6224 | 1.2235 | 3.8459 |  |  |  | 121 | 121 | 3.8459 | 2.6224
122 | 2.3163 | 1.108 | 3.4243 |  |  |  | 122 | 122 | 3.4243 | 2.3163
123 | 2.2538 | 1.0845 | 3.3383 |  |  |  | 123 | 123 | 3.3383 | 2.2538
124 | 2.2289 | 1.0751 | 3.3039 |  |  |  | 124 | 124 | 3.3039 | 2.2289
125 | 2.1976 | 1.0633 | 3.2609 |  |  |  | 125 | 125 | 3.2609 | 2.1976
126 | 2.3038 | 1.1033 | 3.4071 |  |  |  | 126 | 126 | 3.4071 | 2.3038
127 | 3.4283 | 1.5273 | 4.9556 |  |  |  | 127 | 127 | 4.9556 | 3.4283
128 | 4.5902 | 1.9655 | 6.5556 |  |  |  | 128 | 128 | 6.5556 | 4.5902
129 | 5.0962 | 2.1563 | 7.2524 |  |  |  | 129 | 129 | 7.2524 | 5.0962
130 | 5.421 | 2.2788 | 7.6998 |  |  |  | 130 | 130 | 7.6998 | 5.421
131 | 5.5397 | 2.3235 | 7.8632 |  |  |  | 131 | 131 | 7.8632 | 5.5397
132 | 5.3523 | 2.2528 | 7.6051 |  |  |  | 132 | 132 | 7.6051 | 5.3523
133 | 5.8271 | 2.4319 | 8.2589 |  |  |  | 133 | 133 | 8.2589 | 5.8271
134 | 6.052 | 2.5167 | 8.5686 |  |  |  | 134 | 134 | 8.5686 | 6.052
135 | 6.1019 | 2.5355 | 8.6374 |  |  |  | 135 | 135 | 8.6374 | 6.1019
136 | 5.496 | 2.307 | 7.803 |  |  |  | 136 | 136 | 7.803 | 5.496
137 | 5.421 | 2.2788 | 7.6998 |  |  |  | 137 | 137 | 7.6998 | 5.421
138 | 5.3835 | 2.2646 | 7.6482 |  |  |  | 138 | 138 | 7.6482 | 5.3835
139 | 5.1337 | 2.1704 | 7.3041 |  |  |  | 139 | 139 | 7.3041 | 5.1337
140 | 5.1399 | 2.1728 | 7.3127 |  |  |  | 140 | 140 | 7.3127 | 5.1399
141 | 4.6526 | 1.989 | 6.6417 |  |  |  | 141 | 141 | 6.6417 | 4.6526
142 | 4.1779 | 1.81 | 5.9879 |  |  |  | 142 | 142 | 5.9879 | 4.1779
143 | 3.522 | 1.5627 | 5.0846 |  |  |  | 143 | 143 | 5.0846 | 3.522
144 | 3.0659 | 1.3907 | 4.4566 |  |  |  | 144 | 144 | 4.4566 | 3.0659
145 | 2.7161 | 1.2588 | 3.9749 |  |  |  | 145 | 145 | 3.9749 | 2.7161
146 | 2.5599 | 1.1999 | 3.7598 |  |  |  | 146 | 146 | 3.7598 | 2.5599
147 | 2.51 | 1.1811 | 3.691 |  |  |  | 147 | 147 | 3.691 | 2.51
148 | 2.5037 | 1.1787 | 3.6824 |  |  |  | 148 | 148 | 3.6824 | 2.5037
149 | 2.5037 | 1.1787 | 3.6824 |  |  |  | 149 | 149 | 3.6824 | 2.5037
150 | 2.51 | 1.1811 | 3.691 |  |  |  | 150 | 150 | 3.691 | 2.51
151 | 3.3158 | 1.4849 | 4.8007 |  |  |  | 151 | 151 | 4.8007 | 3.3158
152 | 4.4527 | 1.9136 | 6.3664 |  |  |  | 152 | 152 | 6.3664 | 4.4527
153 | 4.9088 | 2.0856 | 6.9944 |  |  |  | 153 | 153 | 6.9944 | 4.9088
154 | 5.3273 | 2.2434 | 7.5707 |  |  |  | 154 | 154 | 7.5707 | 5.3273
155 | 5.2149 | 2.201 | 7.4159 |  |  |  | 155 | 155 | 7.4159 | 5.2149
156 | 5.3398 | 2.2481 | 7.5879 |  |  |  | 156 | 156 | 7.5879 | 5.3398
157 | 5.8708 | 2.4484 | 8.3192 |  |  |  | 157 | 157 | 8.3192 | 5.8708
158 | 6.1144 | 2.5402 | 8.6546 |  |  |  | 158 | 158 | 8.6546 | 6.1144
159 | 6.3143 | 2.6156 | 8.9299 |  |  |  | 159 | 159 | 8.9299 | 6.3143
160 | 6.2206 | 2.5803 | 8.8009 |  |  |  | 160 | 160 | 8.8009 | 6.2206
161 | 6.7891 | 2.7946 | 9.5837 |  |  |  | 161 | 161 | 9.5837 | 6.7891
162 | 6.4205 | 2.6556 | 9.0762 |  |  |  | 162 | 162 | 9.0762 | 6.4205
163 | 6.6891 | 2.7569 | 9.4461 |  |  |  | 163 | 163 | 9.4461 | 6.6891
164 | 5.6834 | 2.3777 | 8.0611 |  |  |  | 164 | 164 | 8.0611 | 5.6834
165 | 8.0135 | 3.2563 | 11.2698 |  |  |  | 165 | 165 | 11.2698 | 8.0135
166 | 6.4892 | 2.6816 | 9.1708 |  |  |  | 166 | 166 | 9.1708 | 6.4892
167 | 3.8031 | 1.6687 | 5.4717 |  |  |  | 167 | 167 | 5.4717 | 3.8031
168 | 3.3221 | 1.4873 | 4.8093 |  |  |  | 168 | 168 | 4.8093 | 3.3221
[7 empty] | 169 | 1 | 3.3125 | 2.2351
[7 empty] | 170 | 2 | 3.2007 | 2.1539
[7 empty] | 171 | 3 | 3.1921 | 2.1476
[7 empty] | 172 | 4 | 3.3297 | 2.2476
[7 empty] | 173 | 5 | 3.3469 | 2.2601
[7 empty] | 174 | 6 | 3.7857 | 2.5787
[7 empty] | 175 | 7 | 4.5255 | 3.1159
[7 empty] | 176 | 8 | 5.2137 | 3.6157
[7 empty] | 177 | 9 | 5.1879 | 3.5969
[7 empty] | 178 | 10 | 6.7449 | 4.7276
[7 empty] | 179 | 11 | 8.8783 | 6.2768
[7 empty] | 180 | 12 | 9.8676 | 6.9952
[7 empty] | 181 | 13 | 10.2547 | 7.2763
[7 empty] | 182 | 14 | 10.031 | 7.1139
[7 empty] | 183 | 15 | 9.9364 | 7.0452
[7 empty] | 184 | 16 | 11.1494 | 7.926
[7 empty] | 185 | 17 | 12.5086 | 8.913
[7 empty] | 186 | 18 | 12.2591 | 8.7319
[7 empty] | 187 | 19 | 12.801 | 9.1254
[7 empty] | 188 | 20 | 12.7322 | 9.0755
[7 empty] | 189 | 21 | 13.3172 | 9.5002
[7 empty] | 190 | 22 | 9.2568 | 6.5517
[7 empty] | 191 | 23 | 5.3857 | 3.7406
[7 empty] | 192 | 24 | 3.6704 | 2.495
[7 empty] | 193 | 25 | 3.5706 | 2.4225
[7 empty] | 194 | 26 | 3.4588 | 2.3413
[7 empty] | 195 | 27 | 3.3555 | 2.2663
[7 empty] | 196 | 28 | 3.4416 | 2.3288
[7 empty] | 197 | 29 | 3.691 | 2.51
[7 empty] | 198 | 30 | 3.9405 | 2.6911
[7 empty] | 199 | 31 | 4.8093 | 3.3221
[7 empty] | 200 | 32 | 5.1706 | 3.5844
[7 empty] | 201 | 33 | 5.8502 | 4.0779
[7 empty] | 202 | 34 | 6.7707 | 4.7464
[7 empty] | 203 | 35 | 8.9987 | 6.3643
[7 empty] | 204 | 36 | 10.0569 | 7.1327
[7 empty] | 205 | 37 | 10.1343 | 7.1889
[7 empty] | 206 | 38 | 10.2117 | 7.2451
[7 empty] | 207 | 39 | 9.8762 | 7.0015
[7 empty] | 208 | 40 | 10.9601 | 7.7886
[7 empty] | 209 | 41 | 11.5279 | 8.2009
[7 empty] | 210 | 42 | 11.5451 | 8.2134
[7 empty] | 211 | 43 | 11.9236 | 8.4882
[7 empty] | 212 | 44 | 13.1107 | 9.3503
[7 empty] | 213 | 45 | 12.6978 | 9.0505
[7 empty] | 214 | 46 | 9.8762 | 7.0015
[7 empty] | 215 | 47 | 6.1771 | 4.3153
[7 empty] | 216 | 48 | 4.6373 | 3.1971
[7 empty] | 217 | 49 | 3.9577 | 2.7036
[7 empty] | 218 | 50 | 3.6394 | 2.4725
[7 empty] | 219 | 51 | 3.5276 | 2.3913
[7 empty] | 220 | 52 | 3.562 | 2.4163
[7 empty] | 221 | 53 | 3.5878 | 2.435
[7 empty] | 222 | 54 | 4.1814 | 2.866
[7 empty] | 223 | 55 | 5.3513 | 3.7156
[7 empty] | 224 | 56 | 5.6008 | 3.8968
[7 empty] | 225 | 57 | 6.5729 | 4.6027
[7 empty] | 226 | 58 | 7.7084 | 5.4273
[7 empty] | 227 | 59 | 8.9471 | 6.3268
[7 empty] | 228 | 60 | 9.5923 | 6.7953
[7 empty] | 229 | 61 | 10.2891 | 7.3013
[7 empty] | 230 | 62 | 10.0827 | 7.1514
[7 empty] | 231 | 63 | 10.6934 | 7.5949
[7 empty] | 232 | 64 | 11.6655 | 8.3008
[7 empty] | 233 | 65 | 12.3021 | 8.7631
[7 empty] | 234 | 66 | 12.1989 | 8.6882
[7 empty] | 235 | 67 | 12.9559 | 9.2379
[7 empty] | 236 | 68 | 13.2054 | 9.419
[7 empty] | 237 | 69 | 12.6806 | 9.038
[7 empty] | 238 | 70 | 10.3235 | 7.3263
[7 empty] | 239 | 71 | 5.6868 | 3.9592
[7 empty] | 240 | 72 | 4.5734 | 3.1507
[7 empty] | 241 | 73 | 3.8373 | 2.6162
[7 empty] | 242 | 74 | 3.605 | 2.4475
[7 empty] | 243 | 75 | 3.5018 | 2.3725
[7 empty] | 244 | 76 | 3.4416 | 2.3288
[7 empty] | 245 | 77 | 3.6222 | 2.46
[7 empty] | 246 | 78 | 4.0351 | 2.7598
[7 empty] | 247 | 79 | 5.1793 | 3.5907
[7 empty] | 248 | 80 | 5.3599 | 3.7219
[7 empty] | 249 | 81 | 6.5729 | 4.6027
[7 empty] | 250 | 82 | 7.6912 | 5.4148
[7 empty] | 251 | 83 | 8.4482 | 5.9645
[7 empty] | 252 | 84 | 9.7214 | 6.889
[7 empty] | 253 | 85 | 9.4117 | 6.6642
[7 empty] | 254 | 86 | 8.8869 | 6.2831
[7 empty] | 255 | 87 | 9.3428 | 6.6142
[7 empty] | 256 | 88 | 10.0224 | 7.1077
[7 empty] | 257 | 89 | 11.4074 | 8.1134
[7 empty] | 258 | 90 | 10.8053 | 7.6762
[7 empty] | 259 | 91 | 11.5107 | 8.1884
[7 empty] | 260 | 92 | 10.8913 | 7.7386
[7 empty] | 261 | 93 | 8.4138 | 5.9395
[7 empty] | 262 | 94 | 7.4847 | 5.2648
[7 empty] | 263 | 95 | 5.575 | 3.878
[7 empty] | 264 | 96 | 4.5599 | 3.1409
[7 empty] | 265 | 97 | 4.5083 | 3.1034
[7 empty] | 266 | 98 | 4.2072 | 2.8848
[7 empty] | 267 | 99 | 4.147 | 2.841
[7 empty] | 268 | 100 | 3.7857 | 2.5787
[7 empty] | 269 | 101 | 3.7254 | 2.5349
[7 empty] | 270 | 102 | 3.9663 | 2.7099
[7 empty] | 271 | 103 | 4.7319 | 3.2658
[7 empty] | 272 | 104 | 4.99 | 3.4532
[7 empty] | 273 | 105 | 5.4889 | 3.8156
[7 empty] | 274 | 106 | 6.9858 | 4.9025
[7 empty] | 275 | 107 | 7.3471 | 5.1649
[7 empty] | 276 | 108 | 8.9643 | 6.3393
[7 empty] | 277 | 109 | 8.2847 | 5.8458
[7 empty] | 278 | 110 | 7.8202 | 5.5085
[7 empty] | 279 | 111 | 7.6568 | 5.3898
[7 empty] | 280 | 112 | 7.7256 | 5.4398
[7 empty] | 281 | 113 | 7.3729 | 5.1836
[7 empty] | 282 | 114 | 7.5449 | 5.3086
[7 empty] | 283 | 115 | 7.0804 | 4.9712
[7 empty] | 284 | 116 | 7.7772 | 5.4772
[7 empty] | 285 | 117 | 7.3471 | 5.1649
[7 empty] | 286 | 118 | 6.5556 | 4.5902
[7 empty] | 287 | 119 | 4.9212 | 3.4033
[7 empty] | 288 | 120 | 4.5954 | 3.1667
[7 empty] | 289 | 121 | 3.8459 | 2.6224
[7 empty] | 290 | 122 | 3.4243 | 2.3163
[7 empty] | 291 | 123 | 3.3383 | 2.2538
[7 empty] | 292 | 124 | 3.3039 | 2.2289
[7 empty] | 293 | 125 | 3.2609 | 2.1976
[7 empty] | 294 | 126 | 3.4071 | 2.3038
[7 empty] | 295 | 127 | 4.9556 | 3.4283
[7 empty] | 296 | 128 | 6.5556 | 4.5902
[7 empty] | 297 | 129 | 7.2524 | 5.0962
[7 empty] | 298 | 130 | 7.6998 | 5.421
[7 empty] | 299 | 131 | 7.8632 | 5.5397
[7 empty] | 300 | 132 | 7.6051 | 5.3523
[7 empty] | 301 | 133 | 8.2589 | 5.8271
[7 empty] | 302 | 134 | 8.5686 | 6.052
[7 empty] | 303 | 135 | 8.6374 | 6.1019
[7 empty] | 304 | 136 | 7.803 | 5.496
[7 empty] | 305 | 137 | 7.6998 | 5.421
[7 empty] | 306 | 138 | 7.6482 | 5.3835
[7 empty] | 307 | 139 | 7.3041 | 5.1337
[7 empty] | 308 | 140 | 7.3127 | 5.1399
[7 empty] | 309 | 141 | 6.6417 | 4.6526
[7 empty] | 310 | 142 | 5.9879 | 4.1779
[7 empty] | 311 | 143 | 5.0846 | 3.522
[7 empty] | 312 | 144 | 4.4566 | 3.0659
[7 empty] | 313 | 145 | 3.9749 | 2.7161
[7 empty] | 314 | 146 | 3.7598 | 2.5599
[7 empty] | 315 | 147 | 3.691 | 2.51
[7 empty] | 316 | 148 | 3.6824 | 2.5037
[7 empty] | 317 | 149 | 3.6824 | 2.5037
[7 empty] | 318 | 150 | 3.691 | 2.51
[7 empty] | 319 | 151 | 4.8007 | 3.3158
[7 empty] | 320 | 152 | 6.3664 | 4.4527
[7 empty] | 321 | 153 | 6.9944 | 4.9088
[7 empty] | 322 | 154 | 7.5707 | 5.3273
[7 empty] | 323 | 155 | 7.4159 | 5.2149
[7 empty] | 324 | 156 | 7.5879 | 5.3398
[7 empty] | 325 | 157 | 8.3192 | 5.8708
[7 empty] | 326 | 158 | 8.6546 | 6.1144
[7 empty] | 327 | 159 | 8.9299 | 6.3143
[7 empty] | 328 | 160 | 8.8009 | 6.2206
[7 empty] | 329 | 161 | 9.5837 | 6.7891
[7 empty] | 330 | 162 | 9.0762 | 6.4205
[7 empty] | 331 | 163 | 9.4461 | 6.6891
[7 empty] | 332 | 164 | 8.0611 | 5.6834
[7 empty] | 333 | 165 | 11.2698 | 8.0135
[7 empty] | 334 | 166 | 9.1708 | 6.4892
[7 empty] | 335 | 167 | 5.4717 | 3.8031
[7 empty] | 336 | 168 | 4.8093 | 3.3221
[7 empty] | 337 | 1 | 3.3125 | 2.2351
[7 empty] | 338 | 2 | 3.2007 | 2.1539
[7 empty] | 339 | 3 | 3.1921 | 2.1476
[7 empty] | 340 | 4 | 3.3297 | 2.2476
[7 empty] | 341 | 5 | 3.3469 | 2.2601
[7 empty] | 342 | 6 | 3.7857 | 2.5787
[7 empty] | 343 | 7 | 4.5255 | 3.1159
[7 empty] | 344 | 8 | 5.2137 | 3.6157
[7 empty] | 345 | 9 | 5.1879 | 3.5969
[7 empty] | 346 | 10 | 6.7449 | 4.7276
[7 empty] | 347 | 11 | 8.8783 | 6.2768
[7 empty] | 348 | 12 | 9.8676 | 6.9952
[7 empty] | 349 | 13 | 10.2547 | 7.2763
[7 empty] | 350 | 14 | 10.031 | 7.1139
[7 empty] | 351 | 15 | 9.9364 | 7.0452
[7 empty] | 352 | 16 | 11.1494 | 7.926
[7 empty] | 353 | 17 | 12.5086 | 8.913
[7 empty] | 354 | 18 | 12.2591 | 8.7319
[7 empty] | 355 | 19 | 12.801 | 9.1254
[7 empty] | 356 | 20 | 12.7322 | 9.0755
[7 empty] | 357 | 21 | 13.3172 | 9.5002
[7 empty] | 358 | 22 | 9.2568 | 6.5517
[7 empty] | 359 | 23 | 5.3857 | 3.7406
[7 empty] | 360 | 24 | 3.6704 | 2.495
[7 empty] | 361 | 25 | 3.5706 | 2.4225
[7 empty] | 362 | 26 | 3.4588 | 2.3413
[7 empty] | 363 | 27 | 3.3555 | 2.2663
[7 empty] | 364 | 28 | 3.4416 | 2.3288
[7 empty] | 365 | 29 | 3.691 | 2.51
[7 empty] | 366 | 30 | 3.9405 | 2.6911
[7 empty] | 367 | 31 | 4.8093 | 3.3221
[7 empty] | 368 | 32 | 5.1706 | 3.5844
[7 empty] | 369 | 33 | 5.8502 | 4.0779
[7 empty] | 370 | 34 | 6.7707 | 4.7464
[7 empty] | 371 | 35 | 8.9987 | 6.3643
[7 empty] | 372 | 36 | 10.0569 | 7.1327
[7 empty] | 373 | 37 | 10.1343 | 7.1889
[7 empty] | 374 | 38 | 10.2117 | 7.2451
[7 empty] | 375 | 39 | 9.8762 | 7.0015
[7 empty] | 376 | 40 | 10.9601 | 7.7886
[7 empty] | 377 | 41 | 11.5279 | 8.2009
[7 empty] | 378 | 42 | 11.5451 | 8.2134
[7 empty] | 379 | 43 | 11.9236 | 8.4882
[7 empty] | 380 | 44 | 13.1107 | 9.3503
[7 empty] | 381 | 45 | 12.6978 | 9.0505
[7 empty] | 382 | 46 | 9.8762 | 7.0015
[7 empty] | 383 | 47 | 6.1771 | 4.3153
[7 empty] | 384 | 48 | 4.6373 | 3.1971
[7 empty] | 385 | 49 | 3.9577 | 2.7036
[7 empty] | 386 | 50 | 3.6394 | 2.4725
[7 empty] | 387 | 51 | 3.5276 | 2.3913
[7 empty] | 388 | 52 | 3.562 | 2.4163
[7 empty] | 389 | 53 | 3.5878 | 2.435
[7 empty] | 390 | 54 | 4.1814 | 2.866
[7 empty] | 391 | 55 | 5.3513 | 3.7156
[7 empty] | 392 | 56 | 5.6008 | 3.8968
[7 empty] | 393 | 57 | 6.5729 | 4.6027
[7 empty] | 394 | 58 | 7.7084 | 5.4273
[7 empty] | 395 | 59 | 8.9471 | 6.3268
[7 empty] | 396 | 60 | 9.5923 | 6.7953
[7 empty] | 397 | 61 | 10.2891 | 7.3013
[7 empty] | 398 | 62 | 10.0827 | 7.1514
[7 empty] | 399 | 63 | 10.6934 | 7.5949
[7 empty] | 400 | 64 | 11.6655 | 8.3008
[7 empty] | 401 | 65 | 12.3021 | 8.7631
[7 empty] | 402 | 66 | 12.1989 | 8.6882
[7 empty] | 403 | 67 | 12.9559 | 9.2379
[7 empty] | 404 | 68 | 13.2054 | 9.419
[7 empty] | 405 | 69 | 12.6806 | 9.038
[7 empty] | 406 | 70 | 10.3235 | 7.3263
[7 empty] | 407 | 71 | 5.6868 | 3.9592
[7 empty] | 408 | 72 | 4.5734 | 3.1507
[7 empty] | 409 | 73 | 3.8373 | 2.6162
[7 empty] | 410 | 74 | 3.605 | 2.4475
[7 empty] | 411 | 75 | 3.5018 | 2.3725
[7 empty] | 412 | 76 | 3.4416 | 2.3288
[7 empty] | 413 | 77 | 3.6222 | 2.46
[7 empty] | 414 | 78 | 4.0351 | 2.7598
[7 empty] | 415 | 79 | 5.1793 | 3.5907
[7 empty] | 416 | 80 | 5.3599 | 3.7219
[7 empty] | 417 | 81 | 6.5729 | 4.6027
[7 empty] | 418 | 82 | 7.6912 | 5.4148
[7 empty] | 419 | 83 | 8.4482 | 5.9645
[7 empty] | 420 | 84 | 9.7214 | 6.889
[7 empty] | 421 | 85 | 9.4117 | 6.6642
[7 empty] | 422 | 86 | 8.8869 | 6.2831
[7 empty] | 423 | 87 | 9.3428 | 6.6142
[7 empty] | 424 | 88 | 10.0224 | 7.1077
[7 empty] | 425 | 89 | 11.4074 | 8.1134
[7 empty] | 426 | 90 | 10.8053 | 7.6762
[7 empty] | 427 | 91 | 11.5107 | 8.1884
[7 empty] | 428 | 92 | 10.8913 | 7.7386
[7 empty] | 429 | 93 | 8.4138 | 5.9395
[7 empty] | 430 | 94 | 7.4847 | 5.2648
[7 empty] | 431 | 95 | 5.575 | 3.878
[7 empty] | 432 | 96 | 4.5599 | 3.1409
[7 empty] | 433 | 97 | 4.5083 | 3.1034
[7 empty] | 434 | 98 | 4.2072 | 2.8848
[7 empty] | 435 | 99 | 4.147 | 2.841
[7 empty] | 436 | 100 | 3.7857 | 2.5787
[7 empty] | 437 | 101 | 3.7254 | 2.5349
[7 empty] | 438 | 102 | 3.9663 | 2.7099
[7 empty] | 439 | 103 | 4.7319 | 3.2658
[7 empty] | 440 | 104 | 4.99 | 3.4532
[7 empty] | 441 | 105 | 5.4889 | 3.8156
[7 empty] | 442 | 106 | 6.9858 | 4.9025
[7 empty] | 443 | 107 | 7.3471 | 5.1649
[7 empty] | 444 | 108 | 8.9643 | 6.3393
[7 empty] | 445 | 109 | 8.2847 | 5.8458
[7 empty] | 446 | 110 | 7.8202 | 5.5085
[7 empty] | 447 | 111 | 7.6568 | 5.3898
[7 empty] | 448 | 112 | 7.7256 | 5.4398
[7 empty] | 449 | 113 | 7.3729 | 5.1836
[7 empty] | 450 | 114 | 7.5449 | 5.3086
[7 empty] | 451 | 115 | 7.0804 | 4.9712
[7 empty] | 452 | 116 | 7.7772 | 5.4772
[7 empty] | 453 | 117 | 7.3471 | 5.1649
[7 empty] | 454 | 118 | 6.5556 | 4.5902
[7 empty] | 455 | 119 | 4.9212 | 3.4033
[7 empty] | 456 | 120 | 4.5954 | 3.1667
[7 empty] | 457 | 121 | 3.8459 | 2.6224
[7 empty] | 458 | 122 | 3.4243 | 2.3163
[7 empty] | 459 | 123 | 3.3383 | 2.2538
[7 empty] | 460 | 124 | 3.3039 | 2.2289
[7 empty] | 461 | 125 | 3.2609 | 2.1976
[7 empty] | 462 | 126 | 3.4071 | 2.3038
[7 empty] | 463 | 127 | 4.9556 | 3.4283
[7 empty] | 464 | 128 | 6.5556 | 4.5902
[7 empty] | 465 | 129 | 7.2524 | 5.0962
[7 empty] | 466 | 130 | 7.6998 | 5.421
[7 empty] | 467 | 131 | 7.8632 | 5.5397
[7 empty] | 468 | 132 | 7.6051 | 5.3523
[7 empty] | 469 | 133 | 8.2589 | 5.8271
[7 empty] | 470 | 134 | 8.5686 | 6.052
[7 empty] | 471 | 135 | 8.6374 | 6.1019
[7 empty] | 472 | 136 | 7.803 | 5.496
[7 empty] | 473 | 137 | 7.6998 | 5.421
[7 empty] | 474 | 138 | 7.6482 | 5.3835
[7 empty] | 475 | 139 | 7.3041 | 5.1337
[7 empty] | 476 | 140 | 7.3127 | 5.1399
[7 empty] | 477 | 141 | 6.6417 | 4.6526
[7 empty] | 478 | 142 | 5.9879 | 4.1779
[7 empty] | 479 | 143 | 5.0846 | 3.522
[7 empty] | 480 | 144 | 4.4566 | 3.0659
[7 empty] | 481 | 145 | 3.9749 | 2.7161
[7 empty] | 482 | 146 | 3.7598 | 2.5599
[7 empty] | 483 | 147 | 3.691 | 2.51
[7 empty] | 484 | 148 | 3.6824 | 2.5037
[7 empty] | 485 | 149 | 3.6824 | 2.5037
[7 empty] | 486 | 150 | 3.691 | 2.51
[7 empty] | 487 | 151 | 4.8007 | 3.3158
[7 empty] | 488 | 152 | 6.3664 | 4.4527
[7 empty] | 489 | 153 | 6.9944 | 4.9088
[7 empty] | 490 | 154 | 7.5707 | 5.3273
[7 empty] | 491 | 155 | 7.4159 | 5.2149
[7 empty] | 492 | 156 | 7.5879 | 5.3398
[7 empty] | 493 | 157 | 8.3192 | 5.8708
[7 empty] | 494 | 158 | 8.6546 | 6.1144
[7 empty] | 495 | 159 | 8.9299 | 6.3143
[7 empty] | 496 | 160 | 8.8009 | 6.2206
[7 empty] | 497 | 161 | 9.5837 | 6.7891
[7 empty] | 498 | 162 | 9.0762 | 6.4205
[7 empty] | 499 | 163 | 9.4461 | 6.6891
[7 empty] | 500 | 164 | 8.0611 | 5.6834
[7 empty] | 501 | 165 | 11.2698 | 8.0135
[7 empty] | 502 | 166 | 9.1708 | 6.4892
[7 empty] | 503 | 167 | 5.4717 | 3.8031
[7 empty] | 504 | 168 | 4.8093 | 3.3221
[7 empty] | 505 | 1 | 3.3125 | 2.2351
[7 empty] | 506 | 2 | 3.2007 | 2.1539
[7 empty] | 507 | 3 | 3.1921 | 2.1476
[7 empty] | 508 | 4 | 3.3297 | 2.2476
[7 empty] | 509 | 5 | 3.3469 | 2.2601
[7 empty] | 510 | 6 | 3.7857 | 2.5787
[7 empty] | 511 | 7 | 4.5255 | 3.1159
[7 empty] | 512 | 8 | 5.2137 | 3.6157
[7 empty] | 513 | 9 | 5.1879 | 3.5969
[7 empty] | 514 | 10 | 6.7449 | 4.7276
[7 empty] | 515 | 11 | 8.8783 | 6.2768
[7 empty] | 516 | 12 | 9.8676 | 6.9952
[7 empty] | 517 | 13 | 10.2547 | 7.2763
[7 empty] | 518 | 14 | 10.031 | 7.1139
[7 empty] | 519 | 15 | 9.9364 | 7.0452
[7 empty] | 520 | 16 | 11.1494 | 7.926
[7 empty] | 521 | 17 | 12.5086 | 8.913
[7 empty] | 522 | 18 | 12.2591 | 8.7319
[7 empty] | 523 | 19 | 12.801 | 9.1254
[7 empty] | 524 | 20 | 12.7322 | 9.0755
[7 empty] | 525 | 21 | 13.3172 | 9.5002
[7 empty] | 526 | 22 | 9.2568 | 6.5517
[7 empty] | 527 | 23 | 5.3857 | 3.7406
[7 empty] | 528 | 24 | 3.6704 | 2.495
[7 empty] | 529 | 25 | 3.5706 | 2.4225
[7 empty] | 530 | 26 | 3.4588 | 2.3413
[7 empty] | 531 | 27 | 3.3555 | 2.2663
[7 empty] | 532 | 28 | 3.4416 | 2.3288
[7 empty] | 533 | 29 | 3.691 | 2.51
[7 empty] | 534 | 30 | 3.9405 | 2.6911
[7 empty] | 535 | 31 | 4.8093 | 3.3221
[7 empty] | 536 | 32 | 5.1706 | 3.5844
[7 empty] | 537 | 33 | 5.8502 | 4.0779
[7 empty] | 538 | 34 | 6.7707 | 4.7464
[7 empty] | 539 | 35 | 8.9987 | 6.3643
[7 empty] | 540 | 36 | 10.0569 | 7.1327
[7 empty] | 541 | 37 | 10.1343 | 7.1889
[7 empty] | 542 | 38 | 10.2117 | 7.2451
[7 empty] | 543 | 39 | 9.8762 | 7.0015
[7 empty] | 544 | 40 | 10.9601 | 7.7886
[7 empty] | 545 | 41 | 11.5279 | 8.2009
[7 empty] | 546 | 42 | 11.5451 | 8.2134
[7 empty] | 547 | 43 | 11.9236 | 8.4882
[7 empty] | 548 | 44 | 13.1107 | 9.3503
[7 empty] | 549 | 45 | 12.6978 | 9.0505
[7 empty] | 550 | 46 | 9.8762 | 7.0015
[7 empty] | 551 | 47 | 6.1771 | 4.3153
[7 empty] | 552 | 48 | 4.6373 | 3.1971
[7 empty] | 553 | 49 | 3.9577 | 2.7036
[7 empty] | 554 | 50 | 3.6394 | 2.4725
[7 empty] | 555 | 51 | 3.5276 | 2.3913
[7 empty] | 556 | 52 | 3.562 | 2.4163
[7 empty] | 557 | 53 | 3.5878 | 2.435
[7 empty] | 558 | 54 | 4.1814 | 2.866
[7 empty] | 559 | 55 | 5.3513 | 3.7156
[7 empty] | 560 | 56 | 5.6008 | 3.8968
[7 empty] | 561 | 57 | 6.5729 | 4.6027
[7 empty] | 562 | 58 | 7.7084 | 5.4273
[7 empty] | 563 | 59 | 8.9471 | 6.3268
[7 empty] | 564 | 60 | 9.5923 | 6.7953
[7 empty] | 565 | 61 | 10.2891 | 7.3013
[7 empty] | 566 | 62 | 10.0827 | 7.1514
[7 empty] | 567 | 63 | 10.6934 | 7.5949
[7 empty] | 568 | 64 | 11.6655 | 8.3008
[7 empty] | 569 | 65 | 12.3021 | 8.7631
[7 empty] | 570 | 66 | 12.1989 | 8.6882
[7 empty] | 571 | 67 | 12.9559 | 9.2379
[7 empty] | 572 | 68 | 13.2054 | 9.419
[7 empty] | 573 | 69 | 12.6806 | 9.038
[7 empty] | 574 | 70 | 10.3235 | 7.3263
[7 empty] | 575 | 71 | 5.6868 | 3.9592
[7 empty] | 576 | 72 | 4.5734 | 3.1507
[7 empty] | 577 | 73 | 3.8373 | 2.6162
[7 empty] | 578 | 74 | 3.605 | 2.4475
[7 empty] | 579 | 75 | 3.5018 | 2.3725
[7 empty] | 580 | 76 | 3.4416 | 2.3288
[7 empty] | 581 | 77 | 3.6222 | 2.46
[7 empty] | 582 | 78 | 4.0351 | 2.7598
[7 empty] | 583 | 79 | 5.1793 | 3.5907
[7 empty] | 584 | 80 | 5.3599 | 3.7219
[7 empty] | 585 | 81 | 6.5729 | 4.6027
[7 empty] | 586 | 82 | 7.6912 | 5.4148
[7 empty] | 587 | 83 | 8.4482 | 5.9645
[7 empty] | 588 | 84 | 9.7214 | 6.889
[7 empty] | 589 | 85 | 9.4117 | 6.6642
[7 empty] | 590 | 86 | 8.8869 | 6.2831
[7 empty] | 591 | 87 | 9.3428 | 6.6142
[7 empty] | 592 | 88 | 10.0224 | 7.1077
[7 empty] | 593 | 89 | 11.4074 | 8.1134
[7 empty] | 594 | 90 | 10.8053 | 7.6762
[7 empty] | 595 | 91 | 11.5107 | 8.1884
[7 empty] | 596 | 92 | 10.8913 | 7.7386
[7 empty] | 597 | 93 | 8.4138 | 5.9395
[7 empty] | 598 | 94 | 7.4847 | 5.2648
[7 empty] | 599 | 95 | 5.575 | 3.878
[7 empty] | 600 | 96 | 4.5599 | 3.1409
[7 empty] | 601 | 97 | 4.5083 | 3.1034
[7 empty] | 602 | 98 | 4.2072 | 2.8848
[7 empty] | 603 | 99 | 4.147 | 2.841
[7 empty] | 604 | 100 | 3.7857 | 2.5787
[7 empty] | 605 | 101 | 3.7254 | 2.5349
[7 empty] | 606 | 102 | 3.9663 | 2.7099
[7 empty] | 607 | 103 | 4.7319 | 3.2658
[7 empty] | 608 | 104 | 4.99 | 3.4532
[7 empty] | 609 | 105 | 5.4889 | 3.8156
[7 empty] | 610 | 106 | 6.9858 | 4.9025
[7 empty] | 611 | 107 | 7.3471 | 5.1649
[7 empty] | 612 | 108 | 8.9643 | 6.3393
[7 empty] | 613 | 109 | 8.2847 | 5.8458
[7 empty] | 614 | 110 | 7.8202 | 5.5085
[7 empty] | 615 | 111 | 7.6568 | 5.3898
[7 empty] | 616 | 112 | 7.7256 | 5.4398
[7 empty] | 617 | 113 | 7.3729 | 5.1836
[7 empty] | 618 | 114 | 7.5449 | 5.3086
[7 empty] | 619 | 115 | 7.0804 | 4.9712
[7 empty] | 620 | 116 | 7.7772 | 5.4772
[7 empty] | 621 | 117 | 7.3471 | 5.1649
[7 empty] | 622 | 118 | 6.5556 | 4.5902
[7 empty] | 623 | 119 | 4.9212 | 3.4033
[7 empty] | 624 | 120 | 4.5954 | 3.1667
[7 empty] | 625 | 121 | 3.8459 | 2.6224
[7 empty] | 626 | 122 | 3.4243 | 2.3163
[7 empty] | 627 | 123 | 3.3383 | 2.2538
[7 empty] | 628 | 124 | 3.3039 | 2.2289
[7 empty] | 629 | 125 | 3.2609 | 2.1976
[7 empty] | 630 | 126 | 3.4071 | 2.3038
[7 empty] | 631 | 127 | 4.9556 | 3.4283
[7 empty] | 632 | 128 | 6.5556 | 4.5902
[7 empty] | 633 | 129 | 7.2524 | 5.0962
[7 empty] | 634 | 130 | 7.6998 | 5.421
[7 empty] | 635 | 131 | 7.8632 | 5.5397
[7 empty] | 636 | 132 | 7.6051 | 5.3523
[7 empty] | 637 | 133 | 8.2589 | 5.8271
[7 empty] | 638 | 134 | 8.5686 | 6.052
[7 empty] | 639 | 135 | 8.6374 | 6.1019
[7 empty] | 640 | 136 | 7.803 | 5.496
[7 empty] | 641 | 137 | 7.6998 | 5.421
[7 empty] | 642 | 138 | 7.6482 | 5.3835
[7 empty] | 643 | 139 | 7.3041 | 5.1337
[7 empty] | 644 | 140 | 7.3127 | 5.1399
[7 empty] | 645 | 141 | 6.6417 | 4.6526
[7 empty] | 646 | 142 | 5.9879 | 4.1779
[7 empty] | 647 | 143 | 5.0846 | 3.522
[7 empty] | 648 | 144 | 4.4566 | 3.0659
[7 empty] | 649 | 145 | 3.9749 | 2.7161
[7 empty] | 650 | 146 | 3.7598 | 2.5599
[7 empty] | 651 | 147 | 3.691 | 2.51
[7 empty] | 652 | 148 | 3.6824 | 2.5037
[7 empty] | 653 | 149 | 3.6824 | 2.5037
[7 empty] | 654 | 150 | 3.691 | 2.51
[7 empty] | 655 | 151 | 4.8007 | 3.3158
[7 empty] | 656 | 152 | 6.3664 | 4.4527
[7 empty] | 657 | 153 | 6.9944 | 4.9088
[7 empty] | 658 | 154 | 7.5707 | 5.3273
[7 empty] | 659 | 155 | 7.4159 | 5.2149
[7 empty] | 660 | 156 | 7.5879 | 5.3398
[7 empty] | 661 | 157 | 8.3192 | 5.8708
[7 empty] | 662 | 158 | 8.6546 | 6.1144
[7 empty] | 663 | 159 | 8.9299 | 6.3143
[7 empty] | 664 | 160 | 8.8009 | 6.2206
[7 empty] | 665 | 161 | 9.5837 | 6.7891
[7 empty] | 666 | 162 | 9.0762 | 6.4205
[7 empty] | 667 | 163 | 9.4461 | 6.6891
[7 empty] | 668 | 164 | 8.0611 | 5.6834
[7 empty] | 669 | 165 | 11.2698 | 8.0135
[7 empty] | 670 | 166 | 9.1708 | 6.4892
[7 empty] | 671 | 167 | 5.4717 | 3.8031
[7 empty] | 672 | 168 | 4.8093 | 3.3221
[7 empty] | 673 | 1 | 3.3125 | 2.2351
[7 empty] | 674 | 2 | 3.2007 | 2.1539
[7 empty] | 675 | 3 | 3.1921 | 2.1476
[7 empty] | 676 | 4 | 3.3297 | 2.2476
[7 empty] | 677 | 5 | 3.3469 | 2.2601
[7 empty] | 678 | 6 | 3.7857 | 2.5787
[7 empty] | 679 | 7 | 4.5255 | 3.1159
[7 empty] | 680 | 8 | 5.2137 | 3.6157
[7 empty] | 681 | 9 | 5.1879 | 3.5969
[7 empty] | 682 | 10 | 6.7449 | 4.7276
[7 empty] | 683 | 11 | 8.8783 | 6.2768
[7 empty] | 684 | 12 | 9.8676 | 6.9952
[7 empty] | 685 | 13 | 10.2547 | 7.2763
[7 empty] | 686 | 14 | 10.031 | 7.1139
[7 empty] | 687 | 15 | 9.9364 | 7.0452
[7 empty] | 688 | 16 | 11.1494 | 7.926
[7 empty] | 689 | 17 | 12.5086 | 8.913
[7 empty] | 690 | 18 | 12.2591 | 8.7319
[7 empty] | 691 | 19 | 12.801 | 9.1254
[7 empty] | 692 | 20 | 12.7322 | 9.0755
[7 empty] | 693 | 21 | 13.3172 | 9.5002
[7 empty] | 694 | 22 | 9.2568 | 6.5517
[7 empty] | 695 | 23 | 5.3857 | 3.7406
[7 empty] | 696 | 24 | 3.6704 | 2.495
[7 empty] | 697 | 25 | 3.5706 | 2.4225
[7 empty] | 698 | 26 | 3.4588 | 2.3413
[7 empty] | 699 | 27 | 3.3555 | 2.2663
[7 empty] | 700 | 28 | 3.4416 | 2.3288
[7 empty] | 701 | 29 | 3.691 | 2.51
[7 empty] | 702 | 30 | 3.9405 | 2.6911
[7 empty] | 703 | 31 | 4.8093 | 3.3221
[7 empty] | 704 | 32 | 5.1706 | 3.5844
[7 empty] | 705 | 33 | 5.8502 | 4.0779
[7 empty] | 706 | 34 | 6.7707 | 4.7464
[7 empty] | 707 | 35 | 8.9987 | 6.3643
[7 empty] | 708 | 36 | 10.0569 | 7.1327
[7 empty] | 709 | 37 | 10.1343 | 7.1889
[7 empty] | 710 | 38 | 10.2117 | 7.2451
[7 empty] | 711 | 39 | 9.8762 | 7.0015
[7 empty] | 712 | 40 | 10.9601 | 7.7886
[7 empty] | 713 | 41 | 11.5279 | 8.2009
[7 empty] | 714 | 42 | 11.5451 | 8.2134
[7 empty] | 715 | 43 | 11.9236 | 8.4882
[7 empty] | 716 | 44 | 13.1107 | 9.3503
[7 empty] | 717 | 45 | 12.6978 | 9.0505
[7 empty] | 718 | 46 | 9.8762 | 7.0015
[7 empty] | 719 | 47 | 6.1771 | 4.3153
[7 empty] | 720 | 48 | 4.6373 | 3.1971
[7 empty] | 721 | 49 | 3.9577 | 2.7036
[7 empty] | 722 | 50 | 3.6394 | 2.4725
[7 empty] | 723 | 51 | 3.5276 | 2.3913
[7 empty] | 724 | 52 | 3.562 | 2.4163
[7 empty] | 725 | 53 | 3.5878 | 2.435
[7 empty] | 726 | 54 | 4.1814 | 2.866
[7 empty] | 727 | 55 | 5.3513 | 3.7156
[7 empty] | 728 | 56 | 5.6008 | 3.8968
[7 empty] | 729 | 57 | 6.5729 | 4.6027
[7 empty] | 730 | 58 | 7.7084 | 5.4273
[7 empty] | 731 | 59 | 8.9471 | 6.3268
[7 empty] | 732 | 60 | 9.5923 | 6.7953
[7 empty] | 733 | 61 | 10.2891 | 7.3013
[7 empty] | 734 | 62 | 10.0827 | 7.1514
[7 empty] | 735 | 63 | 10.6934 | 7.5949
[7 empty] | 736 | 64 | 11.6655 | 8.3008
[7 empty] | 737 | 65 | 12.3021 | 8.7631
[7 empty] | 738 | 66 | 12.1989 | 8.6882
[7 empty] | 739 | 67 | 12.9559 | 9.2379
[7 empty] | 740 | 68 | 13.2054 | 9.419
[7 empty] | 741 | 69 | 12.6806 | 9.038
[7 empty] | 742 | 70 | 10.3235 | 7.3263
[7 empty] | 743 | 71 | 5.6868 | 3.9592
[7 empty] | 744 | 72 | 4.5734 | 3.1507
[7 empty] | 745 | 73 | 3.8373 | 2.6162
[7 empty] | 746 | 74 | 3.605 | 2.4475
[7 empty] | 747 | 75 | 3.5018 | 2.3725
[7 empty] | 748 | 76 | 3.4416 | 2.3288
[7 empty] | 749 | 77 | 3.6222 | 2.46
[7 empty] | 750 | 78 | 4.0351 | 2.7598
[7 empty] | 751 | 79 | 5.1793 | 3.5907
[7 empty] | 752 | 80 | 5.3599 | 3.7219
[7 empty] | 753 | 81 | 6.5729 | 4.6027
[7 empty] | 754 | 82 | 7.6912 | 5.4148
[7 empty] | 755 | 83 | 8.4482 | 5.9645
[7 empty] | 756 | 84 | 9.7214 | 6.889
[7 empty] | 757 | 85 | 9.4117 | 6.6642
[7 empty] | 758 | 86 | 8.8869 | 6.2831
[7 empty] | 759 | 87 | 9.3428 | 6.6142
[7 empty] | 760 | 88 | 10.0224 | 7.1077
[7 empty] | 761 | 89 | 11.4074 | 8.1134
[7 empty] | 762 | 90 | 10.8053 | 7.6762
[7 empty] | 763 | 91 | 11.5107 | 8.1884
[7 empty] | 764 | 92 | 10.8913 | 7.7386
[7 empty] | 765 | 93 | 8.4138 | 5.9395
[7 empty] | 766 | 94 | 7.4847 | 5.2648
[7 empty] | 767 | 95 | 5.575 | 3.878
[7 empty] | 768 | 96 | 4.5599 | 3.1409
[7 empty] | 769 | 97 | 4.5083 | 3.1034
[7 empty] | 770 | 98 | 4.2072 | 2.8848
[7 empty] | 771 | 99 | 4.147 | 2.841
[7 empty] | 772 | 100 | 3.7857 | 2.5787
[7 empty] | 773 | 101 | 3.7254 | 2.5349
[7 empty] | 774 | 102 | 3.9663 | 2.7099
[7 empty] | 775 | 103 | 4.7319 | 3.2658
[7 empty] | 776 | 104 | 4.99 | 3.4532
[7 empty] | 777 | 105 | 5.4889 | 3.8156
[7 empty] | 778 | 106 | 6.9858 | 4.9025
[7 empty] | 779 | 107 | 7.3471 | 5.1649
[7 empty] | 780 | 108 | 8.9643 | 6.3393
[7 empty] | 781 | 109 | 8.2847 | 5.8458
[7 empty] | 782 | 110 | 7.8202 | 5.5085
[7 empty] | 783 | 111 | 7.6568 | 5.3898
[7 empty] | 784 | 112 | 7.7256 | 5.4398
[7 empty] | 785 | 113 | 7.3729 | 5.1836
[7 empty] | 786 | 114 | 7.5449 | 5.3086
[7 empty] | 787 | 115 | 7.0804 | 4.9712
[7 empty] | 788 | 116 | 7.7772 | 5.4772
[7 empty] | 789 | 117 | 7.3471 | 5.1649
[7 empty] | 790 | 118 | 6.5556 | 4.5902
[7 empty] | 791 | 119 | 4.9212 | 3.4033
[7 empty] | 792 | 120 | 4.5954 | 3.1667
[7 empty] | 793 | 121 | 3.8459 | 2.6224
[7 empty] | 794 | 122 | 3.4243 | 2.3163
[7 empty] | 795 | 123 | 3.3383 | 2.2538
[7 empty] | 796 | 124 | 3.3039 | 2.2289
[7 empty] | 797 | 125 | 3.2609 | 2.1976
[7 empty] | 798 | 126 | 3.4071 | 2.3038
[7 empty] | 799 | 127 | 4.9556 | 3.4283
[7 empty] | 800 | 128 | 6.5556 | 4.5902
[7 empty] | 801 | 129 | 7.2524 | 5.0962
[7 empty] | 802 | 130 | 7.6998 | 5.421
[7 empty] | 803 | 131 | 7.8632 | 5.5397
[7 empty] | 804 | 132 | 7.6051 | 5.3523
[7 empty] | 805 | 133 | 8.2589 | 5.8271
[7 empty] | 806 | 134 | 8.5686 | 6.052
[7 empty] | 807 | 135 | 8.6374 | 6.1019
[7 empty] | 808 | 136 | 7.803 | 5.496
[7 empty] | 809 | 137 | 7.6998 | 5.421
[7 empty] | 810 | 138 | 7.6482 | 5.3835
[7 empty] | 811 | 139 | 7.3041 | 5.1337
[7 empty] | 812 | 140 | 7.3127 | 5.1399
[7 empty] | 813 | 141 | 6.6417 | 4.6526
[7 empty] | 814 | 142 | 5.9879 | 4.1779
[7 empty] | 815 | 143 | 5.0846 | 3.522
[7 empty] | 816 | 144 | 4.4566 | 3.0659
[7 empty] | 817 | 145 | 3.9749 | 2.7161
[7 empty] | 818 | 146 | 3.7598 | 2.5599
[7 empty] | 819 | 147 | 3.691 | 2.51
[7 empty] | 820 | 148 | 3.6824 | 2.5037
[7 empty] | 821 | 149 | 3.6824 | 2.5037
[7 empty] | 822 | 150 | 3.691 | 2.51
[7 empty] | 823 | 151 | 4.8007 | 3.3158
[7 empty] | 824 | 152 | 6.3664 | 4.4527
[7 empty] | 825 | 153 | 6.9944 | 4.9088
[7 empty] | 826 | 154 | 7.5707 | 5.3273
[7 empty] | 827 | 155 | 7.4159 | 5.2149
[7 empty] | 828 | 156 | 7.5879 | 5.3398
[7 empty] | 829 | 157 | 8.3192 | 5.8708
[7 empty] | 830 | 158 | 8.6546 | 6.1144
[7 empty] | 831 | 159 | 8.9299 | 6.3143
[7 empty] | 832 | 160 | 8.8009 | 6.2206
[7 empty] | 833 | 161 | 9.5837 | 6.7891
[7 empty] | 834 | 162 | 9.0762 | 6.4205
[7 empty] | 835 | 163 | 9.4461 | 6.6891
[7 empty] | 836 | 164 | 8.0611 | 5.6834
[7 empty] | 837 | 165 | 11.2698 | 8.0135
[7 empty] | 838 | 166 | 9.1708 | 6.4892
[7 empty] | 839 | 167 | 5.4717 | 3.8031
[7 empty] | 840 | 168 | 4.8093 | 3.3221
[7 empty] | 841 | 1 | 3.3125 | 2.2351
[7 empty] | 842 | 2 | 3.2007 | 2.1539
[7 empty] | 843 | 3 | 3.1921 | 2.1476
[7 empty] | 844 | 4 | 3.3297 | 2.2476
[7 empty] | 845 | 5 | 3.3469 | 2.2601
[7 empty] | 846 | 6 | 3.7857 | 2.5787
[7 empty] | 847 | 7 | 4.5255 | 3.1159
[7 empty] | 848 | 8 | 5.2137 | 3.6157
[7 empty] | 849 | 9 | 5.1879 | 3.5969
[7 empty] | 850 | 10 | 6.7449 | 4.7276
[7 empty] | 851 | 11 | 8.8783 | 6.2768
[7 empty] | 852 | 12 | 9.8676 | 6.9952
[7 empty] | 853 | 13 | 10.2547 | 7.2763
[7 empty] | 854 | 14 | 10.031 | 7.1139
[7 empty] | 855 | 15 | 9.9364 | 7.0452
[7 empty] | 856 | 16 | 11.1494 | 7.926
[7 empty] | 857 | 17 | 12.5086 | 8.913
[7 empty] | 858 | 18 | 12.2591 | 8.7319
[7 empty] | 859 | 19 | 12.801 | 9.1254
[7 empty] | 860 | 20 | 12.7322 | 9.0755
[7 empty] | 861 | 21 | 13.3172 | 9.5002
[7 empty] | 862 | 22 | 9.2568 | 6.5517
[7 empty] | 863 | 23 | 5.3857 | 3.7406
[7 empty] | 864 | 24 | 3.6704 | 2.495
[7 empty] | 865 | 25 | 3.5706 | 2.4225
[7 empty] | 866 | 26 | 3.4588 | 2.3413
[7 empty] | 867 | 27 | 3.3555 | 2.2663
[7 empty] | 868 | 28 | 3.4416 | 2.3288
[7 empty] | 869 | 29 | 3.691 | 2.51
[7 empty] | 870 | 30 | 3.9405 | 2.6911
[7 empty] | 871 | 31 | 4.8093 | 3.3221
[7 empty] | 872 | 32 | 5.1706 | 3.5844
[7 empty] | 873 | 33 | 5.8502 | 4.0779
[7 empty] | 874 | 34 | 6.7707 | 4.7464
[7 empty] | 875 | 35 | 8.9987 | 6.3643
[7 empty] | 876 | 36 | 10.0569 | 7.1327
[7 empty] | 877 | 37 | 10.1343 | 7.1889
[7 empty] | 878 | 38 | 10.2117 | 7.2451
[7 empty] | 879 | 39 | 9.8762 | 7.0015
[7 empty] | 880 | 40 | 10.9601 | 7.7886
[7 empty] | 881 | 41 | 11.5279 | 8.2009
[7 empty] | 882 | 42 | 11.5451 | 8.2134
[7 empty] | 883 | 43 | 11.9236 | 8.4882
[7 empty] | 884 | 44 | 13.1107 | 9.3503
[7 empty] | 885 | 45 | 12.6978 | 9.0505
[7 empty] | 886 | 46 | 9.8762 | 7.0015
[7 empty] | 887 | 47 | 6.1771 | 4.3153
[7 empty] | 888 | 48 | 4.6373 | 3.1971
[7 empty] | 889 | 49 | 3.9577 | 2.7036
[7 empty] | 890 | 50 | 3.6394 | 2.4725
[7 empty] | 891 | 51 | 3.5276 | 2.3913
[7 empty] | 892 | 52 | 3.562 | 2.4163
[7 empty] | 893 | 53 | 3.5878 | 2.435
[7 empty] | 894 | 54 | 4.1814 | 2.866
[7 empty] | 895 | 55 | 5.3513 | 3.7156
[7 empty] | 896 | 56 | 5.6008 | 3.8968
[7 empty] | 897 | 57 | 6.5729 | 4.6027
[7 empty] | 898 | 58 | 7.7084 | 5.4273
[7 empty] | 899 | 59 | 8.9471 | 6.3268
[7 empty] | 900 | 60 | 9.5923 | 6.7953
[7 empty] | 901 | 61 | 10.2891 | 7.3013
[7 empty] | 902 | 62 | 10.0827 | 7.1514
[7 empty] | 903 | 63 | 10.6934 | 7.5949
[7 empty] | 904 | 64 | 11.6655 | 8.3008
[7 empty] | 905 | 65 | 12.3021 | 8.7631
[7 empty] | 906 | 66 | 12.1989 | 8.6882
[7 empty] | 907 | 67 | 12.9559 | 9.2379
[7 empty] | 908 | 68 | 13.2054 | 9.419
[7 empty] | 909 | 69 | 12.6806 | 9.038
[7 empty] | 910 | 70 | 10.3235 | 7.3263
[7 empty] | 911 | 71 | 5.6868 | 3.9592
[7 empty] | 912 | 72 | 4.5734 | 3.1507
[7 empty] | 913 | 73 | 3.8373 | 2.6162
[7 empty] | 914 | 74 | 3.605 | 2.4475
[7 empty] | 915 | 75 | 3.5018 | 2.3725
[7 empty] | 916 | 76 | 3.4416 | 2.3288
[7 empty] | 917 | 77 | 3.6222 | 2.46
[7 empty] | 918 | 78 | 4.0351 | 2.7598
[7 empty] | 919 | 79 | 5.1793 | 3.5907
[7 empty] | 920 | 80 | 5.3599 | 3.7219
[7 empty] | 921 | 81 | 6.5729 | 4.6027
[7 empty] | 922 | 82 | 7.6912 | 5.4148
[7 empty] | 923 | 83 | 8.4482 | 5.9645
[7 empty] | 924 | 84 | 9.7214 | 6.889
[7 empty] | 925 | 85 | 9.4117 | 6.6642
[7 empty] | 926 | 86 | 8.8869 | 6.2831
[7 empty] | 927 | 87 | 9.3428 | 6.6142
[7 empty] | 928 | 88 | 10.0224 | 7.1077
[7 empty] | 929 | 89 | 11.4074 | 8.1134
[7 empty] | 930 | 90 | 10.8053 | 7.6762
[7 empty] | 931 | 91 | 11.5107 | 8.1884
[7 empty] | 932 | 92 | 10.8913 | 7.7386
[7 empty] | 933 | 93 | 8.4138 | 5.9395
[7 empty] | 934 | 94 | 7.4847 | 5.2648
[7 empty] | 935 | 95 | 5.575 | 3.878
[7 empty] | 936 | 96 | 4.5599 | 3.1409
[7 empty] | 937 | 97 | 4.5083 | 3.1034
[7 empty] | 938 | 98 | 4.2072 | 2.8848
[7 empty] | 939 | 99 | 4.147 | 2.841
[7 empty] | 940 | 100 | 3.7857 | 2.5787
[7 empty] | 941 | 101 | 3.7254 | 2.5349
[7 empty] | 942 | 102 | 3.9663 | 2.7099
[7 empty] | 943 | 103 | 4.7319 | 3.2658
[7 empty] | 944 | 104 | 4.99 | 3.4532
[7 empty] | 945 | 105 | 5.4889 | 3.8156
[7 empty] | 946 | 106 | 6.9858 | 4.9025
[7 empty] | 947 | 107 | 7.3471 | 5.1649
[7 empty] | 948 | 108 | 8.9643 | 6.3393
[7 empty] | 949 | 109 | 8.2847 | 5.8458
[7 empty] | 950 | 110 | 7.8202 | 5.5085
[7 empty] | 951 | 111 | 7.6568 | 5.3898
[7 empty] | 952 | 112 | 7.7256 | 5.4398
[7 empty] | 953 | 113 | 7.3729 | 5.1836
[7 empty] | 954 | 114 | 7.5449 | 5.3086
[7 empty] | 955 | 115 | 7.0804 | 4.9712
[7 empty] | 956 | 116 | 7.7772 | 5.4772
[7 empty] | 957 | 117 | 7.3471 | 5.1649
[7 empty] | 958 | 118 | 6.5556 | 4.5902
[7 empty] | 959 | 119 | 4.9212 | 3.4033
[7 empty] | 960 | 120 | 4.5954 | 3.1667
[7 empty] | 961 | 121 | 3.8459 | 2.6224
[7 empty] | 962 | 122 | 3.4243 | 2.3163
[7 empty] | 963 | 123 | 3.3383 | 2.2538
[7 empty] | 964 | 124 | 3.3039 | 2.2289
[7 empty] | 965 | 125 | 3.2609 | 2.1976
[7 empty] | 966 | 126 | 3.4071 | 2.3038
[7 empty] | 967 | 127 | 4.9556 | 3.4283
[7 empty] | 968 | 128 | 6.5556 | 4.5902
[7 empty] | 969 | 129 | 7.2524 | 5.0962
[7 empty] | 970 | 130 | 7.6998 | 5.421
[7 empty] | 971 | 131 | 7.8632 | 5.5397
[7 empty] | 972 | 132 | 7.6051 | 5.3523
[7 empty] | 973 | 133 | 8.2589 | 5.8271
[7 empty] | 974 | 134 | 8.5686 | 6.052
[7 empty] | 975 | 135 | 8.6374 | 6.1019
[7 empty] | 976 | 136 | 7.803 | 5.496
[7 empty] | 977 | 137 | 7.6998 | 5.421
[7 empty] | 978 | 138 | 7.6482 | 5.3835
[7 empty] | 979 | 139 | 7.3041 | 5.1337
[7 empty] | 980 | 140 | 7.3127 | 5.1399
[7 empty] | 981 | 141 | 6.6417 | 4.6526
[7 empty] | 982 | 142 | 5.9879 | 4.1779
[7 empty] | 983 | 143 | 5.0846 | 3.522
[7 empty] | 984 | 144 | 4.4566 | 3.0659
[7 empty] | 985 | 145 | 3.9749 | 2.7161
[7 empty] | 986 | 146 | 3.7598 | 2.5599
[7 empty] | 987 | 147 | 3.691 | 2.51
[7 empty] | 988 | 148 | 3.6824 | 2.5037
[7 empty] | 989 | 149 | 3.6824 | 2.5037
[7 empty] | 990 | 150 | 3.691 | 2.51
[7 empty] | 991 | 151 | 4.8007 | 3.3158
[7 empty] | 992 | 152 | 6.3664 | 4.4527
[7 empty] | 993 | 153 | 6.9944 | 4.9088
[7 empty] | 994 | 154 | 7.5707 | 5.3273
[7 empty] | 995 | 155 | 7.4159 | 5.2149
[7 empty] | 996 | 156 | 7.5879 | 5.3398
[7 empty] | 997 | 157 | 8.3192 | 5.8708
[7 empty] | 998 | 158 | 8.6546 | 6.1144
[7 empty] | 999 | 159 | 8.9299 | 6.3143
[7 empty] | 1000 | 160 | 8.8009 | 6.2206
[7 empty] | 1001 | 161 | 9.5837 | 6.7891
[7 empty] | 1002 | 162 | 9.0762 | 6.4205
[7 empty] | 1003 | 163 | 9.4461 | 6.6891
[7 empty] | 1004 | 164 | 8.0611 | 5.6834
[7 empty] | 1005 | 165 | 11.2698 | 8.0135
[7 empty] | 1006 | 166 | 9.1708 | 6.4892
[7 empty] | 1007 | 167 | 5.4717 | 3.8031
[7 empty] | 1008 | 168 | 4.8093 | 3.3221
[7 empty] | 1009 | 1 | 3.3125 | 2.2351
[7 empty] | 1010 | 2 | 3.2007 | 2.1539
[7 empty] | 1011 | 3 | 3.1921 | 2.1476
[7 empty] | 1012 | 4 | 3.3297 | 2.2476
[7 empty] | 1013 | 5 | 3.3469 | 2.2601
[7 empty] | 1014 | 6 | 3.7857 | 2.5787
[7 empty] | 1015 | 7 | 4.5255 | 3.1159
[7 empty] | 1016 | 8 | 5.2137 | 3.6157
[7 empty] | 1017 | 9 | 5.1879 | 3.5969
[7 empty] | 1018 | 10 | 6.7449 | 4.7276
[7 empty] | 1019 | 11 | 8.8783 | 6.2768
[7 empty] | 1020 | 12 | 9.8676 | 6.9952
[7 empty] | 1021 | 13 | 10.2547 | 7.2763
[7 empty] | 1022 | 14 | 10.031 | 7.1139
[7 empty] | 1023 | 15 | 9.9364 | 7.0452
[7 empty] | 1024 | 16 | 11.1494 | 7.926
[7 empty] | 1025 | 17 | 12.5086 | 8.913
[7 empty] | 1026 | 18 | 12.2591 | 8.7319
[7 empty] | 1027 | 19 | 12.801 | 9.1254
[7 empty] | 1028 | 20 | 12.7322 | 9.0755
[7 empty] | 1029 | 21 | 13.3172 | 9.5002
[7 empty] | 1030 | 22 | 9.2568 | 6.5517
[7 empty] | 1031 | 23 | 5.3857 | 3.7406
[7 empty] | 1032 | 24 | 3.6704 | 2.495
[7 empty] | 1033 | 25 | 3.5706 | 2.4225
[7 empty] | 1034 | 26 | 3.4588 | 2.3413
[7 empty] | 1035 | 27 | 3.3555 | 2.2663
[7 empty] | 1036 | 28 | 3.4416 | 2.3288
[7 empty] | 1037 | 29 | 3.691 | 2.51
[7 empty] | 1038 | 30 | 3.9405 | 2.6911
[7 empty] | 1039 | 31 | 4.8093 | 3.3221
[7 empty] | 1040 | 32 | 5.1706 | 3.5844
[7 empty] | 1041 | 33 | 5.8502 | 4.0779
[7 empty] | 1042 | 34 | 6.7707 | 4.7464
[7 empty] | 1043 | 35 | 8.9987 | 6.3643
[7 empty] | 1044 | 36 | 10.0569 | 7.1327
[7 empty] | 1045 | 37 | 10.1343 | 7.1889
[7 empty] | 1046 | 38 | 10.2117 | 7.2451
[7 empty] | 1047 | 39 | 9.8762 | 7.0015
[7 empty] | 1048 | 40 | 10.9601 | 7.7886
[7 empty] | 1049 | 41 | 11.5279 | 8.2009
[7 empty] | 1050 | 42 | 11.5451 | 8.2134
[7 empty] | 1051 | 43 | 11.9236 | 8.4882
[7 empty] | 1052 | 44 | 13.1107 | 9.3503
[7 empty] | 1053 | 45 | 12.6978 | 9.0505
[7 empty] | 1054 | 46 | 9.8762 | 7.0015
[7 empty] | 1055 | 47 | 6.1771 | 4.3153
[7 empty] | 1056 | 48 | 4.6373 | 3.1971
[7 empty] | 1057 | 49 | 3.9577 | 2.7036
[7 empty] | 1058 | 50 | 3.6394 | 2.4725
[7 empty] | 1059 | 51 | 3.5276 | 2.3913
[7 empty] | 1060 | 52 | 3.562 | 2.4163
[7 empty] | 1061 | 53 | 3.5878 | 2.435
[7 empty] | 1062 | 54 | 4.1814 | 2.866
[7 empty] | 1063 | 55 | 5.3513 | 3.7156
[7 empty] | 1064 | 56 | 5.6008 | 3.8968
[7 empty] | 1065 | 57 | 6.5729 | 4.6027
[7 empty] | 1066 | 58 | 7.7084 | 5.4273
[7 empty] | 1067 | 59 | 8.9471 | 6.3268
[7 empty] | 1068 | 60 | 9.5923 | 6.7953
[7 empty] | 1069 | 61 | 10.2891 | 7.3013
[7 empty] | 1070 | 62 | 10.0827 | 7.1514
[7 empty] | 1071 | 63 | 10.6934 | 7.5949
[7 empty] | 1072 | 64 | 11.6655 | 8.3008
[7 empty] | 1073 | 65 | 12.3021 | 8.7631
[7 empty] | 1074 | 66 | 12.1989 | 8.6882
[7 empty] | 1075 | 67 | 12.9559 | 9.2379
[7 empty] | 1076 | 68 | 13.2054 | 9.419
[7 empty] | 1077 | 69 | 12.6806 | 9.038
[7 empty] | 1078 | 70 | 10.3235 | 7.3263
[7 empty] | 1079 | 71 | 5.6868 | 3.9592
[7 empty] | 1080 | 72 | 4.5734 | 3.1507
[7 empty] | 1081 | 73 | 3.8373 | 2.6162
[7 empty] | 1082 | 74 | 3.605 | 2.4475
[7 empty] | 1083 | 75 | 3.5018 | 2.3725
[7 empty] | 1084 | 76 | 3.4416 | 2.3288
[7 empty] | 1085 | 77 | 3.6222 | 2.46
[7 empty] | 1086 | 78 | 4.0351 | 2.7598
[7 empty] | 1087 | 79 | 5.1793 | 3.5907
[7 empty] | 1088 | 80 | 5.3599 | 3.7219
[7 empty] | 1089 | 81 | 6.5729 | 4.6027
[7 empty] | 1090 | 82 | 7.6912 | 5.4148
[7 empty] | 1091 | 83 | 8.4482 | 5.9645
[7 empty] | 1092 | 84 | 9.7214 | 6.889
[7 empty] | 1093 | 85 | 9.4117 | 6.6642
[7 empty] | 1094 | 86 | 8.8869 | 6.2831
[7 empty] | 1095 | 87 | 9.3428 | 6.6142
[7 empty] | 1096 | 88 | 10.0224 | 7.1077
[7 empty] | 1097 | 89 | 11.4074 | 8.1134
[7 empty] | 1098 | 90 | 10.8053 | 7.6762
[7 empty] | 1099 | 91 | 11.5107 | 8.1884
[7 empty] | 1100 | 92 | 10.8913 | 7.7386
[7 empty] | 1101 | 93 | 8.4138 | 5.9395
[7 empty] | 1102 | 94 | 7.4847 | 5.2648
[7 empty] | 1103 | 95 | 5.575 | 3.878
[7 empty] | 1104 | 96 | 4.5599 | 3.1409
[7 empty] | 1105 | 97 | 4.5083 | 3.1034
[7 empty] | 1106 | 98 | 4.2072 | 2.8848
[7 empty] | 1107 | 99 | 4.147 | 2.841
[7 empty] | 1108 | 100 | 3.7857 | 2.5787
[7 empty] | 1109 | 101 | 3.7254 | 2.5349
[7 empty] | 1110 | 102 | 3.9663 | 2.7099
[7 empty] | 1111 | 103 | 4.7319 | 3.2658
[7 empty] | 1112 | 104 | 4.99 | 3.4532
[7 empty] | 1113 | 105 | 5.4889 | 3.8156
[7 empty] | 1114 | 106 | 6.9858 | 4.9025
[7 empty] | 1115 | 107 | 7.3471 | 5.1649
[7 empty] | 1116 | 108 | 8.9643 | 6.3393
[7 empty] | 1117 | 109 | 8.2847 | 5.8458
[7 empty] | 1118 | 110 | 7.8202 | 5.5085
[7 empty] | 1119 | 111 | 7.6568 | 5.3898
[7 empty] | 1120 | 112 | 7.7256 | 5.4398
[7 empty] | 1121 | 113 | 7.3729 | 5.1836
[7 empty] | 1122 | 114 | 7.5449 | 5.3086
[7 empty] | 1123 | 115 | 7.0804 | 4.9712
[7 empty] | 1124 | 116 | 7.7772 | 5.4772
[7 empty] | 1125 | 117 | 7.3471 | 5.1649
[7 empty] | 1126 | 118 | 6.5556 | 4.5902
[7 empty] | 1127 | 119 | 4.9212 | 3.4033
[7 empty] | 1128 | 120 | 4.5954 | 3.1667
[7 empty] | 1129 | 121 | 3.8459 | 2.6224
[7 empty] | 1130 | 122 | 3.4243 | 2.3163
[7 empty] | 1131 | 123 | 3.3383 | 2.2538
[7 empty] | 1132 | 124 | 3.3039 | 2.2289
[7 empty] | 1133 | 125 | 3.2609 | 2.1976
[7 empty] | 1134 | 126 | 3.4071 | 2.3038
[7 empty] | 1135 | 127 | 4.9556 | 3.4283
[7 empty] | 1136 | 128 | 6.5556 | 4.5902
[7 empty] | 1137 | 129 | 7.2524 | 5.0962
[7 empty] | 1138 | 130 | 7.6998 | 5.421
[7 empty] | 1139 | 131 | 7.8632 | 5.5397
[7 empty] | 1140 | 132 | 7.6051 | 5.3523
[7 empty] | 1141 | 133 | 8.2589 | 5.8271
[7 empty] | 1142 | 134 | 8.5686 | 6.052
[7 empty] | 1143 | 135 | 8.6374 | 6.1019
[7 empty] | 1144 | 136 | 7.803 | 5.496
[7 empty] | 1145 | 137 | 7.6998 | 5.421
[7 empty] | 1146 | 138 | 7.6482 | 5.3835
[7 empty] | 1147 | 139 | 7.3041 | 5.1337
[7 empty] | 1148 | 140 | 7.3127 | 5.1399
[7 empty] | 1149 | 141 | 6.6417 | 4.6526
[7 empty] | 1150 | 142 | 5.9879 | 4.1779
[7 empty] | 1151 | 143 | 5.0846 | 3.522
[7 empty] | 1152 | 144 | 4.4566 | 3.0659
[7 empty] | 1153 | 145 | 3.9749 | 2.7161
[7 empty] | 1154 | 146 | 3.7598 | 2.5599
[7 empty] | 1155 | 147 | 3.691 | 2.51
[7 empty] | 1156 | 148 | 3.6824 | 2.5037
[7 empty] | 1157 | 149 | 3.6824 | 2.5037
[7 empty] | 1158 | 150 | 3.691 | 2.51
[7 empty] | 1159 | 151 | 4.8007 | 3.3158
[7 empty] | 1160 | 152 | 6.3664 | 4.4527
[7 empty] | 1161 | 153 | 6.9944 | 4.9088
[7 empty] | 1162 | 154 | 7.5707 | 5.3273
[7 empty] | 1163 | 155 | 7.4159 | 5.2149
[7 empty] | 1164 | 156 | 7.5879 | 5.3398
[7 empty] | 1165 | 157 | 8.3192 | 5.8708
[7 empty] | 1166 | 158 | 8.6546 | 6.1144
[7 empty] | 1167 | 159 | 8.9299 | 6.3143
[7 empty] | 1168 | 160 | 8.8009 | 6.2206
[7 empty] | 1169 | 161 | 9.5837 | 6.7891
[7 empty] | 1170 | 162 | 9.0762 | 6.4205
[7 empty] | 1171 | 163 | 9.4461 | 6.6891
[7 empty] | 1172 | 164 | 8.0611 | 5.6834
[7 empty] | 1173 | 165 | 11.2698 | 8.0135
[7 empty] | 1174 | 166 | 9.1708 | 6.4892
[7 empty] | 1175 | 167 | 5.4717 | 3.8031
[7 empty] | 1176 | 168 | 4.8093 | 3.3221
[7 empty] | 1177 | 1 | 3.3125 | 2.2351
[7 empty] | 1178 | 2 | 3.2007 | 2.1539
[7 empty] | 1179 | 3 | 3.1921 | 2.1476
[7 empty] | 1180 | 4 | 3.3297 | 2.2476
[7 empty] | 1181 | 5 | 3.3469 | 2.2601
[7 empty] | 1182 | 6 | 3.7857 | 2.5787
[7 empty] | 1183 | 7 | 4.5255 | 3.1159
[7 empty] | 1184 | 8 | 5.2137 | 3.6157
[7 empty] | 1185 | 9 | 5.1879 | 3.5969
[7 empty] | 1186 | 10 | 6.7449 | 4.7276
[7 empty] | 1187 | 11 | 8.8783 | 6.2768
[7 empty] | 1188 | 12 | 9.8676 | 6.9952
[7 empty] | 1189 | 13 | 10.2547 | 7.2763
[7 empty] | 1190 | 14 | 10.031 | 7.1139
[7 empty] | 1191 | 15 | 9.9364 | 7.0452
[7 empty] | 1192 | 16 | 11.1494 | 7.926
[7 empty] | 1193 | 17 | 12.5086 | 8.913
[7 empty] | 1194 | 18 | 12.2591 | 8.7319
[7 empty] | 1195 | 19 | 12.801 | 9.1254
[7 empty] | 1196 | 20 | 12.7322 | 9.0755
[7 empty] | 1197 | 21 | 13.3172 | 9.5002
[7 empty] | 1198 | 22 | 9.2568 | 6.5517
[7 empty] | 1199 | 23 | 5.3857 | 3.7406
[7 empty] | 1200 | 24 | 3.6704 | 2.495
[7 empty] | 1201 | 25 | 3.5706 | 2.4225
[7 empty] | 1202 | 26 | 3.4588 | 2.3413
[7 empty] | 1203 | 27 | 3.3555 | 2.2663
[7 empty] | 1204 | 28 | 3.4416 | 2.3288
[7 empty] | 1205 | 29 | 3.691 | 2.51
[7 empty] | 1206 | 30 | 3.9405 | 2.6911
[7 empty] | 1207 | 31 | 4.8093 | 3.3221
[7 empty] | 1208 | 32 | 5.1706 | 3.5844
[7 empty] | 1209 | 33 | 5.8502 | 4.0779
[7 empty] | 1210 | 34 | 6.7707 | 4.7464
[7 empty] | 1211 | 35 | 8.9987 | 6.3643
[7 empty] | 1212 | 36 | 10.0569 | 7.1327
[7 empty] | 1213 | 37 | 10.1343 | 7.1889
[7 empty] | 1214 | 38 | 10.2117 | 7.2451
[7 empty] | 1215 | 39 | 9.8762 | 7.0015
[7 empty] | 1216 | 40 | 10.9601 | 7.7886
[7 empty] | 1217 | 41 | 11.5279 | 8.2009
[7 empty] | 1218 | 42 | 11.5451 | 8.2134
[7 empty] | 1219 | 43 | 11.9236 | 8.4882
[7 empty] | 1220 | 44 | 13.1107 | 9.3503
[7 empty] | 1221 | 45 | 12.6978 | 9.0505
[7 empty] | 1222 | 46 | 9.8762 | 7.0015
[7 empty] | 1223 | 47 | 6.1771 | 4.3153
[7 empty] | 1224 | 48 | 4.6373 | 3.1971
[7 empty] | 1225 | 49 | 3.9577 | 2.7036
[7 empty] | 1226 | 50 | 3.6394 | 2.4725
[7 empty] | 1227 | 51 | 3.5276 | 2.3913
[7 empty] | 1228 | 52 | 3.562 | 2.4163
[7 empty] | 1229 | 53 | 3.5878 | 2.435
[7 empty] | 1230 | 54 | 4.1814 | 2.866
[7 empty] | 1231 | 55 | 5.3513 | 3.7156
[7 empty] | 1232 | 56 | 5.6008 | 3.8968
[7 empty] | 1233 | 57 | 6.5729 | 4.6027
[7 empty] | 1234 | 58 | 7.7084 | 5.4273
[7 empty] | 1235 | 59 | 8.9471 | 6.3268
[7 empty] | 1236 | 60 | 9.5923 | 6.7953
[7 empty] | 1237 | 61 | 10.2891 | 7.3013
[7 empty] | 1238 | 62 | 10.0827 | 7.1514
[7 empty] | 1239 | 63 | 10.6934 | 7.5949
[7 empty] | 1240 | 64 | 11.6655 | 8.3008
[7 empty] | 1241 | 65 | 12.3021 | 8.7631
[7 empty] | 1242 | 66 | 12.1989 | 8.6882
[7 empty] | 1243 | 67 | 12.9559 | 9.2379
[7 empty] | 1244 | 68 | 13.2054 | 9.419
[7 empty] | 1245 | 69 | 12.6806 | 9.038
[7 empty] | 1246 | 70 | 10.3235 | 7.3263
[7 empty] | 1247 | 71 | 5.6868 | 3.9592
[7 empty] | 1248 | 72 | 4.5734 | 3.1507
[7 empty] | 1249 | 73 | 3.8373 | 2.6162
[7 empty] | 1250 | 74 | 3.605 | 2.4475
[7 empty] | 1251 | 75 | 3.5018 | 2.3725
[7 empty] | 1252 | 76 | 3.4416 | 2.3288
[7 empty] | 1253 | 77 | 3.6222 | 2.46
[7 empty] | 1254 | 78 | 4.0351 | 2.7598
[7 empty] | 1255 | 79 | 5.1793 | 3.5907
[7 empty] | 1256 | 80 | 5.3599 | 3.7219
[7 empty] | 1257 | 81 | 6.5729 | 4.6027
[7 empty] | 1258 | 82 | 7.6912 | 5.4148
[7 empty] | 1259 | 83 | 8.4482 | 5.9645
[7 empty] | 1260 | 84 | 9.7214 | 6.889
[7 empty] | 1261 | 85 | 9.4117 | 6.6642
[7 empty] | 1262 | 86 | 8.8869 | 6.2831
[7 empty] | 1263 | 87 | 9.3428 | 6.6142
[7 empty] | 1264 | 88 | 10.0224 | 7.1077
[7 empty] | 1265 | 89 | 11.4074 | 8.1134
[7 empty] | 1266 | 90 | 10.8053 | 7.6762
[7 empty] | 1267 | 91 | 11.5107 | 8.1884
[7 empty] | 1268 | 92 | 10.8913 | 7.7386
[7 empty] | 1269 | 93 | 8.4138 | 5.9395
[7 empty] | 1270 | 94 | 7.4847 | 5.2648
[7 empty] | 1271 | 95 | 5.575 | 3.878
[7 empty] | 1272 | 96 | 4.5599 | 3.1409
[7 empty] | 1273 | 97 | 4.5083 | 3.1034
[7 empty] | 1274 | 98 | 4.2072 | 2.8848
[7 empty] | 1275 | 99 | 4.147 | 2.841
[7 empty] | 1276 | 100 | 3.7857 | 2.5787
[7 empty] | 1277 | 101 | 3.7254 | 2.5349
[7 empty] | 1278 | 102 | 3.9663 | 2.7099
[7 empty] | 1279 | 103 | 4.7319 | 3.2658
[7 empty] | 1280 | 104 | 4.99 | 3.4532
[7 empty] | 1281 | 105 | 5.4889 | 3.8156
[7 empty] | 1282 | 106 | 6.9858 | 4.9025
[7 empty] | 1283 | 107 | 7.3471 | 5.1649
[7 empty] | 1284 | 108 | 8.9643 | 6.3393
[7 empty] | 1285 | 109 | 8.2847 | 5.8458
[7 empty] | 1286 | 110 | 7.8202 | 5.5085
[7 empty] | 1287 | 111 | 7.6568 | 5.3898
[7 empty] | 1288 | 112 | 7.7256 | 5.4398
[7 empty] | 1289 | 113 | 7.3729 | 5.1836
[7 empty] | 1290 | 114 | 7.5449 | 5.3086
[7 empty] | 1291 | 115 | 7.0804 | 4.9712
[7 empty] | 1292 | 116 | 7.7772 | 5.4772
[7 empty] | 1293 | 117 | 7.3471 | 5.1649
[7 empty] | 1294 | 118 | 6.5556 | 4.5902
[7 empty] | 1295 | 119 | 4.9212 | 3.4033
[7 empty] | 1296 | 120 | 4.5954 | 3.1667
[7 empty] | 1297 | 121 | 3.8459 | 2.6224
[7 empty] | 1298 | 122 | 3.4243 | 2.3163
[7 empty] | 1299 | 123 | 3.3383 | 2.2538
[7 empty] | 1300 | 124 | 3.3039 | 2.2289
[7 empty] | 1301 | 125 | 3.2609 | 2.1976
[7 empty] | 1302 | 126 | 3.4071 | 2.3038
[7 empty] | 1303 | 127 | 4.9556 | 3.4283
[7 empty] | 1304 | 128 | 6.5556 | 4.5902
[7 empty] | 1305 | 129 | 7.2524 | 5.0962
[7 empty] | 1306 | 130 | 7.6998 | 5.421
[7 empty] | 1307 | 131 | 7.8632 | 5.5397
[7 empty] | 1308 | 132 | 7.6051 | 5.3523
[7 empty] | 1309 | 133 | 8.2589 | 5.8271
[7 empty] | 1310 | 134 | 8.5686 | 6.052
[7 empty] | 1311 | 135 | 8.6374 | 6.1019
[7 empty] | 1312 | 136 | 7.803 | 5.496
[7 empty] | 1313 | 137 | 7.6998 | 5.421
[7 empty] | 1314 | 138 | 7.6482 | 5.3835
[7 empty] | 1315 | 139 | 7.3041 | 5.1337
[7 empty] | 1316 | 140 | 7.3127 | 5.1399
[7 empty] | 1317 | 141 | 6.6417 | 4.6526
[7 empty] | 1318 | 142 | 5.9879 | 4.1779
[7 empty] | 1319 | 143 | 5.0846 | 3.522
[7 empty] | 1320 | 144 | 4.4566 | 3.0659
[7 empty] | 1321 | 145 | 3.9749 | 2.7161
[7 empty] | 1322 | 146 | 3.7598 | 2.5599
[7 empty] | 1323 | 147 | 3.691 | 2.51
[7 empty] | 1324 | 148 | 3.6824 | 2.5037
[7 empty] | 1325 | 149 | 3.6824 | 2.5037
[7 empty] | 1326 | 150 | 3.691 | 2.51
[7 empty] | 1327 | 151 | 4.8007 | 3.3158
[7 empty] | 1328 | 152 | 6.3664 | 4.4527
[7 empty] | 1329 | 153 | 6.9944 | 4.9088
[7 empty] | 1330 | 154 | 7.5707 | 5.3273
[7 empty] | 1331 | 155 | 7.4159 | 5.2149
[7 empty] | 1332 | 156 | 7.5879 | 5.3398
[7 empty] | 1333 | 157 | 8.3192 | 5.8708
[7 empty] | 1334 | 158 | 8.6546 | 6.1144
[7 empty] | 1335 | 159 | 8.9299 | 6.3143
[7 empty] | 1336 | 160 | 8.8009 | 6.2206
[7 empty] | 1337 | 161 | 9.5837 | 6.7891
[7 empty] | 1338 | 162 | 9.0762 | 6.4205
[7 empty] | 1339 | 163 | 9.4461 | 6.6891
[7 empty] | 1340 | 164 | 8.0611 | 5.6834
[7 empty] | 1341 | 165 | 11.2698 | 8.0135
[7 empty] | 1342 | 166 | 9.1708 | 6.4892
[7 empty] | 1343 | 167 | 5.4717 | 3.8031
[7 empty] | 1344 | 168 | 4.8093 | 3.3221
[7 empty] | 1345 | 1 | 3.3125 | 2.2351
[7 empty] | 1346 | 2 | 3.2007 | 2.1539
[7 empty] | 1347 | 3 | 3.1921 | 2.1476
[7 empty] | 1348 | 4 | 3.3297 | 2.2476
[7 empty] | 1349 | 5 | 3.3469 | 2.2601
[7 empty] | 1350 | 6 | 3.7857 | 2.5787
[7 empty] | 1351 | 7 | 4.5255 | 3.1159
[7 empty] | 1352 | 8 | 5.2137 | 3.6157
[7 empty] | 1353 | 9 | 5.1879 | 3.5969
[7 empty] | 1354 | 10 | 6.7449 | 4.7276
[7 empty] | 1355 | 11 | 8.8783 | 6.2768
[7 empty] | 1356 | 12 | 9.8676 | 6.9952
[7 empty] | 1357 | 13 | 10.2547 | 7.2763
[7 empty] | 1358 | 14 | 10.031 | 7.1139
[7 empty] | 1359 | 15 | 9.9364 | 7.0452
[7 empty] | 1360 | 16 | 11.1494 | 7.926
[7 empty] | 1361 | 17 | 12.5086 | 8.913
[7 empty] | 1362 | 18 | 12.2591 | 8.7319
[7 empty] | 1363 | 19 | 12.801 | 9.1254
[7 empty] | 1364 | 20 | 12.7322 | 9.0755
[7 empty] | 1365 | 21 | 13.3172 | 9.5002
[7 empty] | 1366 | 22 | 9.2568 | 6.5517
[7 empty] | 1367 | 23 | 5.3857 | 3.7406
[7 empty] | 1368 | 24 | 3.6704 | 2.495
[7 empty] | 1369 | 25 | 3.5706 | 2.4225
[7 empty] | 1370 | 26 | 3.4588 | 2.3413
[7 empty] | 1371 | 27 | 3.3555 | 2.2663
[7 empty] | 1372 | 28 | 3.4416 | 2.3288
[7 empty] | 1373 | 29 | 3.691 | 2.51
[7 empty] | 1374 | 30 | 3.9405 | 2.6911
[7 empty] | 1375 | 31 | 4.8093 | 3.3221
[7 empty] | 1376 | 32 | 5.1706 | 3.5844
[7 empty] | 1377 | 33 | 5.8502 | 4.0779
[7 empty] | 1378 | 34 | 6.7707 | 4.7464
[7 empty] | 1379 | 35 | 8.9987 | 6.3643
[7 empty] | 1380 | 36 | 10.0569 | 7.1327
[7 empty] | 1381 | 37 | 10.1343 | 7.1889
[7 empty] | 1382 | 38 | 10.2117 | 7.2451
[7 empty] | 1383 | 39 | 9.8762 | 7.0015
[7 empty] | 1384 | 40 | 10.9601 | 7.7886
[7 empty] | 1385 | 41 | 11.5279 | 8.2009
[7 empty] | 1386 | 42 | 11.5451 | 8.2134
[7 empty] | 1387 | 43 | 11.9236 | 8.4882
[7 empty] | 1388 | 44 | 13.1107 | 9.3503
[7 empty] | 1389 | 45 | 12.6978 | 9.0505
[7 empty] | 1390 | 46 | 9.8762 | 7.0015
[7 empty] | 1391 | 47 | 6.1771 | 4.3153
[7 empty] | 1392 | 48 | 4.6373 | 3.1971
[7 empty] | 1393 | 49 | 3.9577 | 2.7036
[7 empty] | 1394 | 50 | 3.6394 | 2.4725
[7 empty] | 1395 | 51 | 3.5276 | 2.3913
[7 empty] | 1396 | 52 | 3.562 | 2.4163
[7 empty] | 1397 | 53 | 3.5878 | 2.435
[7 empty] | 1398 | 54 | 4.1814 | 2.866
[7 empty] | 1399 | 55 | 5.3513 | 3.7156
[7 empty] | 1400 | 56 | 5.6008 | 3.8968
[7 empty] | 1401 | 57 | 6.5729 | 4.6027
[7 empty] | 1402 | 58 | 7.7084 | 5.4273
[7 empty] | 1403 | 59 | 8.9471 | 6.3268
[7 empty] | 1404 | 60 | 9.5923 | 6.7953
[7 empty] | 1405 | 61 | 10.2891 | 7.3013
[7 empty] | 1406 | 62 | 10.0827 | 7.1514
[7 empty] | 1407 | 63 | 10.6934 | 7.5949
[7 empty] | 1408 | 64 | 11.6655 | 8.3008
[7 empty] | 1409 | 65 | 12.3021 | 8.7631
[7 empty] | 1410 | 66 | 12.1989 | 8.6882
[7 empty] | 1411 | 67 | 12.9559 | 9.2379
[7 empty] | 1412 | 68 | 13.2054 | 9.419
[7 empty] | 1413 | 69 | 12.6806 | 9.038
[7 empty] | 1414 | 70 | 10.3235 | 7.3263
[7 empty] | 1415 | 71 | 5.6868 | 3.9592
[7 empty] | 1416 | 72 | 4.5734 | 3.1507
[7 empty] | 1417 | 73 | 3.8373 | 2.6162
[7 empty] | 1418 | 74 | 3.605 | 2.4475
[7 empty] | 1419 | 75 | 3.5018 | 2.3725
[7 empty] | 1420 | 76 | 3.4416 | 2.3288
[7 empty] | 1421 | 77 | 3.6222 | 2.46
[7 empty] | 1422 | 78 | 4.0351 | 2.7598
[7 empty] | 1423 | 79 | 5.1793 | 3.5907
[7 empty] | 1424 | 80 | 5.3599 | 3.7219
[7 empty] | 1425 | 81 | 6.5729 | 4.6027
[7 empty] | 1426 | 82 | 7.6912 | 5.4148
[7 empty] | 1427 | 83 | 8.4482 | 5.9645
[7 empty] | 1428 | 84 | 9.7214 | 6.889
[7 empty] | 1429 | 85 | 9.4117 | 6.6642
[7 empty] | 1430 | 86 | 8.8869 | 6.2831
[7 empty] | 1431 | 87 | 9.3428 | 6.6142
[7 empty] | 1432 | 88 | 10.0224 | 7.1077
[7 empty] | 1433 | 89 | 11.4074 | 8.1134
[7 empty] | 1434 | 90 | 10.8053 | 7.6762
[7 empty] | 1435 | 91 | 11.5107 | 8.1884
[7 empty] | 1436 | 92 | 10.8913 | 7.7386
[7 empty] | 1437 | 93 | 8.4138 | 5.9395
[7 empty] | 1438 | 94 | 7.4847 | 5.2648
[7 empty] | 1439 | 95 | 5.575 | 3.878
[7 empty] | 1440 | 96 | 4.5599 | 3.1409
[7 empty] | 1441 | 97 | 4.5083 | 3.1034
[7 empty] | 1442 | 98 | 4.2072 | 2.8848
[7 empty] | 1443 | 99 | 4.147 | 2.841
[7 empty] | 1444 | 100 | 3.7857 | 2.5787
[7 empty] | 1445 | 101 | 3.7254 | 2.5349
[7 empty] | 1446 | 102 | 3.9663 | 2.7099
[7 empty] | 1447 | 103 | 4.7319 | 3.2658
[7 empty] | 1448 | 104 | 4.99 | 3.4532
[7 empty] | 1449 | 105 | 5.4889 | 3.8156
[7 empty] | 1450 | 106 | 6.9858 | 4.9025
[7 empty] | 1451 | 107 | 7.3471 | 5.1649
[7 empty] | 1452 | 108 | 8.9643 | 6.3393
[7 empty] | 1453 | 109 | 8.2847 | 5.8458
[7 empty] | 1454 | 110 | 7.8202 | 5.5085
[7 empty] | 1455 | 111 | 7.6568 | 5.3898
[7 empty] | 1456 | 112 | 7.7256 | 5.4398
[7 empty] | 1457 | 113 | 7.3729 | 5.1836
[7 empty] | 1458 | 114 | 7.5449 | 5.3086
[7 empty] | 1459 | 115 | 7.0804 | 4.9712
[7 empty] | 1460 | 116 | 7.7772 | 5.4772
[7 empty] | 1461 | 117 | 7.3471 | 5.1649
[7 empty] | 1462 | 118 | 6.5556 | 4.5902
[7 empty] | 1463 | 119 | 4.9212 | 3.4033
[7 empty] | 1464 | 120 | 4.5954 | 3.1667
[7 empty] | 1465 | 121 | 3.8459 | 2.6224
[7 empty] | 1466 | 122 | 3.4243 | 2.3163
[7 empty] | 1467 | 123 | 3.3383 | 2.2538
[7 empty] | 1468 | 124 | 3.3039 | 2.2289
[7 empty] | 1469 | 125 | 3.2609 | 2.1976
[7 empty] | 1470 | 126 | 3.4071 | 2.3038
[7 empty] | 1471 | 127 | 4.9556 | 3.4283
[7 empty] | 1472 | 128 | 6.5556 | 4.5902
[7 empty] | 1473 | 129 | 7.2524 | 5.0962
[7 empty] | 1474 | 130 | 7.6998 | 5.421
[7 empty] | 1475 | 131 | 7.8632 | 5.5397
[7 empty] | 1476 | 132 | 7.6051 | 5.3523
[7 empty] | 1477 | 133 | 8.2589 | 5.8271
[7 empty] | 1478 | 134 | 8.5686 | 6.052
[7 empty] | 1479 | 135 | 8.6374 | 6.1019
[7 empty] | 1480 | 136 | 7.803 | 5.496
[7 empty] | 1481 | 137 | 7.6998 | 5.421
[7 empty] | 1482 | 138 | 7.6482 | 5.3835
[7 empty] | 1483 | 139 | 7.3041 | 5.1337
[7 empty] | 1484 | 140 | 7.3127 | 5.1399
[7 empty] | 1485 | 141 | 6.6417 | 4.6526
[7 empty] | 1486 | 142 | 5.9879 | 4.1779
[7 empty] | 1487 | 143 | 5.0846 | 3.522
[7 empty] | 1488 | 144 | 4.4566 | 3.0659
[7 empty] | 1489 | 145 | 3.9749 | 2.7161
[7 empty] | 1490 | 146 | 3.7598 | 2.5599
[7 empty] | 1491 | 147 | 3.691 | 2.51
[7 empty] | 1492 | 148 | 3.6824 | 2.5037
[7 empty] | 1493 | 149 | 3.6824 | 2.5037
[7 empty] | 1494 | 150 | 3.691 | 2.51
[7 empty] | 1495 | 151 | 4.8007 | 3.3158
[7 empty] | 1496 | 152 | 6.3664 | 4.4527
[7 empty] | 1497 | 153 | 6.9944 | 4.9088
[7 empty] | 1498 | 154 | 7.5707 | 5.3273
[7 empty] | 1499 | 155 | 7.4159 | 5.2149
[7 empty] | 1500 | 156 | 7.5879 | 5.3398
[7 empty] | 1501 | 157 | 8.3192 | 5.8708
[7 empty] | 1502 | 158 | 8.6546 | 6.1144
[7 empty] | 1503 | 159 | 8.9299 | 6.3143
[7 empty] | 1504 | 160 | 8.8009 | 6.2206
[7 empty] | 1505 | 161 | 9.5837 | 6.7891
[7 empty] | 1506 | 162 | 9.0762 | 6.4205
[7 empty] | 1507 | 163 | 9.4461 | 6.6891
[7 empty] | 1508 | 164 | 8.0611 | 5.6834
[7 empty] | 1509 | 165 | 11.2698 | 8.0135
[7 empty] | 1510 | 166 | 9.1708 | 6.4892
[7 empty] | 1511 | 167 | 5.4717 | 3.8031
[7 empty] | 1512 | 168 | 4.8093 | 3.3221
[7 empty] | 1513 | 1 | 3.3125 | 2.2351
[7 empty] | 1514 | 2 | 3.2007 | 2.1539
[7 empty] | 1515 | 3 | 3.1921 | 2.1476
[7 empty] | 1516 | 4 | 3.3297 | 2.2476
[7 empty] | 1517 | 5 | 3.3469 | 2.2601
[7 empty] | 1518 | 6 | 3.7857 | 2.5787
[7 empty] | 1519 | 7 | 4.5255 | 3.1159
[7 empty] | 1520 | 8 | 5.2137 | 3.6157
[7 empty] | 1521 | 9 | 5.1879 | 3.5969
[7 empty] | 1522 | 10 | 6.7449 | 4.7276
[7 empty] | 1523 | 11 | 8.8783 | 6.2768
[7 empty] | 1524 | 12 | 9.8676 | 6.9952
[7 empty] | 1525 | 13 | 10.2547 | 7.2763
[7 empty] | 1526 | 14 | 10.031 | 7.1139
[7 empty] | 1527 | 15 | 9.9364 | 7.0452
[7 empty] | 1528 | 16 | 11.1494 | 7.926
[7 empty] | 1529 | 17 | 12.5086 | 8.913
[7 empty] | 1530 | 18 | 12.2591 | 8.7319
[7 empty] | 1531 | 19 | 12.801 | 9.1254
[7 empty] | 1532 | 20 | 12.7322 | 9.0755
[7 empty] | 1533 | 21 | 13.3172 | 9.5002
[7 empty] | 1534 | 22 | 9.2568 | 6.5517
[7 empty] | 1535 | 23 | 5.3857 | 3.7406
[7 empty] | 1536 | 24 | 3.6704 | 2.495
[7 empty] | 1537 | 25 | 3.5706 | 2.4225
[7 empty] | 1538 | 26 | 3.4588 | 2.3413
[7 empty] | 1539 | 27 | 3.3555 | 2.2663
[7 empty] | 1540 | 28 | 3.4416 | 2.3288
[7 empty] | 1541 | 29 | 3.691 | 2.51
[7 empty] | 1542 | 30 | 3.9405 | 2.6911
[7 empty] | 1543 | 31 | 4.8093 | 3.3221
[7 empty] | 1544 | 32 | 5.1706 | 3.5844
[7 empty] | 1545 | 33 | 5.8502 | 4.0779
[7 empty] | 1546 | 34 | 6.7707 | 4.7464
[7 empty] | 1547 | 35 | 8.9987 | 6.3643
[7 empty] | 1548 | 36 | 10.0569 | 7.1327
[7 empty] | 1549 | 37 | 10.1343 | 7.1889
[7 empty] | 1550 | 38 | 10.2117 | 7.2451
[7 empty] | 1551 | 39 | 9.8762 | 7.0015
[7 empty] | 1552 | 40 | 10.9601 | 7.7886
[7 empty] | 1553 | 41 | 11.5279 | 8.2009
[7 empty] | 1554 | 42 | 11.5451 | 8.2134
[7 empty] | 1555 | 43 | 11.9236 | 8.4882
[7 empty] | 1556 | 44 | 13.1107 | 9.3503
[7 empty] | 1557 | 45 | 12.6978 | 9.0505
[7 empty] | 1558 | 46 | 9.8762 | 7.0015
[7 empty] | 1559 | 47 | 6.1771 | 4.3153
[7 empty] | 1560 | 48 | 4.6373 | 3.1971
[7 empty] | 1561 | 49 | 3.9577 | 2.7036
[7 empty] | 1562 | 50 | 3.6394 | 2.4725
[7 empty] | 1563 | 51 | 3.5276 | 2.3913
[7 empty] | 1564 | 52 | 3.562 | 2.4163
[7 empty] | 1565 | 53 | 3.5878 | 2.435
[7 empty] | 1566 | 54 | 4.1814 | 2.866
[7 empty] | 1567 | 55 | 5.3513 | 3.7156
[7 empty] | 1568 | 56 | 5.6008 | 3.8968
[7 empty] | 1569 | 57 | 6.5729 | 4.6027
[7 empty] | 1570 | 58 | 7.7084 | 5.4273
[7 empty] | 1571 | 59 | 8.9471 | 6.3268
[7 empty] | 1572 | 60 | 9.5923 | 6.7953
[7 empty] | 1573 | 61 | 10.2891 | 7.3013
[7 empty] | 1574 | 62 | 10.0827 | 7.1514
[7 empty] | 1575 | 63 | 10.6934 | 7.5949
[7 empty] | 1576 | 64 | 11.6655 | 8.3008
[7 empty] | 1577 | 65 | 12.3021 | 8.7631
[7 empty] | 1578 | 66 | 12.1989 | 8.6882
[7 empty] | 1579 | 67 | 12.9559 | 9.2379
[7 empty] | 1580 | 68 | 13.2054 | 9.419
[7 empty] | 1581 | 69 | 12.6806 | 9.038
[7 empty] | 1582 | 70 | 10.3235 | 7.3263
[7 empty] | 1583 | 71 | 5.6868 | 3.9592
[7 empty] | 1584 | 72 | 4.5734 | 3.1507
[7 empty] | 1585 | 73 | 3.8373 | 2.6162
[7 empty] | 1586 | 74 | 3.605 | 2.4475
[7 empty] | 1587 | 75 | 3.5018 | 2.3725
[7 empty] | 1588 | 76 | 3.4416 | 2.3288
[7 empty] | 1589 | 77 | 3.6222 | 2.46
[7 empty] | 1590 | 78 | 4.0351 | 2.7598
[7 empty] | 1591 | 79 | 5.1793 | 3.5907
[7 empty] | 1592 | 80 | 5.3599 | 3.7219
[7 empty] | 1593 | 81 | 6.5729 | 4.6027
[7 empty] | 1594 | 82 | 7.6912 | 5.4148
[7 empty] | 1595 | 83 | 8.4482 | 5.9645
[7 empty] | 1596 | 84 | 9.7214 | 6.889
[7 empty] | 1597 | 85 | 9.4117 | 6.6642
[7 empty] | 1598 | 86 | 8.8869 | 6.2831
[7 empty] | 1599 | 87 | 9.3428 | 6.6142
[7 empty] | 1600 | 88 | 10.0224 | 7.1077
[7 empty] | 1601 | 89 | 11.4074 | 8.1134
[7 empty] | 1602 | 90 | 10.8053 | 7.6762
[7 empty] | 1603 | 91 | 11.5107 | 8.1884
[7 empty] | 1604 | 92 | 10.8913 | 7.7386
[7 empty] | 1605 | 93 | 8.4138 | 5.9395
[7 empty] | 1606 | 94 | 7.4847 | 5.2648
[7 empty] | 1607 | 95 | 5.575 | 3.878
[7 empty] | 1608 | 96 | 4.5599 | 3.1409
[7 empty] | 1609 | 97 | 4.5083 | 3.1034
[7 empty] | 1610 | 98 | 4.2072 | 2.8848
[7 empty] | 1611 | 99 | 4.147 | 2.841
[7 empty] | 1612 | 100 | 3.7857 | 2.5787
[7 empty] | 1613 | 101 | 3.7254 | 2.5349
[7 empty] | 1614 | 102 | 3.9663 | 2.7099
[7 empty] | 1615 | 103 | 4.7319 | 3.2658
[7 empty] | 1616 | 104 | 4.99 | 3.4532
[7 empty] | 1617 | 105 | 5.4889 | 3.8156
[7 empty] | 1618 | 106 | 6.9858 | 4.9025
[7 empty] | 1619 | 107 | 7.3471 | 5.1649
[7 empty] | 1620 | 108 | 8.9643 | 6.3393
[7 empty] | 1621 | 109 | 8.2847 | 5.8458
[7 empty] | 1622 | 110 | 7.8202 | 5.5085
[7 empty] | 1623 | 111 | 7.6568 | 5.3898
[7 empty] | 1624 | 112 | 7.7256 | 5.4398
[7 empty] | 1625 | 113 | 7.3729 | 5.1836
[7 empty] | 1626 | 114 | 7.5449 | 5.3086
[7 empty] | 1627 | 115 | 7.0804 | 4.9712
[7 empty] | 1628 | 116 | 7.7772 | 5.4772
[7 empty] | 1629 | 117 | 7.3471 | 5.1649
[7 empty] | 1630 | 118 | 6.5556 | 4.5902
[7 empty] | 1631 | 119 | 4.9212 | 3.4033
[7 empty] | 1632 | 120 | 4.5954 | 3.1667
[7 empty] | 1633 | 121 | 3.8459 | 2.6224
[7 empty] | 1634 | 122 | 3.4243 | 2.3163
[7 empty] | 1635 | 123 | 3.3383 | 2.2538
[7 empty] | 1636 | 124 | 3.3039 | 2.2289
[7 empty] | 1637 | 125 | 3.2609 | 2.1976
[7 empty] | 1638 | 126 | 3.4071 | 2.3038
[7 empty] | 1639 | 127 | 4.9556 | 3.4283
[7 empty] | 1640 | 128 | 6.5556 | 4.5902
[7 empty] | 1641 | 129 | 7.2524 | 5.0962
[7 empty] | 1642 | 130 | 7.6998 | 5.421
[7 empty] | 1643 | 131 | 7.8632 | 5.5397
[7 empty] | 1644 | 132 | 7.6051 | 5.3523
[7 empty] | 1645 | 133 | 8.2589 | 5.8271
[7 empty] | 1646 | 134 | 8.5686 | 6.052
[7 empty] | 1647 | 135 | 8.6374 | 6.1019
[7 empty] | 1648 | 136 | 7.803 | 5.496
[7 empty] | 1649 | 137 | 7.6998 | 5.421
[7 empty] | 1650 | 138 | 7.6482 | 5.3835
[7 empty] | 1651 | 139 | 7.3041 | 5.1337
[7 empty] | 1652 | 140 | 7.3127 | 5.1399
[7 empty] | 1653 | 141 | 6.6417 | 4.6526
[7 empty] | 1654 | 142 | 5.9879 | 4.1779
[7 empty] | 1655 | 143 | 5.0846 | 3.522
[7 empty] | 1656 | 144 | 4.4566 | 3.0659
[7 empty] | 1657 | 145 | 3.9749 | 2.7161
[7 empty] | 1658 | 146 | 3.7598 | 2.5599
[7 empty] | 1659 | 147 | 3.691 | 2.51
[7 empty] | 1660 | 148 | 3.6824 | 2.5037
[7 empty] | 1661 | 149 | 3.6824 | 2.5037
[7 empty] | 1662 | 150 | 3.691 | 2.51
[7 empty] | 1663 | 151 | 4.8007 | 3.3158
[7 empty] | 1664 | 152 | 6.3664 | 4.4527
[7 empty] | 1665 | 153 | 6.9944 | 4.9088
[7 empty] | 1666 | 154 | 7.5707 | 5.3273
[7 empty] | 1667 | 155 | 7.4159 | 5.2149
[7 empty] | 1668 | 156 | 7.5879 | 5.3398
[7 empty] | 1669 | 157 | 8.3192 | 5.8708
[7 empty] | 1670 | 158 | 8.6546 | 6.1144
[7 empty] | 1671 | 159 | 8.9299 | 6.3143
[7 empty] | 1672 | 160 | 8.8009 | 6.2206
[7 empty] | 1673 | 161 | 9.5837 | 6.7891
[7 empty] | 1674 | 162 | 9.0762 | 6.4205
[7 empty] | 1675 | 163 | 9.4461 | 6.6891
[7 empty] | 1676 | 164 | 8.0611 | 5.6834
[7 empty] | 1677 | 165 | 11.2698 | 8.0135
[7 empty] | 1678 | 166 | 9.1708 | 6.4892
[7 empty] | 1679 | 167 | 5.4717 | 3.8031
[7 empty] | 1680 | 168 | 4.8093 | 3.3221
[7 empty] | 1681 | 1 | 3.3125 | 2.2351
[7 empty] | 1682 | 2 | 3.2007 | 2.1539
[7 empty] | 1683 | 3 | 3.1921 | 2.1476
[7 empty] | 1684 | 4 | 3.3297 | 2.2476
[7 empty] | 1685 | 5 | 3.3469 | 2.2601
[7 empty] | 1686 | 6 | 3.7857 | 2.5787
[7 empty] | 1687 | 7 | 4.5255 | 3.1159
[7 empty] | 1688 | 8 | 5.2137 | 3.6157
[7 empty] | 1689 | 9 | 5.1879 | 3.5969
[7 empty] | 1690 | 10 | 6.7449 | 4.7276
[7 empty] | 1691 | 11 | 8.8783 | 6.2768
[7 empty] | 1692 | 12 | 9.8676 | 6.9952
[7 empty] | 1693 | 13 | 10.2547 | 7.2763
[7 empty] | 1694 | 14 | 10.031 | 7.1139
[7 empty] | 1695 | 15 | 9.9364 | 7.0452
[7 empty] | 1696 | 16 | 11.1494 | 7.926
[7 empty] | 1697 | 17 | 12.5086 | 8.913
[7 empty] | 1698 | 18 | 12.2591 | 8.7319
[7 empty] | 1699 | 19 | 12.801 | 9.1254
[7 empty] | 1700 | 20 | 12.7322 | 9.0755
[7 empty] | 1701 | 21 | 13.3172 | 9.5002
[7 empty] | 1702 | 22 | 9.2568 | 6.5517
[7 empty] | 1703 | 23 | 5.3857 | 3.7406
[7 empty] | 1704 | 24 | 3.6704 | 2.495
[7 empty] | 1705 | 25 | 3.5706 | 2.4225
[7 empty] | 1706 | 26 | 3.4588 | 2.3413
[7 empty] | 1707 | 27 | 3.3555 | 2.2663
[7 empty] | 1708 | 28 | 3.4416 | 2.3288
[7 empty] | 1709 | 29 | 3.691 | 2.51
[7 empty] | 1710 | 30 | 3.9405 | 2.6911
[7 empty] | 1711 | 31 | 4.8093 | 3.3221
[7 empty] | 1712 | 32 | 5.1706 | 3.5844
[7 empty] | 1713 | 33 | 5.8502 | 4.0779
[7 empty] | 1714 | 34 | 6.7707 | 4.7464
[7 empty] | 1715 | 35 | 8.9987 | 6.3643
[7 empty] | 1716 | 36 | 10.0569 | 7.1327
[7 empty] | 1717 | 37 | 10.1343 | 7.1889
[7 empty] | 1718 | 38 | 10.2117 | 7.2451
[7 empty] | 1719 | 39 | 9.8762 | 7.0015
[7 empty] | 1720 | 40 | 10.9601 | 7.7886
[7 empty] | 1721 | 41 | 11.5279 | 8.2009
[7 empty] | 1722 | 42 | 11.5451 | 8.2134
[7 empty] | 1723 | 43 | 11.9236 | 8.4882
[7 empty] | 1724 | 44 | 13.1107 | 9.3503
[7 empty] | 1725 | 45 | 12.6978 | 9.0505
[7 empty] | 1726 | 46 | 9.8762 | 7.0015
[7 empty] | 1727 | 47 | 6.1771 | 4.3153
[7 empty] | 1728 | 48 | 4.6373 | 3.1971
[7 empty] | 1729 | 49 | 3.9577 | 2.7036
[7 empty] | 1730 | 50 | 3.6394 | 2.4725
[7 empty] | 1731 | 51 | 3.5276 | 2.3913
[7 empty] | 1732 | 52 | 3.562 | 2.4163
[7 empty] | 1733 | 53 | 3.5878 | 2.435
[7 empty] | 1734 | 54 | 4.1814 | 2.866
[7 empty] | 1735 | 55 | 5.3513 | 3.7156
[7 empty] | 1736 | 56 | 5.6008 | 3.8968
[7 empty] | 1737 | 57 | 6.5729 | 4.6027
[7 empty] | 1738 | 58 | 7.7084 | 5.4273
[7 empty] | 1739 | 59 | 8.9471 | 6.3268
[7 empty] | 1740 | 60 | 9.5923 | 6.7953
[7 empty] | 1741 | 61 | 10.2891 | 7.3013
[7 empty] | 1742 | 62 | 10.0827 | 7.1514
[7 empty] | 1743 | 63 | 10.6934 | 7.5949
[7 empty] | 1744 | 64 | 11.6655 | 8.3008
[7 empty] | 1745 | 65 | 12.3021 | 8.7631
[7 empty] | 1746 | 66 | 12.1989 | 8.6882
[7 empty] | 1747 | 67 | 12.9559 | 9.2379
[7 empty] | 1748 | 68 | 13.2054 | 9.419
[7 empty] | 1749 | 69 | 12.6806 | 9.038
[7 empty] | 1750 | 70 | 10.3235 | 7.3263
[7 empty] | 1751 | 71 | 5.6868 | 3.9592
[7 empty] | 1752 | 72 | 4.5734 | 3.1507
[7 empty] | 1753 | 73 | 3.8373 | 2.6162
[7 empty] | 1754 | 74 | 3.605 | 2.4475
[7 empty] | 1755 | 75 | 3.5018 | 2.3725
[7 empty] | 1756 | 76 | 3.4416 | 2.3288
[7 empty] | 1757 | 77 | 3.6222 | 2.46
[7 empty] | 1758 | 78 | 4.0351 | 2.7598
[7 empty] | 1759 | 79 | 5.1793 | 3.5907
[7 empty] | 1760 | 80 | 5.3599 | 3.7219
[7 empty] | 1761 | 81 | 6.5729 | 4.6027
[7 empty] | 1762 | 82 | 7.6912 | 5.4148
[7 empty] | 1763 | 83 | 8.4482 | 5.9645
[7 empty] | 1764 | 84 | 9.7214 | 6.889
[7 empty] | 1765 | 85 | 9.4117 | 6.6642
[7 empty] | 1766 | 86 | 8.8869 | 6.2831
[7 empty] | 1767 | 87 | 9.3428 | 6.6142
[7 empty] | 1768 | 88 | 10.0224 | 7.1077
[7 empty] | 1769 | 89 | 11.4074 | 8.1134
[7 empty] | 1770 | 90 | 10.8053 | 7.6762
[7 empty] | 1771 | 91 | 11.5107 | 8.1884
[7 empty] | 1772 | 92 | 10.8913 | 7.7386
[7 empty] | 1773 | 93 | 8.4138 | 5.9395
[7 empty] | 1774 | 94 | 7.4847 | 5.2648
[7 empty] | 1775 | 95 | 5.575 | 3.878
[7 empty] | 1776 | 96 | 4.5599 | 3.1409
[7 empty] | 1777 | 97 | 4.5083 | 3.1034
[7 empty] | 1778 | 98 | 4.2072 | 2.8848
[7 empty] | 1779 | 99 | 4.147 | 2.841
[7 empty] | 1780 | 100 | 3.7857 | 2.5787
[7 empty] | 1781 | 101 | 3.7254 | 2.5349
[7 empty] | 1782 | 102 | 3.9663 | 2.7099
[7 empty] | 1783 | 103 | 4.7319 | 3.2658
[7 empty] | 1784 | 104 | 4.99 | 3.4532
[7 empty] | 1785 | 105 | 5.4889 | 3.8156
[7 empty] | 1786 | 106 | 6.9858 | 4.9025
[7 empty] | 1787 | 107 | 7.3471 | 5.1649
[7 empty] | 1788 | 108 | 8.9643 | 6.3393
[7 empty] | 1789 | 109 | 8.2847 | 5.8458
[7 empty] | 1790 | 110 | 7.8202 | 5.5085
[7 empty] | 1791 | 111 | 7.6568 | 5.3898
[7 empty] | 1792 | 112 | 7.7256 | 5.4398
[7 empty] | 1793 | 113 | 7.3729 | 5.1836
[7 empty] | 1794 | 114 | 7.5449 | 5.3086
[7 empty] | 1795 | 115 | 7.0804 | 4.9712
[7 empty] | 1796 | 116 | 7.7772 | 5.4772
[7 empty] | 1797 | 117 | 7.3471 | 5.1649
[7 empty] | 1798 | 118 | 6.5556 | 4.5902
[7 empty] | 1799 | 119 | 4.9212 | 3.4033
[7 empty] | 1800 | 120 | 4.5954 | 3.1667
[7 empty] | 1801 | 121 | 3.8459 | 2.6224
[7 empty] | 1802 | 122 | 3.4243 | 2.3163
[7 empty] | 1803 | 123 | 3.3383 | 2.2538
[7 empty] | 1804 | 124 | 3.3039 | 2.2289
[7 empty] | 1805 | 125 | 3.2609 | 2.1976
[7 empty] | 1806 | 126 | 3.4071 | 2.3038
[7 empty] | 1807 | 127 | 4.9556 | 3.4283
[7 empty] | 1808 | 128 | 6.5556 | 4.5902
[7 empty] | 1809 | 129 | 7.2524 | 5.0962
[7 empty] | 1810 | 130 | 7.6998 | 5.421
[7 empty] | 1811 | 131 | 7.8632 | 5.5397
[7 empty] | 1812 | 132 | 7.6051 | 5.3523
[7 empty] | 1813 | 133 | 8.2589 | 5.8271
[7 empty] | 1814 | 134 | 8.5686 | 6.052
[7 empty] | 1815 | 135 | 8.6374 | 6.1019
[7 empty] | 1816 | 136 | 7.803 | 5.496
[7 empty] | 1817 | 137 | 7.6998 | 5.421
[7 empty] | 1818 | 138 | 7.6482 | 5.3835
[7 empty] | 1819 | 139 | 7.3041 | 5.1337
[7 empty] | 1820 | 140 | 7.3127 | 5.1399
[7 empty] | 1821 | 141 | 6.6417 | 4.6526
[7 empty] | 1822 | 142 | 5.9879 | 4.1779
[7 empty] | 1823 | 143 | 5.0846 | 3.522
[7 empty] | 1824 | 144 | 4.4566 | 3.0659
[7 empty] | 1825 | 145 | 3.9749 | 2.7161
[7 empty] | 1826 | 146 | 3.7598 | 2.5599
[7 empty] | 1827 | 147 | 3.691 | 2.51
[7 empty] | 1828 | 148 | 3.6824 | 2.5037
[7 empty] | 1829 | 149 | 3.6824 | 2.5037
[7 empty] | 1830 | 150 | 3.691 | 2.51
[7 empty] | 1831 | 151 | 4.8007 | 3.3158
[7 empty] | 1832 | 152 | 6.3664 | 4.4527
[7 empty] | 1833 | 153 | 6.9944 | 4.9088
[7 empty] | 1834 | 154 | 7.5707 | 5.3273
[7 empty] | 1835 | 155 | 7.4159 | 5.2149
[7 empty] | 1836 | 156 | 7.5879 | 5.3398
[7 empty] | 1837 | 157 | 8.3192 | 5.8708
[7 empty] | 1838 | 158 | 8.6546 | 6.1144
[7 empty] | 1839 | 159 | 8.9299 | 6.3143
[7 empty] | 1840 | 160 | 8.8009 | 6.2206
[7 empty] | 1841 | 161 | 9.5837 | 6.7891
[7 empty] | 1842 | 162 | 9.0762 | 6.4205
[7 empty] | 1843 | 163 | 9.4461 | 6.6891
[7 empty] | 1844 | 164 | 8.0611 | 5.6834
[7 empty] | 1845 | 165 | 11.2698 | 8.0135
[7 empty] | 1846 | 166 | 9.1708 | 6.4892
[7 empty] | 1847 | 167 | 5.4717 | 3.8031
[7 empty] | 1848 | 168 | 4.8093 | 3.3221
[7 empty] | 1849 | 1 | 3.3125 | 2.2351
[7 empty] | 1850 | 2 | 3.2007 | 2.1539
[7 empty] | 1851 | 3 | 3.1921 | 2.1476
[7 empty] | 1852 | 4 | 3.3297 | 2.2476
[7 empty] | 1853 | 5 | 3.3469 | 2.2601
[7 empty] | 1854 | 6 | 3.7857 | 2.5787
[7 empty] | 1855 | 7 | 4.5255 | 3.1159
[7 empty] | 1856 | 8 | 5.2137 | 3.6157
[7 empty] | 1857 | 9 | 5.1879 | 3.5969
[7 empty] | 1858 | 10 | 6.7449 | 4.7276
[7 empty] | 1859 | 11 | 8.8783 | 6.2768
[7 empty] | 1860 | 12 | 9.8676 | 6.9952
[7 empty] | 1861 | 13 | 10.2547 | 7.2763
[7 empty] | 1862 | 14 | 10.031 | 7.1139
[7 empty] | 1863 | 15 | 9.9364 | 7.0452
[7 empty] | 1864 | 16 | 11.1494 | 7.926
[7 empty] | 1865 | 17 | 12.5086 | 8.913
[7 empty] | 1866 | 18 | 12.2591 | 8.7319
[7 empty] | 1867 | 19 | 12.801 | 9.1254
[7 empty] | 1868 | 20 | 12.7322 | 9.0755
[7 empty] | 1869 | 21 | 13.3172 | 9.5002
[7 empty] | 1870 | 22 | 9.2568 | 6.5517
[7 empty] | 1871 | 23 | 5.3857 | 3.7406
[7 empty] | 1872 | 24 | 3.6704 | 2.495
[7 empty] | 1873 | 25 | 3.5706 | 2.4225
[7 empty] | 1874 | 26 | 3.4588 | 2.3413
[7 empty] | 1875 | 27 | 3.3555 | 2.2663
[7 empty] | 1876 | 28 | 3.4416 | 2.3288
[7 empty] | 1877 | 29 | 3.691 | 2.51
[7 empty] | 1878 | 30 | 3.9405 | 2.6911
[7 empty] | 1879 | 31 | 4.8093 | 3.3221
[7 empty] | 1880 | 32 | 5.1706 | 3.5844
[7 empty] | 1881 | 33 | 5.8502 | 4.0779
[7 empty] | 1882 | 34 | 6.7707 | 4.7464
[7 empty] | 1883 | 35 | 8.9987 | 6.3643
[7 empty] | 1884 | 36 | 10.0569 | 7.1327
[7 empty] | 1885 | 37 | 10.1343 | 7.1889
[7 empty] | 1886 | 38 | 10.2117 | 7.2451
[7 empty] | 1887 | 39 | 9.8762 | 7.0015
[7 empty] | 1888 | 40 | 10.9601 | 7.7886
[7 empty] | 1889 | 41 | 11.5279 | 8.2009
[7 empty] | 1890 | 42 | 11.5451 | 8.2134
[7 empty] | 1891 | 43 | 11.9236 | 8.4882
[7 empty] | 1892 | 44 | 13.1107 | 9.3503
[7 empty] | 1893 | 45 | 12.6978 | 9.0505
[7 empty] | 1894 | 46 | 9.8762 | 7.0015
[7 empty] | 1895 | 47 | 6.1771 | 4.3153
[7 empty] | 1896 | 48 | 4.6373 | 3.1971
[7 empty] | 1897 | 49 | 3.9577 | 2.7036
[7 empty] | 1898 | 50 | 3.6394 | 2.4725
[7 empty] | 1899 | 51 | 3.5276 | 2.3913
[7 empty] | 1900 | 52 | 3.562 | 2.4163
[7 empty] | 1901 | 53 | 3.5878 | 2.435
[7 empty] | 1902 | 54 | 4.1814 | 2.866
[7 empty] | 1903 | 55 | 5.3513 | 3.7156
[7 empty] | 1904 | 56 | 5.6008 | 3.8968
[7 empty] | 1905 | 57 | 6.5729 | 4.6027
[7 empty] | 1906 | 58 | 7.7084 | 5.4273
[7 empty] | 1907 | 59 | 8.9471 | 6.3268
[7 empty] | 1908 | 60 | 9.5923 | 6.7953
[7 empty] | 1909 | 61 | 10.2891 | 7.3013
[7 empty] | 1910 | 62 | 10.0827 | 7.1514
[7 empty] | 1911 | 63 | 10.6934 | 7.5949
[7 empty] | 1912 | 64 | 11.6655 | 8.3008
[7 empty] | 1913 | 65 | 12.3021 | 8.7631
[7 empty] | 1914 | 66 | 12.1989 | 8.6882
[7 empty] | 1915 | 67 | 12.9559 | 9.2379
[7 empty] | 1916 | 68 | 13.2054 | 9.419
[7 empty] | 1917 | 69 | 12.6806 | 9.038
[7 empty] | 1918 | 70 | 10.3235 | 7.3263
[7 empty] | 1919 | 71 | 5.6868 | 3.9592
[7 empty] | 1920 | 72 | 4.5734 | 3.1507
[7 empty] | 1921 | 73 | 3.8373 | 2.6162
[7 empty] | 1922 | 74 | 3.605 | 2.4475
[7 empty] | 1923 | 75 | 3.5018 | 2.3725
[7 empty] | 1924 | 76 | 3.4416 | 2.3288
[7 empty] | 1925 | 77 | 3.6222 | 2.46
[7 empty] | 1926 | 78 | 4.0351 | 2.7598
[7 empty] | 1927 | 79 | 5.1793 | 3.5907
[7 empty] | 1928 | 80 | 5.3599 | 3.7219
[7 empty] | 1929 | 81 | 6.5729 | 4.6027
[7 empty] | 1930 | 82 | 7.6912 | 5.4148
[7 empty] | 1931 | 83 | 8.4482 | 5.9645
[7 empty] | 1932 | 84 | 9.7214 | 6.889
[7 empty] | 1933 | 85 | 9.4117 | 6.6642
[7 empty] | 1934 | 86 | 8.8869 | 6.2831
[7 empty] | 1935 | 87 | 9.3428 | 6.6142
[7 empty] | 1936 | 88 | 10.0224 | 7.1077
[7 empty] | 1937 | 89 | 11.4074 | 8.1134
[7 empty] | 1938 | 90 | 10.8053 | 7.6762
[7 empty] | 1939 | 91 | 11.5107 | 8.1884
[7 empty] | 1940 | 92 | 10.8913 | 7.7386
[7 empty] | 1941 | 93 | 8.4138 | 5.9395
[7 empty] | 1942 | 94 | 7.4847 | 5.2648
[7 empty] | 1943 | 95 | 5.575 | 3.878
[7 empty] | 1944 | 96 | 4.5599 | 3.1409
[7 empty] | 1945 | 97 | 4.5083 | 3.1034
[7 empty] | 1946 | 98 | 4.2072 | 2.8848
[7 empty] | 1947 | 99 | 4.147 | 2.841
[7 empty] | 1948 | 100 | 3.7857 | 2.5787
[7 empty] | 1949 | 101 | 3.7254 | 2.5349
[7 empty] | 1950 | 102 | 3.9663 | 2.7099
[7 empty] | 1951 | 103 | 4.7319 | 3.2658
[7 empty] | 1952 | 104 | 4.99 | 3.4532
[7 empty] | 1953 | 105 | 5.4889 | 3.8156
[7 empty] | 1954 | 106 | 6.9858 | 4.9025
[7 empty] | 1955 | 107 | 7.3471 | 5.1649
[7 empty] | 1956 | 108 | 8.9643 | 6.3393
[7 empty] | 1957 | 109 | 8.2847 | 5.8458
[7 empty] | 1958 | 110 | 7.8202 | 5.5085
[7 empty] | 1959 | 111 | 7.6568 | 5.3898
[7 empty] | 1960 | 112 | 7.7256 | 5.4398
[7 empty] | 1961 | 113 | 7.3729 | 5.1836
[7 empty] | 1962 | 114 | 7.5449 | 5.3086
[7 empty] | 1963 | 115 | 7.0804 | 4.9712
[7 empty] | 1964 | 116 | 7.7772 | 5.4772
[7 empty] | 1965 | 117 | 7.3471 | 5.1649
[7 empty] | 1966 | 118 | 6.5556 | 4.5902
[7 empty] | 1967 | 119 | 4.9212 | 3.4033
[7 empty] | 1968 | 120 | 4.5954 | 3.1667
[7 empty] | 1969 | 121 | 3.8459 | 2.6224
[7 empty] | 1970 | 122 | 3.4243 | 2.3163
[7 empty] | 1971 | 123 | 3.3383 | 2.2538
[7 empty] | 1972 | 124 | 3.3039 | 2.2289
[7 empty] | 1973 | 125 | 3.2609 | 2.1976
[7 empty] | 1974 | 126 | 3.4071 | 2.3038
[7 empty] | 1975 | 127 | 4.9556 | 3.4283
[7 empty] | 1976 | 128 | 6.5556 | 4.5902
[7 empty] | 1977 | 129 | 7.2524 | 5.0962
[7 empty] | 1978 | 130 | 7.6998 | 5.421
[7 empty] | 1979 | 131 | 7.8632 | 5.5397
[7 empty] | 1980 | 132 | 7.6051 | 5.3523
[7 empty] | 1981 | 133 | 8.2589 | 5.8271
[7 empty] | 1982 | 134 | 8.5686 | 6.052
[7 empty] | 1983 | 135 | 8.6374 | 6.1019
[7 empty] | 1984 | 136 | 7.803 | 5.496
[7 empty] | 1985 | 137 | 7.6998 | 5.421
[7 empty] | 1986 | 138 | 7.6482 | 5.3835
[7 empty] | 1987 | 139 | 7.3041 | 5.1337
[7 empty] | 1988 | 140 | 7.3127 | 5.1399
[7 empty] | 1989 | 141 | 6.6417 | 4.6526
[7 empty] | 1990 | 142 | 5.9879 | 4.1779
[7 empty] | 1991 | 143 | 5.0846 | 3.522
[7 empty] | 1992 | 144 | 4.4566 | 3.0659
[7 empty] | 1993 | 145 | 3.9749 | 2.7161
[7 empty] | 1994 | 146 | 3.7598 | 2.5599
[7 empty] | 1995 | 147 | 3.691 | 2.51
[7 empty] | 1996 | 148 | 3.6824 | 2.5037
[7 empty] | 1997 | 149 | 3.6824 | 2.5037
[7 empty] | 1998 | 150 | 3.691 | 2.51
[7 empty] | 1999 | 151 | 4.8007 | 3.3158
[7 empty] | 2000 | 152 | 6.3664 | 4.4527
[7 empty] | 2001 | 153 | 6.9944 | 4.9088
[7 empty] | 2002 | 154 | 7.5707 | 5.3273
[7 empty] | 2003 | 155 | 7.4159 | 5.2149
[7 empty] | 2004 | 156 | 7.5879 | 5.3398
[7 empty] | 2005 | 157 | 8.3192 | 5.8708
[7 empty] | 2006 | 158 | 8.6546 | 6.1144
[7 empty] | 2007 | 159 | 8.9299 | 6.3143
[7 empty] | 2008 | 160 | 8.8009 | 6.2206
[7 empty] | 2009 | 161 | 9.5837 | 6.7891
[7 empty] | 2010 | 162 | 9.0762 | 6.4205
[7 empty] | 2011 | 163 | 9.4461 | 6.6891
[7 empty] | 2012 | 164 | 8.0611 | 5.6834
[7 empty] | 2013 | 165 | 11.2698 | 8.0135
[7 empty] | 2014 | 166 | 9.1708 | 6.4892
[7 empty] | 2015 | 167 | 5.4717 | 3.8031
[7 empty] | 2016 | 168 | 4.8093 | 3.3221
[7 empty] | 2017 | 1 | 3.3125 | 2.2351
[7 empty] | 2018 | 2 | 3.2007 | 2.1539
[7 empty] | 2019 | 3 | 3.1921 | 2.1476
[7 empty] | 2020 | 4 | 3.3297 | 2.2476
[7 empty] | 2021 | 5 | 3.3469 | 2.2601
[7 empty] | 2022 | 6 | 3.7857 | 2.5787
[7 empty] | 2023 | 7 | 4.5255 | 3.1159
[7 empty] | 2024 | 8 | 5.2137 | 3.6157
[7 empty] | 2025 | 9 | 5.1879 | 3.5969
[7 empty] | 2026 | 10 | 6.7449 | 4.7276
[7 empty] | 2027 | 11 | 8.8783 | 6.2768
[7 empty] | 2028 | 12 | 9.8676 | 6.9952
[7 empty] | 2029 | 13 | 10.2547 | 7.2763
[7 empty] | 2030 | 14 | 10.031 | 7.1139
[7 empty] | 2031 | 15 | 9.9364 | 7.0452
[7 empty] | 2032 | 16 | 11.1494 | 7.926
[7 empty] | 2033 | 17 | 12.5086 | 8.913
[7 empty] | 2034 | 18 | 12.2591 | 8.7319
[7 empty] | 2035 | 19 | 12.801 | 9.1254
[7 empty] | 2036 | 20 | 12.7322 | 9.0755
[7 empty] | 2037 | 21 | 13.3172 | 9.5002
[7 empty] | 2038 | 22 | 9.2568 | 6.5517
[7 empty] | 2039 | 23 | 5.3857 | 3.7406
[7 empty] | 2040 | 24 | 3.6704 | 2.495
[7 empty] | 2041 | 25 | 3.5706 | 2.4225
[7 empty] | 2042 | 26 | 3.4588 | 2.3413
[7 empty] | 2043 | 27 | 3.3555 | 2.2663
[7 empty] | 2044 | 28 | 3.4416 | 2.3288
[7 empty] | 2045 | 29 | 3.691 | 2.51
[7 empty] | 2046 | 30 | 3.9405 | 2.6911
[7 empty] | 2047 | 31 | 4.8093 | 3.3221
[7 empty] | 2048 | 32 | 5.1706 | 3.5844
[7 empty] | 2049 | 33 | 5.8502 | 4.0779
[7 empty] | 2050 | 34 | 6.7707 | 4.7464
[7 empty] | 2051 | 35 | 8.9987 | 6.3643
[7 empty] | 2052 | 36 | 10.0569 | 7.1327
[7 empty] | 2053 | 37 | 10.1343 | 7.1889
[7 empty] | 2054 | 38 | 10.2117 | 7.2451
[7 empty] | 2055 | 39 | 9.8762 | 7.0015
[7 empty] | 2056 | 40 | 10.9601 | 7.7886
[7 empty] | 2057 | 41 | 11.5279 | 8.2009
[7 empty] | 2058 | 42 | 11.5451 | 8.2134
[7 empty] | 2059 | 43 | 11.9236 | 8.4882
[7 empty] | 2060 | 44 | 13.1107 | 9.3503
[7 empty] | 2061 | 45 | 12.6978 | 9.0505
[7 empty] | 2062 | 46 | 9.8762 | 7.0015
[7 empty] | 2063 | 47 | 6.1771 | 4.3153
[7 empty] | 2064 | 48 | 4.6373 | 3.1971
[7 empty] | 2065 | 49 | 3.9577 | 2.7036
[7 empty] | 2066 | 50 | 3.6394 | 2.4725
[7 empty] | 2067 | 51 | 3.5276 | 2.3913
[7 empty] | 2068 | 52 | 3.562 | 2.4163
[7 empty] | 2069 | 53 | 3.5878 | 2.435
[7 empty] | 2070 | 54 | 4.1814 | 2.866
[7 empty] | 2071 | 55 | 5.3513 | 3.7156
[7 empty] | 2072 | 56 | 5.6008 | 3.8968
[7 empty] | 2073 | 57 | 6.5729 | 4.6027
[7 empty] | 2074 | 58 | 7.7084 | 5.4273
[7 empty] | 2075 | 59 | 8.9471 | 6.3268
[7 empty] | 2076 | 60 | 9.5923 | 6.7953
[7 empty] | 2077 | 61 | 10.2891 | 7.3013
[7 empty] | 2078 | 62 | 10.0827 | 7.1514
[7 empty] | 2079 | 63 | 10.6934 | 7.5949
[7 empty] | 2080 | 64 | 11.6655 | 8.3008
[7 empty] | 2081 | 65 | 12.3021 | 8.7631
[7 empty] | 2082 | 66 | 12.1989 | 8.6882
[7 empty] | 2083 | 67 | 12.9559 | 9.2379
[7 empty] | 2084 | 68 | 13.2054 | 9.419
[7 empty] | 2085 | 69 | 12.6806 | 9.038
[7 empty] | 2086 | 70 | 10.3235 | 7.3263
[7 empty] | 2087 | 71 | 5.6868 | 3.9592
[7 empty] | 2088 | 72 | 4.5734 | 3.1507
[7 empty] | 2089 | 73 | 3.8373 | 2.6162
[7 empty] | 2090 | 74 | 3.605 | 2.4475
[7 empty] | 2091 | 75 | 3.5018 | 2.3725
[7 empty] | 2092 | 76 | 3.4416 | 2.3288
[7 empty] | 2093 | 77 | 3.6222 | 2.46
[7 empty] | 2094 | 78 | 4.0351 | 2.7598
[7 empty] | 2095 | 79 | 5.1793 | 3.5907
[7 empty] | 2096 | 80 | 5.3599 | 3.7219
[7 empty] | 2097 | 81 | 6.5729 | 4.6027
[7 empty] | 2098 | 82 | 7.6912 | 5.4148
[7 empty] | 2099 | 83 | 8.4482 | 5.9645
[7 empty] | 2100 | 84 | 9.7214 | 6.889
[7 empty] | 2101 | 85 | 9.4117 | 6.6642
[7 empty] | 2102 | 86 | 8.8869 | 6.2831
[7 empty] | 2103 | 87 | 9.3428 | 6.6142
[7 empty] | 2104 | 88 | 10.0224 | 7.1077
[7 empty] | 2105 | 89 | 11.4074 | 8.1134
[7 empty] | 2106 | 90 | 10.8053 | 7.6762
[7 empty] | 2107 | 91 | 11.5107 | 8.1884
[7 empty] | 2108 | 92 | 10.8913 | 7.7386
[7 empty] | 2109 | 93 | 8.4138 | 5.9395
[7 empty] | 2110 | 94 | 7.4847 | 5.2648
[7 empty] | 2111 | 95 | 5.575 | 3.878
[7 empty] | 2112 | 96 | 4.5599 | 3.1409
[7 empty] | 2113 | 97 | 4.5083 | 3.1034
[7 empty] | 2114 | 98 | 4.2072 | 2.8848
[7 empty] | 2115 | 99 | 4.147 | 2.841
[7 empty] | 2116 | 100 | 3.7857 | 2.5787
[7 empty] | 2117 | 101 | 3.7254 | 2.5349
[7 empty] | 2118 | 102 | 3.9663 | 2.7099
[7 empty] | 2119 | 103 | 4.7319 | 3.2658
[7 empty] | 2120 | 104 | 4.99 | 3.4532
[7 empty] | 2121 | 105 | 5.4889 | 3.8156
[7 empty] | 2122 | 106 | 6.9858 | 4.9025
[7 empty] | 2123 | 107 | 7.3471 | 5.1649
[7 empty] | 2124 | 108 | 8.9643 | 6.3393
[7 empty] | 2125 | 109 | 8.2847 | 5.8458
[7 empty] | 2126 | 110 | 7.8202 | 5.5085
[7 empty] | 2127 | 111 | 7.6568 | 5.3898
[7 empty] | 2128 | 112 | 7.7256 | 5.4398
[7 empty] | 2129 | 113 | 7.3729 | 5.1836
[7 empty] | 2130 | 114 | 7.5449 | 5.3086
[7 empty] | 2131 | 115 | 7.0804 | 4.9712
[7 empty] | 2132 | 116 | 7.7772 | 5.4772
[7 empty] | 2133 | 117 | 7.3471 | 5.1649
[7 empty] | 2134 | 118 | 6.5556 | 4.5902
[7 empty] | 2135 | 119 | 4.9212 | 3.4033
[7 empty] | 2136 | 120 | 4.5954 | 3.1667
[7 empty] | 2137 | 121 | 3.8459 | 2.6224
[7 empty] | 2138 | 122 | 3.4243 | 2.3163
[7 empty] | 2139 | 123 | 3.3383 | 2.2538
[7 empty] | 2140 | 124 | 3.3039 | 2.2289
[7 empty] | 2141 | 125 | 3.2609 | 2.1976
[7 empty] | 2142 | 126 | 3.4071 | 2.3038
[7 empty] | 2143 | 127 | 4.9556 | 3.4283
[7 empty] | 2144 | 128 | 6.5556 | 4.5902
[7 empty] | 2145 | 129 | 7.2524 | 5.0962
[7 empty] | 2146 | 130 | 7.6998 | 5.421
[7 empty] | 2147 | 131 | 7.8632 | 5.5397
[7 empty] | 2148 | 132 | 7.6051 | 5.3523
[7 empty] | 2149 | 133 | 8.2589 | 5.8271
[7 empty] | 2150 | 134 | 8.5686 | 6.052
[7 empty] | 2151 | 135 | 8.6374 | 6.1019
[7 empty] | 2152 | 136 | 7.803 | 5.496
[7 empty] | 2153 | 137 | 7.6998 | 5.421
[7 empty] | 2154 | 138 | 7.6482 | 5.3835
[7 empty] | 2155 | 139 | 7.3041 | 5.1337
[7 empty] | 2156 | 140 | 7.3127 | 5.1399
[7 empty] | 2157 | 141 | 6.6417 | 4.6526
[7 empty] | 2158 | 142 | 5.9879 | 4.1779
[7 empty] | 2159 | 143 | 5.0846 | 3.522
[7 empty] | 2160 | 144 | 4.4566 | 3.0659
[7 empty] | 2161 | 145 | 3.9749 | 2.7161
[7 empty] | 2162 | 146 | 3.7598 | 2.5599
[7 empty] | 2163 | 147 | 3.691 | 2.51
[7 empty] | 2164 | 148 | 3.6824 | 2.5037
[7 empty] | 2165 | 149 | 3.6824 | 2.5037
[7 empty] | 2166 | 150 | 3.691 | 2.51
[7 empty] | 2167 | 151 | 4.8007 | 3.3158
[7 empty] | 2168 | 152 | 6.3664 | 4.4527
[7 empty] | 2169 | 153 | 6.9944 | 4.9088
[7 empty] | 2170 | 154 | 7.5707 | 5.3273
[7 empty] | 2171 | 155 | 7.4159 | 5.2149
[7 empty] | 2172 | 156 | 7.5879 | 5.3398
[7 empty] | 2173 | 157 | 8.3192 | 5.8708
[7 empty] | 2174 | 158 | 8.6546 | 6.1144
[7 empty] | 2175 | 159 | 8.9299 | 6.3143
[7 empty] | 2176 | 160 | 8.8009 | 6.2206
[7 empty] | 2177 | 161 | 9.5837 | 6.7891
[7 empty] | 2178 | 162 | 9.0762 | 6.4205
[7 empty] | 2179 | 163 | 9.4461 | 6.6891
[7 empty] | 2180 | 164 | 8.0611 | 5.6834
[7 empty] | 2181 | 165 | 11.2698 | 8.0135
[7 empty] | 2182 | 166 | 9.1708 | 6.4892
[7 empty] | 2183 | 167 | 5.4717 | 3.8031
[7 empty] | 2184 | 168 | 4.8093 | 3.3221
[7 empty] | 2185 | 1 | 3.3125 | 2.2351
[7 empty] | 2186 | 2 | 3.2007 | 2.1539
[7 empty] | 2187 | 3 | 3.1921 | 2.1476
[7 empty] | 2188 | 4 | 3.3297 | 2.2476
[7 empty] | 2189 | 5 | 3.3469 | 2.2601
[7 empty] | 2190 | 6 | 3.7857 | 2.5787
[7 empty] | 2191 | 7 | 4.5255 | 3.1159
[7 empty] | 2192 | 8 | 5.2137 | 3.6157
[7 empty] | 2193 | 9 | 5.1879 | 3.5969
[7 empty] | 2194 | 10 | 6.7449 | 4.7276
[7 empty] | 2195 | 11 | 8.8783 | 6.2768
[7 empty] | 2196 | 12 | 9.8676 | 6.9952
[7 empty] | 2197 | 13 | 10.2547 | 7.2763
[7 empty] | 2198 | 14 | 10.031 | 7.1139
[7 empty] | 2199 | 15 | 9.9364 | 7.0452
[7 empty] | 2200 | 16 | 11.1494 | 7.926
[7 empty] | 2201 | 17 | 12.5086 | 8.913
[7 empty] | 2202 | 18 | 12.2591 | 8.7319
[7 empty] | 2203 | 19 | 12.801 | 9.1254
[7 empty] | 2204 | 20 | 12.7322 | 9.0755
[7 empty] | 2205 | 21 | 13.3172 | 9.5002
[7 empty] | 2206 | 22 | 9.2568 | 6.5517
[7 empty] | 2207 | 23 | 5.3857 | 3.7406
[7 empty] | 2208 | 24 | 3.6704 | 2.495
[7 empty] | 2209 | 25 | 3.5706 | 2.4225
[7 empty] | 2210 | 26 | 3.4588 | 2.3413
[7 empty] | 2211 | 27 | 3.3555 | 2.2663
[7 empty] | 2212 | 28 | 3.4416 | 2.3288
[7 empty] | 2213 | 29 | 3.691 | 2.51
[7 empty] | 2214 | 30 | 3.9405 | 2.6911
[7 empty] | 2215 | 31 | 4.8093 | 3.3221
[7 empty] | 2216 | 32 | 5.1706 | 3.5844
[7 empty] | 2217 | 33 | 5.8502 | 4.0779
[7 empty] | 2218 | 34 | 6.7707 | 4.7464
[7 empty] | 2219 | 35 | 8.9987 | 6.3643
[7 empty] | 2220 | 36 | 10.0569 | 7.1327
[7 empty] | 2221 | 37 | 10.1343 | 7.1889
[7 empty] | 2222 | 38 | 10.2117 | 7.2451
[7 empty] | 2223 | 39 | 9.8762 | 7.0015
[7 empty] | 2224 | 40 | 10.9601 | 7.7886
[7 empty] | 2225 | 41 | 11.5279 | 8.2009
[7 empty] | 2226 | 42 | 11.5451 | 8.2134
[7 empty] | 2227 | 43 | 11.9236 | 8.4882
[7 empty] | 2228 | 44 | 13.1107 | 9.3503
[7 empty] | 2229 | 45 | 12.6978 | 9.0505
[7 empty] | 2230 | 46 | 9.8762 | 7.0015
[7 empty] | 2231 | 47 | 6.1771 | 4.3153
[7 empty] | 2232 | 48 | 4.6373 | 3.1971
[7 empty] | 2233 | 49 | 3.9577 | 2.7036
[7 empty] | 2234 | 50 | 3.6394 | 2.4725
[7 empty] | 2235 | 51 | 3.5276 | 2.3913
[7 empty] | 2236 | 52 | 3.562 | 2.4163
[7 empty] | 2237 | 53 | 3.5878 | 2.435
[7 empty] | 2238 | 54 | 4.1814 | 2.866
[7 empty] | 2239 | 55 | 5.3513 | 3.7156
[7 empty] | 2240 | 56 | 5.6008 | 3.8968
[7 empty] | 2241 | 57 | 6.5729 | 4.6027
[7 empty] | 2242 | 58 | 7.7084 | 5.4273
[7 empty] | 2243 | 59 | 8.9471 | 6.3268
[7 empty] | 2244 | 60 | 9.5923 | 6.7953
[7 empty] | 2245 | 61 | 10.2891 | 7.3013
[7 empty] | 2246 | 62 | 10.0827 | 7.1514
[7 empty] | 2247 | 63 | 10.6934 | 7.5949
[7 empty] | 2248 | 64 | 11.6655 | 8.3008
[7 empty] | 2249 | 65 | 12.3021 | 8.7631
[7 empty] | 2250 | 66 | 12.1989 | 8.6882
[7 empty] | 2251 | 67 | 12.9559 | 9.2379
[7 empty] | 2252 | 68 | 13.2054 | 9.419
[7 empty] | 2253 | 69 | 12.6806 | 9.038
[7 empty] | 2254 | 70 | 10.3235 | 7.3263
[7 empty] | 2255 | 71 | 5.6868 | 3.9592
[7 empty] | 2256 | 72 | 4.5734 | 3.1507
[7 empty] | 2257 | 73 | 3.8373 | 2.6162
[7 empty] | 2258 | 74 | 3.605 | 2.4475
[7 empty] | 2259 | 75 | 3.5018 | 2.3725
[7 empty] | 2260 | 76 | 3.4416 | 2.3288
[7 empty] | 2261 | 77 | 3.6222 | 2.46
[7 empty] | 2262 | 78 | 4.0351 | 2.7598
[7 empty] | 2263 | 79 | 5.1793 | 3.5907
[7 empty] | 2264 | 80 | 5.3599 | 3.7219
[7 empty] | 2265 | 81 | 6.5729 | 4.6027
[7 empty] | 2266 | 82 | 7.6912 | 5.4148
[7 empty] | 2267 | 83 | 8.4482 | 5.9645
[7 empty] | 2268 | 84 | 9.7214 | 6.889
[7 empty] | 2269 | 85 | 9.4117 | 6.6642
[7 empty] | 2270 | 86 | 8.8869 | 6.2831
[7 empty] | 2271 | 87 | 9.3428 | 6.6142
[7 empty] | 2272 | 88 | 10.0224 | 7.1077
[7 empty] | 2273 | 89 | 11.4074 | 8.1134
[7 empty] | 2274 | 90 | 10.8053 | 7.6762
[7 empty] | 2275 | 91 | 11.5107 | 8.1884
[7 empty] | 2276 | 92 | 10.8913 | 7.7386
[7 empty] | 2277 | 93 | 8.4138 | 5.9395
[7 empty] | 2278 | 94 | 7.4847 | 5.2648
[7 empty] | 2279 | 95 | 5.575 | 3.878
[7 empty] | 2280 | 96 | 4.5599 | 3.1409
[7 empty] | 2281 | 97 | 4.5083 | 3.1034
[7 empty] | 2282 | 98 | 4.2072 | 2.8848
[7 empty] | 2283 | 99 | 4.147 | 2.841
[7 empty] | 2284 | 100 | 3.7857 | 2.5787
[7 empty] | 2285 | 101 | 3.7254 | 2.5349
[7 empty] | 2286 | 102 | 3.9663 | 2.7099
[7 empty] | 2287 | 103 | 4.7319 | 3.2658
[7 empty] | 2288 | 104 | 4.99 | 3.4532
[7 empty] | 2289 | 105 | 5.4889 | 3.8156
[7 empty] | 2290 | 106 | 6.9858 | 4.9025
[7 empty] | 2291 | 107 | 7.3471 | 5.1649
[7 empty] | 2292 | 108 | 8.9643 | 6.3393
[7 empty] | 2293 | 109 | 8.2847 | 5.8458
[7 empty] | 2294 | 110 | 7.8202 | 5.5085
[7 empty] | 2295 | 111 | 7.6568 | 5.3898
[7 empty] | 2296 | 112 | 7.7256 | 5.4398
[7 empty] | 2297 | 113 | 7.3729 | 5.1836
[7 empty] | 2298 | 114 | 7.5449 | 5.3086
[7 empty] | 2299 | 115 | 7.0804 | 4.9712
[7 empty] | 2300 | 116 | 7.7772 | 5.4772
[7 empty] | 2301 | 117 | 7.3471 | 5.1649
[7 empty] | 2302 | 118 | 6.5556 | 4.5902
[7 empty] | 2303 | 119 | 4.9212 | 3.4033
[7 empty] | 2304 | 120 | 4.5954 | 3.1667
[7 empty] | 2305 | 121 | 3.8459 | 2.6224
[7 empty] | 2306 | 122 | 3.4243 | 2.3163
[7 empty] | 2307 | 123 | 3.3383 | 2.2538
[7 empty] | 2308 | 124 | 3.3039 | 2.2289
[7 empty] | 2309 | 125 | 3.2609 | 2.1976
[7 empty] | 2310 | 126 | 3.4071 | 2.3038
[7 empty] | 2311 | 127 | 4.9556 | 3.4283
[7 empty] | 2312 | 128 | 6.5556 | 4.5902
[7 empty] | 2313 | 129 | 7.2524 | 5.0962
[7 empty] | 2314 | 130 | 7.6998 | 5.421
[7 empty] | 2315 | 131 | 7.8632 | 5.5397
[7 empty] | 2316 | 132 | 7.6051 | 5.3523
[7 empty] | 2317 | 133 | 8.2589 | 5.8271
[7 empty] | 2318 | 134 | 8.5686 | 6.052
[7 empty] | 2319 | 135 | 8.6374 | 6.1019
[7 empty] | 2320 | 136 | 7.803 | 5.496
[7 empty] | 2321 | 137 | 7.6998 | 5.421
[7 empty] | 2322 | 138 | 7.6482 | 5.3835
[7 empty] | 2323 | 139 | 7.3041 | 5.1337
[7 empty] | 2324 | 140 | 7.3127 | 5.1399
[7 empty] | 2325 | 141 | 6.6417 | 4.6526
[7 empty] | 2326 | 142 | 5.9879 | 4.1779
[7 empty] | 2327 | 143 | 5.0846 | 3.522
[7 empty] | 2328 | 144 | 4.4566 | 3.0659
[7 empty] | 2329 | 145 | 3.9749 | 2.7161
[7 empty] | 2330 | 146 | 3.7598 | 2.5599
[7 empty] | 2331 | 147 | 3.691 | 2.51
[7 empty] | 2332 | 148 | 3.6824 | 2.5037
[7 empty] | 2333 | 149 | 3.6824 | 2.5037
[7 empty] | 2334 | 150 | 3.691 | 2.51
[7 empty] | 2335 | 151 | 4.8007 | 3.3158
[7 empty] | 2336 | 152 | 6.3664 | 4.4527
[7 empty] | 2337 | 153 | 6.9944 | 4.9088
[7 empty] | 2338 | 154 | 7.5707 | 5.3273
[7 empty] | 2339 | 155 | 7.4159 | 5.2149
[7 empty] | 2340 | 156 | 7.5879 | 5.3398
[7 empty] | 2341 | 157 | 8.3192 | 5.8708
[7 empty] | 2342 | 158 | 8.6546 | 6.1144
[7 empty] | 2343 | 159 | 8.9299 | 6.3143
[7 empty] | 2344 | 160 | 8.8009 | 6.2206
[7 empty] | 2345 | 161 | 9.5837 | 6.7891
[7 empty] | 2346 | 162 | 9.0762 | 6.4205
[7 empty] | 2347 | 163 | 9.4461 | 6.6891
[7 empty] | 2348 | 164 | 8.0611 | 5.6834
[7 empty] | 2349 | 165 | 11.2698 | 8.0135
[7 empty] | 2350 | 166 | 9.1708 | 6.4892
[7 empty] | 2351 | 167 | 5.4717 | 3.8031
[7 empty] | 2352 | 168 | 4.8093 | 3.3221
[7 empty] | 2353 | 1 | 3.3125 | 2.2351
[7 empty] | 2354 | 2 | 3.2007 | 2.1539
[7 empty] | 2355 | 3 | 3.1921 | 2.1476
[7 empty] | 2356 | 4 | 3.3297 | 2.2476
[7 empty] | 2357 | 5 | 3.3469 | 2.2601
[7 empty] | 2358 | 6 | 3.7857 | 2.5787
[7 empty] | 2359 | 7 | 4.5255 | 3.1159
[7 empty] | 2360 | 8 | 5.2137 | 3.6157
[7 empty] | 2361 | 9 | 5.1879 | 3.5969
[7 empty] | 2362 | 10 | 6.7449 | 4.7276
[7 empty] | 2363 | 11 | 8.8783 | 6.2768
[7 empty] | 2364 | 12 | 9.8676 | 6.9952
[7 empty] | 2365 | 13 | 10.2547 | 7.2763
[7 empty] | 2366 | 14 | 10.031 | 7.1139
[7 empty] | 2367 | 15 | 9.9364 | 7.0452
[7 empty] | 2368 | 16 | 11.1494 | 7.926
[7 empty] | 2369 | 17 | 12.5086 | 8.913
[7 empty] | 2370 | 18 | 12.2591 | 8.7319
[7 empty] | 2371 | 19 | 12.801 | 9.1254
[7 empty] | 2372 | 20 | 12.7322 | 9.0755
[7 empty] | 2373 | 21 | 13.3172 | 9.5002
[7 empty] | 2374 | 22 | 9.2568 | 6.5517
[7 empty] | 2375 | 23 | 5.3857 | 3.7406
[7 empty] | 2376 | 24 | 3.6704 | 2.495
[7 empty] | 2377 | 25 | 3.5706 | 2.4225
[7 empty] | 2378 | 26 | 3.4588 | 2.3413
[7 empty] | 2379 | 27 | 3.3555 | 2.2663
[7 empty] | 2380 | 28 | 3.4416 | 2.3288
[7 empty] | 2381 | 29 | 3.691 | 2.51
[7 empty] | 2382 | 30 | 3.9405 | 2.6911
[7 empty] | 2383 | 31 | 4.8093 | 3.3221
[7 empty] | 2384 | 32 | 5.1706 | 3.5844
[7 empty] | 2385 | 33 | 5.8502 | 4.0779
[7 empty] | 2386 | 34 | 6.7707 | 4.7464
[7 empty] | 2387 | 35 | 8.9987 | 6.3643
[7 empty] | 2388 | 36 | 10.0569 | 7.1327
[7 empty] | 2389 | 37 | 10.1343 | 7.1889
[7 empty] | 2390 | 38 | 10.2117 | 7.2451
[7 empty] | 2391 | 39 | 9.8762 | 7.0015
[7 empty] | 2392 | 40 | 10.9601 | 7.7886
[7 empty] | 2393 | 41 | 11.5279 | 8.2009
[7 empty] | 2394 | 42 | 11.5451 | 8.2134
[7 empty] | 2395 | 43 | 11.9236 | 8.4882
[7 empty] | 2396 | 44 | 13.1107 | 9.3503
[7 empty] | 2397 | 45 | 12.6978 | 9.0505
[7 empty] | 2398 | 46 | 9.8762 | 7.0015
[7 empty] | 2399 | 47 | 6.1771 | 4.3153
[7 empty] | 2400 | 48 | 4.6373 | 3.1971
[7 empty] | 2401 | 49 | 3.9577 | 2.7036
[7 empty] | 2402 | 50 | 3.6394 | 2.4725
[7 empty] | 2403 | 51 | 3.5276 | 2.3913
[7 empty] | 2404 | 52 | 3.562 | 2.4163
[7 empty] | 2405 | 53 | 3.5878 | 2.435
[7 empty] | 2406 | 54 | 4.1814 | 2.866
[7 empty] | 2407 | 55 | 5.3513 | 3.7156
[7 empty] | 2408 | 56 | 5.6008 | 3.8968
[7 empty] | 2409 | 57 | 6.5729 | 4.6027
[7 empty] | 2410 | 58 | 7.7084 | 5.4273
[7 empty] | 2411 | 59 | 8.9471 | 6.3268
[7 empty] | 2412 | 60 | 9.5923 | 6.7953
[7 empty] | 2413 | 61 | 10.2891 | 7.3013
[7 empty] | 2414 | 62 | 10.0827 | 7.1514
[7 empty] | 2415 | 63 | 10.6934 | 7.5949
[7 empty] | 2416 | 64 | 11.6655 | 8.3008
[7 empty] | 2417 | 65 | 12.3021 | 8.7631
[7 empty] | 2418 | 66 | 12.1989 | 8.6882
[7 empty] | 2419 | 67 | 12.9559 | 9.2379
[7 empty] | 2420 | 68 | 13.2054 | 9.419
[7 empty] | 2421 | 69 | 12.6806 | 9.038
[7 empty] | 2422 | 70 | 10.3235 | 7.3263
[7 empty] | 2423 | 71 | 5.6868 | 3.9592
[7 empty] | 2424 | 72 | 4.5734 | 3.1507
[7 empty] | 2425 | 73 | 3.8373 | 2.6162
[7 empty] | 2426 | 74 | 3.605 | 2.4475
[7 empty] | 2427 | 75 | 3.5018 | 2.3725
[7 empty] | 2428 | 76 | 3.4416 | 2.3288
[7 empty] | 2429 | 77 | 3.6222 | 2.46
[7 empty] | 2430 | 78 | 4.0351 | 2.7598
[7 empty] | 2431 | 79 | 5.1793 | 3.5907
[7 empty] | 2432 | 80 | 5.3599 | 3.7219
[7 empty] | 2433 | 81 | 6.5729 | 4.6027
[7 empty] | 2434 | 82 | 7.6912 | 5.4148
[7 empty] | 2435 | 83 | 8.4482 | 5.9645
[7 empty] | 2436 | 84 | 9.7214 | 6.889
[7 empty] | 2437 | 85 | 9.4117 | 6.6642
[7 empty] | 2438 | 86 | 8.8869 | 6.2831
[7 empty] | 2439 | 87 | 9.3428 | 6.6142
[7 empty] | 2440 | 88 | 10.0224 | 7.1077
[7 empty] | 2441 | 89 | 11.4074 | 8.1134
[7 empty] | 2442 | 90 | 10.8053 | 7.6762
[7 empty] | 2443 | 91 | 11.5107 | 8.1884
[7 empty] | 2444 | 92 | 10.8913 | 7.7386
[7 empty] | 2445 | 93 | 8.4138 | 5.9395
[7 empty] | 2446 | 94 | 7.4847 | 5.2648
[7 empty] | 2447 | 95 | 5.575 | 3.878
[7 empty] | 2448 | 96 | 4.5599 | 3.1409
[7 empty] | 2449 | 97 | 4.5083 | 3.1034
[7 empty] | 2450 | 98 | 4.2072 | 2.8848
[7 empty] | 2451 | 99 | 4.147 | 2.841
[7 empty] | 2452 | 100 | 3.7857 | 2.5787
[7 empty] | 2453 | 101 | 3.7254 | 2.5349
[7 empty] | 2454 | 102 | 3.9663 | 2.7099
[7 empty] | 2455 | 103 | 4.7319 | 3.2658
[7 empty] | 2456 | 104 | 4.99 | 3.4532
[7 empty] | 2457 | 105 | 5.4889 | 3.8156
[7 empty] | 2458 | 106 | 6.9858 | 4.9025
[7 empty] | 2459 | 107 | 7.3471 | 5.1649
[7 empty] | 2460 | 108 | 8.9643 | 6.3393
[7 empty] | 2461 | 109 | 8.2847 | 5.8458
[7 empty] | 2462 | 110 | 7.8202 | 5.5085
[7 empty] | 2463 | 111 | 7.6568 | 5.3898
[7 empty] | 2464 | 112 | 7.7256 | 5.4398
[7 empty] | 2465 | 113 | 7.3729 | 5.1836
[7 empty] | 2466 | 114 | 7.5449 | 5.3086
[7 empty] | 2467 | 115 | 7.0804 | 4.9712
[7 empty] | 2468 | 116 | 7.7772 | 5.4772
[7 empty] | 2469 | 117 | 7.3471 | 5.1649
[7 empty] | 2470 | 118 | 6.5556 | 4.5902
[7 empty] | 2471 | 119 | 4.9212 | 3.4033
[7 empty] | 2472 | 120 | 4.5954 | 3.1667
[7 empty] | 2473 | 121 | 3.8459 | 2.6224
[7 empty] | 2474 | 122 | 3.4243 | 2.3163
[7 empty] | 2475 | 123 | 3.3383 | 2.2538
[7 empty] | 2476 | 124 | 3.3039 | 2.2289
[7 empty] | 2477 | 125 | 3.2609 | 2.1976
[7 empty] | 2478 | 126 | 3.4071 | 2.3038
[7 empty] | 2479 | 127 | 4.9556 | 3.4283
[7 empty] | 2480 | 128 | 6.5556 | 4.5902
[7 empty] | 2481 | 129 | 7.2524 | 5.0962
[7 empty] | 2482 | 130 | 7.6998 | 5.421
[7 empty] | 2483 | 131 | 7.8632 | 5.5397
[7 empty] | 2484 | 132 | 7.6051 | 5.3523
[7 empty] | 2485 | 133 | 8.2589 | 5.8271
[7 empty] | 2486 | 134 | 8.5686 | 6.052
[7 empty] | 2487 | 135 | 8.6374 | 6.1019
[7 empty] | 2488 | 136 | 7.803 | 5.496
[7 empty] | 2489 | 137 | 7.6998 | 5.421
[7 empty] | 2490 | 138 | 7.6482 | 5.3835
[7 empty] | 2491 | 139 | 7.3041 | 5.1337
[7 empty] | 2492 | 140 | 7.3127 | 5.1399
[7 empty] | 2493 | 141 | 6.6417 | 4.6526
[7 empty] | 2494 | 142 | 5.9879 | 4.1779
[7 empty] | 2495 | 143 | 5.0846 | 3.522
[7 empty] | 2496 | 144 | 4.4566 | 3.0659
[7 empty] | 2497 | 145 | 3.9749 | 2.7161
[7 empty] | 2498 | 146 | 3.7598 | 2.5599
[7 empty] | 2499 | 147 | 3.691 | 2.51
[7 empty] | 2500 | 148 | 3.6824 | 2.5037
[7 empty] | 2501 | 149 | 3.6824 | 2.5037
[7 empty] | 2502 | 150 | 3.691 | 2.51
[7 empty] | 2503 | 151 | 4.8007 | 3.3158
[7 empty] | 2504 | 152 | 6.3664 | 4.4527
[7 empty] | 2505 | 153 | 6.9944 | 4.9088
[7 empty] | 2506 | 154 | 7.5707 | 5.3273
[7 empty] | 2507 | 155 | 7.4159 | 5.2149
[7 empty] | 2508 | 156 | 7.5879 | 5.3398
[7 empty] | 2509 | 157 | 8.3192 | 5.8708
[7 empty] | 2510 | 158 | 8.6546 | 6.1144
[7 empty] | 2511 | 159 | 8.9299 | 6.3143
[7 empty] | 2512 | 160 | 8.8009 | 6.2206
[7 empty] | 2513 | 161 | 9.5837 | 6.7891
[7 empty] | 2514 | 162 | 9.0762 | 6.4205
[7 empty] | 2515 | 163 | 9.4461 | 6.6891
[7 empty] | 2516 | 164 | 8.0611 | 5.6834
[7 empty] | 2517 | 165 | 11.2698 | 8.0135
[7 empty] | 2518 | 166 | 9.1708 | 6.4892
[7 empty] | 2519 | 167 | 5.4717 | 3.8031
[7 empty] | 2520 | 168 | 4.8093 | 3.3221
[7 empty] | 2521 | 1 | 3.3125 | 2.2351
[7 empty] | 2522 | 2 | 3.2007 | 2.1539
[7 empty] | 2523 | 3 | 3.1921 | 2.1476
[7 empty] | 2524 | 4 | 3.3297 | 2.2476
[7 empty] | 2525 | 5 | 3.3469 | 2.2601
[7 empty] | 2526 | 6 | 3.7857 | 2.5787
[7 empty] | 2527 | 7 | 4.5255 | 3.1159
[7 empty] | 2528 | 8 | 5.2137 | 3.6157
[7 empty] | 2529 | 9 | 5.1879 | 3.5969
[7 empty] | 2530 | 10 | 6.7449 | 4.7276
[7 empty] | 2531 | 11 | 8.8783 | 6.2768
[7 empty] | 2532 | 12 | 9.8676 | 6.9952
[7 empty] | 2533 | 13 | 10.2547 | 7.2763
[7 empty] | 2534 | 14 | 10.031 | 7.1139
[7 empty] | 2535 | 15 | 9.9364 | 7.0452
[7 empty] | 2536 | 16 | 11.1494 | 7.926
[7 empty] | 2537 | 17 | 12.5086 | 8.913
[7 empty] | 2538 | 18 | 12.2591 | 8.7319
[7 empty] | 2539 | 19 | 12.801 | 9.1254
[7 empty] | 2540 | 20 | 12.7322 | 9.0755
[7 empty] | 2541 | 21 | 13.3172 | 9.5002
[7 empty] | 2542 | 22 | 9.2568 | 6.5517
[7 empty] | 2543 | 23 | 5.3857 | 3.7406
[7 empty] | 2544 | 24 | 3.6704 | 2.495
[7 empty] | 2545 | 25 | 3.5706 | 2.4225
[7 empty] | 2546 | 26 | 3.4588 | 2.3413
[7 empty] | 2547 | 27 | 3.3555 | 2.2663
[7 empty] | 2548 | 28 | 3.4416 | 2.3288
[7 empty] | 2549 | 29 | 3.691 | 2.51
[7 empty] | 2550 | 30 | 3.9405 | 2.6911
[7 empty] | 2551 | 31 | 4.8093 | 3.3221
[7 empty] | 2552 | 32 | 5.1706 | 3.5844
[7 empty] | 2553 | 33 | 5.8502 | 4.0779
[7 empty] | 2554 | 34 | 6.7707 | 4.7464
[7 empty] | 2555 | 35 | 8.9987 | 6.3643
[7 empty] | 2556 | 36 | 10.0569 | 7.1327
[7 empty] | 2557 | 37 | 10.1343 | 7.1889
[7 empty] | 2558 | 38 | 10.2117 | 7.2451
[7 empty] | 2559 | 39 | 9.8762 | 7.0015
[7 empty] | 2560 | 40 | 10.9601 | 7.7886
[7 empty] | 2561 | 41 | 11.5279 | 8.2009
[7 empty] | 2562 | 42 | 11.5451 | 8.2134
[7 empty] | 2563 | 43 | 11.9236 | 8.4882
[7 empty] | 2564 | 44 | 13.1107 | 9.3503
[7 empty] | 2565 | 45 | 12.6978 | 9.0505
[7 empty] | 2566 | 46 | 9.8762 | 7.0015
[7 empty] | 2567 | 47 | 6.1771 | 4.3153
[7 empty] | 2568 | 48 | 4.6373 | 3.1971
[7 empty] | 2569 | 49 | 3.9577 | 2.7036
[7 empty] | 2570 | 50 | 3.6394 | 2.4725
[7 empty] | 2571 | 51 | 3.5276 | 2.3913
[7 empty] | 2572 | 52 | 3.562 | 2.4163
[7 empty] | 2573 | 53 | 3.5878 | 2.435
[7 empty] | 2574 | 54 | 4.1814 | 2.866
[7 empty] | 2575 | 55 | 5.3513 | 3.7156
[7 empty] | 2576 | 56 | 5.6008 | 3.8968
[7 empty] | 2577 | 57 | 6.5729 | 4.6027
[7 empty] | 2578 | 58 | 7.7084 | 5.4273
[7 empty] | 2579 | 59 | 8.9471 | 6.3268
[7 empty] | 2580 | 60 | 9.5923 | 6.7953
[7 empty] | 2581 | 61 | 10.2891 | 7.3013
[7 empty] | 2582 | 62 | 10.0827 | 7.1514
[7 empty] | 2583 | 63 | 10.6934 | 7.5949
[7 empty] | 2584 | 64 | 11.6655 | 8.3008
[7 empty] | 2585 | 65 | 12.3021 | 8.7631
[7 empty] | 2586 | 66 | 12.1989 | 8.6882
[7 empty] | 2587 | 67 | 12.9559 | 9.2379
[7 empty] | 2588 | 68 | 13.2054 | 9.419
[7 empty] | 2589 | 69 | 12.6806 | 9.038
[7 empty] | 2590 | 70 | 10.3235 | 7.3263
[7 empty] | 2591 | 71 | 5.6868 | 3.9592
[7 empty] | 2592 | 72 | 4.5734 | 3.1507
[7 empty] | 2593 | 73 | 3.8373 | 2.6162
[7 empty] | 2594 | 74 | 3.605 | 2.4475
[7 empty] | 2595 | 75 | 3.5018 | 2.3725
[7 empty] | 2596 | 76 | 3.4416 | 2.3288
[7 empty] | 2597 | 77 | 3.6222 | 2.46
[7 empty] | 2598 | 78 | 4.0351 | 2.7598
[7 empty] | 2599 | 79 | 5.1793 | 3.5907
[7 empty] | 2600 | 80 | 5.3599 | 3.7219
[7 empty] | 2601 | 81 | 6.5729 | 4.6027
[7 empty] | 2602 | 82 | 7.6912 | 5.4148
[7 empty] | 2603 | 83 | 8.4482 | 5.9645
[7 empty] | 2604 | 84 | 9.7214 | 6.889
[7 empty] | 2605 | 85 | 9.4117 | 6.6642
[7 empty] | 2606 | 86 | 8.8869 | 6.2831
[7 empty] | 2607 | 87 | 9.3428 | 6.6142
[7 empty] | 2608 | 88 | 10.0224 | 7.1077
[7 empty] | 2609 | 89 | 11.4074 | 8.1134
[7 empty] | 2610 | 90 | 10.8053 | 7.6762
[7 empty] | 2611 | 91 | 11.5107 | 8.1884
[7 empty] | 2612 | 92 | 10.8913 | 7.7386
[7 empty] | 2613 | 93 | 8.4138 | 5.9395
[7 empty] | 2614 | 94 | 7.4847 | 5.2648
[7 empty] | 2615 | 95 | 5.575 | 3.878
[7 empty] | 2616 | 96 | 4.5599 | 3.1409
[7 empty] | 2617 | 97 | 4.5083 | 3.1034
[7 empty] | 2618 | 98 | 4.2072 | 2.8848
[7 empty] | 2619 | 99 | 4.147 | 2.841
[7 empty] | 2620 | 100 | 3.7857 | 2.5787
[7 empty] | 2621 | 101 | 3.7254 | 2.5349
[7 empty] | 2622 | 102 | 3.9663 | 2.7099
[7 empty] | 2623 | 103 | 4.7319 | 3.2658
[7 empty] | 2624 | 104 | 4.99 | 3.4532
[7 empty] | 2625 | 105 | 5.4889 | 3.8156
[7 empty] | 2626 | 106 | 6.9858 | 4.9025
[7 empty] | 2627 | 107 | 7.3471 | 5.1649
[7 empty] | 2628 | 108 | 8.9643 | 6.3393
[7 empty] | 2629 | 109 | 8.2847 | 5.8458
[7 empty] | 2630 | 110 | 7.8202 | 5.5085
[7 empty] | 2631 | 111 | 7.6568 | 5.3898
[7 empty] | 2632 | 112 | 7.7256 | 5.4398
[7 empty] | 2633 | 113 | 7.3729 | 5.1836
[7 empty] | 2634 | 114 | 7.5449 | 5.3086
[7 empty] | 2635 | 115 | 7.0804 | 4.9712
[7 empty] | 2636 | 116 | 7.7772 | 5.4772
[7 empty] | 2637 | 117 | 7.3471 | 5.1649
[7 empty] | 2638 | 118 | 6.5556 | 4.5902
[7 empty] | 2639 | 119 | 4.9212 | 3.4033
[7 empty] | 2640 | 120 | 4.5954 | 3.1667
[7 empty] | 2641 | 121 | 3.8459 | 2.6224
[7 empty] | 2642 | 122 | 3.4243 | 2.3163
[7 empty] | 2643 | 123 | 3.3383 | 2.2538
[7 empty] | 2644 | 124 | 3.3039 | 2.2289
[7 empty] | 2645 | 125 | 3.2609 | 2.1976
[7 empty] | 2646 | 126 | 3.4071 | 2.3038
[7 empty] | 2647 | 127 | 4.9556 | 3.4283
[7 empty] | 2648 | 128 | 6.5556 | 4.5902
[7 empty] | 2649 | 129 | 7.2524 | 5.0962
[7 empty] | 2650 | 130 | 7.6998 | 5.421
[7 empty] | 2651 | 131 | 7.8632 | 5.5397
[7 empty] | 2652 | 132 | 7.6051 | 5.3523
[7 empty] | 2653 | 133 | 8.2589 | 5.8271
[7 empty] | 2654 | 134 | 8.5686 | 6.052
[7 empty] | 2655 | 135 | 8.6374 | 6.1019
[7 empty] | 2656 | 136 | 7.803 | 5.496
[7 empty] | 2657 | 137 | 7.6998 | 5.421
[7 empty] | 2658 | 138 | 7.6482 | 5.3835
[7 empty] | 2659 | 139 | 7.3041 | 5.1337
[7 empty] | 2660 | 140 | 7.3127 | 5.1399
[7 empty] | 2661 | 141 | 6.6417 | 4.6526
[7 empty] | 2662 | 142 | 5.9879 | 4.1779
[7 empty] | 2663 | 143 | 5.0846 | 3.522
[7 empty] | 2664 | 144 | 4.4566 | 3.0659
[7 empty] | 2665 | 145 | 3.9749 | 2.7161
[7 empty] | 2666 | 146 | 3.7598 | 2.5599
[7 empty] | 2667 | 147 | 3.691 | 2.51
[7 empty] | 2668 | 148 | 3.6824 | 2.5037
[7 empty] | 2669 | 149 | 3.6824 | 2.5037
[7 empty] | 2670 | 150 | 3.691 | 2.51
[7 empty] | 2671 | 151 | 4.8007 | 3.3158
[7 empty] | 2672 | 152 | 6.3664 | 4.4527
[7 empty] | 2673 | 153 | 6.9944 | 4.9088
[7 empty] | 2674 | 154 | 7.5707 | 5.3273
[7 empty] | 2675 | 155 | 7.4159 | 5.2149
[7 empty] | 2676 | 156 | 7.5879 | 5.3398
[7 empty] | 2677 | 157 | 8.3192 | 5.8708
[7 empty] | 2678 | 158 | 8.6546 | 6.1144
[7 empty] | 2679 | 159 | 8.9299 | 6.3143
[7 empty] | 2680 | 160 | 8.8009 | 6.2206
[7 empty] | 2681 | 161 | 9.5837 | 6.7891
[7 empty] | 2682 | 162 | 9.0762 | 6.4205
[7 empty] | 2683 | 163 | 9.4461 | 6.6891
[7 empty] | 2684 | 164 | 8.0611 | 5.6834
[7 empty] | 2685 | 165 | 11.2698 | 8.0135
[7 empty] | 2686 | 166 | 9.1708 | 6.4892
[7 empty] | 2687 | 167 | 5.4717 | 3.8031
[7 empty] | 2688 | 168 | 4.8093 | 3.3221
[7 empty] | 2689 | 1 | 3.3125 | 2.2351
[7 empty] | 2690 | 2 | 3.2007 | 2.1539
[7 empty] | 2691 | 3 | 3.1921 | 2.1476
[7 empty] | 2692 | 4 | 3.3297 | 2.2476
[7 empty] | 2693 | 5 | 3.3469 | 2.2601
[7 empty] | 2694 | 6 | 3.7857 | 2.5787
[7 empty] | 2695 | 7 | 4.5255 | 3.1159
[7 empty] | 2696 | 8 | 5.2137 | 3.6157
[7 empty] | 2697 | 9 | 5.1879 | 3.5969
[7 empty] | 2698 | 10 | 6.7449 | 4.7276
[7 empty] | 2699 | 11 | 8.8783 | 6.2768
[7 empty] | 2700 | 12 | 9.8676 | 6.9952
[7 empty] | 2701 | 13 | 10.2547 | 7.2763
[7 empty] | 2702 | 14 | 10.031 | 7.1139
[7 empty] | 2703 | 15 | 9.9364 | 7.0452
[7 empty] | 2704 | 16 | 11.1494 | 7.926
[7 empty] | 2705 | 17 | 12.5086 | 8.913
[7 empty] | 2706 | 18 | 12.2591 | 8.7319
[7 empty] | 2707 | 19 | 12.801 | 9.1254
[7 empty] | 2708 | 20 | 12.7322 | 9.0755
[7 empty] | 2709 | 21 | 13.3172 | 9.5002
[7 empty] | 2710 | 22 | 9.2568 | 6.5517
[7 empty] | 2711 | 23 | 5.3857 | 3.7406
[7 empty] | 2712 | 24 | 3.6704 | 2.495
[7 empty] | 2713 | 25 | 3.5706 | 2.4225
[7 empty] | 2714 | 26 | 3.4588 | 2.3413
[7 empty] | 2715 | 27 | 3.3555 | 2.2663
[7 empty] | 2716 | 28 | 3.4416 | 2.3288
[7 empty] | 2717 | 29 | 3.691 | 2.51
[7 empty] | 2718 | 30 | 3.9405 | 2.6911
[7 empty] | 2719 | 31 | 4.8093 | 3.3221
[7 empty] | 2720 | 32 | 5.1706 | 3.5844
[7 empty] | 2721 | 33 | 5.8502 | 4.0779
[7 empty] | 2722 | 34 | 6.7707 | 4.7464
[7 empty] | 2723 | 35 | 8.9987 | 6.3643
[7 empty] | 2724 | 36 | 10.0569 | 7.1327
[7 empty] | 2725 | 37 | 10.1343 | 7.1889
[7 empty] | 2726 | 38 | 10.2117 | 7.2451
[7 empty] | 2727 | 39 | 9.8762 | 7.0015
[7 empty] | 2728 | 40 | 10.9601 | 7.7886
[7 empty] | 2729 | 41 | 11.5279 | 8.2009
[7 empty] | 2730 | 42 | 11.5451 | 8.2134
[7 empty] | 2731 | 43 | 11.9236 | 8.4882
[7 empty] | 2732 | 44 | 13.1107 | 9.3503
[7 empty] | 2733 | 45 | 12.6978 | 9.0505
[7 empty] | 2734 | 46 | 9.8762 | 7.0015
[7 empty] | 2735 | 47 | 6.1771 | 4.3153
[7 empty] | 2736 | 48 | 4.6373 | 3.1971
[7 empty] | 2737 | 49 | 3.9577 | 2.7036
[7 empty] | 2738 | 50 | 3.6394 | 2.4725
[7 empty] | 2739 | 51 | 3.5276 | 2.3913
[7 empty] | 2740 | 52 | 3.562 | 2.4163
[7 empty] | 2741 | 53 | 3.5878 | 2.435
[7 empty] | 2742 | 54 | 4.1814 | 2.866
[7 empty] | 2743 | 55 | 5.3513 | 3.7156
[7 empty] | 2744 | 56 | 5.6008 | 3.8968
[7 empty] | 2745 | 57 | 6.5729 | 4.6027
[7 empty] | 2746 | 58 | 7.7084 | 5.4273
[7 empty] | 2747 | 59 | 8.9471 | 6.3268
[7 empty] | 2748 | 60 | 9.5923 | 6.7953
[7 empty] | 2749 | 61 | 10.2891 | 7.3013
[7 empty] | 2750 | 62 | 10.0827 | 7.1514
[7 empty] | 2751 | 63 | 10.6934 | 7.5949
[7 empty] | 2752 | 64 | 11.6655 | 8.3008
[7 empty] | 2753 | 65 | 12.3021 | 8.7631
[7 empty] | 2754 | 66 | 12.1989 | 8.6882
[7 empty] | 2755 | 67 | 12.9559 | 9.2379
[7 empty] | 2756 | 68 | 13.2054 | 9.419
[7 empty] | 2757 | 69 | 12.6806 | 9.038
[7 empty] | 2758 | 70 | 10.3235 | 7.3263
[7 empty] | 2759 | 71 | 5.6868 | 3.9592
[7 empty] | 2760 | 72 | 4.5734 | 3.1507
[7 empty] | 2761 | 73 | 3.8373 | 2.6162
[7 empty] | 2762 | 74 | 3.605 | 2.4475
[7 empty] | 2763 | 75 | 3.5018 | 2.3725
[7 empty] | 2764 | 76 | 3.4416 | 2.3288
[7 empty] | 2765 | 77 | 3.6222 | 2.46
[7 empty] | 2766 | 78 | 4.0351 | 2.7598
[7 empty] | 2767 | 79 | 5.1793 | 3.5907
[7 empty] | 2768 | 80 | 5.3599 | 3.7219
[7 empty] | 2769 | 81 | 6.5729 | 4.6027
[7 empty] | 2770 | 82 | 7.6912 | 5.4148
[7 empty] | 2771 | 83 | 8.4482 | 5.9645
[7 empty] | 2772 | 84 | 9.7214 | 6.889
[7 empty] | 2773 | 85 | 9.4117 | 6.6642
[7 empty] | 2774 | 86 | 8.8869 | 6.2831
[7 empty] | 2775 | 87 | 9.3428 | 6.6142
[7 empty] | 2776 | 88 | 10.0224 | 7.1077
[7 empty] | 2777 | 89 | 11.4074 | 8.1134
[7 empty] | 2778 | 90 | 10.8053 | 7.6762
[7 empty] | 2779 | 91 | 11.5107 | 8.1884
[7 empty] | 2780 | 92 | 10.8913 | 7.7386
[7 empty] | 2781 | 93 | 8.4138 | 5.9395
[7 empty] | 2782 | 94 | 7.4847 | 5.2648
[7 empty] | 2783 | 95 | 5.575 | 3.878
[7 empty] | 2784 | 96 | 4.5599 | 3.1409
[7 empty] | 2785 | 97 | 4.5083 | 3.1034
[7 empty] | 2786 | 98 | 4.2072 | 2.8848
[7 empty] | 2787 | 99 | 4.147 | 2.841
[7 empty] | 2788 | 100 | 3.7857 | 2.5787
[7 empty] | 2789 | 101 | 3.7254 | 2.5349
[7 empty] | 2790 | 102 | 3.9663 | 2.7099
[7 empty] | 2791 | 103 | 4.7319 | 3.2658
[7 empty] | 2792 | 104 | 4.99 | 3.4532
[7 empty] | 2793 | 105 | 5.4889 | 3.8156
[7 empty] | 2794 | 106 | 6.9858 | 4.9025
[7 empty] | 2795 | 107 | 7.3471 | 5.1649
[7 empty] | 2796 | 108 | 8.9643 | 6.3393
[7 empty] | 2797 | 109 | 8.2847 | 5.8458
[7 empty] | 2798 | 110 | 7.8202 | 5.5085
[7 empty] | 2799 | 111 | 7.6568 | 5.3898
[7 empty] | 2800 | 112 | 7.7256 | 5.4398
[7 empty] | 2801 | 113 | 7.3729 | 5.1836
[7 empty] | 2802 | 114 | 7.5449 | 5.3086
[7 empty] | 2803 | 115 | 7.0804 | 4.9712
[7 empty] | 2804 | 116 | 7.7772 | 5.4772
[7 empty] | 2805 | 117 | 7.3471 | 5.1649
[7 empty] | 2806 | 118 | 6.5556 | 4.5902
[7 empty] | 2807 | 119 | 4.9212 | 3.4033
[7 empty] | 2808 | 120 | 4.5954 | 3.1667
[7 empty] | 2809 | 121 | 3.8459 | 2.6224
[7 empty] | 2810 | 122 | 3.4243 | 2.3163
[7 empty] | 2811 | 123 | 3.3383 | 2.2538
[7 empty] | 2812 | 124 | 3.3039 | 2.2289
[7 empty] | 2813 | 125 | 3.2609 | 2.1976
[7 empty] | 2814 | 126 | 3.4071 | 2.3038
[7 empty] | 2815 | 127 | 4.9556 | 3.4283
[7 empty] | 2816 | 128 | 6.5556 | 4.5902
[7 empty] | 2817 | 129 | 7.2524 | 5.0962
[7 empty] | 2818 | 130 | 7.6998 | 5.421
[7 empty] | 2819 | 131 | 7.8632 | 5.5397
[7 empty] | 2820 | 132 | 7.6051 | 5.3523
[7 empty] | 2821 | 133 | 8.2589 | 5.8271
[7 empty] | 2822 | 134 | 8.5686 | 6.052
[7 empty] | 2823 | 135 | 8.6374 | 6.1019
[7 empty] | 2824 | 136 | 7.803 | 5.496
[7 empty] | 2825 | 137 | 7.6998 | 5.421
[7 empty] | 2826 | 138 | 7.6482 | 5.3835
[7 empty] | 2827 | 139 | 7.3041 | 5.1337
[7 empty] | 2828 | 140 | 7.3127 | 5.1399
[7 empty] | 2829 | 141 | 6.6417 | 4.6526
[7 empty] | 2830 | 142 | 5.9879 | 4.1779
[7 empty] | 2831 | 143 | 5.0846 | 3.522
[7 empty] | 2832 | 144 | 4.4566 | 3.0659
[7 empty] | 2833 | 145 | 3.9749 | 2.7161
[7 empty] | 2834 | 146 | 3.7598 | 2.5599
[7 empty] | 2835 | 147 | 3.691 | 2.51
[7 empty] | 2836 | 148 | 3.6824 | 2.5037
[7 empty] | 2837 | 149 | 3.6824 | 2.5037
[7 empty] | 2838 | 150 | 3.691 | 2.51
[7 empty] | 2839 | 151 | 4.8007 | 3.3158
[7 empty] | 2840 | 152 | 6.3664 | 4.4527
[7 empty] | 2841 | 153 | 6.9944 | 4.9088
[7 empty] | 2842 | 154 | 7.5707 | 5.3273
[7 empty] | 2843 | 155 | 7.4159 | 5.2149
[7 empty] | 2844 | 156 | 7.5879 | 5.3398
[7 empty] | 2845 | 157 | 8.3192 | 5.8708
[7 empty] | 2846 | 158 | 8.6546 | 6.1144
[7 empty] | 2847 | 159 | 8.9299 | 6.3143
[7 empty] | 2848 | 160 | 8.8009 | 6.2206
[7 empty] | 2849 | 161 | 9.5837 | 6.7891
[7 empty] | 2850 | 162 | 9.0762 | 6.4205
[7 empty] | 2851 | 163 | 9.4461 | 6.6891
[7 empty] | 2852 | 164 | 8.0611 | 5.6834
[7 empty] | 2853 | 165 | 11.2698 | 8.0135
[7 empty] | 2854 | 166 | 9.1708 | 6.4892
[7 empty] | 2855 | 167 | 5.4717 | 3.8031
[7 empty] | 2856 | 168 | 4.8093 | 3.3221
[7 empty] | 2857 | 1 | 3.3125 | 2.2351
[7 empty] | 2858 | 2 | 3.2007 | 2.1539
[7 empty] | 2859 | 3 | 3.1921 | 2.1476
[7 empty] | 2860 | 4 | 3.3297 | 2.2476
[7 empty] | 2861 | 5 | 3.3469 | 2.2601
[7 empty] | 2862 | 6 | 3.7857 | 2.5787
[7 empty] | 2863 | 7 | 4.5255 | 3.1159
[7 empty] | 2864 | 8 | 5.2137 | 3.6157
[7 empty] | 2865 | 9 | 5.1879 | 3.5969
[7 empty] | 2866 | 10 | 6.7449 | 4.7276
[7 empty] | 2867 | 11 | 8.8783 | 6.2768
[7 empty] | 2868 | 12 | 9.8676 | 6.9952
[7 empty] | 2869 | 13 | 10.2547 | 7.2763
[7 empty] | 2870 | 14 | 10.031 | 7.1139
[7 empty] | 2871 | 15 | 9.9364 | 7.0452
[7 empty] | 2872 | 16 | 11.1494 | 7.926
[7 empty] | 2873 | 17 | 12.5086 | 8.913
[7 empty] | 2874 | 18 | 12.2591 | 8.7319
[7 empty] | 2875 | 19 | 12.801 | 9.1254
[7 empty] | 2876 | 20 | 12.7322 | 9.0755
[7 empty] | 2877 | 21 | 13.3172 | 9.5002
[7 empty] | 2878 | 22 | 9.2568 | 6.5517
[7 empty] | 2879 | 23 | 5.3857 | 3.7406
[7 empty] | 2880 | 24 | 3.6704 | 2.495
[7 empty] | 2881 | 25 | 3.5706 | 2.4225
[7 empty] | 2882 | 26 | 3.4588 | 2.3413
[7 empty] | 2883 | 27 | 3.3555 | 2.2663
[7 empty] | 2884 | 28 | 3.4416 | 2.3288
[7 empty] | 2885 | 29 | 3.691 | 2.51
[7 empty] | 2886 | 30 | 3.9405 | 2.6911
[7 empty] | 2887 | 31 | 4.8093 | 3.3221
[7 empty] | 2888 | 32 | 5.1706 | 3.5844
[7 empty] | 2889 | 33 | 5.8502 | 4.0779
[7 empty] | 2890 | 34 | 6.7707 | 4.7464
[7 empty] | 2891 | 35 | 8.9987 | 6.3643
[7 empty] | 2892 | 36 | 10.0569 | 7.1327
[7 empty] | 2893 | 37 | 10.1343 | 7.1889
[7 empty] | 2894 | 38 | 10.2117 | 7.2451
[7 empty] | 2895 | 39 | 9.8762 | 7.0015
[7 empty] | 2896 | 40 | 10.9601 | 7.7886
[7 empty] | 2897 | 41 | 11.5279 | 8.2009
[7 empty] | 2898 | 42 | 11.5451 | 8.2134
[7 empty] | 2899 | 43 | 11.9236 | 8.4882
[7 empty] | 2900 | 44 | 13.1107 | 9.3503
[7 empty] | 2901 | 45 | 12.6978 | 9.0505
[7 empty] | 2902 | 46 | 9.8762 | 7.0015
[7 empty] | 2903 | 47 | 6.1771 | 4.3153
[7 empty] | 2904 | 48 | 4.6373 | 3.1971
[7 empty] | 2905 | 49 | 3.9577 | 2.7036
[7 empty] | 2906 | 50 | 3.6394 | 2.4725
[7 empty] | 2907 | 51 | 3.5276 | 2.3913
[7 empty] | 2908 | 52 | 3.562 | 2.4163
[7 empty] | 2909 | 53 | 3.5878 | 2.435
[7 empty] | 2910 | 54 | 4.1814 | 2.866
[7 empty] | 2911 | 55 | 5.3513 | 3.7156
[7 empty] | 2912 | 56 | 5.6008 | 3.8968
[7 empty] | 2913 | 57 | 6.5729 | 4.6027
[7 empty] | 2914 | 58 | 7.7084 | 5.4273
[7 empty] | 2915 | 59 | 8.9471 | 6.3268
[7 empty] | 2916 | 60 | 9.5923 | 6.7953
[7 empty] | 2917 | 61 | 10.2891 | 7.3013
[7 empty] | 2918 | 62 | 10.0827 | 7.1514
[7 empty] | 2919 | 63 | 10.6934 | 7.5949
[7 empty] | 2920 | 64 | 11.6655 | 8.3008
[7 empty] | 2921 | 65 | 12.3021 | 8.7631
[7 empty] | 2922 | 66 | 12.1989 | 8.6882
[7 empty] | 2923 | 67 | 12.9559 | 9.2379
[7 empty] | 2924 | 68 | 13.2054 | 9.419
[7 empty] | 2925 | 69 | 12.6806 | 9.038
[7 empty] | 2926 | 70 | 10.3235 | 7.3263
[7 empty] | 2927 | 71 | 5.6868 | 3.9592
[7 empty] | 2928 | 72 | 4.5734 | 3.1507
[7 empty] | 2929 | 73 | 3.8373 | 2.6162
[7 empty] | 2930 | 74 | 3.605 | 2.4475
[7 empty] | 2931 | 75 | 3.5018 | 2.3725
[7 empty] | 2932 | 76 | 3.4416 | 2.3288
[7 empty] | 2933 | 77 | 3.6222 | 2.46
[7 empty] | 2934 | 78 | 4.0351 | 2.7598
[7 empty] | 2935 | 79 | 5.1793 | 3.5907
[7 empty] | 2936 | 80 | 5.3599 | 3.7219
[7 empty] | 2937 | 81 | 6.5729 | 4.6027
[7 empty] | 2938 | 82 | 7.6912 | 5.4148
[7 empty] | 2939 | 83 | 8.4482 | 5.9645
[7 empty] | 2940 | 84 | 9.7214 | 6.889
[7 empty] | 2941 | 85 | 9.4117 | 6.6642
[7 empty] | 2942 | 86 | 8.8869 | 6.2831
[7 empty] | 2943 | 87 | 9.3428 | 6.6142
[7 empty] | 2944 | 88 | 10.0224 | 7.1077
[7 empty] | 2945 | 89 | 11.4074 | 8.1134
[7 empty] | 2946 | 90 | 10.8053 | 7.6762
[7 empty] | 2947 | 91 | 11.5107 | 8.1884
[7 empty] | 2948 | 92 | 10.8913 | 7.7386
[7 empty] | 2949 | 93 | 8.4138 | 5.9395
[7 empty] | 2950 | 94 | 7.4847 | 5.2648
[7 empty] | 2951 | 95 | 5.575 | 3.878
[7 empty] | 2952 | 96 | 4.5599 | 3.1409
[7 empty] | 2953 | 97 | 4.5083 | 3.1034
[7 empty] | 2954 | 98 | 4.2072 | 2.8848
[7 empty] | 2955 | 99 | 4.147 | 2.841
[7 empty] | 2956 | 100 | 3.7857 | 2.5787
[7 empty] | 2957 | 101 | 3.7254 | 2.5349
[7 empty] | 2958 | 102 | 3.9663 | 2.7099
[7 empty] | 2959 | 103 | 4.7319 | 3.2658
[7 empty] | 2960 | 104 | 4.99 | 3.4532
[7 empty] | 2961 | 105 | 5.4889 | 3.8156
[7 empty] | 2962 | 106 | 6.9858 | 4.9025
[7 empty] | 2963 | 107 | 7.3471 | 5.1649
[7 empty] | 2964 | 108 | 8.9643 | 6.3393
[7 empty] | 2965 | 109 | 8.2847 | 5.8458
[7 empty] | 2966 | 110 | 7.8202 | 5.5085
[7 empty] | 2967 | 111 | 7.6568 | 5.3898
[7 empty] | 2968 | 112 | 7.7256 | 5.4398
[7 empty] | 2969 | 113 | 7.3729 | 5.1836
[7 empty] | 2970 | 114 | 7.5449 | 5.3086
[7 empty] | 2971 | 115 | 7.0804 | 4.9712
[7 empty] | 2972 | 116 | 7.7772 | 5.4772
[7 empty] | 2973 | 117 | 7.3471 | 5.1649
[7 empty] | 2974 | 118 | 6.5556 | 4.5902
[7 empty] | 2975 | 119 | 4.9212 | 3.4033
[7 empty] | 2976 | 120 | 4.5954 | 3.1667
[7 empty] | 2977 | 121 | 3.8459 | 2.6224
[7 empty] | 2978 | 122 | 3.4243 | 2.3163
[7 empty] | 2979 | 123 | 3.3383 | 2.2538
[7 empty] | 2980 | 124 | 3.3039 | 2.2289
[7 empty] | 2981 | 125 | 3.2609 | 2.1976
[7 empty] | 2982 | 126 | 3.4071 | 2.3038
[7 empty] | 2983 | 127 | 4.9556 | 3.4283
[7 empty] | 2984 | 128 | 6.5556 | 4.5902
[7 empty] | 2985 | 129 | 7.2524 | 5.0962
[7 empty] | 2986 | 130 | 7.6998 | 5.421
[7 empty] | 2987 | 131 | 7.8632 | 5.5397
[7 empty] | 2988 | 132 | 7.6051 | 5.3523
[7 empty] | 2989 | 133 | 8.2589 | 5.8271
[7 empty] | 2990 | 134 | 8.5686 | 6.052
[7 empty] | 2991 | 135 | 8.6374 | 6.1019
[7 empty] | 2992 | 136 | 7.803 | 5.496
[7 empty] | 2993 | 137 | 7.6998 | 5.421
[7 empty] | 2994 | 138 | 7.6482 | 5.3835
[7 empty] | 2995 | 139 | 7.3041 | 5.1337
[7 empty] | 2996 | 140 | 7.3127 | 5.1399
[7 empty] | 2997 | 141 | 6.6417 | 4.6526
[7 empty] | 2998 | 142 | 5.9879 | 4.1779
[7 empty] | 2999 | 143 | 5.0846 | 3.522
[7 empty] | 3000 | 144 | 4.4566 | 3.0659
[7 empty] | 3001 | 145 | 3.9749 | 2.7161
[7 empty] | 3002 | 146 | 3.7598 | 2.5599
[7 empty] | 3003 | 147 | 3.691 | 2.51
[7 empty] | 3004 | 148 | 3.6824 | 2.5037
[7 empty] | 3005 | 149 | 3.6824 | 2.5037
[7 empty] | 3006 | 150 | 3.691 | 2.51
[7 empty] | 3007 | 151 | 4.8007 | 3.3158
[7 empty] | 3008 | 152 | 6.3664 | 4.4527
[7 empty] | 3009 | 153 | 6.9944 | 4.9088
[7 empty] | 3010 | 154 | 7.5707 | 5.3273
[7 empty] | 3011 | 155 | 7.4159 | 5.2149
[7 empty] | 3012 | 156 | 7.5879 | 5.3398
[7 empty] | 3013 | 157 | 8.3192 | 5.8708
[7 empty] | 3014 | 158 | 8.6546 | 6.1144
[7 empty] | 3015 | 159 | 8.9299 | 6.3143
[7 empty] | 3016 | 160 | 8.8009 | 6.2206
[7 empty] | 3017 | 161 | 9.5837 | 6.7891
[7 empty] | 3018 | 162 | 9.0762 | 6.4205
[7 empty] | 3019 | 163 | 9.4461 | 6.6891
[7 empty] | 3020 | 164 | 8.0611 | 5.6834
[7 empty] | 3021 | 165 | 11.2698 | 8.0135
[7 empty] | 3022 | 166 | 9.1708 | 6.4892
[7 empty] | 3023 | 167 | 5.4717 | 3.8031
[7 empty] | 3024 | 168 | 4.8093 | 3.3221
[7 empty] | 3025 | 1 | 3.3125 | 2.2351
[7 empty] | 3026 | 2 | 3.2007 | 2.1539
[7 empty] | 3027 | 3 | 3.1921 | 2.1476
[7 empty] | 3028 | 4 | 3.3297 | 2.2476
[7 empty] | 3029 | 5 | 3.3469 | 2.2601
[7 empty] | 3030 | 6 | 3.7857 | 2.5787
[7 empty] | 3031 | 7 | 4.5255 | 3.1159
[7 empty] | 3032 | 8 | 5.2137 | 3.6157
[7 empty] | 3033 | 9 | 5.1879 | 3.5969
[7 empty] | 3034 | 10 | 6.7449 | 4.7276
[7 empty] | 3035 | 11 | 8.8783 | 6.2768
[7 empty] | 3036 | 12 | 9.8676 | 6.9952
[7 empty] | 3037 | 13 | 10.2547 | 7.2763
[7 empty] | 3038 | 14 | 10.031 | 7.1139
[7 empty] | 3039 | 15 | 9.9364 | 7.0452
[7 empty] | 3040 | 16 | 11.1494 | 7.926
[7 empty] | 3041 | 17 | 12.5086 | 8.913
[7 empty] | 3042 | 18 | 12.2591 | 8.7319
[7 empty] | 3043 | 19 | 12.801 | 9.1254
[7 empty] | 3044 | 20 | 12.7322 | 9.0755
[7 empty] | 3045 | 21 | 13.3172 | 9.5002
[7 empty] | 3046 | 22 | 9.2568 | 6.5517
[7 empty] | 3047 | 23 | 5.3857 | 3.7406
[7 empty] | 3048 | 24 | 3.6704 | 2.495
[7 empty] | 3049 | 25 | 3.5706 | 2.4225
[7 empty] | 3050 | 26 | 3.4588 | 2.3413
[7 empty] | 3051 | 27 | 3.3555 | 2.2663
[7 empty] | 3052 | 28 | 3.4416 | 2.3288
[7 empty] | 3053 | 29 | 3.691 | 2.51
[7 empty] | 3054 | 30 | 3.9405 | 2.6911
[7 empty] | 3055 | 31 | 4.8093 | 3.3221
[7 empty] | 3056 | 32 | 5.1706 | 3.5844
[7 empty] | 3057 | 33 | 5.8502 | 4.0779
[7 empty] | 3058 | 34 | 6.7707 | 4.7464
[7 empty] | 3059 | 35 | 8.9987 | 6.3643
[7 empty] | 3060 | 36 | 10.0569 | 7.1327
[7 empty] | 3061 | 37 | 10.1343 | 7.1889
[7 empty] | 3062 | 38 | 10.2117 | 7.2451
[7 empty] | 3063 | 39 | 9.8762 | 7.0015
[7 empty] | 3064 | 40 | 10.9601 | 7.7886
[7 empty] | 3065 | 41 | 11.5279 | 8.2009
[7 empty] | 3066 | 42 | 11.5451 | 8.2134
[7 empty] | 3067 | 43 | 11.9236 | 8.4882
[7 empty] | 3068 | 44 | 13.1107 | 9.3503
[7 empty] | 3069 | 45 | 12.6978 | 9.0505
[7 empty] | 3070 | 46 | 9.8762 | 7.0015
[7 empty] | 3071 | 47 | 6.1771 | 4.3153
[7 empty] | 3072 | 48 | 4.6373 | 3.1971
[7 empty] | 3073 | 49 | 3.9577 | 2.7036
[7 empty] | 3074 | 50 | 3.6394 | 2.4725
[7 empty] | 3075 | 51 | 3.5276 | 2.3913
[7 empty] | 3076 | 52 | 3.562 | 2.4163
[7 empty] | 3077 | 53 | 3.5878 | 2.435
[7 empty] | 3078 | 54 | 4.1814 | 2.866
[7 empty] | 3079 | 55 | 5.3513 | 3.7156
[7 empty] | 3080 | 56 | 5.6008 | 3.8968
[7 empty] | 3081 | 57 | 6.5729 | 4.6027
[7 empty] | 3082 | 58 | 7.7084 | 5.4273
[7 empty] | 3083 | 59 | 8.9471 | 6.3268
[7 empty] | 3084 | 60 | 9.5923 | 6.7953
[7 empty] | 3085 | 61 | 10.2891 | 7.3013
[7 empty] | 3086 | 62 | 10.0827 | 7.1514
[7 empty] | 3087 | 63 | 10.6934 | 7.5949
[7 empty] | 3088 | 64 | 11.6655 | 8.3008
[7 empty] | 3089 | 65 | 12.3021 | 8.7631
[7 empty] | 3090 | 66 | 12.1989 | 8.6882
[7 empty] | 3091 | 67 | 12.9559 | 9.2379
[7 empty] | 3092 | 68 | 13.2054 | 9.419
[7 empty] | 3093 | 69 | 12.6806 | 9.038
[7 empty] | 3094 | 70 | 10.3235 | 7.3263
[7 empty] | 3095 | 71 | 5.6868 | 3.9592
[7 empty] | 3096 | 72 | 4.5734 | 3.1507
[7 empty] | 3097 | 73 | 3.8373 | 2.6162
[7 empty] | 3098 | 74 | 3.605 | 2.4475
[7 empty] | 3099 | 75 | 3.5018 | 2.3725
[7 empty] | 3100 | 76 | 3.4416 | 2.3288
[7 empty] | 3101 | 77 | 3.6222 | 2.46
[7 empty] | 3102 | 78 | 4.0351 | 2.7598
[7 empty] | 3103 | 79 | 5.1793 | 3.5907
[7 empty] | 3104 | 80 | 5.3599 | 3.7219
[7 empty] | 3105 | 81 | 6.5729 | 4.6027
[7 empty] | 3106 | 82 | 7.6912 | 5.4148
[7 empty] | 3107 | 83 | 8.4482 | 5.9645
[7 empty] | 3108 | 84 | 9.7214 | 6.889
[7 empty] | 3109 | 85 | 9.4117 | 6.6642
[7 empty] | 3110 | 86 | 8.8869 | 6.2831
[7 empty] | 3111 | 87 | 9.3428 | 6.6142
[7 empty] | 3112 | 88 | 10.0224 | 7.1077
[7 empty] | 3113 | 89 | 11.4074 | 8.1134
[7 empty] | 3114 | 90 | 10.8053 | 7.6762
[7 empty] | 3115 | 91 | 11.5107 | 8.1884
[7 empty] | 3116 | 92 | 10.8913 | 7.7386
[7 empty] | 3117 | 93 | 8.4138 | 5.9395
[7 empty] | 3118 | 94 | 7.4847 | 5.2648
[7 empty] | 3119 | 95 | 5.575 | 3.878
[7 empty] | 3120 | 96 | 4.5599 | 3.1409
[7 empty] | 3121 | 97 | 4.5083 | 3.1034
[7 empty] | 3122 | 98 | 4.2072 | 2.8848
[7 empty] | 3123 | 99 | 4.147 | 2.841
[7 empty] | 3124 | 100 | 3.7857 | 2.5787
[7 empty] | 3125 | 101 | 3.7254 | 2.5349
[7 empty] | 3126 | 102 | 3.9663 | 2.7099
[7 empty] | 3127 | 103 | 4.7319 | 3.2658
[7 empty] | 3128 | 104 | 4.99 | 3.4532
[7 empty] | 3129 | 105 | 5.4889 | 3.8156
[7 empty] | 3130 | 106 | 6.9858 | 4.9025
[7 empty] | 3131 | 107 | 7.3471 | 5.1649
[7 empty] | 3132 | 108 | 8.9643 | 6.3393
[7 empty] | 3133 | 109 | 8.2847 | 5.8458
[7 empty] | 3134 | 110 | 7.8202 | 5.5085
[7 empty] | 3135 | 111 | 7.6568 | 5.3898
[7 empty] | 3136 | 112 | 7.7256 | 5.4398
[7 empty] | 3137 | 113 | 7.3729 | 5.1836
[7 empty] | 3138 | 114 | 7.5449 | 5.3086
[7 empty] | 3139 | 115 | 7.0804 | 4.9712
[7 empty] | 3140 | 116 | 7.7772 | 5.4772
[7 empty] | 3141 | 117 | 7.3471 | 5.1649
[7 empty] | 3142 | 118 | 6.5556 | 4.5902
[7 empty] | 3143 | 119 | 4.9212 | 3.4033
[7 empty] | 3144 | 120 | 4.5954 | 3.1667
[7 empty] | 3145 | 121 | 3.8459 | 2.6224
[7 empty] | 3146 | 122 | 3.4243 | 2.3163
[7 empty] | 3147 | 123 | 3.3383 | 2.2538
[7 empty] | 3148 | 124 | 3.3039 | 2.2289
[7 empty] | 3149 | 125 | 3.2609 | 2.1976
[7 empty] | 3150 | 126 | 3.4071 | 2.3038
[7 empty] | 3151 | 127 | 4.9556 | 3.4283
[7 empty] | 3152 | 128 | 6.5556 | 4.5902
[7 empty] | 3153 | 129 | 7.2524 | 5.0962
[7 empty] | 3154 | 130 | 7.6998 | 5.421
[7 empty] | 3155 | 131 | 7.8632 | 5.5397
[7 empty] | 3156 | 132 | 7.6051 | 5.3523
[7 empty] | 3157 | 133 | 8.2589 | 5.8271
[7 empty] | 3158 | 134 | 8.5686 | 6.052
[7 empty] | 3159 | 135 | 8.6374 | 6.1019
[7 empty] | 3160 | 136 | 7.803 | 5.496
[7 empty] | 3161 | 137 | 7.6998 | 5.421
[7 empty] | 3162 | 138 | 7.6482 | 5.3835
[7 empty] | 3163 | 139 | 7.3041 | 5.1337
[7 empty] | 3164 | 140 | 7.3127 | 5.1399
[7 empty] | 3165 | 141 | 6.6417 | 4.6526
[7 empty] | 3166 | 142 | 5.9879 | 4.1779
[7 empty] | 3167 | 143 | 5.0846 | 3.522
[7 empty] | 3168 | 144 | 4.4566 | 3.0659
[7 empty] | 3169 | 145 | 3.9749 | 2.7161
[7 empty] | 3170 | 146 | 3.7598 | 2.5599
[7 empty] | 3171 | 147 | 3.691 | 2.51
[7 empty] | 3172 | 148 | 3.6824 | 2.5037
[7 empty] | 3173 | 149 | 3.6824 | 2.5037
[7 empty] | 3174 | 150 | 3.691 | 2.51
[7 empty] | 3175 | 151 | 4.8007 | 3.3158
[7 empty] | 3176 | 152 | 6.3664 | 4.4527
[7 empty] | 3177 | 153 | 6.9944 | 4.9088
[7 empty] | 3178 | 154 | 7.5707 | 5.3273
[7 empty] | 3179 | 155 | 7.4159 | 5.2149
[7 empty] | 3180 | 156 | 7.5879 | 5.3398
[7 empty] | 3181 | 157 | 8.3192 | 5.8708
[7 empty] | 3182 | 158 | 8.6546 | 6.1144
[7 empty] | 3183 | 159 | 8.9299 | 6.3143
[7 empty] | 3184 | 160 | 8.8009 | 6.2206
[7 empty] | 3185 | 161 | 9.5837 | 6.7891
[7 empty] | 3186 | 162 | 9.0762 | 6.4205
[7 empty] | 3187 | 163 | 9.4461 | 6.6891
[7 empty] | 3188 | 164 | 8.0611 | 5.6834
[7 empty] | 3189 | 165 | 11.2698 | 8.0135
[7 empty] | 3190 | 166 | 9.1708 | 6.4892
[7 empty] | 3191 | 167 | 5.4717 | 3.8031
[7 empty] | 3192 | 168 | 4.8093 | 3.3221
[7 empty] | 3193 | 1 | 3.3125 | 2.2351
[7 empty] | 3194 | 2 | 3.2007 | 2.1539
[7 empty] | 3195 | 3 | 3.1921 | 2.1476
[7 empty] | 3196 | 4 | 3.3297 | 2.2476
[7 empty] | 3197 | 5 | 3.3469 | 2.2601
[7 empty] | 3198 | 6 | 3.7857 | 2.5787
[7 empty] | 3199 | 7 | 4.5255 | 3.1159
[7 empty] | 3200 | 8 | 5.2137 | 3.6157
[7 empty] | 3201 | 9 | 5.1879 | 3.5969
[7 empty] | 3202 | 10 | 6.7449 | 4.7276
[7 empty] | 3203 | 11 | 8.8783 | 6.2768
[7 empty] | 3204 | 12 | 9.8676 | 6.9952
[7 empty] | 3205 | 13 | 10.2547 | 7.2763
[7 empty] | 3206 | 14 | 10.031 | 7.1139
[7 empty] | 3207 | 15 | 9.9364 | 7.0452
[7 empty] | 3208 | 16 | 11.1494 | 7.926
[7 empty] | 3209 | 17 | 12.5086 | 8.913
[7 empty] | 3210 | 18 | 12.2591 | 8.7319
[7 empty] | 3211 | 19 | 12.801 | 9.1254
[7 empty] | 3212 | 20 | 12.7322 | 9.0755
[7 empty] | 3213 | 21 | 13.3172 | 9.5002
[7 empty] | 3214 | 22 | 9.2568 | 6.5517
[7 empty] | 3215 | 23 | 5.3857 | 3.7406
[7 empty] | 3216 | 24 | 3.6704 | 2.495
[7 empty] | 3217 | 25 | 3.5706 | 2.4225
[7 empty] | 3218 | 26 | 3.4588 | 2.3413
[7 empty] | 3219 | 27 | 3.3555 | 2.2663
[7 empty] | 3220 | 28 | 3.4416 | 2.3288
[7 empty] | 3221 | 29 | 3.691 | 2.51
[7 empty] | 3222 | 30 | 3.9405 | 2.6911
[7 empty] | 3223 | 31 | 4.8093 | 3.3221
[7 empty] | 3224 | 32 | 5.1706 | 3.5844
[7 empty] | 3225 | 33 | 5.8502 | 4.0779
[7 empty] | 3226 | 34 | 6.7707 | 4.7464
[7 empty] | 3227 | 35 | 8.9987 | 6.3643
[7 empty] | 3228 | 36 | 10.0569 | 7.1327
[7 empty] | 3229 | 37 | 10.1343 | 7.1889
[7 empty] | 3230 | 38 | 10.2117 | 7.2451
[7 empty] | 3231 | 39 | 9.8762 | 7.0015
[7 empty] | 3232 | 40 | 10.9601 | 7.7886
[7 empty] | 3233 | 41 | 11.5279 | 8.2009
[7 empty] | 3234 | 42 | 11.5451 | 8.2134
[7 empty] | 3235 | 43 | 11.9236 | 8.4882
[7 empty] | 3236 | 44 | 13.1107 | 9.3503
[7 empty] | 3237 | 45 | 12.6978 | 9.0505
[7 empty] | 3238 | 46 | 9.8762 | 7.0015
[7 empty] | 3239 | 47 | 6.1771 | 4.3153
[7 empty] | 3240 | 48 | 4.6373 | 3.1971
[7 empty] | 3241 | 49 | 3.9577 | 2.7036
[7 empty] | 3242 | 50 | 3.6394 | 2.4725
[7 empty] | 3243 | 51 | 3.5276 | 2.3913
[7 empty] | 3244 | 52 | 3.562 | 2.4163
[7 empty] | 3245 | 53 | 3.5878 | 2.435
[7 empty] | 3246 | 54 | 4.1814 | 2.866
[7 empty] | 3247 | 55 | 5.3513 | 3.7156
[7 empty] | 3248 | 56 | 5.6008 | 3.8968
[7 empty] | 3249 | 57 | 6.5729 | 4.6027
[7 empty] | 3250 | 58 | 7.7084 | 5.4273
[7 empty] | 3251 | 59 | 8.9471 | 6.3268
[7 empty] | 3252 | 60 | 9.5923 | 6.7953
[7 empty] | 3253 | 61 | 10.2891 | 7.3013
[7 empty] | 3254 | 62 | 10.0827 | 7.1514
[7 empty] | 3255 | 63 | 10.6934 | 7.5949
[7 empty] | 3256 | 64 | 11.6655 | 8.3008
[7 empty] | 3257 | 65 | 12.3021 | 8.7631
[7 empty] | 3258 | 66 | 12.1989 | 8.6882
[7 empty] | 3259 | 67 | 12.9559 | 9.2379
[7 empty] | 3260 | 68 | 13.2054 | 9.419
[7 empty] | 3261 | 69 | 12.6806 | 9.038
[7 empty] | 3262 | 70 | 10.3235 | 7.3263
[7 empty] | 3263 | 71 | 5.6868 | 3.9592
[7 empty] | 3264 | 72 | 4.5734 | 3.1507
[7 empty] | 3265 | 73 | 3.8373 | 2.6162
[7 empty] | 3266 | 74 | 3.605 | 2.4475
[7 empty] | 3267 | 75 | 3.5018 | 2.3725
[7 empty] | 3268 | 76 | 3.4416 | 2.3288
[7 empty] | 3269 | 77 | 3.6222 | 2.46
[7 empty] | 3270 | 78 | 4.0351 | 2.7598
[7 empty] | 3271 | 79 | 5.1793 | 3.5907
[7 empty] | 3272 | 80 | 5.3599 | 3.7219
[7 empty] | 3273 | 81 | 6.5729 | 4.6027
[7 empty] | 3274 | 82 | 7.6912 | 5.4148
[7 empty] | 3275 | 83 | 8.4482 | 5.9645
[7 empty] | 3276 | 84 | 9.7214 | 6.889
[7 empty] | 3277 | 85 | 9.4117 | 6.6642
[7 empty] | 3278 | 86 | 8.8869 | 6.2831
[7 empty] | 3279 | 87 | 9.3428 | 6.6142
[7 empty] | 3280 | 88 | 10.0224 | 7.1077
[7 empty] | 3281 | 89 | 11.4074 | 8.1134
[7 empty] | 3282 | 90 | 10.8053 | 7.6762
[7 empty] | 3283 | 91 | 11.5107 | 8.1884
[7 empty] | 3284 | 92 | 10.8913 | 7.7386
[7 empty] | 3285 | 93 | 8.4138 | 5.9395
[7 empty] | 3286 | 94 | 7.4847 | 5.2648
[7 empty] | 3287 | 95 | 5.575 | 3.878
[7 empty] | 3288 | 96 | 4.5599 | 3.1409
[7 empty] | 3289 | 97 | 4.5083 | 3.1034
[7 empty] | 3290 | 98 | 4.2072 | 2.8848
[7 empty] | 3291 | 99 | 4.147 | 2.841
[7 empty] | 3292 | 100 | 3.7857 | 2.5787
[7 empty] | 3293 | 101 | 3.7254 | 2.5349
[7 empty] | 3294 | 102 | 3.9663 | 2.7099
[7 empty] | 3295 | 103 | 4.7319 | 3.2658
[7 empty] | 3296 | 104 | 4.99 | 3.4532
[7 empty] | 3297 | 105 | 5.4889 | 3.8156
[7 empty] | 3298 | 106 | 6.9858 | 4.9025
[7 empty] | 3299 | 107 | 7.3471 | 5.1649
[7 empty] | 3300 | 108 | 8.9643 | 6.3393
[7 empty] | 3301 | 109 | 8.2847 | 5.8458
[7 empty] | 3302 | 110 | 7.8202 | 5.5085
[7 empty] | 3303 | 111 | 7.6568 | 5.3898
[7 empty] | 3304 | 112 | 7.7256 | 5.4398
[7 empty] | 3305 | 113 | 7.3729 | 5.1836
[7 empty] | 3306 | 114 | 7.5449 | 5.3086
[7 empty] | 3307 | 115 | 7.0804 | 4.9712
[7 empty] | 3308 | 116 | 7.7772 | 5.4772
[7 empty] | 3309 | 117 | 7.3471 | 5.1649
[7 empty] | 3310 | 118 | 6.5556 | 4.5902
[7 empty] | 3311 | 119 | 4.9212 | 3.4033
[7 empty] | 3312 | 120 | 4.5954 | 3.1667
[7 empty] | 3313 | 121 | 3.8459 | 2.6224
[7 empty] | 3314 | 122 | 3.4243 | 2.3163
[7 empty] | 3315 | 123 | 3.3383 | 2.2538
[7 empty] | 3316 | 124 | 3.3039 | 2.2289
[7 empty] | 3317 | 125 | 3.2609 | 2.1976
[7 empty] | 3318 | 126 | 3.4071 | 2.3038
[7 empty] | 3319 | 127 | 4.9556 | 3.4283
[7 empty] | 3320 | 128 | 6.5556 | 4.5902
[7 empty] | 3321 | 129 | 7.2524 | 5.0962
[7 empty] | 3322 | 130 | 7.6998 | 5.421
[7 empty] | 3323 | 131 | 7.8632 | 5.5397
[7 empty] | 3324 | 132 | 7.6051 | 5.3523
[7 empty] | 3325 | 133 | 8.2589 | 5.8271
[7 empty] | 3326 | 134 | 8.5686 | 6.052
[7 empty] | 3327 | 135 | 8.6374 | 6.1019
[7 empty] | 3328 | 136 | 7.803 | 5.496
[7 empty] | 3329 | 137 | 7.6998 | 5.421
[7 empty] | 3330 | 138 | 7.6482 | 5.3835
[7 empty] | 3331 | 139 | 7.3041 | 5.1337
[7 empty] | 3332 | 140 | 7.3127 | 5.1399
[7 empty] | 3333 | 141 | 6.6417 | 4.6526
[7 empty] | 3334 | 142 | 5.9879 | 4.1779
[7 empty] | 3335 | 143 | 5.0846 | 3.522
[7 empty] | 3336 | 144 | 4.4566 | 3.0659
[7 empty] | 3337 | 145 | 3.9749 | 2.7161
[7 empty] | 3338 | 146 | 3.7598 | 2.5599
[7 empty] | 3339 | 147 | 3.691 | 2.51
[7 empty] | 3340 | 148 | 3.6824 | 2.5037
[7 empty] | 3341 | 149 | 3.6824 | 2.5037
[7 empty] | 3342 | 150 | 3.691 | 2.51
[7 empty] | 3343 | 151 | 4.8007 | 3.3158
[7 empty] | 3344 | 152 | 6.3664 | 4.4527
[7 empty] | 3345 | 153 | 6.9944 | 4.9088
[7 empty] | 3346 | 154 | 7.5707 | 5.3273
[7 empty] | 3347 | 155 | 7.4159 | 5.2149
[7 empty] | 3348 | 156 | 7.5879 | 5.3398
[7 empty] | 3349 | 157 | 8.3192 | 5.8708
[7 empty] | 3350 | 158 | 8.6546 | 6.1144
[7 empty] | 3351 | 159 | 8.9299 | 6.3143
[7 empty] | 3352 | 160 | 8.8009 | 6.2206
[7 empty] | 3353 | 161 | 9.5837 | 6.7891
[7 empty] | 3354 | 162 | 9.0762 | 6.4205
[7 empty] | 3355 | 163 | 9.4461 | 6.6891
[7 empty] | 3356 | 164 | 8.0611 | 5.6834
[7 empty] | 3357 | 165 | 11.2698 | 8.0135
[7 empty] | 3358 | 166 | 9.1708 | 6.4892
[7 empty] | 3359 | 167 | 5.4717 | 3.8031
[7 empty] | 3360 | 168 | 4.8093 | 3.3221
[7 empty] | 3361 | 1 | 3.3125 | 2.2351
[7 empty] | 3362 | 2 | 3.2007 | 2.1539
[7 empty] | 3363 | 3 | 3.1921 | 2.1476
[7 empty] | 3364 | 4 | 3.3297 | 2.2476
[7 empty] | 3365 | 5 | 3.3469 | 2.2601
[7 empty] | 3366 | 6 | 3.7857 | 2.5787
[7 empty] | 3367 | 7 | 4.5255 | 3.1159
[7 empty] | 3368 | 8 | 5.2137 | 3.6157
[7 empty] | 3369 | 9 | 5.1879 | 3.5969
[7 empty] | 3370 | 10 | 6.7449 | 4.7276
[7 empty] | 3371 | 11 | 8.8783 | 6.2768
[7 empty] | 3372 | 12 | 9.8676 | 6.9952
[7 empty] | 3373 | 13 | 10.2547 | 7.2763
[7 empty] | 3374 | 14 | 10.031 | 7.1139
[7 empty] | 3375 | 15 | 9.9364 | 7.0452
[7 empty] | 3376 | 16 | 11.1494 | 7.926
[7 empty] | 3377 | 17 | 12.5086 | 8.913
[7 empty] | 3378 | 18 | 12.2591 | 8.7319
[7 empty] | 3379 | 19 | 12.801 | 9.1254
[7 empty] | 3380 | 20 | 12.7322 | 9.0755
[7 empty] | 3381 | 21 | 13.3172 | 9.5002
[7 empty] | 3382 | 22 | 9.2568 | 6.5517
[7 empty] | 3383 | 23 | 5.3857 | 3.7406
[7 empty] | 3384 | 24 | 3.6704 | 2.495
[7 empty] | 3385 | 25 | 3.5706 | 2.4225
[7 empty] | 3386 | 26 | 3.4588 | 2.3413
[7 empty] | 3387 | 27 | 3.3555 | 2.2663
[7 empty] | 3388 | 28 | 3.4416 | 2.3288
[7 empty] | 3389 | 29 | 3.691 | 2.51
[7 empty] | 3390 | 30 | 3.9405 | 2.6911
[7 empty] | 3391 | 31 | 4.8093 | 3.3221
[7 empty] | 3392 | 32 | 5.1706 | 3.5844
[7 empty] | 3393 | 33 | 5.8502 | 4.0779
[7 empty] | 3394 | 34 | 6.7707 | 4.7464
[7 empty] | 3395 | 35 | 8.9987 | 6.3643
[7 empty] | 3396 | 36 | 10.0569 | 7.1327
[7 empty] | 3397 | 37 | 10.1343 | 7.1889
[7 empty] | 3398 | 38 | 10.2117 | 7.2451
[7 empty] | 3399 | 39 | 9.8762 | 7.0015
[7 empty] | 3400 | 40 | 10.9601 | 7.7886
[7 empty] | 3401 | 41 | 11.5279 | 8.2009
[7 empty] | 3402 | 42 | 11.5451 | 8.2134
[7 empty] | 3403 | 43 | 11.9236 | 8.4882
[7 empty] | 3404 | 44 | 13.1107 | 9.3503
[7 empty] | 3405 | 45 | 12.6978 | 9.0505
[7 empty] | 3406 | 46 | 9.8762 | 7.0015
[7 empty] | 3407 | 47 | 6.1771 | 4.3153
[7 empty] | 3408 | 48 | 4.6373 | 3.1971
[7 empty] | 3409 | 49 | 3.9577 | 2.7036
[7 empty] | 3410 | 50 | 3.6394 | 2.4725
[7 empty] | 3411 | 51 | 3.5276 | 2.3913
[7 empty] | 3412 | 52 | 3.562 | 2.4163
[7 empty] | 3413 | 53 | 3.5878 | 2.435
[7 empty] | 3414 | 54 | 4.1814 | 2.866
[7 empty] | 3415 | 55 | 5.3513 | 3.7156
[7 empty] | 3416 | 56 | 5.6008 | 3.8968
[7 empty] | 3417 | 57 | 6.5729 | 4.6027
[7 empty] | 3418 | 58 | 7.7084 | 5.4273
[7 empty] | 3419 | 59 | 8.9471 | 6.3268
[7 empty] | 3420 | 60 | 9.5923 | 6.7953
[7 empty] | 3421 | 61 | 10.2891 | 7.3013
[7 empty] | 3422 | 62 | 10.0827 | 7.1514
[7 empty] | 3423 | 63 | 10.6934 | 7.5949
[7 empty] | 3424 | 64 | 11.6655 | 8.3008
[7 empty] | 3425 | 65 | 12.3021 | 8.7631
[7 empty] | 3426 | 66 | 12.1989 | 8.6882
[7 empty] | 3427 | 67 | 12.9559 | 9.2379
[7 empty] | 3428 | 68 | 13.2054 | 9.419
[7 empty] | 3429 | 69 | 12.6806 | 9.038
[7 empty] | 3430 | 70 | 10.3235 | 7.3263
[7 empty] | 3431 | 71 | 5.6868 | 3.9592
[7 empty] | 3432 | 72 | 4.5734 | 3.1507
[7 empty] | 3433 | 73 | 3.8373 | 2.6162
[7 empty] | 3434 | 74 | 3.605 | 2.4475
[7 empty] | 3435 | 75 | 3.5018 | 2.3725
[7 empty] | 3436 | 76 | 3.4416 | 2.3288
[7 empty] | 3437 | 77 | 3.6222 | 2.46
[7 empty] | 3438 | 78 | 4.0351 | 2.7598
[7 empty] | 3439 | 79 | 5.1793 | 3.5907
[7 empty] | 3440 | 80 | 5.3599 | 3.7219
[7 empty] | 3441 | 81 | 6.5729 | 4.6027
[7 empty] | 3442 | 82 | 7.6912 | 5.4148
[7 empty] | 3443 | 83 | 8.4482 | 5.9645
[7 empty] | 3444 | 84 | 9.7214 | 6.889
[7 empty] | 3445 | 85 | 9.4117 | 6.6642
[7 empty] | 3446 | 86 | 8.8869 | 6.2831
[7 empty] | 3447 | 87 | 9.3428 | 6.6142
[7 empty] | 3448 | 88 | 10.0224 | 7.1077
[7 empty] | 3449 | 89 | 11.4074 | 8.1134
[7 empty] | 3450 | 90 | 10.8053 | 7.6762
[7 empty] | 3451 | 91 | 11.5107 | 8.1884
[7 empty] | 3452 | 92 | 10.8913 | 7.7386
[7 empty] | 3453 | 93 | 8.4138 | 5.9395
[7 empty] | 3454 | 94 | 7.4847 | 5.2648
[7 empty] | 3455 | 95 | 5.575 | 3.878
[7 empty] | 3456 | 96 | 4.5599 | 3.1409
[7 empty] | 3457 | 97 | 4.5083 | 3.1034
[7 empty] | 3458 | 98 | 4.2072 | 2.8848
[7 empty] | 3459 | 99 | 4.147 | 2.841
[7 empty] | 3460 | 100 | 3.7857 | 2.5787
[7 empty] | 3461 | 101 | 3.7254 | 2.5349
[7 empty] | 3462 | 102 | 3.9663 | 2.7099
[7 empty] | 3463 | 103 | 4.7319 | 3.2658
[7 empty] | 3464 | 104 | 4.99 | 3.4532
[7 empty] | 3465 | 105 | 5.4889 | 3.8156
[7 empty] | 3466 | 106 | 6.9858 | 4.9025
[7 empty] | 3467 | 107 | 7.3471 | 5.1649
[7 empty] | 3468 | 108 | 8.9643 | 6.3393
[7 empty] | 3469 | 109 | 8.2847 | 5.8458
[7 empty] | 3470 | 110 | 7.8202 | 5.5085
[7 empty] | 3471 | 111 | 7.6568 | 5.3898
[7 empty] | 3472 | 112 | 7.7256 | 5.4398
[7 empty] | 3473 | 113 | 7.3729 | 5.1836
[7 empty] | 3474 | 114 | 7.5449 | 5.3086
[7 empty] | 3475 | 115 | 7.0804 | 4.9712
[7 empty] | 3476 | 116 | 7.7772 | 5.4772
[7 empty] | 3477 | 117 | 7.3471 | 5.1649
[7 empty] | 3478 | 118 | 6.5556 | 4.5902
[7 empty] | 3479 | 119 | 4.9212 | 3.4033
[7 empty] | 3480 | 120 | 4.5954 | 3.1667
[7 empty] | 3481 | 121 | 3.8459 | 2.6224
[7 empty] | 3482 | 122 | 3.4243 | 2.3163
[7 empty] | 3483 | 123 | 3.3383 | 2.2538
[7 empty] | 3484 | 124 | 3.3039 | 2.2289
[7 empty] | 3485 | 125 | 3.2609 | 2.1976
[7 empty] | 3486 | 126 | 3.4071 | 2.3038
[7 empty] | 3487 | 127 | 4.9556 | 3.4283
[7 empty] | 3488 | 128 | 6.5556 | 4.5902
[7 empty] | 3489 | 129 | 7.2524 | 5.0962
[7 empty] | 3490 | 130 | 7.6998 | 5.421
[7 empty] | 3491 | 131 | 7.8632 | 5.5397
[7 empty] | 3492 | 132 | 7.6051 | 5.3523
[7 empty] | 3493 | 133 | 8.2589 | 5.8271
[7 empty] | 3494 | 134 | 8.5686 | 6.052
[7 empty] | 3495 | 135 | 8.6374 | 6.1019
[7 empty] | 3496 | 136 | 7.803 | 5.496
[7 empty] | 3497 | 137 | 7.6998 | 5.421
[7 empty] | 3498 | 138 | 7.6482 | 5.3835
[7 empty] | 3499 | 139 | 7.3041 | 5.1337
[7 empty] | 3500 | 140 | 7.3127 | 5.1399
[7 empty] | 3501 | 141 | 6.6417 | 4.6526
[7 empty] | 3502 | 142 | 5.9879 | 4.1779
[7 empty] | 3503 | 143 | 5.0846 | 3.522
[7 empty] | 3504 | 144 | 4.4566 | 3.0659
[7 empty] | 3505 | 145 | 3.9749 | 2.7161
[7 empty] | 3506 | 146 | 3.7598 | 2.5599
[7 empty] | 3507 | 147 | 3.691 | 2.51
[7 empty] | 3508 | 148 | 3.6824 | 2.5037
[7 empty] | 3509 | 149 | 3.6824 | 2.5037
[7 empty] | 3510 | 150 | 3.691 | 2.51
[7 empty] | 3511 | 151 | 4.8007 | 3.3158
[7 empty] | 3512 | 152 | 6.3664 | 4.4527
[7 empty] | 3513 | 153 | 6.9944 | 4.9088
[7 empty] | 3514 | 154 | 7.5707 | 5.3273
[7 empty] | 3515 | 155 | 7.4159 | 5.2149
[7 empty] | 3516 | 156 | 7.5879 | 5.3398
[7 empty] | 3517 | 157 | 8.3192 | 5.8708
[7 empty] | 3518 | 158 | 8.6546 | 6.1144
[7 empty] | 3519 | 159 | 8.9299 | 6.3143
[7 empty] | 3520 | 160 | 8.8009 | 6.2206
[7 empty] | 3521 | 161 | 9.5837 | 6.7891
[7 empty] | 3522 | 162 | 9.0762 | 6.4205
[7 empty] | 3523 | 163 | 9.4461 | 6.6891
[7 empty] | 3524 | 164 | 8.0611 | 5.6834
[7 empty] | 3525 | 165 | 11.2698 | 8.0135
[7 empty] | 3526 | 166 | 9.1708 | 6.4892
[7 empty] | 3527 | 167 | 5.4717 | 3.8031
[7 empty] | 3528 | 168 | 4.8093 | 3.3221
[7 empty] | 3529 | 1 | 3.3125 | 2.2351
[7 empty] | 3530 | 2 | 3.2007 | 2.1539
[7 empty] | 3531 | 3 | 3.1921 | 2.1476
[7 empty] | 3532 | 4 | 3.3297 | 2.2476
[7 empty] | 3533 | 5 | 3.3469 | 2.2601
[7 empty] | 3534 | 6 | 3.7857 | 2.5787
[7 empty] | 3535 | 7 | 4.5255 | 3.1159
[7 empty] | 3536 | 8 | 5.2137 | 3.6157
[7 empty] | 3537 | 9 | 5.1879 | 3.5969
[7 empty] | 3538 | 10 | 6.7449 | 4.7276
[7 empty] | 3539 | 11 | 8.8783 | 6.2768
[7 empty] | 3540 | 12 | 9.8676 | 6.9952
[7 empty] | 3541 | 13 | 10.2547 | 7.2763
[7 empty] | 3542 | 14 | 10.031 | 7.1139
[7 empty] | 3543 | 15 | 9.9364 | 7.0452
[7 empty] | 3544 | 16 | 11.1494 | 7.926
[7 empty] | 3545 | 17 | 12.5086 | 8.913
[7 empty] | 3546 | 18 | 12.2591 | 8.7319
[7 empty] | 3547 | 19 | 12.801 | 9.1254
[7 empty] | 3548 | 20 | 12.7322 | 9.0755
[7 empty] | 3549 | 21 | 13.3172 | 9.5002
[7 empty] | 3550 | 22 | 9.2568 | 6.5517
[7 empty] | 3551 | 23 | 5.3857 | 3.7406
[7 empty] | 3552 | 24 | 3.6704 | 2.495
[7 empty] | 3553 | 25 | 3.5706 | 2.4225
[7 empty] | 3554 | 26 | 3.4588 | 2.3413
[7 empty] | 3555 | 27 | 3.3555 | 2.2663
[7 empty] | 3556 | 28 | 3.4416 | 2.3288
[7 empty] | 3557 | 29 | 3.691 | 2.51
[7 empty] | 3558 | 30 | 3.9405 | 2.6911
[7 empty] | 3559 | 31 | 4.8093 | 3.3221
[7 empty] | 3560 | 32 | 5.1706 | 3.5844
[7 empty] | 3561 | 33 | 5.8502 | 4.0779
[7 empty] | 3562 | 34 | 6.7707 | 4.7464
[7 empty] | 3563 | 35 | 8.9987 | 6.3643
[7 empty] | 3564 | 36 | 10.0569 | 7.1327
[7 empty] | 3565 | 37 | 10.1343 | 7.1889
[7 empty] | 3566 | 38 | 10.2117 | 7.2451
[7 empty] | 3567 | 39 | 9.8762 | 7.0015
[7 empty] | 3568 | 40 | 10.9601 | 7.7886
[7 empty] | 3569 | 41 | 11.5279 | 8.2009
[7 empty] | 3570 | 42 | 11.5451 | 8.2134
[7 empty] | 3571 | 43 | 11.9236 | 8.4882
[7 empty] | 3572 | 44 | 13.1107 | 9.3503
[7 empty] | 3573 | 45 | 12.6978 | 9.0505
[7 empty] | 3574 | 46 | 9.8762 | 7.0015
[7 empty] | 3575 | 47 | 6.1771 | 4.3153
[7 empty] | 3576 | 48 | 4.6373 | 3.1971
[7 empty] | 3577 | 49 | 3.9577 | 2.7036
[7 empty] | 3578 | 50 | 3.6394 | 2.4725
[7 empty] | 3579 | 51 | 3.5276 | 2.3913
[7 empty] | 3580 | 52 | 3.562 | 2.4163
[7 empty] | 3581 | 53 | 3.5878 | 2.435
[7 empty] | 3582 | 54 | 4.1814 | 2.866
[7 empty] | 3583 | 55 | 5.3513 | 3.7156
[7 empty] | 3584 | 56 | 5.6008 | 3.8968
[7 empty] | 3585 | 57 | 6.5729 | 4.6027
[7 empty] | 3586 | 58 | 7.7084 | 5.4273
[7 empty] | 3587 | 59 | 8.9471 | 6.3268
[7 empty] | 3588 | 60 | 9.5923 | 6.7953
[7 empty] | 3589 | 61 | 10.2891 | 7.3013
[7 empty] | 3590 | 62 | 10.0827 | 7.1514
[7 empty] | 3591 | 63 | 10.6934 | 7.5949
[7 empty] | 3592 | 64 | 11.6655 | 8.3008
[7 empty] | 3593 | 65 | 12.3021 | 8.7631
[7 empty] | 3594 | 66 | 12.1989 | 8.6882
[7 empty] | 3595 | 67 | 12.9559 | 9.2379
[7 empty] | 3596 | 68 | 13.2054 | 9.419
[7 empty] | 3597 | 69 | 12.6806 | 9.038
[7 empty] | 3598 | 70 | 10.3235 | 7.3263
[7 empty] | 3599 | 71 | 5.6868 | 3.9592
[7 empty] | 3600 | 72 | 4.5734 | 3.1507
[7 empty] | 3601 | 73 | 3.8373 | 2.6162
[7 empty] | 3602 | 74 | 3.605 | 2.4475
[7 empty] | 3603 | 75 | 3.5018 | 2.3725
[7 empty] | 3604 | 76 | 3.4416 | 2.3288
[7 empty] | 3605 | 77 | 3.6222 | 2.46
[7 empty] | 3606 | 78 | 4.0351 | 2.7598
[7 empty] | 3607 | 79 | 5.1793 | 3.5907
[7 empty] | 3608 | 80 | 5.3599 | 3.7219
[7 empty] | 3609 | 81 | 6.5729 | 4.6027
[7 empty] | 3610 | 82 | 7.6912 | 5.4148
[7 empty] | 3611 | 83 | 8.4482 | 5.9645
[7 empty] | 3612 | 84 | 9.7214 | 6.889
[7 empty] | 3613 | 85 | 9.4117 | 6.6642
[7 empty] | 3614 | 86 | 8.8869 | 6.2831
[7 empty] | 3615 | 87 | 9.3428 | 6.6142
[7 empty] | 3616 | 88 | 10.0224 | 7.1077
[7 empty] | 3617 | 89 | 11.4074 | 8.1134
[7 empty] | 3618 | 90 | 10.8053 | 7.6762
[7 empty] | 3619 | 91 | 11.5107 | 8.1884
[7 empty] | 3620 | 92 | 10.8913 | 7.7386
[7 empty] | 3621 | 93 | 8.4138 | 5.9395
[7 empty] | 3622 | 94 | 7.4847 | 5.2648
[7 empty] | 3623 | 95 | 5.575 | 3.878
[7 empty] | 3624 | 96 | 4.5599 | 3.1409
[7 empty] | 3625 | 97 | 4.5083 | 3.1034
[7 empty] | 3626 | 98 | 4.2072 | 2.8848
[7 empty] | 3627 | 99 | 4.147 | 2.841
[7 empty] | 3628 | 100 | 3.7857 | 2.5787
[7 empty] | 3629 | 101 | 3.7254 | 2.5349
[7 empty] | 3630 | 102 | 3.9663 | 2.7099
[7 empty] | 3631 | 103 | 4.7319 | 3.2658
[7 empty] | 3632 | 104 | 4.99 | 3.4532
[7 empty] | 3633 | 105 | 5.4889 | 3.8156
[7 empty] | 3634 | 106 | 6.9858 | 4.9025
[7 empty] | 3635 | 107 | 7.3471 | 5.1649
[7 empty] | 3636 | 108 | 8.9643 | 6.3393
[7 empty] | 3637 | 109 | 8.2847 | 5.8458
[7 empty] | 3638 | 110 | 7.8202 | 5.5085
[7 empty] | 3639 | 111 | 7.6568 | 5.3898
[7 empty] | 3640 | 112 | 7.7256 | 5.4398
[7 empty] | 3641 | 113 | 7.3729 | 5.1836
[7 empty] | 3642 | 114 | 7.5449 | 5.3086
[7 empty] | 3643 | 115 | 7.0804 | 4.9712
[7 empty] | 3644 | 116 | 7.7772 | 5.4772
[7 empty] | 3645 | 117 | 7.3471 | 5.1649
[7 empty] | 3646 | 118 | 6.5556 | 4.5902
[7 empty] | 3647 | 119 | 4.9212 | 3.4033
[7 empty] | 3648 | 120 | 4.5954 | 3.1667
[7 empty] | 3649 | 121 | 3.8459 | 2.6224
[7 empty] | 3650 | 122 | 3.4243 | 2.3163
[7 empty] | 3651 | 123 | 3.3383 | 2.2538
[7 empty] | 3652 | 124 | 3.3039 | 2.2289
[7 empty] | 3653 | 125 | 3.2609 | 2.1976
[7 empty] | 3654 | 126 | 3.4071 | 2.3038
[7 empty] | 3655 | 127 | 4.9556 | 3.4283
[7 empty] | 3656 | 128 | 6.5556 | 4.5902
[7 empty] | 3657 | 129 | 7.2524 | 5.0962
[7 empty] | 3658 | 130 | 7.6998 | 5.421
[7 empty] | 3659 | 131 | 7.8632 | 5.5397
[7 empty] | 3660 | 132 | 7.6051 | 5.3523
[7 empty] | 3661 | 133 | 8.2589 | 5.8271
[7 empty] | 3662 | 134 | 8.5686 | 6.052
[7 empty] | 3663 | 135 | 8.6374 | 6.1019
[7 empty] | 3664 | 136 | 7.803 | 5.496
[7 empty] | 3665 | 137 | 7.6998 | 5.421
[7 empty] | 3666 | 138 | 7.6482 | 5.3835
[7 empty] | 3667 | 139 | 7.3041 | 5.1337
[7 empty] | 3668 | 140 | 7.3127 | 5.1399
[7 empty] | 3669 | 141 | 6.6417 | 4.6526
[7 empty] | 3670 | 142 | 5.9879 | 4.1779
[7 empty] | 3671 | 143 | 5.0846 | 3.522
[7 empty] | 3672 | 144 | 4.4566 | 3.0659
[7 empty] | 3673 | 145 | 3.9749 | 2.7161
[7 empty] | 3674 | 146 | 3.7598 | 2.5599
[7 empty] | 3675 | 147 | 3.691 | 2.51
[7 empty] | 3676 | 148 | 3.6824 | 2.5037
[7 empty] | 3677 | 149 | 3.6824 | 2.5037
[7 empty] | 3678 | 150 | 3.691 | 2.51
[7 empty] | 3679 | 151 | 4.8007 | 3.3158
[7 empty] | 3680 | 152 | 6.3664 | 4.4527
[7 empty] | 3681 | 153 | 6.9944 | 4.9088
[7 empty] | 3682 | 154 | 7.5707 | 5.3273
[7 empty] | 3683 | 155 | 7.4159 | 5.2149
[7 empty] | 3684 | 156 | 7.5879 | 5.3398
[7 empty] | 3685 | 157 | 8.3192 | 5.8708
[7 empty] | 3686 | 158 | 8.6546 | 6.1144
[7 empty] | 3687 | 159 | 8.9299 | 6.3143
[7 empty] | 3688 | 160 | 8.8009 | 6.2206
[7 empty] | 3689 | 161 | 9.5837 | 6.7891
[7 empty] | 3690 | 162 | 9.0762 | 6.4205
[7 empty] | 3691 | 163 | 9.4461 | 6.6891
[7 empty] | 3692 | 164 | 8.0611 | 5.6834
[7 empty] | 3693 | 165 | 11.2698 | 8.0135
[7 empty] | 3694 | 166 | 9.1708 | 6.4892
[7 empty] | 3695 | 167 | 5.4717 | 3.8031
[7 empty] | 3696 | 168 | 4.8093 | 3.3221
[7 empty] | 3697 | 1 | 3.3125 | 2.2351
[7 empty] | 3698 | 2 | 3.2007 | 2.1539
[7 empty] | 3699 | 3 | 3.1921 | 2.1476
[7 empty] | 3700 | 4 | 3.3297 | 2.2476
[7 empty] | 3701 | 5 | 3.3469 | 2.2601
[7 empty] | 3702 | 6 | 3.7857 | 2.5787
[7 empty] | 3703 | 7 | 4.5255 | 3.1159
[7 empty] | 3704 | 8 | 5.2137 | 3.6157
[7 empty] | 3705 | 9 | 5.1879 | 3.5969
[7 empty] | 3706 | 10 | 6.7449 | 4.7276
[7 empty] | 3707 | 11 | 8.8783 | 6.2768
[7 empty] | 3708 | 12 | 9.8676 | 6.9952
[7 empty] | 3709 | 13 | 10.2547 | 7.2763
[7 empty] | 3710 | 14 | 10.031 | 7.1139
[7 empty] | 3711 | 15 | 9.9364 | 7.0452
[7 empty] | 3712 | 16 | 11.1494 | 7.926
[7 empty] | 3713 | 17 | 12.5086 | 8.913
[7 empty] | 3714 | 18 | 12.2591 | 8.7319
[7 empty] | 3715 | 19 | 12.801 | 9.1254
[7 empty] | 3716 | 20 | 12.7322 | 9.0755
[7 empty] | 3717 | 21 | 13.3172 | 9.5002
[7 empty] | 3718 | 22 | 9.2568 | 6.5517
[7 empty] | 3719 | 23 | 5.3857 | 3.7406
[7 empty] | 3720 | 24 | 3.6704 | 2.495
[7 empty] | 3721 | 25 | 3.5706 | 2.4225
[7 empty] | 3722 | 26 | 3.4588 | 2.3413
[7 empty] | 3723 | 27 | 3.3555 | 2.2663
[7 empty] | 3724 | 28 | 3.4416 | 2.3288
[7 empty] | 3725 | 29 | 3.691 | 2.51
[7 empty] | 3726 | 30 | 3.9405 | 2.6911
[7 empty] | 3727 | 31 | 4.8093 | 3.3221
[7 empty] | 3728 | 32 | 5.1706 | 3.5844
[7 empty] | 3729 | 33 | 5.8502 | 4.0779
[7 empty] | 3730 | 34 | 6.7707 | 4.7464
[7 empty] | 3731 | 35 | 8.9987 | 6.3643
[7 empty] | 3732 | 36 | 10.0569 | 7.1327
[7 empty] | 3733 | 37 | 10.1343 | 7.1889
[7 empty] | 3734 | 38 | 10.2117 | 7.2451
[7 empty] | 3735 | 39 | 9.8762 | 7.0015
[7 empty] | 3736 | 40 | 10.9601 | 7.7886
[7 empty] | 3737 | 41 | 11.5279 | 8.2009
[7 empty] | 3738 | 42 | 11.5451 | 8.2134
[7 empty] | 3739 | 43 | 11.9236 | 8.4882
[7 empty] | 3740 | 44 | 13.1107 | 9.3503
[7 empty] | 3741 | 45 | 12.6978 | 9.0505
[7 empty] | 3742 | 46 | 9.8762 | 7.0015
[7 empty] | 3743 | 47 | 6.1771 | 4.3153
[7 empty] | 3744 | 48 | 4.6373 | 3.1971
[7 empty] | 3745 | 49 | 3.9577 | 2.7036
[7 empty] | 3746 | 50 | 3.6394 | 2.4725
[7 empty] | 3747 | 51 | 3.5276 | 2.3913
[7 empty] | 3748 | 52 | 3.562 | 2.4163
[7 empty] | 3749 | 53 | 3.5878 | 2.435
[7 empty] | 3750 | 54 | 4.1814 | 2.866
[7 empty] | 3751 | 55 | 5.3513 | 3.7156
[7 empty] | 3752 | 56 | 5.6008 | 3.8968
[7 empty] | 3753 | 57 | 6.5729 | 4.6027
[7 empty] | 3754 | 58 | 7.7084 | 5.4273
[7 empty] | 3755 | 59 | 8.9471 | 6.3268
[7 empty] | 3756 | 60 | 9.5923 | 6.7953
[7 empty] | 3757 | 61 | 10.2891 | 7.3013
[7 empty] | 3758 | 62 | 10.0827 | 7.1514
[7 empty] | 3759 | 63 | 10.6934 | 7.5949
[7 empty] | 3760 | 64 | 11.6655 | 8.3008
[7 empty] | 3761 | 65 | 12.3021 | 8.7631
[7 empty] | 3762 | 66 | 12.1989 | 8.6882
[7 empty] | 3763 | 67 | 12.9559 | 9.2379
[7 empty] | 3764 | 68 | 13.2054 | 9.419
[7 empty] | 3765 | 69 | 12.6806 | 9.038
[7 empty] | 3766 | 70 | 10.3235 | 7.3263
[7 empty] | 3767 | 71 | 5.6868 | 3.9592
[7 empty] | 3768 | 72 | 4.5734 | 3.1507
[7 empty] | 3769 | 73 | 3.8373 | 2.6162
[7 empty] | 3770 | 74 | 3.605 | 2.4475
[7 empty] | 3771 | 75 | 3.5018 | 2.3725
[7 empty] | 3772 | 76 | 3.4416 | 2.3288
[7 empty] | 3773 | 77 | 3.6222 | 2.46
[7 empty] | 3774 | 78 | 4.0351 | 2.7598
[7 empty] | 3775 | 79 | 5.1793 | 3.5907
[7 empty] | 3776 | 80 | 5.3599 | 3.7219
[7 empty] | 3777 | 81 | 6.5729 | 4.6027
[7 empty] | 3778 | 82 | 7.6912 | 5.4148
[7 empty] | 3779 | 83 | 8.4482 | 5.9645
[7 empty] | 3780 | 84 | 9.7214 | 6.889
[7 empty] | 3781 | 85 | 9.4117 | 6.6642
[7 empty] | 3782 | 86 | 8.8869 | 6.2831
[7 empty] | 3783 | 87 | 9.3428 | 6.6142
[7 empty] | 3784 | 88 | 10.0224 | 7.1077
[7 empty] | 3785 | 89 | 11.4074 | 8.1134
[7 empty] | 3786 | 90 | 10.8053 | 7.6762
[7 empty] | 3787 | 91 | 11.5107 | 8.1884
[7 empty] | 3788 | 92 | 10.8913 | 7.7386
[7 empty] | 3789 | 93 | 8.4138 | 5.9395
[7 empty] | 3790 | 94 | 7.4847 | 5.2648
[7 empty] | 3791 | 95 | 5.575 | 3.878
[7 empty] | 3792 | 96 | 4.5599 | 3.1409
[7 empty] | 3793 | 97 | 4.5083 | 3.1034
[7 empty] | 3794 | 98 | 4.2072 | 2.8848
[7 empty] | 3795 | 99 | 4.147 | 2.841
[7 empty] | 3796 | 100 | 3.7857 | 2.5787
[7 empty] | 3797 | 101 | 3.7254 | 2.5349
[7 empty] | 3798 | 102 | 3.9663 | 2.7099
[7 empty] | 3799 | 103 | 4.7319 | 3.2658
[7 empty] | 3800 | 104 | 4.99 | 3.4532
[7 empty] | 3801 | 105 | 5.4889 | 3.8156
[7 empty] | 3802 | 106 | 6.9858 | 4.9025
[7 empty] | 3803 | 107 | 7.3471 | 5.1649
[7 empty] | 3804 | 108 | 8.9643 | 6.3393
[7 empty] | 3805 | 109 | 8.2847 | 5.8458
[7 empty] | 3806 | 110 | 7.8202 | 5.5085
[7 empty] | 3807 | 111 | 7.6568 | 5.3898
[7 empty] | 3808 | 112 | 7.7256 | 5.4398
[7 empty] | 3809 | 113 | 7.3729 | 5.1836
[7 empty] | 3810 | 114 | 7.5449 | 5.3086
[7 empty] | 3811 | 115 | 7.0804 | 4.9712
[7 empty] | 3812 | 116 | 7.7772 | 5.4772
[7 empty] | 3813 | 117 | 7.3471 | 5.1649
[7 empty] | 3814 | 118 | 6.5556 | 4.5902
[7 empty] | 3815 | 119 | 4.9212 | 3.4033
[7 empty] | 3816 | 120 | 4.5954 | 3.1667
[7 empty] | 3817 | 121 | 3.8459 | 2.6224
[7 empty] | 3818 | 122 | 3.4243 | 2.3163
[7 empty] | 3819 | 123 | 3.3383 | 2.2538
[7 empty] | 3820 | 124 | 3.3039 | 2.2289
[7 empty] | 3821 | 125 | 3.2609 | 2.1976
[7 empty] | 3822 | 126 | 3.4071 | 2.3038
[7 empty] | 3823 | 127 | 4.9556 | 3.4283
[7 empty] | 3824 | 128 | 6.5556 | 4.5902
[7 empty] | 3825 | 129 | 7.2524 | 5.0962
[7 empty] | 3826 | 130 | 7.6998 | 5.421
[7 empty] | 3827 | 131 | 7.8632 | 5.5397
[7 empty] | 3828 | 132 | 7.6051 | 5.3523
[7 empty] | 3829 | 133 | 8.2589 | 5.8271
[7 empty] | 3830 | 134 | 8.5686 | 6.052
[7 empty] | 3831 | 135 | 8.6374 | 6.1019
[7 empty] | 3832 | 136 | 7.803 | 5.496
[7 empty] | 3833 | 137 | 7.6998 | 5.421
[7 empty] | 3834 | 138 | 7.6482 | 5.3835
[7 empty] | 3835 | 139 | 7.3041 | 5.1337
[7 empty] | 3836 | 140 | 7.3127 | 5.1399
[7 empty] | 3837 | 141 | 6.6417 | 4.6526
[7 empty] | 3838 | 142 | 5.9879 | 4.1779
[7 empty] | 3839 | 143 | 5.0846 | 3.522
[7 empty] | 3840 | 144 | 4.4566 | 3.0659
[7 empty] | 3841 | 145 | 3.9749 | 2.7161
[7 empty] | 3842 | 146 | 3.7598 | 2.5599
[7 empty] | 3843 | 147 | 3.691 | 2.51
[7 empty] | 3844 | 148 | 3.6824 | 2.5037
[7 empty] | 3845 | 149 | 3.6824 | 2.5037
[7 empty] | 3846 | 150 | 3.691 | 2.51
[7 empty] | 3847 | 151 | 4.8007 | 3.3158
[7 empty] | 3848 | 152 | 6.3664 | 4.4527
[7 empty] | 3849 | 153 | 6.9944 | 4.9088
[7 empty] | 3850 | 154 | 7.5707 | 5.3273
[7 empty] | 3851 | 155 | 7.4159 | 5.2149
[7 empty] | 3852 | 156 | 7.5879 | 5.3398
[7 empty] | 3853 | 157 | 8.3192 | 5.8708
[7 empty] | 3854 | 158 | 8.6546 | 6.1144
[7 empty] | 3855 | 159 | 8.9299 | 6.3143
[7 empty] | 3856 | 160 | 8.8009 | 6.2206
[7 empty] | 3857 | 161 | 9.5837 | 6.7891
[7 empty] | 3858 | 162 | 9.0762 | 6.4205
[7 empty] | 3859 | 163 | 9.4461 | 6.6891
[7 empty] | 3860 | 164 | 8.0611 | 5.6834
[7 empty] | 3861 | 165 | 11.2698 | 8.0135
[7 empty] | 3862 | 166 | 9.1708 | 6.4892
[7 empty] | 3863 | 167 | 5.4717 | 3.8031
[7 empty] | 3864 | 168 | 4.8093 | 3.3221
[7 empty] | 3865 | 1 | 3.3125 | 2.2351
[7 empty] | 3866 | 2 | 3.2007 | 2.1539
[7 empty] | 3867 | 3 | 3.1921 | 2.1476
[7 empty] | 3868 | 4 | 3.3297 | 2.2476
[7 empty] | 3869 | 5 | 3.3469 | 2.2601
[7 empty] | 3870 | 6 | 3.7857 | 2.5787
[7 empty] | 3871 | 7 | 4.5255 | 3.1159
[7 empty] | 3872 | 8 | 5.2137 | 3.6157
[7 empty] | 3873 | 9 | 5.1879 | 3.5969
[7 empty] | 3874 | 10 | 6.7449 | 4.7276
[7 empty] | 3875 | 11 | 8.8783 | 6.2768
[7 empty] | 3876 | 12 | 9.8676 | 6.9952
[7 empty] | 3877 | 13 | 10.2547 | 7.2763
[7 empty] | 3878 | 14 | 10.031 | 7.1139
[7 empty] | 3879 | 15 | 9.9364 | 7.0452
[7 empty] | 3880 | 16 | 11.1494 | 7.926
[7 empty] | 3881 | 17 | 12.5086 | 8.913
[7 empty] | 3882 | 18 | 12.2591 | 8.7319
[7 empty] | 3883 | 19 | 12.801 | 9.1254
[7 empty] | 3884 | 20 | 12.7322 | 9.0755
[7 empty] | 3885 | 21 | 13.3172 | 9.5002
[7 empty] | 3886 | 22 | 9.2568 | 6.5517
[7 empty] | 3887 | 23 | 5.3857 | 3.7406
[7 empty] | 3888 | 24 | 3.6704 | 2.495
[7 empty] | 3889 | 25 | 3.5706 | 2.4225
[7 empty] | 3890 | 26 | 3.4588 | 2.3413
[7 empty] | 3891 | 27 | 3.3555 | 2.2663
[7 empty] | 3892 | 28 | 3.4416 | 2.3288
[7 empty] | 3893 | 29 | 3.691 | 2.51
[7 empty] | 3894 | 30 | 3.9405 | 2.6911
[7 empty] | 3895 | 31 | 4.8093 | 3.3221
[7 empty] | 3896 | 32 | 5.1706 | 3.5844
[7 empty] | 3897 | 33 | 5.8502 | 4.0779
[7 empty] | 3898 | 34 | 6.7707 | 4.7464
[7 empty] | 3899 | 35 | 8.9987 | 6.3643
[7 empty] | 3900 | 36 | 10.0569 | 7.1327
[7 empty] | 3901 | 37 | 10.1343 | 7.1889
[7 empty] | 3902 | 38 | 10.2117 | 7.2451
[7 empty] | 3903 | 39 | 9.8762 | 7.0015
[7 empty] | 3904 | 40 | 10.9601 | 7.7886
[7 empty] | 3905 | 41 | 11.5279 | 8.2009
[7 empty] | 3906 | 42 | 11.5451 | 8.2134
[7 empty] | 3907 | 43 | 11.9236 | 8.4882
[7 empty] | 3908 | 44 | 13.1107 | 9.3503
[7 empty] | 3909 | 45 | 12.6978 | 9.0505
[7 empty] | 3910 | 46 | 9.8762 | 7.0015
[7 empty] | 3911 | 47 | 6.1771 | 4.3153
[7 empty] | 3912 | 48 | 4.6373 | 3.1971
[7 empty] | 3913 | 49 | 3.9577 | 2.7036
[7 empty] | 3914 | 50 | 3.6394 | 2.4725
[7 empty] | 3915 | 51 | 3.5276 | 2.3913
[7 empty] | 3916 | 52 | 3.562 | 2.4163
[7 empty] | 3917 | 53 | 3.5878 | 2.435
[7 empty] | 3918 | 54 | 4.1814 | 2.866
[7 empty] | 3919 | 55 | 5.3513 | 3.7156
[7 empty] | 3920 | 56 | 5.6008 | 3.8968
[7 empty] | 3921 | 57 | 6.5729 | 4.6027
[7 empty] | 3922 | 58 | 7.7084 | 5.4273
[7 empty] | 3923 | 59 | 8.9471 | 6.3268
[7 empty] | 3924 | 60 | 9.5923 | 6.7953
[7 empty] | 3925 | 61 | 10.2891 | 7.3013
[7 empty] | 3926 | 62 | 10.0827 | 7.1514
[7 empty] | 3927 | 63 | 10.6934 | 7.5949
[7 empty] | 3928 | 64 | 11.6655 | 8.3008
[7 empty] | 3929 | 65 | 12.3021 | 8.7631
[7 empty] | 3930 | 66 | 12.1989 | 8.6882
[7 empty] | 3931 | 67 | 12.9559 | 9.2379
[7 empty] | 3932 | 68 | 13.2054 | 9.419
[7 empty] | 3933 | 69 | 12.6806 | 9.038
[7 empty] | 3934 | 70 | 10.3235 | 7.3263
[7 empty] | 3935 | 71 | 5.6868 | 3.9592
[7 empty] | 3936 | 72 | 4.5734 | 3.1507
[7 empty] | 3937 | 73 | 3.8373 | 2.6162
[7 empty] | 3938 | 74 | 3.605 | 2.4475
[7 empty] | 3939 | 75 | 3.5018 | 2.3725
[7 empty] | 3940 | 76 | 3.4416 | 2.3288
[7 empty] | 3941 | 77 | 3.6222 | 2.46
[7 empty] | 3942 | 78 | 4.0351 | 2.7598
[7 empty] | 3943 | 79 | 5.1793 | 3.5907
[7 empty] | 3944 | 80 | 5.3599 | 3.7219
[7 empty] | 3945 | 81 | 6.5729 | 4.6027
[7 empty] | 3946 | 82 | 7.6912 | 5.4148
[7 empty] | 3947 | 83 | 8.4482 | 5.9645
[7 empty] | 3948 | 84 | 9.7214 | 6.889
[7 empty] | 3949 | 85 | 9.4117 | 6.6642
[7 empty] | 3950 | 86 | 8.8869 | 6.2831
[7 empty] | 3951 | 87 | 9.3428 | 6.6142
[7 empty] | 3952 | 88 | 10.0224 | 7.1077
[7 empty] | 3953 | 89 | 11.4074 | 8.1134
[7 empty] | 3954 | 90 | 10.8053 | 7.6762
[7 empty] | 3955 | 91 | 11.5107 | 8.1884
[7 empty] | 3956 | 92 | 10.8913 | 7.7386
[7 empty] | 3957 | 93 | 8.4138 | 5.9395
[7 empty] | 3958 | 94 | 7.4847 | 5.2648
[7 empty] | 3959 | 95 | 5.575 | 3.878
[7 empty] | 3960 | 96 | 4.5599 | 3.1409
[7 empty] | 3961 | 97 | 4.5083 | 3.1034
[7 empty] | 3962 | 98 | 4.2072 | 2.8848
[7 empty] | 3963 | 99 | 4.147 | 2.841
[7 empty] | 3964 | 100 | 3.7857 | 2.5787
[7 empty] | 3965 | 101 | 3.7254 | 2.5349
[7 empty] | 3966 | 102 | 3.9663 | 2.7099
[7 empty] | 3967 | 103 | 4.7319 | 3.2658
[7 empty] | 3968 | 104 | 4.99 | 3.4532
[7 empty] | 3969 | 105 | 5.4889 | 3.8156
[7 empty] | 3970 | 106 | 6.9858 | 4.9025
[7 empty] | 3971 | 107 | 7.3471 | 5.1649
[7 empty] | 3972 | 108 | 8.9643 | 6.3393
[7 empty] | 3973 | 109 | 8.2847 | 5.8458
[7 empty] | 3974 | 110 | 7.8202 | 5.5085
[7 empty] | 3975 | 111 | 7.6568 | 5.3898
[7 empty] | 3976 | 112 | 7.7256 | 5.4398
[7 empty] | 3977 | 113 | 7.3729 | 5.1836
[7 empty] | 3978 | 114 | 7.5449 | 5.3086
[7 empty] | 3979 | 115 | 7.0804 | 4.9712
[7 empty] | 3980 | 116 | 7.7772 | 5.4772
[7 empty] | 3981 | 117 | 7.3471 | 5.1649
[7 empty] | 3982 | 118 | 6.5556 | 4.5902
[7 empty] | 3983 | 119 | 4.9212 | 3.4033
[7 empty] | 3984 | 120 | 4.5954 | 3.1667
[7 empty] | 3985 | 121 | 3.8459 | 2.6224
[7 empty] | 3986 | 122 | 3.4243 | 2.3163
[7 empty] | 3987 | 123 | 3.3383 | 2.2538
[7 empty] | 3988 | 124 | 3.3039 | 2.2289
[7 empty] | 3989 | 125 | 3.2609 | 2.1976
[7 empty] | 3990 | 126 | 3.4071 | 2.3038
[7 empty] | 3991 | 127 | 4.9556 | 3.4283
[7 empty] | 3992 | 128 | 6.5556 | 4.5902
[7 empty] | 3993 | 129 | 7.2524 | 5.0962
[7 empty] | 3994 | 130 | 7.6998 | 5.421
[7 empty] | 3995 | 131 | 7.8632 | 5.5397
[7 empty] | 3996 | 132 | 7.6051 | 5.3523
[7 empty] | 3997 | 133 | 8.2589 | 5.8271
[7 empty] | 3998 | 134 | 8.5686 | 6.052
[7 empty] | 3999 | 135 | 8.6374 | 6.1019
[7 empty] | 4000 | 136 | 7.803 | 5.496
[7 empty] | 4001 | 137 | 7.6998 | 5.421
[7 empty] | 4002 | 138 | 7.6482 | 5.3835
[7 empty] | 4003 | 139 | 7.3041 | 5.1337
[7 empty] | 4004 | 140 | 7.3127 | 5.1399
[7 empty] | 4005 | 141 | 6.6417 | 4.6526
[7 empty] | 4006 | 142 | 5.9879 | 4.1779
[7 empty] | 4007 | 143 | 5.0846 | 3.522
[7 empty] | 4008 | 144 | 4.4566 | 3.0659
[7 empty] | 4009 | 145 | 3.9749 | 2.7161
[7 empty] | 4010 | 146 | 3.7598 | 2.5599
[7 empty] | 4011 | 147 | 3.691 | 2.51
[7 empty] | 4012 | 148 | 3.6824 | 2.5037
[7 empty] | 4013 | 149 | 3.6824 | 2.5037
[7 empty] | 4014 | 150 | 3.691 | 2.51
[7 empty] | 4015 | 151 | 4.8007 | 3.3158
[7 empty] | 4016 | 152 | 6.3664 | 4.4527
[7 empty] | 4017 | 153 | 6.9944 | 4.9088
[7 empty] | 4018 | 154 | 7.5707 | 5.3273
[7 empty] | 4019 | 155 | 7.4159 | 5.2149
[7 empty] | 4020 | 156 | 7.5879 | 5.3398
[7 empty] | 4021 | 157 | 8.3192 | 5.8708
[7 empty] | 4022 | 158 | 8.6546 | 6.1144
[7 empty] | 4023 | 159 | 8.9299 | 6.3143
[7 empty] | 4024 | 160 | 8.8009 | 6.2206
[7 empty] | 4025 | 161 | 9.5837 | 6.7891
[7 empty] | 4026 | 162 | 9.0762 | 6.4205
[7 empty] | 4027 | 163 | 9.4461 | 6.6891
[7 empty] | 4028 | 164 | 8.0611 | 5.6834
[7 empty] | 4029 | 165 | 11.2698 | 8.0135
[7 empty] | 4030 | 166 | 9.1708 | 6.4892
[7 empty] | 4031 | 167 | 5.4717 | 3.8031
[7 empty] | 4032 | 168 | 4.8093 | 3.3221
[7 empty] | 4033 | 1 | 3.3125 | 2.2351
[7 empty] | 4034 | 2 | 3.2007 | 2.1539
[7 empty] | 4035 | 3 | 3.1921 | 2.1476
[7 empty] | 4036 | 4 | 3.3297 | 2.2476
[7 empty] | 4037 | 5 | 3.3469 | 2.2601
[7 empty] | 4038 | 6 | 3.7857 | 2.5787
[7 empty] | 4039 | 7 | 4.5255 | 3.1159
[7 empty] | 4040 | 8 | 5.2137 | 3.6157
[7 empty] | 4041 | 9 | 5.1879 | 3.5969
[7 empty] | 4042 | 10 | 6.7449 | 4.7276
[7 empty] | 4043 | 11 | 8.8783 | 6.2768
[7 empty] | 4044 | 12 | 9.8676 | 6.9952
[7 empty] | 4045 | 13 | 10.2547 | 7.2763
[7 empty] | 4046 | 14 | 10.031 | 7.1139
[7 empty] | 4047 | 15 | 9.9364 | 7.0452
[7 empty] | 4048 | 16 | 11.1494 | 7.926
[7 empty] | 4049 | 17 | 12.5086 | 8.913
[7 empty] | 4050 | 18 | 12.2591 | 8.7319
[7 empty] | 4051 | 19 | 12.801 | 9.1254
[7 empty] | 4052 | 20 | 12.7322 | 9.0755
[7 empty] | 4053 | 21 | 13.3172 | 9.5002
[7 empty] | 4054 | 22 | 9.2568 | 6.5517
[7 empty] | 4055 | 23 | 5.3857 | 3.7406
[7 empty] | 4056 | 24 | 3.6704 | 2.495
[7 empty] | 4057 | 25 | 3.5706 | 2.4225
[7 empty] | 4058 | 26 | 3.4588 | 2.3413
[7 empty] | 4059 | 27 | 3.3555 | 2.2663
[7 empty] | 4060 | 28 | 3.4416 | 2.3288
[7 empty] | 4061 | 29 | 3.691 | 2.51
[7 empty] | 4062 | 30 | 3.9405 | 2.6911
[7 empty] | 4063 | 31 | 4.8093 | 3.3221
[7 empty] | 4064 | 32 | 5.1706 | 3.5844
[7 empty] | 4065 | 33 | 5.8502 | 4.0779
[7 empty] | 4066 | 34 | 6.7707 | 4.7464
[7 empty] | 4067 | 35 | 8.9987 | 6.3643
[7 empty] | 4068 | 36 | 10.0569 | 7.1327
[7 empty] | 4069 | 37 | 10.1343 | 7.1889
[7 empty] | 4070 | 38 | 10.2117 | 7.2451
[7 empty] | 4071 | 39 | 9.8762 | 7.0015
[7 empty] | 4072 | 40 | 10.9601 | 7.7886
[7 empty] | 4073 | 41 | 11.5279 | 8.2009
[7 empty] | 4074 | 42 | 11.5451 | 8.2134
[7 empty] | 4075 | 43 | 11.9236 | 8.4882
[7 empty] | 4076 | 44 | 13.1107 | 9.3503
[7 empty] | 4077 | 45 | 12.6978 | 9.0505
[7 empty] | 4078 | 46 | 9.8762 | 7.0015
[7 empty] | 4079 | 47 | 6.1771 | 4.3153
[7 empty] | 4080 | 48 | 4.6373 | 3.1971
[7 empty] | 4081 | 49 | 3.9577 | 2.7036
[7 empty] | 4082 | 50 | 3.6394 | 2.4725
[7 empty] | 4083 | 51 | 3.5276 | 2.3913
[7 empty] | 4084 | 52 | 3.562 | 2.4163
[7 empty] | 4085 | 53 | 3.5878 | 2.435
[7 empty] | 4086 | 54 | 4.1814 | 2.866
[7 empty] | 4087 | 55 | 5.3513 | 3.7156
[7 empty] | 4088 | 56 | 5.6008 | 3.8968
[7 empty] | 4089 | 57 | 6.5729 | 4.6027
[7 empty] | 4090 | 58 | 7.7084 | 5.4273
[7 empty] | 4091 | 59 | 8.9471 | 6.3268
[7 empty] | 4092 | 60 | 9.5923 | 6.7953
[7 empty] | 4093 | 61 | 10.2891 | 7.3013
[7 empty] | 4094 | 62 | 10.0827 | 7.1514
[7 empty] | 4095 | 63 | 10.6934 | 7.5949
[7 empty] | 4096 | 64 | 11.6655 | 8.3008
[7 empty] | 4097 | 65 | 12.3021 | 8.7631
[7 empty] | 4098 | 66 | 12.1989 | 8.6882
[7 empty] | 4099 | 67 | 12.9559 | 9.2379
[7 empty] | 4100 | 68 | 13.2054 | 9.419
[7 empty] | 4101 | 69 | 12.6806 | 9.038
[7 empty] | 4102 | 70 | 10.3235 | 7.3263
[7 empty] | 4103 | 71 | 5.6868 | 3.9592
[7 empty] | 4104 | 72 | 4.5734 | 3.1507
[7 empty] | 4105 | 73 | 3.8373 | 2.6162
[7 empty] | 4106 | 74 | 3.605 | 2.4475
[7 empty] | 4107 | 75 | 3.5018 | 2.3725
[7 empty] | 4108 | 76 | 3.4416 | 2.3288
[7 empty] | 4109 | 77 | 3.6222 | 2.46
[7 empty] | 4110 | 78 | 4.0351 | 2.7598
[7 empty] | 4111 | 79 | 5.1793 | 3.5907
[7 empty] | 4112 | 80 | 5.3599 | 3.7219
[7 empty] | 4113 | 81 | 6.5729 | 4.6027
[7 empty] | 4114 | 82 | 7.6912 | 5.4148
[7 empty] | 4115 | 83 | 8.4482 | 5.9645
[7 empty] | 4116 | 84 | 9.7214 | 6.889
[7 empty] | 4117 | 85 | 9.4117 | 6.6642
[7 empty] | 4118 | 86 | 8.8869 | 6.2831
[7 empty] | 4119 | 87 | 9.3428 | 6.6142
[7 empty] | 4120 | 88 | 10.0224 | 7.1077
[7 empty] | 4121 | 89 | 11.4074 | 8.1134
[7 empty] | 4122 | 90 | 10.8053 | 7.6762
[7 empty] | 4123 | 91 | 11.5107 | 8.1884
[7 empty] | 4124 | 92 | 10.8913 | 7.7386
[7 empty] | 4125 | 93 | 8.4138 | 5.9395
[7 empty] | 4126 | 94 | 7.4847 | 5.2648
[7 empty] | 4127 | 95 | 5.575 | 3.878
[7 empty] | 4128 | 96 | 4.5599 | 3.1409
[7 empty] | 4129 | 97 | 4.5083 | 3.1034
[7 empty] | 4130 | 98 | 4.2072 | 2.8848
[7 empty] | 4131 | 99 | 4.147 | 2.841
[7 empty] | 4132 | 100 | 3.7857 | 2.5787
[7 empty] | 4133 | 101 | 3.7254 | 2.5349
[7 empty] | 4134 | 102 | 3.9663 | 2.7099
[7 empty] | 4135 | 103 | 4.7319 | 3.2658
[7 empty] | 4136 | 104 | 4.99 | 3.4532
[7 empty] | 4137 | 105 | 5.4889 | 3.8156
[7 empty] | 4138 | 106 | 6.9858 | 4.9025
[7 empty] | 4139 | 107 | 7.3471 | 5.1649
[7 empty] | 4140 | 108 | 8.9643 | 6.3393
[7 empty] | 4141 | 109 | 8.2847 | 5.8458
[7 empty] | 4142 | 110 | 7.8202 | 5.5085
[7 empty] | 4143 | 111 | 7.6568 | 5.3898
[7 empty] | 4144 | 112 | 7.7256 | 5.4398
[7 empty] | 4145 | 113 | 7.3729 | 5.1836
[7 empty] | 4146 | 114 | 7.5449 | 5.3086
[7 empty] | 4147 | 115 | 7.0804 | 4.9712
[7 empty] | 4148 | 116 | 7.7772 | 5.4772
[7 empty] | 4149 | 117 | 7.3471 | 5.1649
[7 empty] | 4150 | 118 | 6.5556 | 4.5902
[7 empty] | 4151 | 119 | 4.9212 | 3.4033
[7 empty] | 4152 | 120 | 4.5954 | 3.1667
[7 empty] | 4153 | 121 | 3.8459 | 2.6224
[7 empty] | 4154 | 122 | 3.4243 | 2.3163
[7 empty] | 4155 | 123 | 3.3383 | 2.2538
[7 empty] | 4156 | 124 | 3.3039 | 2.2289
[7 empty] | 4157 | 125 | 3.2609 | 2.1976
[7 empty] | 4158 | 126 | 3.4071 | 2.3038
[7 empty] | 4159 | 127 | 4.9556 | 3.4283
[7 empty] | 4160 | 128 | 6.5556 | 4.5902
[7 empty] | 4161 | 129 | 7.2524 | 5.0962
[7 empty] | 4162 | 130 | 7.6998 | 5.421
[7 empty] | 4163 | 131 | 7.8632 | 5.5397
[7 empty] | 4164 | 132 | 7.6051 | 5.3523
[7 empty] | 4165 | 133 | 8.2589 | 5.8271
[7 empty] | 4166 | 134 | 8.5686 | 6.052
[7 empty] | 4167 | 135 | 8.6374 | 6.1019
[7 empty] | 4168 | 136 | 7.803 | 5.496
[7 empty] | 4169 | 137 | 7.6998 | 5.421
[7 empty] | 4170 | 138 | 7.6482 | 5.3835
[7 empty] | 4171 | 139 | 7.3041 | 5.1337
[7 empty] | 4172 | 140 | 7.3127 | 5.1399
[7 empty] | 4173 | 141 | 6.6417 | 4.6526
[7 empty] | 4174 | 142 | 5.9879 | 4.1779
[7 empty] | 4175 | 143 | 5.0846 | 3.522
[7 empty] | 4176 | 144 | 4.4566 | 3.0659
[7 empty] | 4177 | 145 | 3.9749 | 2.7161
[7 empty] | 4178 | 146 | 3.7598 | 2.5599
[7 empty] | 4179 | 147 | 3.691 | 2.51
[7 empty] | 4180 | 148 | 3.6824 | 2.5037
[7 empty] | 4181 | 149 | 3.6824 | 2.5037
[7 empty] | 4182 | 150 | 3.691 | 2.51
[7 empty] | 4183 | 151 | 4.8007 | 3.3158
[7 empty] | 4184 | 152 | 6.3664 | 4.4527
[7 empty] | 4185 | 153 | 6.9944 | 4.9088
[7 empty] | 4186 | 154 | 7.5707 | 5.3273
[7 empty] | 4187 | 155 | 7.4159 | 5.2149
[7 empty] | 4188 | 156 | 7.5879 | 5.3398
[7 empty] | 4189 | 157 | 8.3192 | 5.8708
[7 empty] | 4190 | 158 | 8.6546 | 6.1144
[7 empty] | 4191 | 159 | 8.9299 | 6.3143
[7 empty] | 4192 | 160 | 8.8009 | 6.2206
[7 empty] | 4193 | 161 | 9.5837 | 6.7891
[7 empty] | 4194 | 162 | 9.0762 | 6.4205
[7 empty] | 4195 | 163 | 9.4461 | 6.6891
[7 empty] | 4196 | 164 | 8.0611 | 5.6834
[7 empty] | 4197 | 165 | 11.2698 | 8.0135
[7 empty] | 4198 | 166 | 9.1708 | 6.4892
[7 empty] | 4199 | 167 | 5.4717 | 3.8031
[7 empty] | 4200 | 168 | 4.8093 | 3.3221
[7 empty] | 4201 | 1 | 3.3125 | 2.2351
[7 empty] | 4202 | 2 | 3.2007 | 2.1539
[7 empty] | 4203 | 3 | 3.1921 | 2.1476
[7 empty] | 4204 | 4 | 3.3297 | 2.2476
[7 empty] | 4205 | 5 | 3.3469 | 2.2601
[7 empty] | 4206 | 6 | 3.7857 | 2.5787
[7 empty] | 4207 | 7 | 4.5255 | 3.1159
[7 empty] | 4208 | 8 | 5.2137 | 3.6157
[7 empty] | 4209 | 9 | 5.1879 | 3.5969
[7 empty] | 4210 | 10 | 6.7449 | 4.7276
[7 empty] | 4211 | 11 | 8.8783 | 6.2768
[7 empty] | 4212 | 12 | 9.8676 | 6.9952
[7 empty] | 4213 | 13 | 10.2547 | 7.2763
[7 empty] | 4214 | 14 | 10.031 | 7.1139
[7 empty] | 4215 | 15 | 9.9364 | 7.0452
[7 empty] | 4216 | 16 | 11.1494 | 7.926
[7 empty] | 4217 | 17 | 12.5086 | 8.913
[7 empty] | 4218 | 18 | 12.2591 | 8.7319
[7 empty] | 4219 | 19 | 12.801 | 9.1254
[7 empty] | 4220 | 20 | 12.7322 | 9.0755
[7 empty] | 4221 | 21 | 13.3172 | 9.5002
[7 empty] | 4222 | 22 | 9.2568 | 6.5517
[7 empty] | 4223 | 23 | 5.3857 | 3.7406
[7 empty] | 4224 | 24 | 3.6704 | 2.495
[7 empty] | 4225 | 25 | 3.5706 | 2.4225
[7 empty] | 4226 | 26 | 3.4588 | 2.3413
[7 empty] | 4227 | 27 | 3.3555 | 2.2663
[7 empty] | 4228 | 28 | 3.4416 | 2.3288
[7 empty] | 4229 | 29 | 3.691 | 2.51
[7 empty] | 4230 | 30 | 3.9405 | 2.6911
[7 empty] | 4231 | 31 | 4.8093 | 3.3221
[7 empty] | 4232 | 32 | 5.1706 | 3.5844
[7 empty] | 4233 | 33 | 5.8502 | 4.0779
[7 empty] | 4234 | 34 | 6.7707 | 4.7464
[7 empty] | 4235 | 35 | 8.9987 | 6.3643
[7 empty] | 4236 | 36 | 10.0569 | 7.1327
[7 empty] | 4237 | 37 | 10.1343 | 7.1889
[7 empty] | 4238 | 38 | 10.2117 | 7.2451
[7 empty] | 4239 | 39 | 9.8762 | 7.0015
[7 empty] | 4240 | 40 | 10.9601 | 7.7886
[7 empty] | 4241 | 41 | 11.5279 | 8.2009
[7 empty] | 4242 | 42 | 11.5451 | 8.2134
[7 empty] | 4243 | 43 | 11.9236 | 8.4882
[7 empty] | 4244 | 44 | 13.1107 | 9.3503
[7 empty] | 4245 | 45 | 12.6978 | 9.0505
[7 empty] | 4246 | 46 | 9.8762 | 7.0015
[7 empty] | 4247 | 47 | 6.1771 | 4.3153
[7 empty] | 4248 | 48 | 4.6373 | 3.1971
[7 empty] | 4249 | 49 | 3.9577 | 2.7036
[7 empty] | 4250 | 50 | 3.6394 | 2.4725
[7 empty] | 4251 | 51 | 3.5276 | 2.3913
[7 empty] | 4252 | 52 | 3.562 | 2.4163
[7 empty] | 4253 | 53 | 3.5878 | 2.435
[7 empty] | 4254 | 54 | 4.1814 | 2.866
[7 empty] | 4255 | 55 | 5.3513 | 3.7156
[7 empty] | 4256 | 56 | 5.6008 | 3.8968
[7 empty] | 4257 | 57 | 6.5729 | 4.6027
[7 empty] | 4258 | 58 | 7.7084 | 5.4273
[7 empty] | 4259 | 59 | 8.9471 | 6.3268
[7 empty] | 4260 | 60 | 9.5923 | 6.7953
[7 empty] | 4261 | 61 | 10.2891 | 7.3013
[7 empty] | 4262 | 62 | 10.0827 | 7.1514
[7 empty] | 4263 | 63 | 10.6934 | 7.5949
[7 empty] | 4264 | 64 | 11.6655 | 8.3008
[7 empty] | 4265 | 65 | 12.3021 | 8.7631
[7 empty] | 4266 | 66 | 12.1989 | 8.6882
[7 empty] | 4267 | 67 | 12.9559 | 9.2379
[7 empty] | 4268 | 68 | 13.2054 | 9.419
[7 empty] | 4269 | 69 | 12.6806 | 9.038
[7 empty] | 4270 | 70 | 10.3235 | 7.3263
[7 empty] | 4271 | 71 | 5.6868 | 3.9592
[7 empty] | 4272 | 72 | 4.5734 | 3.1507
[7 empty] | 4273 | 73 | 3.8373 | 2.6162
[7 empty] | 4274 | 74 | 3.605 | 2.4475
[7 empty] | 4275 | 75 | 3.5018 | 2.3725
[7 empty] | 4276 | 76 | 3.4416 | 2.3288
[7 empty] | 4277 | 77 | 3.6222 | 2.46
[7 empty] | 4278 | 78 | 4.0351 | 2.7598
[7 empty] | 4279 | 79 | 5.1793 | 3.5907
[7 empty] | 4280 | 80 | 5.3599 | 3.7219
[7 empty] | 4281 | 81 | 6.5729 | 4.6027
[7 empty] | 4282 | 82 | 7.6912 | 5.4148
[7 empty] | 4283 | 83 | 8.4482 | 5.9645
[7 empty] | 4284 | 84 | 9.7214 | 6.889
[7 empty] | 4285 | 85 | 9.4117 | 6.6642
[7 empty] | 4286 | 86 | 8.8869 | 6.2831
[7 empty] | 4287 | 87 | 9.3428 | 6.6142
[7 empty] | 4288 | 88 | 10.0224 | 7.1077
[7 empty] | 4289 | 89 | 11.4074 | 8.1134
[7 empty] | 4290 | 90 | 10.8053 | 7.6762
[7 empty] | 4291 | 91 | 11.5107 | 8.1884
[7 empty] | 4292 | 92 | 10.8913 | 7.7386
[7 empty] | 4293 | 93 | 8.4138 | 5.9395
[7 empty] | 4294 | 94 | 7.4847 | 5.2648
[7 empty] | 4295 | 95 | 5.575 | 3.878
[7 empty] | 4296 | 96 | 4.5599 | 3.1409
[7 empty] | 4297 | 97 | 4.5083 | 3.1034
[7 empty] | 4298 | 98 | 4.2072 | 2.8848
[7 empty] | 4299 | 99 | 4.147 | 2.841
[7 empty] | 4300 | 100 | 3.7857 | 2.5787
[7 empty] | 4301 | 101 | 3.7254 | 2.5349
[7 empty] | 4302 | 102 | 3.9663 | 2.7099
[7 empty] | 4303 | 103 | 4.7319 | 3.2658
[7 empty] | 4304 | 104 | 4.99 | 3.4532
[7 empty] | 4305 | 105 | 5.4889 | 3.8156
[7 empty] | 4306 | 106 | 6.9858 | 4.9025
[7 empty] | 4307 | 107 | 7.3471 | 5.1649
[7 empty] | 4308 | 108 | 8.9643 | 6.3393
[7 empty] | 4309 | 109 | 8.2847 | 5.8458
[7 empty] | 4310 | 110 | 7.8202 | 5.5085
[7 empty] | 4311 | 111 | 7.6568 | 5.3898
[7 empty] | 4312 | 112 | 7.7256 | 5.4398
[7 empty] | 4313 | 113 | 7.3729 | 5.1836
[7 empty] | 4314 | 114 | 7.5449 | 5.3086
[7 empty] | 4315 | 115 | 7.0804 | 4.9712
[7 empty] | 4316 | 116 | 7.7772 | 5.4772
[7 empty] | 4317 | 117 | 7.3471 | 5.1649
[7 empty] | 4318 | 118 | 6.5556 | 4.5902
[7 empty] | 4319 | 119 | 4.9212 | 3.4033
[7 empty] | 4320 | 120 | 4.5954 | 3.1667
[7 empty] | 4321 | 121 | 3.8459 | 2.6224
[7 empty] | 4322 | 122 | 3.4243 | 2.3163
[7 empty] | 4323 | 123 | 3.3383 | 2.2538
[7 empty] | 4324 | 124 | 3.3039 | 2.2289
[7 empty] | 4325 | 125 | 3.2609 | 2.1976
[7 empty] | 4326 | 126 | 3.4071 | 2.3038
[7 empty] | 4327 | 127 | 4.9556 | 3.4283
[7 empty] | 4328 | 128 | 6.5556 | 4.5902
[7 empty] | 4329 | 129 | 7.2524 | 5.0962
[7 empty] | 4330 | 130 | 7.6998 | 5.421
[7 empty] | 4331 | 131 | 7.8632 | 5.5397
[7 empty] | 4332 | 132 | 7.6051 | 5.3523
[7 empty] | 4333 | 133 | 8.2589 | 5.8271
[7 empty] | 4334 | 134 | 8.5686 | 6.052
[7 empty] | 4335 | 135 | 8.6374 | 6.1019
[7 empty] | 4336 | 136 | 7.803 | 5.496
[7 empty] | 4337 | 137 | 7.6998 | 5.421
[7 empty] | 4338 | 138 | 7.6482 | 5.3835
[7 empty] | 4339 | 139 | 7.3041 | 5.1337
[7 empty] | 4340 | 140 | 7.3127 | 5.1399
[7 empty] | 4341 | 141 | 6.6417 | 4.6526
[7 empty] | 4342 | 142 | 5.9879 | 4.1779
[7 empty] | 4343 | 143 | 5.0846 | 3.522
[7 empty] | 4344 | 144 | 4.4566 | 3.0659
[7 empty] | 4345 | 145 | 3.9749 | 2.7161
[7 empty] | 4346 | 146 | 3.7598 | 2.5599
[7 empty] | 4347 | 147 | 3.691 | 2.51
[7 empty] | 4348 | 148 | 3.6824 | 2.5037
[7 empty] | 4349 | 149 | 3.6824 | 2.5037
[7 empty] | 4350 | 150 | 3.691 | 2.51
[7 empty] | 4351 | 151 | 4.8007 | 3.3158
[7 empty] | 4352 | 152 | 6.3664 | 4.4527
[7 empty] | 4353 | 153 | 6.9944 | 4.9088
[7 empty] | 4354 | 154 | 7.5707 | 5.3273
[7 empty] | 4355 | 155 | 7.4159 | 5.2149
[7 empty] | 4356 | 156 | 7.5879 | 5.3398
[7 empty] | 4357 | 157 | 8.3192 | 5.8708
[7 empty] | 4358 | 158 | 8.6546 | 6.1144
[7 empty] | 4359 | 159 | 8.9299 | 6.3143
[7 empty] | 4360 | 160 | 8.8009 | 6.2206
[7 empty] | 4361 | 161 | 9.5837 | 6.7891
[7 empty] | 4362 | 162 | 9.0762 | 6.4205
[7 empty] | 4363 | 163 | 9.4461 | 6.6891
[7 empty] | 4364 | 164 | 8.0611 | 5.6834
[7 empty] | 4365 | 165 | 11.2698 | 8.0135
[7 empty] | 4366 | 166 | 9.1708 | 6.4892
[7 empty] | 4367 | 167 | 5.4717 | 3.8031
[7 empty] | 4368 | 168 | 4.8093 | 3.3221
[7 empty] | 4369 | 1 | 3.3125 | 2.2351
[7 empty] | 4370 | 2 | 3.2007 | 2.1539
[7 empty] | 4371 | 3 | 3.1921 | 2.1476
[7 empty] | 4372 | 4 | 3.3297 | 2.2476
[7 empty] | 4373 | 5 | 3.3469 | 2.2601
[7 empty] | 4374 | 6 | 3.7857 | 2.5787
[7 empty] | 4375 | 7 | 4.5255 | 3.1159
[7 empty] | 4376 | 8 | 5.2137 | 3.6157
[7 empty] | 4377 | 9 | 5.1879 | 3.5969
[7 empty] | 4378 | 10 | 6.7449 | 4.7276
[7 empty] | 4379 | 11 | 8.8783 | 6.2768
[7 empty] | 4380 | 12 | 9.8676 | 6.9952
[7 empty] | 4381 | 13 | 10.2547 | 7.2763
[7 empty] | 4382 | 14 | 10.031 | 7.1139
[7 empty] | 4383 | 15 | 9.9364 | 7.0452
[7 empty] | 4384 | 16 | 11.1494 | 7.926
[7 empty] | 4385 | 17 | 12.5086 | 8.913
[7 empty] | 4386 | 18 | 12.2591 | 8.7319
[7 empty] | 4387 | 19 | 12.801 | 9.1254
[7 empty] | 4388 | 20 | 12.7322 | 9.0755
[7 empty] | 4389 | 21 | 13.3172 | 9.5002
[7 empty] | 4390 | 22 | 9.2568 | 6.5517
[7 empty] | 4391 | 23 | 5.3857 | 3.7406
[7 empty] | 4392 | 24 | 3.6704 | 2.495
[7 empty] | 4393 | 25 | 3.5706 | 2.4225
[7 empty] | 4394 | 26 | 3.4588 | 2.3413
[7 empty] | 4395 | 27 | 3.3555 | 2.2663
[7 empty] | 4396 | 28 | 3.4416 | 2.3288
[7 empty] | 4397 | 29 | 3.691 | 2.51
[7 empty] | 4398 | 30 | 3.9405 | 2.6911
[7 empty] | 4399 | 31 | 4.8093 | 3.3221
[7 empty] | 4400 | 32 | 5.1706 | 3.5844
[7 empty] | 4401 | 33 | 5.8502 | 4.0779
[7 empty] | 4402 | 34 | 6.7707 | 4.7464
[7 empty] | 4403 | 35 | 8.9987 | 6.3643
[7 empty] | 4404 | 36 | 10.0569 | 7.1327
[7 empty] | 4405 | 37 | 10.1343 | 7.1889
[7 empty] | 4406 | 38 | 10.2117 | 7.2451
[7 empty] | 4407 | 39 | 9.8762 | 7.0015
[7 empty] | 4408 | 40 | 10.9601 | 7.7886
[7 empty] | 4409 | 41 | 11.5279 | 8.2009
[7 empty] | 4410 | 42 | 11.5451 | 8.2134
[7 empty] | 4411 | 43 | 11.9236 | 8.4882
[7 empty] | 4412 | 44 | 13.1107 | 9.3503
[7 empty] | 4413 | 45 | 12.6978 | 9.0505
[7 empty] | 4414 | 46 | 9.8762 | 7.0015
[7 empty] | 4415 | 47 | 6.1771 | 4.3153
[7 empty] | 4416 | 48 | 4.6373 | 3.1971
[7 empty] | 4417 | 49 | 3.9577 | 2.7036
[7 empty] | 4418 | 50 | 3.6394 | 2.4725
[7 empty] | 4419 | 51 | 3.5276 | 2.3913
[7 empty] | 4420 | 52 | 3.562 | 2.4163
[7 empty] | 4421 | 53 | 3.5878 | 2.435
[7 empty] | 4422 | 54 | 4.1814 | 2.866
[7 empty] | 4423 | 55 | 5.3513 | 3.7156
[7 empty] | 4424 | 56 | 5.6008 | 3.8968
[7 empty] | 4425 | 57 | 6.5729 | 4.6027
[7 empty] | 4426 | 58 | 7.7084 | 5.4273
[7 empty] | 4427 | 59 | 8.9471 | 6.3268
[7 empty] | 4428 | 60 | 9.5923 | 6.7953
[7 empty] | 4429 | 61 | 10.2891 | 7.3013
[7 empty] | 4430 | 62 | 10.0827 | 7.1514
[7 empty] | 4431 | 63 | 10.6934 | 7.5949
[7 empty] | 4432 | 64 | 11.6655 | 8.3008
[7 empty] | 4433 | 65 | 12.3021 | 8.7631
[7 empty] | 4434 | 66 | 12.1989 | 8.6882
[7 empty] | 4435 | 67 | 12.9559 | 9.2379
[7 empty] | 4436 | 68 | 13.2054 | 9.419
[7 empty] | 4437 | 69 | 12.6806 | 9.038
[7 empty] | 4438 | 70 | 10.3235 | 7.3263
[7 empty] | 4439 | 71 | 5.6868 | 3.9592
[7 empty] | 4440 | 72 | 4.5734 | 3.1507
[7 empty] | 4441 | 73 | 3.8373 | 2.6162
[7 empty] | 4442 | 74 | 3.605 | 2.4475
[7 empty] | 4443 | 75 | 3.5018 | 2.3725
[7 empty] | 4444 | 76 | 3.4416 | 2.3288
[7 empty] | 4445 | 77 | 3.6222 | 2.46
[7 empty] | 4446 | 78 | 4.0351 | 2.7598
[7 empty] | 4447 | 79 | 5.1793 | 3.5907
[7 empty] | 4448 | 80 | 5.3599 | 3.7219
[7 empty] | 4449 | 81 | 6.5729 | 4.6027
[7 empty] | 4450 | 82 | 7.6912 | 5.4148
[7 empty] | 4451 | 83 | 8.4482 | 5.9645
[7 empty] | 4452 | 84 | 9.7214 | 6.889
[7 empty] | 4453 | 85 | 9.4117 | 6.6642
[7 empty] | 4454 | 86 | 8.8869 | 6.2831
[7 empty] | 4455 | 87 | 9.3428 | 6.6142
[7 empty] | 4456 | 88 | 10.0224 | 7.1077
[7 empty] | 4457 | 89 | 11.4074 | 8.1134
[7 empty] | 4458 | 90 | 10.8053 | 7.6762
[7 empty] | 4459 | 91 | 11.5107 | 8.1884
[7 empty] | 4460 | 92 | 10.8913 | 7.7386
[7 empty] | 4461 | 93 | 8.4138 | 5.9395
[7 empty] | 4462 | 94 | 7.4847 | 5.2648
[7 empty] | 4463 | 95 | 5.575 | 3.878
[7 empty] | 4464 | 96 | 4.5599 | 3.1409
[7 empty] | 4465 | 97 | 4.5083 | 3.1034
[7 empty] | 4466 | 98 | 4.2072 | 2.8848
[7 empty] | 4467 | 99 | 4.147 | 2.841
[7 empty] | 4468 | 100 | 3.7857 | 2.5787
[7 empty] | 4469 | 101 | 3.7254 | 2.5349
[7 empty] | 4470 | 102 | 3.9663 | 2.7099
[7 empty] | 4471 | 103 | 4.7319 | 3.2658
[7 empty] | 4472 | 104 | 4.99 | 3.4532
[7 empty] | 4473 | 105 | 5.4889 | 3.8156
[7 empty] | 4474 | 106 | 6.9858 | 4.9025
[7 empty] | 4475 | 107 | 7.3471 | 5.1649
[7 empty] | 4476 | 108 | 8.9643 | 6.3393
[7 empty] | 4477 | 109 | 8.2847 | 5.8458
[7 empty] | 4478 | 110 | 7.8202 | 5.5085
[7 empty] | 4479 | 111 | 7.6568 | 5.3898
[7 empty] | 4480 | 112 | 7.7256 | 5.4398
[7 empty] | 4481 | 113 | 7.3729 | 5.1836
[7 empty] | 4482 | 114 | 7.5449 | 5.3086
[7 empty] | 4483 | 115 | 7.0804 | 4.9712
[7 empty] | 4484 | 116 | 7.7772 | 5.4772
[7 empty] | 4485 | 117 | 7.3471 | 5.1649
[7 empty] | 4486 | 118 | 6.5556 | 4.5902
[7 empty] | 4487 | 119 | 4.9212 | 3.4033
[7 empty] | 4488 | 120 | 4.5954 | 3.1667
[7 empty] | 4489 | 121 | 3.8459 | 2.6224
[7 empty] | 4490 | 122 | 3.4243 | 2.3163
[7 empty] | 4491 | 123 | 3.3383 | 2.2538
[7 empty] | 4492 | 124 | 3.3039 | 2.2289
[7 empty] | 4493 | 125 | 3.2609 | 2.1976
[7 empty] | 4494 | 126 | 3.4071 | 2.3038
[7 empty] | 4495 | 127 | 4.9556 | 3.4283
[7 empty] | 4496 | 128 | 6.5556 | 4.5902
[7 empty] | 4497 | 129 | 7.2524 | 5.0962
[7 empty] | 4498 | 130 | 7.6998 | 5.421
[7 empty] | 4499 | 131 | 7.8632 | 5.5397
[7 empty] | 4500 | 132 | 7.6051 | 5.3523
[7 empty] | 4501 | 133 | 8.2589 | 5.8271
[7 empty] | 4502 | 134 | 8.5686 | 6.052
[7 empty] | 4503 | 135 | 8.6374 | 6.1019
[7 empty] | 4504 | 136 | 7.803 | 5.496
[7 empty] | 4505 | 137 | 7.6998 | 5.421
[7 empty] | 4506 | 138 | 7.6482 | 5.3835
[7 empty] | 4507 | 139 | 7.3041 | 5.1337
[7 empty] | 4508 | 140 | 7.3127 | 5.1399
[7 empty] | 4509 | 141 | 6.6417 | 4.6526
[7 empty] | 4510 | 142 | 5.9879 | 4.1779
[7 empty] | 4511 | 143 | 5.0846 | 3.522
[7 empty] | 4512 | 144 | 4.4566 | 3.0659
[7 empty] | 4513 | 145 | 3.9749 | 2.7161
[7 empty] | 4514 | 146 | 3.7598 | 2.5599
[7 empty] | 4515 | 147 | 3.691 | 2.51
[7 empty] | 4516 | 148 | 3.6824 | 2.5037
[7 empty] | 4517 | 149 | 3.6824 | 2.5037
[7 empty] | 4518 | 150 | 3.691 | 2.51
[7 empty] | 4519 | 151 | 4.8007 | 3.3158
[7 empty] | 4520 | 152 | 6.3664 | 4.4527
[7 empty] | 4521 | 153 | 6.9944 | 4.9088
[7 empty] | 4522 | 154 | 7.5707 | 5.3273
[7 empty] | 4523 | 155 | 7.4159 | 5.2149
[7 empty] | 4524 | 156 | 7.5879 | 5.3398
[7 empty] | 4525 | 157 | 8.3192 | 5.8708
[7 empty] | 4526 | 158 | 8.6546 | 6.1144
[7 empty] | 4527 | 159 | 8.9299 | 6.3143
[7 empty] | 4528 | 160 | 8.8009 | 6.2206
[7 empty] | 4529 | 161 | 9.5837 | 6.7891
[7 empty] | 4530 | 162 | 9.0762 | 6.4205
[7 empty] | 4531 | 163 | 9.4461 | 6.6891
[7 empty] | 4532 | 164 | 8.0611 | 5.6834
[7 empty] | 4533 | 165 | 11.2698 | 8.0135
[7 empty] | 4534 | 166 | 9.1708 | 6.4892
[7 empty] | 4535 | 167 | 5.4717 | 3.8031
[7 empty] | 4536 | 168 | 4.8093 | 3.3221
[7 empty] | 4537 | 1 | 3.3125 | 2.2351
[7 empty] | 4538 | 2 | 3.2007 | 2.1539
[7 empty] | 4539 | 3 | 3.1921 | 2.1476
[7 empty] | 4540 | 4 | 3.3297 | 2.2476
[7 empty] | 4541 | 5 | 3.3469 | 2.2601
[7 empty] | 4542 | 6 | 3.7857 | 2.5787
[7 empty] | 4543 | 7 | 4.5255 | 3.1159
[7 empty] | 4544 | 8 | 5.2137 | 3.6157
[7 empty] | 4545 | 9 | 5.1879 | 3.5969
[7 empty] | 4546 | 10 | 6.7449 | 4.7276
[7 empty] | 4547 | 11 | 8.8783 | 6.2768
[7 empty] | 4548 | 12 | 9.8676 | 6.9952
[7 empty] | 4549 | 13 | 10.2547 | 7.2763
[7 empty] | 4550 | 14 | 10.031 | 7.1139
[7 empty] | 4551 | 15 | 9.9364 | 7.0452
[7 empty] | 4552 | 16 | 11.1494 | 7.926
[7 empty] | 4553 | 17 | 12.5086 | 8.913
[7 empty] | 4554 | 18 | 12.2591 | 8.7319
[7 empty] | 4555 | 19 | 12.801 | 9.1254
[7 empty] | 4556 | 20 | 12.7322 | 9.0755
[7 empty] | 4557 | 21 | 13.3172 | 9.5002
[7 empty] | 4558 | 22 | 9.2568 | 6.5517
[7 empty] | 4559 | 23 | 5.3857 | 3.7406
[7 empty] | 4560 | 24 | 3.6704 | 2.495
[7 empty] | 4561 | 25 | 3.5706 | 2.4225
[7 empty] | 4562 | 26 | 3.4588 | 2.3413
[7 empty] | 4563 | 27 | 3.3555 | 2.2663
[7 empty] | 4564 | 28 | 3.4416 | 2.3288
[7 empty] | 4565 | 29 | 3.691 | 2.51
[7 empty] | 4566 | 30 | 3.9405 | 2.6911
[7 empty] | 4567 | 31 | 4.8093 | 3.3221
[7 empty] | 4568 | 32 | 5.1706 | 3.5844
[7 empty] | 4569 | 33 | 5.8502 | 4.0779
[7 empty] | 4570 | 34 | 6.7707 | 4.7464
[7 empty] | 4571 | 35 | 8.9987 | 6.3643
[7 empty] | 4572 | 36 | 10.0569 | 7.1327
[7 empty] | 4573 | 37 | 10.1343 | 7.1889
[7 empty] | 4574 | 38 | 10.2117 | 7.2451
[7 empty] | 4575 | 39 | 9.8762 | 7.0015
[7 empty] | 4576 | 40 | 10.9601 | 7.7886
[7 empty] | 4577 | 41 | 11.5279 | 8.2009
[7 empty] | 4578 | 42 | 11.5451 | 8.2134
[7 empty] | 4579 | 43 | 11.9236 | 8.4882
[7 empty] | 4580 | 44 | 13.1107 | 9.3503
[7 empty] | 4581 | 45 | 12.6978 | 9.0505
[7 empty] | 4582 | 46 | 9.8762 | 7.0015
[7 empty] | 4583 | 47 | 6.1771 | 4.3153
[7 empty] | 4584 | 48 | 4.6373 | 3.1971
[7 empty] | 4585 | 49 | 3.9577 | 2.7036
[7 empty] | 4586 | 50 | 3.6394 | 2.4725
[7 empty] | 4587 | 51 | 3.5276 | 2.3913
[7 empty] | 4588 | 52 | 3.562 | 2.4163
[7 empty] | 4589 | 53 | 3.5878 | 2.435
[7 empty] | 4590 | 54 | 4.1814 | 2.866
[7 empty] | 4591 | 55 | 5.3513 | 3.7156
[7 empty] | 4592 | 56 | 5.6008 | 3.8968
[7 empty] | 4593 | 57 | 6.5729 | 4.6027
[7 empty] | 4594 | 58 | 7.7084 | 5.4273
[7 empty] | 4595 | 59 | 8.9471 | 6.3268
[7 empty] | 4596 | 60 | 9.5923 | 6.7953
[7 empty] | 4597 | 61 | 10.2891 | 7.3013
[7 empty] | 4598 | 62 | 10.0827 | 7.1514
[7 empty] | 4599 | 63 | 10.6934 | 7.5949
[7 empty] | 4600 | 64 | 11.6655 | 8.3008
[7 empty] | 4601 | 65 | 12.3021 | 8.7631
[7 empty] | 4602 | 66 | 12.1989 | 8.6882
[7 empty] | 4603 | 67 | 12.9559 | 9.2379
[7 empty] | 4604 | 68 | 13.2054 | 9.419
[7 empty] | 4605 | 69 | 12.6806 | 9.038
[7 empty] | 4606 | 70 | 10.3235 | 7.3263
[7 empty] | 4607 | 71 | 5.6868 | 3.9592
[7 empty] | 4608 | 72 | 4.5734 | 3.1507
[7 empty] | 4609 | 73 | 3.8373 | 2.6162
[7 empty] | 4610 | 74 | 3.605 | 2.4475
[7 empty] | 4611 | 75 | 3.5018 | 2.3725
[7 empty] | 4612 | 76 | 3.4416 | 2.3288
[7 empty] | 4613 | 77 | 3.6222 | 2.46
[7 empty] | 4614 | 78 | 4.0351 | 2.7598
[7 empty] | 4615 | 79 | 5.1793 | 3.5907
[7 empty] | 4616 | 80 | 5.3599 | 3.7219
[7 empty] | 4617 | 81 | 6.5729 | 4.6027
[7 empty] | 4618 | 82 | 7.6912 | 5.4148
[7 empty] | 4619 | 83 | 8.4482 | 5.9645
[7 empty] | 4620 | 84 | 9.7214 | 6.889
[7 empty] | 4621 | 85 | 9.4117 | 6.6642
[7 empty] | 4622 | 86 | 8.8869 | 6.2831
[7 empty] | 4623 | 87 | 9.3428 | 6.6142
[7 empty] | 4624 | 88 | 10.0224 | 7.1077
[7 empty] | 4625 | 89 | 11.4074 | 8.1134
[7 empty] | 4626 | 90 | 10.8053 | 7.6762
[7 empty] | 4627 | 91 | 11.5107 | 8.1884
[7 empty] | 4628 | 92 | 10.8913 | 7.7386
[7 empty] | 4629 | 93 | 8.4138 | 5.9395
[7 empty] | 4630 | 94 | 7.4847 | 5.2648
[7 empty] | 4631 | 95 | 5.575 | 3.878
[7 empty] | 4632 | 96 | 4.5599 | 3.1409
[7 empty] | 4633 | 97 | 4.5083 | 3.1034
[7 empty] | 4634 | 98 | 4.2072 | 2.8848
[7 empty] | 4635 | 99 | 4.147 | 2.841
[7 empty] | 4636 | 100 | 3.7857 | 2.5787
[7 empty] | 4637 | 101 | 3.7254 | 2.5349
[7 empty] | 4638 | 102 | 3.9663 | 2.7099
[7 empty] | 4639 | 103 | 4.7319 | 3.2658
[7 empty] | 4640 | 104 | 4.99 | 3.4532
[7 empty] | 4641 | 105 | 5.4889 | 3.8156
[7 empty] | 4642 | 106 | 6.9858 | 4.9025
[7 empty] | 4643 | 107 | 7.3471 | 5.1649
[7 empty] | 4644 | 108 | 8.9643 | 6.3393
[7 empty] | 4645 | 109 | 8.2847 | 5.8458
[7 empty] | 4646 | 110 | 7.8202 | 5.5085
[7 empty] | 4647 | 111 | 7.6568 | 5.3898
[7 empty] | 4648 | 112 | 7.7256 | 5.4398
[7 empty] | 4649 | 113 | 7.3729 | 5.1836
[7 empty] | 4650 | 114 | 7.5449 | 5.3086
[7 empty] | 4651 | 115 | 7.0804 | 4.9712
[7 empty] | 4652 | 116 | 7.7772 | 5.4772
[7 empty] | 4653 | 117 | 7.3471 | 5.1649
[7 empty] | 4654 | 118 | 6.5556 | 4.5902
[7 empty] | 4655 | 119 | 4.9212 | 3.4033
[7 empty] | 4656 | 120 | 4.5954 | 3.1667
[7 empty] | 4657 | 121 | 3.8459 | 2.6224
[7 empty] | 4658 | 122 | 3.4243 | 2.3163
[7 empty] | 4659 | 123 | 3.3383 | 2.2538
[7 empty] | 4660 | 124 | 3.3039 | 2.2289
[7 empty] | 4661 | 125 | 3.2609 | 2.1976
[7 empty] | 4662 | 126 | 3.4071 | 2.3038
[7 empty] | 4663 | 127 | 4.9556 | 3.4283
[7 empty] | 4664 | 128 | 6.5556 | 4.5902
[7 empty] | 4665 | 129 | 7.2524 | 5.0962
[7 empty] | 4666 | 130 | 7.6998 | 5.421
[7 empty] | 4667 | 131 | 7.8632 | 5.5397
[7 empty] | 4668 | 132 | 7.6051 | 5.3523
[7 empty] | 4669 | 133 | 8.2589 | 5.8271
[7 empty] | 4670 | 134 | 8.5686 | 6.052
[7 empty] | 4671 | 135 | 8.6374 | 6.1019
[7 empty] | 4672 | 136 | 7.803 | 5.496
[7 empty] | 4673 | 137 | 7.6998 | 5.421
[7 empty] | 4674 | 138 | 7.6482 | 5.3835
[7 empty] | 4675 | 139 | 7.3041 | 5.1337
[7 empty] | 4676 | 140 | 7.3127 | 5.1399
[7 empty] | 4677 | 141 | 6.6417 | 4.6526
[7 empty] | 4678 | 142 | 5.9879 | 4.1779
[7 empty] | 4679 | 143 | 5.0846 | 3.522
[7 empty] | 4680 | 144 | 4.4566 | 3.0659
[7 empty] | 4681 | 145 | 3.9749 | 2.7161
[7 empty] | 4682 | 146 | 3.7598 | 2.5599
[7 empty] | 4683 | 147 | 3.691 | 2.51
[7 empty] | 4684 | 148 | 3.6824 | 2.5037
[7 empty] | 4685 | 149 | 3.6824 | 2.5037
[7 empty] | 4686 | 150 | 3.691 | 2.51
[7 empty] | 4687 | 151 | 4.8007 | 3.3158
[7 empty] | 4688 | 152 | 6.3664 | 4.4527
[7 empty] | 4689 | 153 | 6.9944 | 4.9088
[7 empty] | 4690 | 154 | 7.5707 | 5.3273
[7 empty] | 4691 | 155 | 7.4159 | 5.2149
[7 empty] | 4692 | 156 | 7.5879 | 5.3398
[7 empty] | 4693 | 157 | 8.3192 | 5.8708
[7 empty] | 4694 | 158 | 8.6546 | 6.1144
[7 empty] | 4695 | 159 | 8.9299 | 6.3143
[7 empty] | 4696 | 160 | 8.8009 | 6.2206
[7 empty] | 4697 | 161 | 9.5837 | 6.7891
[7 empty] | 4698 | 162 | 9.0762 | 6.4205
[7 empty] | 4699 | 163 | 9.4461 | 6.6891
[7 empty] | 4700 | 164 | 8.0611 | 5.6834
[7 empty] | 4701 | 165 | 11.2698 | 8.0135
[7 empty] | 4702 | 166 | 9.1708 | 6.4892
[7 empty] | 4703 | 167 | 5.4717 | 3.8031
[7 empty] | 4704 | 168 | 4.8093 | 3.3221
[7 empty] | 4705 | 1 | 3.3125 | 2.2351
[7 empty] | 4706 | 2 | 3.2007 | 2.1539
[7 empty] | 4707 | 3 | 3.1921 | 2.1476
[7 empty] | 4708 | 4 | 3.3297 | 2.2476
[7 empty] | 4709 | 5 | 3.3469 | 2.2601
[7 empty] | 4710 | 6 | 3.7857 | 2.5787
[7 empty] | 4711 | 7 | 4.5255 | 3.1159
[7 empty] | 4712 | 8 | 5.2137 | 3.6157
[7 empty] | 4713 | 9 | 5.1879 | 3.5969
[7 empty] | 4714 | 10 | 6.7449 | 4.7276
[7 empty] | 4715 | 11 | 8.8783 | 6.2768
[7 empty] | 4716 | 12 | 9.8676 | 6.9952
[7 empty] | 4717 | 13 | 10.2547 | 7.2763
[7 empty] | 4718 | 14 | 10.031 | 7.1139
[7 empty] | 4719 | 15 | 9.9364 | 7.0452
[7 empty] | 4720 | 16 | 11.1494 | 7.926
[7 empty] | 4721 | 17 | 12.5086 | 8.913
[7 empty] | 4722 | 18 | 12.2591 | 8.7319
[7 empty] | 4723 | 19 | 12.801 | 9.1254
[7 empty] | 4724 | 20 | 12.7322 | 9.0755
[7 empty] | 4725 | 21 | 13.3172 | 9.5002
[7 empty] | 4726 | 22 | 9.2568 | 6.5517
[7 empty] | 4727 | 23 | 5.3857 | 3.7406
[7 empty] | 4728 | 24 | 3.6704 | 2.495
[7 empty] | 4729 | 25 | 3.5706 | 2.4225
[7 empty] | 4730 | 26 | 3.4588 | 2.3413
[7 empty] | 4731 | 27 | 3.3555 | 2.2663
[7 empty] | 4732 | 28 | 3.4416 | 2.3288
[7 empty] | 4733 | 29 | 3.691 | 2.51
[7 empty] | 4734 | 30 | 3.9405 | 2.6911
[7 empty] | 4735 | 31 | 4.8093 | 3.3221
[7 empty] | 4736 | 32 | 5.1706 | 3.5844
[7 empty] | 4737 | 33 | 5.8502 | 4.0779
[7 empty] | 4738 | 34 | 6.7707 | 4.7464
[7 empty] | 4739 | 35 | 8.9987 | 6.3643
[7 empty] | 4740 | 36 | 10.0569 | 7.1327
[7 empty] | 4741 | 37 | 10.1343 | 7.1889
[7 empty] | 4742 | 38 | 10.2117 | 7.2451
[7 empty] | 4743 | 39 | 9.8762 | 7.0015
[7 empty] | 4744 | 40 | 10.9601 | 7.7886
[7 empty] | 4745 | 41 | 11.5279 | 8.2009
[7 empty] | 4746 | 42 | 11.5451 | 8.2134
[7 empty] | 4747 | 43 | 11.9236 | 8.4882
[7 empty] | 4748 | 44 | 13.1107 | 9.3503
[7 empty] | 4749 | 45 | 12.6978 | 9.0505
[7 empty] | 4750 | 46 | 9.8762 | 7.0015
[7 empty] | 4751 | 47 | 6.1771 | 4.3153
[7 empty] | 4752 | 48 | 4.6373 | 3.1971
[7 empty] | 4753 | 49 | 3.9577 | 2.7036
[7 empty] | 4754 | 50 | 3.6394 | 2.4725
[7 empty] | 4755 | 51 | 3.5276 | 2.3913
[7 empty] | 4756 | 52 | 3.562 | 2.4163
[7 empty] | 4757 | 53 | 3.5878 | 2.435
[7 empty] | 4758 | 54 | 4.1814 | 2.866
[7 empty] | 4759 | 55 | 5.3513 | 3.7156
[7 empty] | 4760 | 56 | 5.6008 | 3.8968
[7 empty] | 4761 | 57 | 6.5729 | 4.6027
[7 empty] | 4762 | 58 | 7.7084 | 5.4273
[7 empty] | 4763 | 59 | 8.9471 | 6.3268
[7 empty] | 4764 | 60 | 9.5923 | 6.7953
[7 empty] | 4765 | 61 | 10.2891 | 7.3013
[7 empty] | 4766 | 62 | 10.0827 | 7.1514
[7 empty] | 4767 | 63 | 10.6934 | 7.5949
[7 empty] | 4768 | 64 | 11.6655 | 8.3008
[7 empty] | 4769 | 65 | 12.3021 | 8.7631
[7 empty] | 4770 | 66 | 12.1989 | 8.6882
[7 empty] | 4771 | 67 | 12.9559 | 9.2379
[7 empty] | 4772 | 68 | 13.2054 | 9.419
[7 empty] | 4773 | 69 | 12.6806 | 9.038
[7 empty] | 4774 | 70 | 10.3235 | 7.3263
[7 empty] | 4775 | 71 | 5.6868 | 3.9592
[7 empty] | 4776 | 72 | 4.5734 | 3.1507
[7 empty] | 4777 | 73 | 3.8373 | 2.6162
[7 empty] | 4778 | 74 | 3.605 | 2.4475
[7 empty] | 4779 | 75 | 3.5018 | 2.3725
[7 empty] | 4780 | 76 | 3.4416 | 2.3288
[7 empty] | 4781 | 77 | 3.6222 | 2.46
[7 empty] | 4782 | 78 | 4.0351 | 2.7598
[7 empty] | 4783 | 79 | 5.1793 | 3.5907
[7 empty] | 4784 | 80 | 5.3599 | 3.7219
[7 empty] | 4785 | 81 | 6.5729 | 4.6027
[7 empty] | 4786 | 82 | 7.6912 | 5.4148
[7 empty] | 4787 | 83 | 8.4482 | 5.9645
[7 empty] | 4788 | 84 | 9.7214 | 6.889
[7 empty] | 4789 | 85 | 9.4117 | 6.6642
[7 empty] | 4790 | 86 | 8.8869 | 6.2831
[7 empty] | 4791 | 87 | 9.3428 | 6.6142
[7 empty] | 4792 | 88 | 10.0224 | 7.1077
[7 empty] | 4793 | 89 | 11.4074 | 8.1134
[7 empty] | 4794 | 90 | 10.8053 | 7.6762
[7 empty] | 4795 | 91 | 11.5107 | 8.1884
[7 empty] | 4796 | 92 | 10.8913 | 7.7386
[7 empty] | 4797 | 93 | 8.4138 | 5.9395
[7 empty] | 4798 | 94 | 7.4847 | 5.2648
[7 empty] | 4799 | 95 | 5.575 | 3.878
[7 empty] | 4800 | 96 | 4.5599 | 3.1409
[7 empty] | 4801 | 97 | 4.5083 | 3.1034
[7 empty] | 4802 | 98 | 4.2072 | 2.8848
[7 empty] | 4803 | 99 | 4.147 | 2.841
[7 empty] | 4804 | 100 | 3.7857 | 2.5787
[7 empty] | 4805 | 101 | 3.7254 | 2.5349
[7 empty] | 4806 | 102 | 3.9663 | 2.7099
[7 empty] | 4807 | 103 | 4.7319 | 3.2658
[7 empty] | 4808 | 104 | 4.99 | 3.4532
[7 empty] | 4809 | 105 | 5.4889 | 3.8156
[7 empty] | 4810 | 106 | 6.9858 | 4.9025
[7 empty] | 4811 | 107 | 7.3471 | 5.1649
[7 empty] | 4812 | 108 | 8.9643 | 6.3393
[7 empty] | 4813 | 109 | 8.2847 | 5.8458
[7 empty] | 4814 | 110 | 7.8202 | 5.5085
[7 empty] | 4815 | 111 | 7.6568 | 5.3898
[7 empty] | 4816 | 112 | 7.7256 | 5.4398
[7 empty] | 4817 | 113 | 7.3729 | 5.1836
[7 empty] | 4818 | 114 | 7.5449 | 5.3086
[7 empty] | 4819 | 115 | 7.0804 | 4.9712
[7 empty] | 4820 | 116 | 7.7772 | 5.4772
[7 empty] | 4821 | 117 | 7.3471 | 5.1649
[7 empty] | 4822 | 118 | 6.5556 | 4.5902
[7 empty] | 4823 | 119 | 4.9212 | 3.4033
[7 empty] | 4824 | 120 | 4.5954 | 3.1667
[7 empty] | 4825 | 121 | 3.8459 | 2.6224
[7 empty] | 4826 | 122 | 3.4243 | 2.3163
[7 empty] | 4827 | 123 | 3.3383 | 2.2538
[7 empty] | 4828 | 124 | 3.3039 | 2.2289
[7 empty] | 4829 | 125 | 3.2609 | 2.1976
[7 empty] | 4830 | 126 | 3.4071 | 2.3038
[7 empty] | 4831 | 127 | 4.9556 | 3.4283
[7 empty] | 4832 | 128 | 6.5556 | 4.5902
[7 empty] | 4833 | 129 | 7.2524 | 5.0962
[7 empty] | 4834 | 130 | 7.6998 | 5.421
[7 empty] | 4835 | 131 | 7.8632 | 5.5397
[7 empty] | 4836 | 132 | 7.6051 | 5.3523
[7 empty] | 4837 | 133 | 8.2589 | 5.8271
[7 empty] | 4838 | 134 | 8.5686 | 6.052
[7 empty] | 4839 | 135 | 8.6374 | 6.1019
[7 empty] | 4840 | 136 | 7.803 | 5.496
[7 empty] | 4841 | 137 | 7.6998 | 5.421
[7 empty] | 4842 | 138 | 7.6482 | 5.3835
[7 empty] | 4843 | 139 | 7.3041 | 5.1337
[7 empty] | 4844 | 140 | 7.3127 | 5.1399
[7 empty] | 4845 | 141 | 6.6417 | 4.6526
[7 empty] | 4846 | 142 | 5.9879 | 4.1779
[7 empty] | 4847 | 143 | 5.0846 | 3.522
[7 empty] | 4848 | 144 | 4.4566 | 3.0659
[7 empty] | 4849 | 145 | 3.9749 | 2.7161
[7 empty] | 4850 | 146 | 3.7598 | 2.5599
[7 empty] | 4851 | 147 | 3.691 | 2.51
[7 empty] | 4852 | 148 | 3.6824 | 2.5037
[7 empty] | 4853 | 149 | 3.6824 | 2.5037
[7 empty] | 4854 | 150 | 3.691 | 2.51
[7 empty] | 4855 | 151 | 4.8007 | 3.3158
[7 empty] | 4856 | 152 | 6.3664 | 4.4527
[7 empty] | 4857 | 153 | 6.9944 | 4.9088
[7 empty] | 4858 | 154 | 7.5707 | 5.3273
[7 empty] | 4859 | 155 | 7.4159 | 5.2149
[7 empty] | 4860 | 156 | 7.5879 | 5.3398
[7 empty] | 4861 | 157 | 8.3192 | 5.8708
[7 empty] | 4862 | 158 | 8.6546 | 6.1144
[7 empty] | 4863 | 159 | 8.9299 | 6.3143
[7 empty] | 4864 | 160 | 8.8009 | 6.2206
[7 empty] | 4865 | 161 | 9.5837 | 6.7891
[7 empty] | 4866 | 162 | 9.0762 | 6.4205
[7 empty] | 4867 | 163 | 9.4461 | 6.6891
[7 empty] | 4868 | 164 | 8.0611 | 5.6834
[7 empty] | 4869 | 165 | 11.2698 | 8.0135
[7 empty] | 4870 | 166 | 9.1708 | 6.4892
[7 empty] | 4871 | 167 | 5.4717 | 3.8031
[7 empty] | 4872 | 168 | 4.8093 | 3.3221
[7 empty] | 4873 | 1 | 3.3125 | 2.2351
[7 empty] | 4874 | 2 | 3.2007 | 2.1539
[7 empty] | 4875 | 3 | 3.1921 | 2.1476
[7 empty] | 4876 | 4 | 3.3297 | 2.2476
[7 empty] | 4877 | 5 | 3.3469 | 2.2601
[7 empty] | 4878 | 6 | 3.7857 | 2.5787
[7 empty] | 4879 | 7 | 4.5255 | 3.1159
[7 empty] | 4880 | 8 | 5.2137 | 3.6157
[7 empty] | 4881 | 9 | 5.1879 | 3.5969
[7 empty] | 4882 | 10 | 6.7449 | 4.7276
[7 empty] | 4883 | 11 | 8.8783 | 6.2768
[7 empty] | 4884 | 12 | 9.8676 | 6.9952
[7 empty] | 4885 | 13 | 10.2547 | 7.2763
[7 empty] | 4886 | 14 | 10.031 | 7.1139
[7 empty] | 4887 | 15 | 9.9364 | 7.0452
[7 empty] | 4888 | 16 | 11.1494 | 7.926
[7 empty] | 4889 | 17 | 12.5086 | 8.913
[7 empty] | 4890 | 18 | 12.2591 | 8.7319
[7 empty] | 4891 | 19 | 12.801 | 9.1254
[7 empty] | 4892 | 20 | 12.7322 | 9.0755
[7 empty] | 4893 | 21 | 13.3172 | 9.5002
[7 empty] | 4894 | 22 | 9.2568 | 6.5517
[7 empty] | 4895 | 23 | 5.3857 | 3.7406
[7 empty] | 4896 | 24 | 3.6704 | 2.495
[7 empty] | 4897 | 25 | 3.5706 | 2.4225
[7 empty] | 4898 | 26 | 3.4588 | 2.3413
[7 empty] | 4899 | 27 | 3.3555 | 2.2663
[7 empty] | 4900 | 28 | 3.4416 | 2.3288
[7 empty] | 4901 | 29 | 3.691 | 2.51
[7 empty] | 4902 | 30 | 3.9405 | 2.6911
[7 empty] | 4903 | 31 | 4.8093 | 3.3221
[7 empty] | 4904 | 32 | 5.1706 | 3.5844
[7 empty] | 4905 | 33 | 5.8502 | 4.0779
[7 empty] | 4906 | 34 | 6.7707 | 4.7464
[7 empty] | 4907 | 35 | 8.9987 | 6.3643
[7 empty] | 4908 | 36 | 10.0569 | 7.1327
[7 empty] | 4909 | 37 | 10.1343 | 7.1889
[7 empty] | 4910 | 38 | 10.2117 | 7.2451
[7 empty] | 4911 | 39 | 9.8762 | 7.0015
[7 empty] | 4912 | 40 | 10.9601 | 7.7886
[7 empty] | 4913 | 41 | 11.5279 | 8.2009
[7 empty] | 4914 | 42 | 11.5451 | 8.2134
[7 empty] | 4915 | 43 | 11.9236 | 8.4882
[7 empty] | 4916 | 44 | 13.1107 | 9.3503
[7 empty] | 4917 | 45 | 12.6978 | 9.0505
[7 empty] | 4918 | 46 | 9.8762 | 7.0015
[7 empty] | 4919 | 47 | 6.1771 | 4.3153
[7 empty] | 4920 | 48 | 4.6373 | 3.1971
[7 empty] | 4921 | 49 | 3.9577 | 2.7036
[7 empty] | 4922 | 50 | 3.6394 | 2.4725
[7 empty] | 4923 | 51 | 3.5276 | 2.3913
[7 empty] | 4924 | 52 | 3.562 | 2.4163
[7 empty] | 4925 | 53 | 3.5878 | 2.435
[7 empty] | 4926 | 54 | 4.1814 | 2.866
[7 empty] | 4927 | 55 | 5.3513 | 3.7156
[7 empty] | 4928 | 56 | 5.6008 | 3.8968
[7 empty] | 4929 | 57 | 6.5729 | 4.6027
[7 empty] | 4930 | 58 | 7.7084 | 5.4273
[7 empty] | 4931 | 59 | 8.9471 | 6.3268
[7 empty] | 4932 | 60 | 9.5923 | 6.7953
[7 empty] | 4933 | 61 | 10.2891 | 7.3013
[7 empty] | 4934 | 62 | 10.0827 | 7.1514
[7 empty] | 4935 | 63 | 10.6934 | 7.5949
[7 empty] | 4936 | 64 | 11.6655 | 8.3008
[7 empty] | 4937 | 65 | 12.3021 | 8.7631
[7 empty] | 4938 | 66 | 12.1989 | 8.6882
[7 empty] | 4939 | 67 | 12.9559 | 9.2379
[7 empty] | 4940 | 68 | 13.2054 | 9.419
[7 empty] | 4941 | 69 | 12.6806 | 9.038
[7 empty] | 4942 | 70 | 10.3235 | 7.3263
[7 empty] | 4943 | 71 | 5.6868 | 3.9592
[7 empty] | 4944 | 72 | 4.5734 | 3.1507
[7 empty] | 4945 | 73 | 3.8373 | 2.6162
[7 empty] | 4946 | 74 | 3.605 | 2.4475
[7 empty] | 4947 | 75 | 3.5018 | 2.3725
[7 empty] | 4948 | 76 | 3.4416 | 2.3288
[7 empty] | 4949 | 77 | 3.6222 | 2.46
[7 empty] | 4950 | 78 | 4.0351 | 2.7598
[7 empty] | 4951 | 79 | 5.1793 | 3.5907
[7 empty] | 4952 | 80 | 5.3599 | 3.7219
[7 empty] | 4953 | 81 | 6.5729 | 4.6027
[7 empty] | 4954 | 82 | 7.6912 | 5.4148
[7 empty] | 4955 | 83 | 8.4482 | 5.9645
[7 empty] | 4956 | 84 | 9.7214 | 6.889
[7 empty] | 4957 | 85 | 9.4117 | 6.6642
[7 empty] | 4958 | 86 | 8.8869 | 6.2831
[7 empty] | 4959 | 87 | 9.3428 | 6.6142
[7 empty] | 4960 | 88 | 10.0224 | 7.1077
[7 empty] | 4961 | 89 | 11.4074 | 8.1134
[7 empty] | 4962 | 90 | 10.8053 | 7.6762
[7 empty] | 4963 | 91 | 11.5107 | 8.1884
[7 empty] | 4964 | 92 | 10.8913 | 7.7386
[7 empty] | 4965 | 93 | 8.4138 | 5.9395
[7 empty] | 4966 | 94 | 7.4847 | 5.2648
[7 empty] | 4967 | 95 | 5.575 | 3.878
[7 empty] | 4968 | 96 | 4.5599 | 3.1409
[7 empty] | 4969 | 97 | 4.5083 | 3.1034
[7 empty] | 4970 | 98 | 4.2072 | 2.8848
[7 empty] | 4971 | 99 | 4.147 | 2.841
[7 empty] | 4972 | 100 | 3.7857 | 2.5787
[7 empty] | 4973 | 101 | 3.7254 | 2.5349
[7 empty] | 4974 | 102 | 3.9663 | 2.7099
[7 empty] | 4975 | 103 | 4.7319 | 3.2658
[7 empty] | 4976 | 104 | 4.99 | 3.4532
[7 empty] | 4977 | 105 | 5.4889 | 3.8156
[7 empty] | 4978 | 106 | 6.9858 | 4.9025
[7 empty] | 4979 | 107 | 7.3471 | 5.1649
[7 empty] | 4980 | 108 | 8.9643 | 6.3393
[7 empty] | 4981 | 109 | 8.2847 | 5.8458
[7 empty] | 4982 | 110 | 7.8202 | 5.5085
[7 empty] | 4983 | 111 | 7.6568 | 5.3898
[7 empty] | 4984 | 112 | 7.7256 | 5.4398
[7 empty] | 4985 | 113 | 7.3729 | 5.1836
[7 empty] | 4986 | 114 | 7.5449 | 5.3086
[7 empty] | 4987 | 115 | 7.0804 | 4.9712
[7 empty] | 4988 | 116 | 7.7772 | 5.4772
[7 empty] | 4989 | 117 | 7.3471 | 5.1649
[7 empty] | 4990 | 118 | 6.5556 | 4.5902
[7 empty] | 4991 | 119 | 4.9212 | 3.4033
[7 empty] | 4992 | 120 | 4.5954 | 3.1667
[7 empty] | 4993 | 121 | 3.8459 | 2.6224
[7 empty] | 4994 | 122 | 3.4243 | 2.3163
[7 empty] | 4995 | 123 | 3.3383 | 2.2538
[7 empty] | 4996 | 124 | 3.3039 | 2.2289
[7 empty] | 4997 | 125 | 3.2609 | 2.1976
[7 empty] | 4998 | 126 | 3.4071 | 2.3038
[7 empty] | 4999 | 127 | 4.9556 | 3.4283
[7 empty] | 5000 | 128 | 6.5556 | 4.5902
[7 empty] | 5001 | 129 | 7.2524 | 5.0962
[7 empty] | 5002 | 130 | 7.6998 | 5.421
[7 empty] | 5003 | 131 | 7.8632 | 5.5397
[7 empty] | 5004 | 132 | 7.6051 | 5.3523
[7 empty] | 5005 | 133 | 8.2589 | 5.8271
[7 empty] | 5006 | 134 | 8.5686 | 6.052
[7 empty] | 5007 | 135 | 8.6374 | 6.1019
[7 empty] | 5008 | 136 | 7.803 | 5.496
[7 empty] | 5009 | 137 | 7.6998 | 5.421
[7 empty] | 5010 | 138 | 7.6482 | 5.3835
[7 empty] | 5011 | 139 | 7.3041 | 5.1337
[7 empty] | 5012 | 140 | 7.3127 | 5.1399
[7 empty] | 5013 | 141 | 6.6417 | 4.6526
[7 empty] | 5014 | 142 | 5.9879 | 4.1779
[7 empty] | 5015 | 143 | 5.0846 | 3.522
[7 empty] | 5016 | 144 | 4.4566 | 3.0659
[7 empty] | 5017 | 145 | 3.9749 | 2.7161
[7 empty] | 5018 | 146 | 3.7598 | 2.5599
[7 empty] | 5019 | 147 | 3.691 | 2.51
[7 empty] | 5020 | 148 | 3.6824 | 2.5037
[7 empty] | 5021 | 149 | 3.6824 | 2.5037
[7 empty] | 5022 | 150 | 3.691 | 2.51
[7 empty] | 5023 | 151 | 4.8007 | 3.3158
[7 empty] | 5024 | 152 | 6.3664 | 4.4527
[7 empty] | 5025 | 153 | 6.9944 | 4.9088
[7 empty] | 5026 | 154 | 7.5707 | 5.3273
[7 empty] | 5027 | 155 | 7.4159 | 5.2149
[7 empty] | 5028 | 156 | 7.5879 | 5.3398
[7 empty] | 5029 | 157 | 8.3192 | 5.8708
[7 empty] | 5030 | 158 | 8.6546 | 6.1144
[7 empty] | 5031 | 159 | 8.9299 | 6.3143
[7 empty] | 5032 | 160 | 8.8009 | 6.2206
[7 empty] | 5033 | 161 | 9.5837 | 6.7891
[7 empty] | 5034 | 162 | 9.0762 | 6.4205
[7 empty] | 5035 | 163 | 9.4461 | 6.6891
[7 empty] | 5036 | 164 | 8.0611 | 5.6834
[7 empty] | 5037 | 165 | 11.2698 | 8.0135
[7 empty] | 5038 | 166 | 9.1708 | 6.4892
[7 empty] | 5039 | 167 | 5.4717 | 3.8031
[7 empty] | 5040 | 168 | 4.8093 | 3.3221
[7 empty] | 5041 | 1 | 3.3125 | 2.2351
[7 empty] | 5042 | 2 | 3.2007 | 2.1539
[7 empty] | 5043 | 3 | 3.1921 | 2.1476
[7 empty] | 5044 | 4 | 3.3297 | 2.2476
[7 empty] | 5045 | 5 | 3.3469 | 2.2601
[7 empty] | 5046 | 6 | 3.7857 | 2.5787
[7 empty] | 5047 | 7 | 4.5255 | 3.1159
[7 empty] | 5048 | 8 | 5.2137 | 3.6157
[7 empty] | 5049 | 9 | 5.1879 | 3.5969
[7 empty] | 5050 | 10 | 6.7449 | 4.7276
[7 empty] | 5051 | 11 | 8.8783 | 6.2768
[7 empty] | 5052 | 12 | 9.8676 | 6.9952
[7 empty] | 5053 | 13 | 10.2547 | 7.2763
[7 empty] | 5054 | 14 | 10.031 | 7.1139
[7 empty] | 5055 | 15 | 9.9364 | 7.0452
[7 empty] | 5056 | 16 | 11.1494 | 7.926
[7 empty] | 5057 | 17 | 12.5086 | 8.913
[7 empty] | 5058 | 18 | 12.2591 | 8.7319
[7 empty] | 5059 | 19 | 12.801 | 9.1254
[7 empty] | 5060 | 20 | 12.7322 | 9.0755
[7 empty] | 5061 | 21 | 13.3172 | 9.5002
[7 empty] | 5062 | 22 | 9.2568 | 6.5517
[7 empty] | 5063 | 23 | 5.3857 | 3.7406
[7 empty] | 5064 | 24 | 3.6704 | 2.495
[7 empty] | 5065 | 25 | 3.5706 | 2.4225
[7 empty] | 5066 | 26 | 3.4588 | 2.3413
[7 empty] | 5067 | 27 | 3.3555 | 2.2663
[7 empty] | 5068 | 28 | 3.4416 | 2.3288
[7 empty] | 5069 | 29 | 3.691 | 2.51
[7 empty] | 5070 | 30 | 3.9405 | 2.6911
[7 empty] | 5071 | 31 | 4.8093 | 3.3221
[7 empty] | 5072 | 32 | 5.1706 | 3.5844
[7 empty] | 5073 | 33 | 5.8502 | 4.0779
[7 empty] | 5074 | 34 | 6.7707 | 4.7464
[7 empty] | 5075 | 35 | 8.9987 | 6.3643
[7 empty] | 5076 | 36 | 10.0569 | 7.1327
[7 empty] | 5077 | 37 | 10.1343 | 7.1889
[7 empty] | 5078 | 38 | 10.2117 | 7.2451
[7 empty] | 5079 | 39 | 9.8762 | 7.0015
[7 empty] | 5080 | 40 | 10.9601 | 7.7886
[7 empty] | 5081 | 41 | 11.5279 | 8.2009
[7 empty] | 5082 | 42 | 11.5451 | 8.2134
[7 empty] | 5083 | 43 | 11.9236 | 8.4882
[7 empty] | 5084 | 44 | 13.1107 | 9.3503
[7 empty] | 5085 | 45 | 12.6978 | 9.0505
[7 empty] | 5086 | 46 | 9.8762 | 7.0015
[7 empty] | 5087 | 47 | 6.1771 | 4.3153
[7 empty] | 5088 | 48 | 4.6373 | 3.1971
[7 empty] | 5089 | 49 | 3.9577 | 2.7036
[7 empty] | 5090 | 50 | 3.6394 | 2.4725
[7 empty] | 5091 | 51 | 3.5276 | 2.3913
[7 empty] | 5092 | 52 | 3.562 | 2.4163
[7 empty] | 5093 | 53 | 3.5878 | 2.435
[7 empty] | 5094 | 54 | 4.1814 | 2.866
[7 empty] | 5095 | 55 | 5.3513 | 3.7156
[7 empty] | 5096 | 56 | 5.6008 | 3.8968
[7 empty] | 5097 | 57 | 6.5729 | 4.6027
[7 empty] | 5098 | 58 | 7.7084 | 5.4273
[7 empty] | 5099 | 59 | 8.9471 | 6.3268
[7 empty] | 5100 | 60 | 9.5923 | 6.7953
[7 empty] | 5101 | 61 | 10.2891 | 7.3013
[7 empty] | 5102 | 62 | 10.0827 | 7.1514
[7 empty] | 5103 | 63 | 10.6934 | 7.5949
[7 empty] | 5104 | 64 | 11.6655 | 8.3008
[7 empty] | 5105 | 65 | 12.3021 | 8.7631
[7 empty] | 5106 | 66 | 12.1989 | 8.6882
[7 empty] | 5107 | 67 | 12.9559 | 9.2379
[7 empty] | 5108 | 68 | 13.2054 | 9.419
[7 empty] | 5109 | 69 | 12.6806 | 9.038
[7 empty] | 5110 | 70 | 10.3235 | 7.3263
[7 empty] | 5111 | 71 | 5.6868 | 3.9592
[7 empty] | 5112 | 72 | 4.5734 | 3.1507
[7 empty] | 5113 | 73 | 3.8373 | 2.6162
[7 empty] | 5114 | 74 | 3.605 | 2.4475
[7 empty] | 5115 | 75 | 3.5018 | 2.3725
[7 empty] | 5116 | 76 | 3.4416 | 2.3288
[7 empty] | 5117 | 77 | 3.6222 | 2.46
[7 empty] | 5118 | 78 | 4.0351 | 2.7598
[7 empty] | 5119 | 79 | 5.1793 | 3.5907
[7 empty] | 5120 | 80 | 5.3599 | 3.7219
[7 empty] | 5121 | 81 | 6.5729 | 4.6027
[7 empty] | 5122 | 82 | 7.6912 | 5.4148
[7 empty] | 5123 | 83 | 8.4482 | 5.9645
[7 empty] | 5124 | 84 | 9.7214 | 6.889
[7 empty] | 5125 | 85 | 9.4117 | 6.6642
[7 empty] | 5126 | 86 | 8.8869 | 6.2831
[7 empty] | 5127 | 87 | 9.3428 | 6.6142
[7 empty] | 5128 | 88 | 10.0224 | 7.1077
[7 empty] | 5129 | 89 | 11.4074 | 8.1134
[7 empty] | 5130 | 90 | 10.8053 | 7.6762
[7 empty] | 5131 | 91 | 11.5107 | 8.1884
[7 empty] | 5132 | 92 | 10.8913 | 7.7386
[7 empty] | 5133 | 93 | 8.4138 | 5.9395
[7 empty] | 5134 | 94 | 7.4847 | 5.2648
[7 empty] | 5135 | 95 | 5.575 | 3.878
[7 empty] | 5136 | 96 | 4.5599 | 3.1409
[7 empty] | 5137 | 97 | 4.5083 | 3.1034
[7 empty] | 5138 | 98 | 4.2072 | 2.8848
[7 empty] | 5139 | 99 | 4.147 | 2.841
[7 empty] | 5140 | 100 | 3.7857 | 2.5787
[7 empty] | 5141 | 101 | 3.7254 | 2.5349
[7 empty] | 5142 | 102 | 3.9663 | 2.7099
[7 empty] | 5143 | 103 | 4.7319 | 3.2658
[7 empty] | 5144 | 104 | 4.99 | 3.4532
[7 empty] | 5145 | 105 | 5.4889 | 3.8156
[7 empty] | 5146 | 106 | 6.9858 | 4.9025
[7 empty] | 5147 | 107 | 7.3471 | 5.1649
[7 empty] | 5148 | 108 | 8.9643 | 6.3393
[7 empty] | 5149 | 109 | 8.2847 | 5.8458
[7 empty] | 5150 | 110 | 7.8202 | 5.5085
[7 empty] | 5151 | 111 | 7.6568 | 5.3898
[7 empty] | 5152 | 112 | 7.7256 | 5.4398
[7 empty] | 5153 | 113 | 7.3729 | 5.1836
[7 empty] | 5154 | 114 | 7.5449 | 5.3086
[7 empty] | 5155 | 115 | 7.0804 | 4.9712
[7 empty] | 5156 | 116 | 7.7772 | 5.4772
[7 empty] | 5157 | 117 | 7.3471 | 5.1649
[7 empty] | 5158 | 118 | 6.5556 | 4.5902
[7 empty] | 5159 | 119 | 4.9212 | 3.4033
[7 empty] | 5160 | 120 | 4.5954 | 3.1667
[7 empty] | 5161 | 121 | 3.8459 | 2.6224
[7 empty] | 5162 | 122 | 3.4243 | 2.3163
[7 empty] | 5163 | 123 | 3.3383 | 2.2538
[7 empty] | 5164 | 124 | 3.3039 | 2.2289
[7 empty] | 5165 | 125 | 3.2609 | 2.1976
[7 empty] | 5166 | 126 | 3.4071 | 2.3038
[7 empty] | 5167 | 127 | 4.9556 | 3.4283
[7 empty] | 5168 | 128 | 6.5556 | 4.5902
[7 empty] | 5169 | 129 | 7.2524 | 5.0962
[7 empty] | 5170 | 130 | 7.6998 | 5.421
[7 empty] | 5171 | 131 | 7.8632 | 5.5397
[7 empty] | 5172 | 132 | 7.6051 | 5.3523
[7 empty] | 5173 | 133 | 8.2589 | 5.8271
[7 empty] | 5174 | 134 | 8.5686 | 6.052
[7 empty] | 5175 | 135 | 8.6374 | 6.1019
[7 empty] | 5176 | 136 | 7.803 | 5.496
[7 empty] | 5177 | 137 | 7.6998 | 5.421
[7 empty] | 5178 | 138 | 7.6482 | 5.3835
[7 empty] | 5179 | 139 | 7.3041 | 5.1337
[7 empty] | 5180 | 140 | 7.3127 | 5.1399
[7 empty] | 5181 | 141 | 6.6417 | 4.6526
[7 empty] | 5182 | 142 | 5.9879 | 4.1779
[7 empty] | 5183 | 143 | 5.0846 | 3.522
[7 empty] | 5184 | 144 | 4.4566 | 3.0659
[7 empty] | 5185 | 145 | 3.9749 | 2.7161
[7 empty] | 5186 | 146 | 3.7598 | 2.5599
[7 empty] | 5187 | 147 | 3.691 | 2.51
[7 empty] | 5188 | 148 | 3.6824 | 2.5037
[7 empty] | 5189 | 149 | 3.6824 | 2.5037
[7 empty] | 5190 | 150 | 3.691 | 2.51
[7 empty] | 5191 | 151 | 4.8007 | 3.3158
[7 empty] | 5192 | 152 | 6.3664 | 4.4527
[7 empty] | 5193 | 153 | 6.9944 | 4.9088
[7 empty] | 5194 | 154 | 7.5707 | 5.3273
[7 empty] | 5195 | 155 | 7.4159 | 5.2149
[7 empty] | 5196 | 156 | 7.5879 | 5.3398
[7 empty] | 5197 | 157 | 8.3192 | 5.8708
[7 empty] | 5198 | 158 | 8.6546 | 6.1144
[7 empty] | 5199 | 159 | 8.9299 | 6.3143
[7 empty] | 5200 | 160 | 8.8009 | 6.2206
[7 empty] | 5201 | 161 | 9.5837 | 6.7891
[7 empty] | 5202 | 162 | 9.0762 | 6.4205
[7 empty] | 5203 | 163 | 9.4461 | 6.6891
[7 empty] | 5204 | 164 | 8.0611 | 5.6834
[7 empty] | 5205 | 165 | 11.2698 | 8.0135
[7 empty] | 5206 | 166 | 9.1708 | 6.4892
[7 empty] | 5207 | 167 | 5.4717 | 3.8031
[7 empty] | 5208 | 168 | 4.8093 | 3.3221
[7 empty] | 5209 | 1 | 3.3125 | 2.2351
[7 empty] | 5210 | 2 | 3.2007 | 2.1539
[7 empty] | 5211 | 3 | 3.1921 | 2.1476
[7 empty] | 5212 | 4 | 3.3297 | 2.2476
[7 empty] | 5213 | 5 | 3.3469 | 2.2601
[7 empty] | 5214 | 6 | 3.7857 | 2.5787
[7 empty] | 5215 | 7 | 4.5255 | 3.1159
[7 empty] | 5216 | 8 | 5.2137 | 3.6157
[7 empty] | 5217 | 9 | 5.1879 | 3.5969
[7 empty] | 5218 | 10 | 6.7449 | 4.7276
[7 empty] | 5219 | 11 | 8.8783 | 6.2768
[7 empty] | 5220 | 12 | 9.8676 | 6.9952
[7 empty] | 5221 | 13 | 10.2547 | 7.2763
[7 empty] | 5222 | 14 | 10.031 | 7.1139
[7 empty] | 5223 | 15 | 9.9364 | 7.0452
[7 empty] | 5224 | 16 | 11.1494 | 7.926
[7 empty] | 5225 | 17 | 12.5086 | 8.913
[7 empty] | 5226 | 18 | 12.2591 | 8.7319
[7 empty] | 5227 | 19 | 12.801 | 9.1254
[7 empty] | 5228 | 20 | 12.7322 | 9.0755
[7 empty] | 5229 | 21 | 13.3172 | 9.5002
[7 empty] | 5230 | 22 | 9.2568 | 6.5517
[7 empty] | 5231 | 23 | 5.3857 | 3.7406
[7 empty] | 5232 | 24 | 3.6704 | 2.495
[7 empty] | 5233 | 25 | 3.5706 | 2.4225
[7 empty] | 5234 | 26 | 3.4588 | 2.3413
[7 empty] | 5235 | 27 | 3.3555 | 2.2663
[7 empty] | 5236 | 28 | 3.4416 | 2.3288
[7 empty] | 5237 | 29 | 3.691 | 2.51
[7 empty] | 5238 | 30 | 3.9405 | 2.6911
[7 empty] | 5239 | 31 | 4.8093 | 3.3221
[7 empty] | 5240 | 32 | 5.1706 | 3.5844
[7 empty] | 5241 | 33 | 5.8502 | 4.0779
[7 empty] | 5242 | 34 | 6.7707 | 4.7464
[7 empty] | 5243 | 35 | 8.9987 | 6.3643
[7 empty] | 5244 | 36 | 10.0569 | 7.1327
[7 empty] | 5245 | 37 | 10.1343 | 7.1889
[7 empty] | 5246 | 38 | 10.2117 | 7.2451
[7 empty] | 5247 | 39 | 9.8762 | 7.0015
[7 empty] | 5248 | 40 | 10.9601 | 7.7886
[7 empty] | 5249 | 41 | 11.5279 | 8.2009
[7 empty] | 5250 | 42 | 11.5451 | 8.2134
[7 empty] | 5251 | 43 | 11.9236 | 8.4882
[7 empty] | 5252 | 44 | 13.1107 | 9.3503
[7 empty] | 5253 | 45 | 12.6978 | 9.0505
[7 empty] | 5254 | 46 | 9.8762 | 7.0015
[7 empty] | 5255 | 47 | 6.1771 | 4.3153
[7 empty] | 5256 | 48 | 4.6373 | 3.1971
[7 empty] | 5257 | 49 | 3.9577 | 2.7036
[7 empty] | 5258 | 50 | 3.6394 | 2.4725
[7 empty] | 5259 | 51 | 3.5276 | 2.3913
[7 empty] | 5260 | 52 | 3.562 | 2.4163
[7 empty] | 5261 | 53 | 3.5878 | 2.435
[7 empty] | 5262 | 54 | 4.1814 | 2.866
[7 empty] | 5263 | 55 | 5.3513 | 3.7156
[7 empty] | 5264 | 56 | 5.6008 | 3.8968
[7 empty] | 5265 | 57 | 6.5729 | 4.6027
[7 empty] | 5266 | 58 | 7.7084 | 5.4273
[7 empty] | 5267 | 59 | 8.9471 | 6.3268
[7 empty] | 5268 | 60 | 9.5923 | 6.7953
[7 empty] | 5269 | 61 | 10.2891 | 7.3013
[7 empty] | 5270 | 62 | 10.0827 | 7.1514
[7 empty] | 5271 | 63 | 10.6934 | 7.5949
[7 empty] | 5272 | 64 | 11.6655 | 8.3008
[7 empty] | 5273 | 65 | 12.3021 | 8.7631
[7 empty] | 5274 | 66 | 12.1989 | 8.6882
[7 empty] | 5275 | 67 | 12.9559 | 9.2379
[7 empty] | 5276 | 68 | 13.2054 | 9.419
[7 empty] | 5277 | 69 | 12.6806 | 9.038
[7 empty] | 5278 | 70 | 10.3235 | 7.3263
[7 empty] | 5279 | 71 | 5.6868 | 3.9592
[7 empty] | 5280 | 72 | 4.5734 | 3.1507
[7 empty] | 5281 | 73 | 3.8373 | 2.6162
[7 empty] | 5282 | 74 | 3.605 | 2.4475
[7 empty] | 5283 | 75 | 3.5018 | 2.3725
[7 empty] | 5284 | 76 | 3.4416 | 2.3288
[7 empty] | 5285 | 77 | 3.6222 | 2.46
[7 empty] | 5286 | 78 | 4.0351 | 2.7598
[7 empty] | 5287 | 79 | 5.1793 | 3.5907
[7 empty] | 5288 | 80 | 5.3599 | 3.7219
[7 empty] | 5289 | 81 | 6.5729 | 4.6027
[7 empty] | 5290 | 82 | 7.6912 | 5.4148
[7 empty] | 5291 | 83 | 8.4482 | 5.9645
[7 empty] | 5292 | 84 | 9.7214 | 6.889
[7 empty] | 5293 | 85 | 9.4117 | 6.6642
[7 empty] | 5294 | 86 | 8.8869 | 6.2831
[7 empty] | 5295 | 87 | 9.3428 | 6.6142
[7 empty] | 5296 | 88 | 10.0224 | 7.1077
[7 empty] | 5297 | 89 | 11.4074 | 8.1134
[7 empty] | 5298 | 90 | 10.8053 | 7.6762
[7 empty] | 5299 | 91 | 11.5107 | 8.1884
[7 empty] | 5300 | 92 | 10.8913 | 7.7386
[7 empty] | 5301 | 93 | 8.4138 | 5.9395
[7 empty] | 5302 | 94 | 7.4847 | 5.2648
[7 empty] | 5303 | 95 | 5.575 | 3.878
[7 empty] | 5304 | 96 | 4.5599 | 3.1409
[7 empty] | 5305 | 97 | 4.5083 | 3.1034
[7 empty] | 5306 | 98 | 4.2072 | 2.8848
[7 empty] | 5307 | 99 | 4.147 | 2.841
[7 empty] | 5308 | 100 | 3.7857 | 2.5787
[7 empty] | 5309 | 101 | 3.7254 | 2.5349
[7 empty] | 5310 | 102 | 3.9663 | 2.7099
[7 empty] | 5311 | 103 | 4.7319 | 3.2658
[7 empty] | 5312 | 104 | 4.99 | 3.4532
[7 empty] | 5313 | 105 | 5.4889 | 3.8156
[7 empty] | 5314 | 106 | 6.9858 | 4.9025
[7 empty] | 5315 | 107 | 7.3471 | 5.1649
[7 empty] | 5316 | 108 | 8.9643 | 6.3393
[7 empty] | 5317 | 109 | 8.2847 | 5.8458
[7 empty] | 5318 | 110 | 7.8202 | 5.5085
[7 empty] | 5319 | 111 | 7.6568 | 5.3898
[7 empty] | 5320 | 112 | 7.7256 | 5.4398
[7 empty] | 5321 | 113 | 7.3729 | 5.1836
[7 empty] | 5322 | 114 | 7.5449 | 5.3086
[7 empty] | 5323 | 115 | 7.0804 | 4.9712
[7 empty] | 5324 | 116 | 7.7772 | 5.4772
[7 empty] | 5325 | 117 | 7.3471 | 5.1649
[7 empty] | 5326 | 118 | 6.5556 | 4.5902
[7 empty] | 5327 | 119 | 4.9212 | 3.4033
[7 empty] | 5328 | 120 | 4.5954 | 3.1667
[7 empty] | 5329 | 121 | 3.8459 | 2.6224
[7 empty] | 5330 | 122 | 3.4243 | 2.3163
[7 empty] | 5331 | 123 | 3.3383 | 2.2538
[7 empty] | 5332 | 124 | 3.3039 | 2.2289
[7 empty] | 5333 | 125 | 3.2609 | 2.1976
[7 empty] | 5334 | 126 | 3.4071 | 2.3038
[7 empty] | 5335 | 127 | 4.9556 | 3.4283
[7 empty] | 5336 | 128 | 6.5556 | 4.5902
[7 empty] | 5337 | 129 | 7.2524 | 5.0962
[7 empty] | 5338 | 130 | 7.6998 | 5.421
[7 empty] | 5339 | 131 | 7.8632 | 5.5397
[7 empty] | 5340 | 132 | 7.6051 | 5.3523
[7 empty] | 5341 | 133 | 8.2589 | 5.8271
[7 empty] | 5342 | 134 | 8.5686 | 6.052
[7 empty] | 5343 | 135 | 8.6374 | 6.1019
[7 empty] | 5344 | 136 | 7.803 | 5.496
[7 empty] | 5345 | 137 | 7.6998 | 5.421
[7 empty] | 5346 | 138 | 7.6482 | 5.3835
[7 empty] | 5347 | 139 | 7.3041 | 5.1337
[7 empty] | 5348 | 140 | 7.3127 | 5.1399
[7 empty] | 5349 | 141 | 6.6417 | 4.6526
[7 empty] | 5350 | 142 | 5.9879 | 4.1779
[7 empty] | 5351 | 143 | 5.0846 | 3.522
[7 empty] | 5352 | 144 | 4.4566 | 3.0659
[7 empty] | 5353 | 145 | 3.9749 | 2.7161
[7 empty] | 5354 | 146 | 3.7598 | 2.5599
[7 empty] | 5355 | 147 | 3.691 | 2.51
[7 empty] | 5356 | 148 | 3.6824 | 2.5037
[7 empty] | 5357 | 149 | 3.6824 | 2.5037
[7 empty] | 5358 | 150 | 3.691 | 2.51
[7 empty] | 5359 | 151 | 4.8007 | 3.3158
[7 empty] | 5360 | 152 | 6.3664 | 4.4527
[7 empty] | 5361 | 153 | 6.9944 | 4.9088
[7 empty] | 5362 | 154 | 7.5707 | 5.3273
[7 empty] | 5363 | 155 | 7.4159 | 5.2149
[7 empty] | 5364 | 156 | 7.5879 | 5.3398
[7 empty] | 5365 | 157 | 8.3192 | 5.8708
[7 empty] | 5366 | 158 | 8.6546 | 6.1144
[7 empty] | 5367 | 159 | 8.9299 | 6.3143
[7 empty] | 5368 | 160 | 8.8009 | 6.2206
[7 empty] | 5369 | 161 | 9.5837 | 6.7891
[7 empty] | 5370 | 162 | 9.0762 | 6.4205
[7 empty] | 5371 | 163 | 9.4461 | 6.6891
[7 empty] | 5372 | 164 | 8.0611 | 5.6834
[7 empty] | 5373 | 165 | 11.2698 | 8.0135
[7 empty] | 5374 | 166 | 9.1708 | 6.4892
[7 empty] | 5375 | 167 | 5.4717 | 3.8031
[7 empty] | 5376 | 168 | 4.8093 | 3.3221
[7 empty] | 5377 | 1 | 3.3125 | 2.2351
[7 empty] | 5378 | 2 | 3.2007 | 2.1539
[7 empty] | 5379 | 3 | 3.1921 | 2.1476
[7 empty] | 5380 | 4 | 3.3297 | 2.2476
[7 empty] | 5381 | 5 | 3.3469 | 2.2601
[7 empty] | 5382 | 6 | 3.7857 | 2.5787
[7 empty] | 5383 | 7 | 4.5255 | 3.1159
[7 empty] | 5384 | 8 | 5.2137 | 3.6157
[7 empty] | 5385 | 9 | 5.1879 | 3.5969
[7 empty] | 5386 | 10 | 6.7449 | 4.7276
[7 empty] | 5387 | 11 | 8.8783 | 6.2768
[7 empty] | 5388 | 12 | 9.8676 | 6.9952
[7 empty] | 5389 | 13 | 10.2547 | 7.2763
[7 empty] | 5390 | 14 | 10.031 | 7.1139
[7 empty] | 5391 | 15 | 9.9364 | 7.0452
[7 empty] | 5392 | 16 | 11.1494 | 7.926
[7 empty] | 5393 | 17 | 12.5086 | 8.913
[7 empty] | 5394 | 18 | 12.2591 | 8.7319
[7 empty] | 5395 | 19 | 12.801 | 9.1254
[7 empty] | 5396 | 20 | 12.7322 | 9.0755
[7 empty] | 5397 | 21 | 13.3172 | 9.5002
[7 empty] | 5398 | 22 | 9.2568 | 6.5517
[7 empty] | 5399 | 23 | 5.3857 | 3.7406
[7 empty] | 5400 | 24 | 3.6704 | 2.495
[7 empty] | 5401 | 25 | 3.5706 | 2.4225
[7 empty] | 5402 | 26 | 3.4588 | 2.3413
[7 empty] | 5403 | 27 | 3.3555 | 2.2663
[7 empty] | 5404 | 28 | 3.4416 | 2.3288
[7 empty] | 5405 | 29 | 3.691 | 2.51
[7 empty] | 5406 | 30 | 3.9405 | 2.6911
[7 empty] | 5407 | 31 | 4.8093 | 3.3221
[7 empty] | 5408 | 32 | 5.1706 | 3.5844
[7 empty] | 5409 | 33 | 5.8502 | 4.0779
[7 empty] | 5410 | 34 | 6.7707 | 4.7464
[7 empty] | 5411 | 35 | 8.9987 | 6.3643
[7 empty] | 5412 | 36 | 10.0569 | 7.1327
[7 empty] | 5413 | 37 | 10.1343 | 7.1889
[7 empty] | 5414 | 38 | 10.2117 | 7.2451
[7 empty] | 5415 | 39 | 9.8762 | 7.0015
[7 empty] | 5416 | 40 | 10.9601 | 7.7886
[7 empty] | 5417 | 41 | 11.5279 | 8.2009
[7 empty] | 5418 | 42 | 11.5451 | 8.2134
[7 empty] | 5419 | 43 | 11.9236 | 8.4882
[7 empty] | 5420 | 44 | 13.1107 | 9.3503
[7 empty] | 5421 | 45 | 12.6978 | 9.0505
[7 empty] | 5422 | 46 | 9.8762 | 7.0015
[7 empty] | 5423 | 47 | 6.1771 | 4.3153
[7 empty] | 5424 | 48 | 4.6373 | 3.1971
[7 empty] | 5425 | 49 | 3.9577 | 2.7036
[7 empty] | 5426 | 50 | 3.6394 | 2.4725
[7 empty] | 5427 | 51 | 3.5276 | 2.3913
[7 empty] | 5428 | 52 | 3.562 | 2.4163
[7 empty] | 5429 | 53 | 3.5878 | 2.435
[7 empty] | 5430 | 54 | 4.1814 | 2.866
[7 empty] | 5431 | 55 | 5.3513 | 3.7156
[7 empty] | 5432 | 56 | 5.6008 | 3.8968
[7 empty] | 5433 | 57 | 6.5729 | 4.6027
[7 empty] | 5434 | 58 | 7.7084 | 5.4273
[7 empty] | 5435 | 59 | 8.9471 | 6.3268
[7 empty] | 5436 | 60 | 9.5923 | 6.7953
[7 empty] | 5437 | 61 | 10.2891 | 7.3013
[7 empty] | 5438 | 62 | 10.0827 | 7.1514
[7 empty] | 5439 | 63 | 10.6934 | 7.5949
[7 empty] | 5440 | 64 | 11.6655 | 8.3008
[7 empty] | 5441 | 65 | 12.3021 | 8.7631
[7 empty] | 5442 | 66 | 12.1989 | 8.6882
[7 empty] | 5443 | 67 | 12.9559 | 9.2379
[7 empty] | 5444 | 68 | 13.2054 | 9.419
[7 empty] | 5445 | 69 | 12.6806 | 9.038
[7 empty] | 5446 | 70 | 10.3235 | 7.3263
[7 empty] | 5447 | 71 | 5.6868 | 3.9592
[7 empty] | 5448 | 72 | 4.5734 | 3.1507
[7 empty] | 5449 | 73 | 3.8373 | 2.6162
[7 empty] | 5450 | 74 | 3.605 | 2.4475
[7 empty] | 5451 | 75 | 3.5018 | 2.3725
[7 empty] | 5452 | 76 | 3.4416 | 2.3288
[7 empty] | 5453 | 77 | 3.6222 | 2.46
[7 empty] | 5454 | 78 | 4.0351 | 2.7598
[7 empty] | 5455 | 79 | 5.1793 | 3.5907
[7 empty] | 5456 | 80 | 5.3599 | 3.7219
[7 empty] | 5457 | 81 | 6.5729 | 4.6027
[7 empty] | 5458 | 82 | 7.6912 | 5.4148
[7 empty] | 5459 | 83 | 8.4482 | 5.9645
[7 empty] | 5460 | 84 | 9.7214 | 6.889
[7 empty] | 5461 | 85 | 9.4117 | 6.6642
[7 empty] | 5462 | 86 | 8.8869 | 6.2831
[7 empty] | 5463 | 87 | 9.3428 | 6.6142
[7 empty] | 5464 | 88 | 10.0224 | 7.1077
[7 empty] | 5465 | 89 | 11.4074 | 8.1134
[7 empty] | 5466 | 90 | 10.8053 | 7.6762
[7 empty] | 5467 | 91 | 11.5107 | 8.1884
[7 empty] | 5468 | 92 | 10.8913 | 7.7386
[7 empty] | 5469 | 93 | 8.4138 | 5.9395
[7 empty] | 5470 | 94 | 7.4847 | 5.2648
[7 empty] | 5471 | 95 | 5.575 | 3.878
[7 empty] | 5472 | 96 | 4.5599 | 3.1409
[7 empty] | 5473 | 97 | 4.5083 | 3.1034
[7 empty] | 5474 | 98 | 4.2072 | 2.8848
[7 empty] | 5475 | 99 | 4.147 | 2.841
[7 empty] | 5476 | 100 | 3.7857 | 2.5787
[7 empty] | 5477 | 101 | 3.7254 | 2.5349
[7 empty] | 5478 | 102 | 3.9663 | 2.7099
[7 empty] | 5479 | 103 | 4.7319 | 3.2658
[7 empty] | 5480 | 104 | 4.99 | 3.4532
[7 empty] | 5481 | 105 | 5.4889 | 3.8156
[7 empty] | 5482 | 106 | 6.9858 | 4.9025
[7 empty] | 5483 | 107 | 7.3471 | 5.1649
[7 empty] | 5484 | 108 | 8.9643 | 6.3393
[7 empty] | 5485 | 109 | 8.2847 | 5.8458
[7 empty] | 5486 | 110 | 7.8202 | 5.5085
[7 empty] | 5487 | 111 | 7.6568 | 5.3898
[7 empty] | 5488 | 112 | 7.7256 | 5.4398
[7 empty] | 5489 | 113 | 7.3729 | 5.1836
[7 empty] | 5490 | 114 | 7.5449 | 5.3086
[7 empty] | 5491 | 115 | 7.0804 | 4.9712
[7 empty] | 5492 | 116 | 7.7772 | 5.4772
[7 empty] | 5493 | 117 | 7.3471 | 5.1649
[7 empty] | 5494 | 118 | 6.5556 | 4.5902
[7 empty] | 5495 | 119 | 4.9212 | 3.4033
[7 empty] | 5496 | 120 | 4.5954 | 3.1667
[7 empty] | 5497 | 121 | 3.8459 | 2.6224
[7 empty] | 5498 | 122 | 3.4243 | 2.3163
[7 empty] | 5499 | 123 | 3.3383 | 2.2538
[7 empty] | 5500 | 124 | 3.3039 | 2.2289
[7 empty] | 5501 | 125 | 3.2609 | 2.1976
[7 empty] | 5502 | 126 | 3.4071 | 2.3038
[7 empty] | 5503 | 127 | 4.9556 | 3.4283
[7 empty] | 5504 | 128 | 6.5556 | 4.5902
[7 empty] | 5505 | 129 | 7.2524 | 5.0962
[7 empty] | 5506 | 130 | 7.6998 | 5.421
[7 empty] | 5507 | 131 | 7.8632 | 5.5397
[7 empty] | 5508 | 132 | 7.6051 | 5.3523
[7 empty] | 5509 | 133 | 8.2589 | 5.8271
[7 empty] | 5510 | 134 | 8.5686 | 6.052
[7 empty] | 5511 | 135 | 8.6374 | 6.1019
[7 empty] | 5512 | 136 | 7.803 | 5.496
[7 empty] | 5513 | 137 | 7.6998 | 5.421
[7 empty] | 5514 | 138 | 7.6482 | 5.3835
[7 empty] | 5515 | 139 | 7.3041 | 5.1337
[7 empty] | 5516 | 140 | 7.3127 | 5.1399
[7 empty] | 5517 | 141 | 6.6417 | 4.6526
[7 empty] | 5518 | 142 | 5.9879 | 4.1779
[7 empty] | 5519 | 143 | 5.0846 | 3.522
[7 empty] | 5520 | 144 | 4.4566 | 3.0659
[7 empty] | 5521 | 145 | 3.9749 | 2.7161
[7 empty] | 5522 | 146 | 3.7598 | 2.5599
[7 empty] | 5523 | 147 | 3.691 | 2.51
[7 empty] | 5524 | 148 | 3.6824 | 2.5037
[7 empty] | 5525 | 149 | 3.6824 | 2.5037
[7 empty] | 5526 | 150 | 3.691 | 2.51
[7 empty] | 5527 | 151 | 4.8007 | 3.3158
[7 empty] | 5528 | 152 | 6.3664 | 4.4527
[7 empty] | 5529 | 153 | 6.9944 | 4.9088
[7 empty] | 5530 | 154 | 7.5707 | 5.3273
[7 empty] | 5531 | 155 | 7.4159 | 5.2149
[7 empty] | 5532 | 156 | 7.5879 | 5.3398
[7 empty] | 5533 | 157 | 8.3192 | 5.8708
[7 empty] | 5534 | 158 | 8.6546 | 6.1144
[7 empty] | 5535 | 159 | 8.9299 | 6.3143
[7 empty] | 5536 | 160 | 8.8009 | 6.2206
[7 empty] | 5537 | 161 | 9.5837 | 6.7891
[7 empty] | 5538 | 162 | 9.0762 | 6.4205
[7 empty] | 5539 | 163 | 9.4461 | 6.6891
[7 empty] | 5540 | 164 | 8.0611 | 5.6834
[7 empty] | 5541 | 165 | 11.2698 | 8.0135
[7 empty] | 5542 | 166 | 9.1708 | 6.4892
[7 empty] | 5543 | 167 | 5.4717 | 3.8031
[7 empty] | 5544 | 168 | 4.8093 | 3.3221
[7 empty] | 5545 | 1 | 3.3125 | 2.2351
[7 empty] | 5546 | 2 | 3.2007 | 2.1539
[7 empty] | 5547 | 3 | 3.1921 | 2.1476
[7 empty] | 5548 | 4 | 3.3297 | 2.2476
[7 empty] | 5549 | 5 | 3.3469 | 2.2601
[7 empty] | 5550 | 6 | 3.7857 | 2.5787
[7 empty] | 5551 | 7 | 4.5255 | 3.1159
[7 empty] | 5552 | 8 | 5.2137 | 3.6157
[7 empty] | 5553 | 9 | 5.1879 | 3.5969
[7 empty] | 5554 | 10 | 6.7449 | 4.7276
[7 empty] | 5555 | 11 | 8.8783 | 6.2768
[7 empty] | 5556 | 12 | 9.8676 | 6.9952
[7 empty] | 5557 | 13 | 10.2547 | 7.2763
[7 empty] | 5558 | 14 | 10.031 | 7.1139
[7 empty] | 5559 | 15 | 9.9364 | 7.0452
[7 empty] | 5560 | 16 | 11.1494 | 7.926
[7 empty] | 5561 | 17 | 12.5086 | 8.913
[7 empty] | 5562 | 18 | 12.2591 | 8.7319
[7 empty] | 5563 | 19 | 12.801 | 9.1254
[7 empty] | 5564 | 20 | 12.7322 | 9.0755
[7 empty] | 5565 | 21 | 13.3172 | 9.5002
[7 empty] | 5566 | 22 | 9.2568 | 6.5517
[7 empty] | 5567 | 23 | 5.3857 | 3.7406
[7 empty] | 5568 | 24 | 3.6704 | 2.495
[7 empty] | 5569 | 25 | 3.5706 | 2.4225
[7 empty] | 5570 | 26 | 3.4588 | 2.3413
[7 empty] | 5571 | 27 | 3.3555 | 2.2663
[7 empty] | 5572 | 28 | 3.4416 | 2.3288
[7 empty] | 5573 | 29 | 3.691 | 2.51
[7 empty] | 5574 | 30 | 3.9405 | 2.6911
[7 empty] | 5575 | 31 | 4.8093 | 3.3221
[7 empty] | 5576 | 32 | 5.1706 | 3.5844
[7 empty] | 5577 | 33 | 5.8502 | 4.0779
[7 empty] | 5578 | 34 | 6.7707 | 4.7464
[7 empty] | 5579 | 35 | 8.9987 | 6.3643
[7 empty] | 5580 | 36 | 10.0569 | 7.1327
[7 empty] | 5581 | 37 | 10.1343 | 7.1889
[7 empty] | 5582 | 38 | 10.2117 | 7.2451
[7 empty] | 5583 | 39 | 9.8762 | 7.0015
[7 empty] | 5584 | 40 | 10.9601 | 7.7886
[7 empty] | 5585 | 41 | 11.5279 | 8.2009
[7 empty] | 5586 | 42 | 11.5451 | 8.2134
[7 empty] | 5587 | 43 | 11.9236 | 8.4882
[7 empty] | 5588 | 44 | 13.1107 | 9.3503
[7 empty] | 5589 | 45 | 12.6978 | 9.0505
[7 empty] | 5590 | 46 | 9.8762 | 7.0015
[7 empty] | 5591 | 47 | 6.1771 | 4.3153
[7 empty] | 5592 | 48 | 4.6373 | 3.1971
[7 empty] | 5593 | 49 | 3.9577 | 2.7036
[7 empty] | 5594 | 50 | 3.6394 | 2.4725
[7 empty] | 5595 | 51 | 3.5276 | 2.3913
[7 empty] | 5596 | 52 | 3.562 | 2.4163
[7 empty] | 5597 | 53 | 3.5878 | 2.435
[7 empty] | 5598 | 54 | 4.1814 | 2.866
[7 empty] | 5599 | 55 | 5.3513 | 3.7156
[7 empty] | 5600 | 56 | 5.6008 | 3.8968
[7 empty] | 5601 | 57 | 6.5729 | 4.6027
[7 empty] | 5602 | 58 | 7.7084 | 5.4273
[7 empty] | 5603 | 59 | 8.9471 | 6.3268
[7 empty] | 5604 | 60 | 9.5923 | 6.7953
[7 empty] | 5605 | 61 | 10.2891 | 7.3013
[7 empty] | 5606 | 62 | 10.0827 | 7.1514
[7 empty] | 5607 | 63 | 10.6934 | 7.5949
[7 empty] | 5608 | 64 | 11.6655 | 8.3008
[7 empty] | 5609 | 65 | 12.3021 | 8.7631
[7 empty] | 5610 | 66 | 12.1989 | 8.6882
[7 empty] | 5611 | 67 | 12.9559 | 9.2379
[7 empty] | 5612 | 68 | 13.2054 | 9.419
[7 empty] | 5613 | 69 | 12.6806 | 9.038
[7 empty] | 5614 | 70 | 10.3235 | 7.3263
[7 empty] | 5615 | 71 | 5.6868 | 3.9592
[7 empty] | 5616 | 72 | 4.5734 | 3.1507
[7 empty] | 5617 | 73 | 3.8373 | 2.6162
[7 empty] | 5618 | 74 | 3.605 | 2.4475
[7 empty] | 5619 | 75 | 3.5018 | 2.3725
[7 empty] | 5620 | 76 | 3.4416 | 2.3288
[7 empty] | 5621 | 77 | 3.6222 | 2.46
[7 empty] | 5622 | 78 | 4.0351 | 2.7598
[7 empty] | 5623 | 79 | 5.1793 | 3.5907
[7 empty] | 5624 | 80 | 5.3599 | 3.7219
[7 empty] | 5625 | 81 | 6.5729 | 4.6027
[7 empty] | 5626 | 82 | 7.6912 | 5.4148
[7 empty] | 5627 | 83 | 8.4482 | 5.9645
[7 empty] | 5628 | 84 | 9.7214 | 6.889
[7 empty] | 5629 | 85 | 9.4117 | 6.6642
[7 empty] | 5630 | 86 | 8.8869 | 6.2831
[7 empty] | 5631 | 87 | 9.3428 | 6.6142
[7 empty] | 5632 | 88 | 10.0224 | 7.1077
[7 empty] | 5633 | 89 | 11.4074 | 8.1134
[7 empty] | 5634 | 90 | 10.8053 | 7.6762
[7 empty] | 5635 | 91 | 11.5107 | 8.1884
[7 empty] | 5636 | 92 | 10.8913 | 7.7386
[7 empty] | 5637 | 93 | 8.4138 | 5.9395
[7 empty] | 5638 | 94 | 7.4847 | 5.2648
[7 empty] | 5639 | 95 | 5.575 | 3.878
[7 empty] | 5640 | 96 | 4.5599 | 3.1409
[7 empty] | 5641 | 97 | 4.5083 | 3.1034
[7 empty] | 5642 | 98 | 4.2072 | 2.8848
[7 empty] | 5643 | 99 | 4.147 | 2.841
[7 empty] | 5644 | 100 | 3.7857 | 2.5787
[7 empty] | 5645 | 101 | 3.7254 | 2.5349
[7 empty] | 5646 | 102 | 3.9663 | 2.7099
[7 empty] | 5647 | 103 | 4.7319 | 3.2658
[7 empty] | 5648 | 104 | 4.99 | 3.4532
[7 empty] | 5649 | 105 | 5.4889 | 3.8156
[7 empty] | 5650 | 106 | 6.9858 | 4.9025
[7 empty] | 5651 | 107 | 7.3471 | 5.1649
[7 empty] | 5652 | 108 | 8.9643 | 6.3393
[7 empty] | 5653 | 109 | 8.2847 | 5.8458
[7 empty] | 5654 | 110 | 7.8202 | 5.5085
[7 empty] | 5655 | 111 | 7.6568 | 5.3898
[7 empty] | 5656 | 112 | 7.7256 | 5.4398
[7 empty] | 5657 | 113 | 7.3729 | 5.1836
[7 empty] | 5658 | 114 | 7.5449 | 5.3086
[7 empty] | 5659 | 115 | 7.0804 | 4.9712
[7 empty] | 5660 | 116 | 7.7772 | 5.4772
[7 empty] | 5661 | 117 | 7.3471 | 5.1649
[7 empty] | 5662 | 118 | 6.5556 | 4.5902
[7 empty] | 5663 | 119 | 4.9212 | 3.4033
[7 empty] | 5664 | 120 | 4.5954 | 3.1667
[7 empty] | 5665 | 121 | 3.8459 | 2.6224
[7 empty] | 5666 | 122 | 3.4243 | 2.3163
[7 empty] | 5667 | 123 | 3.3383 | 2.2538
[7 empty] | 5668 | 124 | 3.3039 | 2.2289
[7 empty] | 5669 | 125 | 3.2609 | 2.1976
[7 empty] | 5670 | 126 | 3.4071 | 2.3038
[7 empty] | 5671 | 127 | 4.9556 | 3.4283
[7 empty] | 5672 | 128 | 6.5556 | 4.5902
[7 empty] | 5673 | 129 | 7.2524 | 5.0962
[7 empty] | 5674 | 130 | 7.6998 | 5.421
[7 empty] | 5675 | 131 | 7.8632 | 5.5397
[7 empty] | 5676 | 132 | 7.6051 | 5.3523
[7 empty] | 5677 | 133 | 8.2589 | 5.8271
[7 empty] | 5678 | 134 | 8.5686 | 6.052
[7 empty] | 5679 | 135 | 8.6374 | 6.1019
[7 empty] | 5680 | 136 | 7.803 | 5.496
[7 empty] | 5681 | 137 | 7.6998 | 5.421
[7 empty] | 5682 | 138 | 7.6482 | 5.3835
[7 empty] | 5683 | 139 | 7.3041 | 5.1337
[7 empty] | 5684 | 140 | 7.3127 | 5.1399
[7 empty] | 5685 | 141 | 6.6417 | 4.6526
[7 empty] | 5686 | 142 | 5.9879 | 4.1779
[7 empty] | 5687 | 143 | 5.0846 | 3.522
[7 empty] | 5688 | 144 | 4.4566 | 3.0659
[7 empty] | 5689 | 145 | 3.9749 | 2.7161
[7 empty] | 5690 | 146 | 3.7598 | 2.5599
[7 empty] | 5691 | 147 | 3.691 | 2.51
[7 empty] | 5692 | 148 | 3.6824 | 2.5037
[7 empty] | 5693 | 149 | 3.6824 | 2.5037
[7 empty] | 5694 | 150 | 3.691 | 2.51
[7 empty] | 5695 | 151 | 4.8007 | 3.3158
[7 empty] | 5696 | 152 | 6.3664 | 4.4527
[7 empty] | 5697 | 153 | 6.9944 | 4.9088
[7 empty] | 5698 | 154 | 7.5707 | 5.3273
[7 empty] | 5699 | 155 | 7.4159 | 5.2149
[7 empty] | 5700 | 156 | 7.5879 | 5.3398
[7 empty] | 5701 | 157 | 8.3192 | 5.8708
[7 empty] | 5702 | 158 | 8.6546 | 6.1144
[7 empty] | 5703 | 159 | 8.9299 | 6.3143
[7 empty] | 5704 | 160 | 8.8009 | 6.2206
[7 empty] | 5705 | 161 | 9.5837 | 6.7891
[7 empty] | 5706 | 162 | 9.0762 | 6.4205
[7 empty] | 5707 | 163 | 9.4461 | 6.6891
[7 empty] | 5708 | 164 | 8.0611 | 5.6834
[7 empty] | 5709 | 165 | 11.2698 | 8.0135
[7 empty] | 5710 | 166 | 9.1708 | 6.4892
[7 empty] | 5711 | 167 | 5.4717 | 3.8031
[7 empty] | 5712 | 168 | 4.8093 | 3.3221
[7 empty] | 5713 | 1 | 3.3125 | 2.2351
[7 empty] | 5714 | 2 | 3.2007 | 2.1539
[7 empty] | 5715 | 3 | 3.1921 | 2.1476
[7 empty] | 5716 | 4 | 3.3297 | 2.2476
[7 empty] | 5717 | 5 | 3.3469 | 2.2601
[7 empty] | 5718 | 6 | 3.7857 | 2.5787
[7 empty] | 5719 | 7 | 4.5255 | 3.1159
[7 empty] | 5720 | 8 | 5.2137 | 3.6157
[7 empty] | 5721 | 9 | 5.1879 | 3.5969
[7 empty] | 5722 | 10 | 6.7449 | 4.7276
[7 empty] | 5723 | 11 | 8.8783 | 6.2768
[7 empty] | 5724 | 12 | 9.8676 | 6.9952
[7 empty] | 5725 | 13 | 10.2547 | 7.2763
[7 empty] | 5726 | 14 | 10.031 | 7.1139
[7 empty] | 5727 | 15 | 9.9364 | 7.0452
[7 empty] | 5728 | 16 | 11.1494 | 7.926
[7 empty] | 5729 | 17 | 12.5086 | 8.913
[7 empty] | 5730 | 18 | 12.2591 | 8.7319
[7 empty] | 5731 | 19 | 12.801 | 9.1254
[7 empty] | 5732 | 20 | 12.7322 | 9.0755
[7 empty] | 5733 | 21 | 13.3172 | 9.5002
[7 empty] | 5734 | 22 | 9.2568 | 6.5517
[7 empty] | 5735 | 23 | 5.3857 | 3.7406
[7 empty] | 5736 | 24 | 3.6704 | 2.495
[7 empty] | 5737 | 25 | 3.5706 | 2.4225
[7 empty] | 5738 | 26 | 3.4588 | 2.3413
[7 empty] | 5739 | 27 | 3.3555 | 2.2663
[7 empty] | 5740 | 28 | 3.4416 | 2.3288
[7 empty] | 5741 | 29 | 3.691 | 2.51
[7 empty] | 5742 | 30 | 3.9405 | 2.6911
[7 empty] | 5743 | 31 | 4.8093 | 3.3221
[7 empty] | 5744 | 32 | 5.1706 | 3.5844
[7 empty] | 5745 | 33 | 5.8502 | 4.0779
[7 empty] | 5746 | 34 | 6.7707 | 4.7464
[7 empty] | 5747 | 35 | 8.9987 | 6.3643
[7 empty] | 5748 | 36 | 10.0569 | 7.1327
[7 empty] | 5749 | 37 | 10.1343 | 7.1889
[7 empty] | 5750 | 38 | 10.2117 | 7.2451
[7 empty] | 5751 | 39 | 9.8762 | 7.0015
[7 empty] | 5752 | 40 | 10.9601 | 7.7886
[7 empty] | 5753 | 41 | 11.5279 | 8.2009
[7 empty] | 5754 | 42 | 11.5451 | 8.2134
[7 empty] | 5755 | 43 | 11.9236 | 8.4882
[7 empty] | 5756 | 44 | 13.1107 | 9.3503
[7 empty] | 5757 | 45 | 12.6978 | 9.0505
[7 empty] | 5758 | 46 | 9.8762 | 7.0015
[7 empty] | 5759 | 47 | 6.1771 | 4.3153
[7 empty] | 5760 | 48 | 4.6373 | 3.1971
[7 empty] | 5761 | 49 | 3.9577 | 2.7036
[7 empty] | 5762 | 50 | 3.6394 | 2.4725
[7 empty] | 5763 | 51 | 3.5276 | 2.3913
[7 empty] | 5764 | 52 | 3.562 | 2.4163
[7 empty] | 5765 | 53 | 3.5878 | 2.435
[7 empty] | 5766 | 54 | 4.1814 | 2.866
[7 empty] | 5767 | 55 | 5.3513 | 3.7156
[7 empty] | 5768 | 56 | 5.6008 | 3.8968
[7 empty] | 5769 | 57 | 6.5729 | 4.6027
[7 empty] | 5770 | 58 | 7.7084 | 5.4273
[7 empty] | 5771 | 59 | 8.9471 | 6.3268
[7 empty] | 5772 | 60 | 9.5923 | 6.7953
[7 empty] | 5773 | 61 | 10.2891 | 7.3013
[7 empty] | 5774 | 62 | 10.0827 | 7.1514
[7 empty] | 5775 | 63 | 10.6934 | 7.5949
[7 empty] | 5776 | 64 | 11.6655 | 8.3008
[7 empty] | 5777 | 65 | 12.3021 | 8.7631
[7 empty] | 5778 | 66 | 12.1989 | 8.6882
[7 empty] | 5779 | 67 | 12.9559 | 9.2379
[7 empty] | 5780 | 68 | 13.2054 | 9.419
[7 empty] | 5781 | 69 | 12.6806 | 9.038
[7 empty] | 5782 | 70 | 10.3235 | 7.3263
[7 empty] | 5783 | 71 | 5.6868 | 3.9592
[7 empty] | 5784 | 72 | 4.5734 | 3.1507
[7 empty] | 5785 | 73 | 3.8373 | 2.6162
[7 empty] | 5786 | 74 | 3.605 | 2.4475
[7 empty] | 5787 | 75 | 3.5018 | 2.3725
[7 empty] | 5788 | 76 | 3.4416 | 2.3288
[7 empty] | 5789 | 77 | 3.6222 | 2.46
[7 empty] | 5790 | 78 | 4.0351 | 2.7598
[7 empty] | 5791 | 79 | 5.1793 | 3.5907
[7 empty] | 5792 | 80 | 5.3599 | 3.7219
[7 empty] | 5793 | 81 | 6.5729 | 4.6027
[7 empty] | 5794 | 82 | 7.6912 | 5.4148
[7 empty] | 5795 | 83 | 8.4482 | 5.9645
[7 empty] | 5796 | 84 | 9.7214 | 6.889
[7 empty] | 5797 | 85 | 9.4117 | 6.6642
[7 empty] | 5798 | 86 | 8.8869 | 6.2831
[7 empty] | 5799 | 87 | 9.3428 | 6.6142
[7 empty] | 5800 | 88 | 10.0224 | 7.1077
[7 empty] | 5801 | 89 | 11.4074 | 8.1134
[7 empty] | 5802 | 90 | 10.8053 | 7.6762
[7 empty] | 5803 | 91 | 11.5107 | 8.1884
[7 empty] | 5804 | 92 | 10.8913 | 7.7386
[7 empty] | 5805 | 93 | 8.4138 | 5.9395
[7 empty] | 5806 | 94 | 7.4847 | 5.2648
[7 empty] | 5807 | 95 | 5.575 | 3.878
[7 empty] | 5808 | 96 | 4.5599 | 3.1409
[7 empty] | 5809 | 97 | 4.5083 | 3.1034
[7 empty] | 5810 | 98 | 4.2072 | 2.8848
[7 empty] | 5811 | 99 | 4.147 | 2.841
[7 empty] | 5812 | 100 | 3.7857 | 2.5787
[7 empty] | 5813 | 101 | 3.7254 | 2.5349
[7 empty] | 5814 | 102 | 3.9663 | 2.7099
[7 empty] | 5815 | 103 | 4.7319 | 3.2658
[7 empty] | 5816 | 104 | 4.99 | 3.4532
[7 empty] | 5817 | 105 | 5.4889 | 3.8156
[7 empty] | 5818 | 106 | 6.9858 | 4.9025
[7 empty] | 5819 | 107 | 7.3471 | 5.1649
[7 empty] | 5820 | 108 | 8.9643 | 6.3393
[7 empty] | 5821 | 109 | 8.2847 | 5.8458
[7 empty] | 5822 | 110 | 7.8202 | 5.5085
[7 empty] | 5823 | 111 | 7.6568 | 5.3898
[7 empty] | 5824 | 112 | 7.7256 | 5.4398
[7 empty] | 5825 | 113 | 7.3729 | 5.1836
[7 empty] | 5826 | 114 | 7.5449 | 5.3086
[7 empty] | 5827 | 115 | 7.0804 | 4.9712
[7 empty] | 5828 | 116 | 7.7772 | 5.4772
[7 empty] | 5829 | 117 | 7.3471 | 5.1649
[7 empty] | 5830 | 118 | 6.5556 | 4.5902
[7 empty] | 5831 | 119 | 4.9212 | 3.4033
[7 empty] | 5832 | 120 | 4.5954 | 3.1667
[7 empty] | 5833 | 121 | 3.8459 | 2.6224
[7 empty] | 5834 | 122 | 3.4243 | 2.3163
[7 empty] | 5835 | 123 | 3.3383 | 2.2538
[7 empty] | 5836 | 124 | 3.3039 | 2.2289
[7 empty] | 5837 | 125 | 3.2609 | 2.1976
[7 empty] | 5838 | 126 | 3.4071 | 2.3038
[7 empty] | 5839 | 127 | 4.9556 | 3.4283
[7 empty] | 5840 | 128 | 6.5556 | 4.5902
[7 empty] | 5841 | 129 | 7.2524 | 5.0962
[7 empty] | 5842 | 130 | 7.6998 | 5.421
[7 empty] | 5843 | 131 | 7.8632 | 5.5397
[7 empty] | 5844 | 132 | 7.6051 | 5.3523
[7 empty] | 5845 | 133 | 8.2589 | 5.8271
[7 empty] | 5846 | 134 | 8.5686 | 6.052
[7 empty] | 5847 | 135 | 8.6374 | 6.1019
[7 empty] | 5848 | 136 | 7.803 | 5.496
[7 empty] | 5849 | 137 | 7.6998 | 5.421
[7 empty] | 5850 | 138 | 7.6482 | 5.3835
[7 empty] | 5851 | 139 | 7.3041 | 5.1337
[7 empty] | 5852 | 140 | 7.3127 | 5.1399
[7 empty] | 5853 | 141 | 6.6417 | 4.6526
[7 empty] | 5854 | 142 | 5.9879 | 4.1779
[7 empty] | 5855 | 143 | 5.0846 | 3.522
[7 empty] | 5856 | 144 | 4.4566 | 3.0659
[7 empty] | 5857 | 145 | 3.9749 | 2.7161
[7 empty] | 5858 | 146 | 3.7598 | 2.5599
[7 empty] | 5859 | 147 | 3.691 | 2.51
[7 empty] | 5860 | 148 | 3.6824 | 2.5037
[7 empty] | 5861 | 149 | 3.6824 | 2.5037
[7 empty] | 5862 | 150 | 3.691 | 2.51
[7 empty] | 5863 | 151 | 4.8007 | 3.3158
[7 empty] | 5864 | 152 | 6.3664 | 4.4527
[7 empty] | 5865 | 153 | 6.9944 | 4.9088
[7 empty] | 5866 | 154 | 7.5707 | 5.3273
[7 empty] | 5867 | 155 | 7.4159 | 5.2149
[7 empty] | 5868 | 156 | 7.5879 | 5.3398
[7 empty] | 5869 | 157 | 8.3192 | 5.8708
[7 empty] | 5870 | 158 | 8.6546 | 6.1144
[7 empty] | 5871 | 159 | 8.9299 | 6.3143
[7 empty] | 5872 | 160 | 8.8009 | 6.2206
[7 empty] | 5873 | 161 | 9.5837 | 6.7891
[7 empty] | 5874 | 162 | 9.0762 | 6.4205
[7 empty] | 5875 | 163 | 9.4461 | 6.6891
[7 empty] | 5876 | 164 | 8.0611 | 5.6834
[7 empty] | 5877 | 165 | 11.2698 | 8.0135
[7 empty] | 5878 | 166 | 9.1708 | 6.4892
[7 empty] | 5879 | 167 | 5.4717 | 3.8031
[7 empty] | 5880 | 168 | 4.8093 | 3.3221
[7 empty] | 5881 | 1 | 3.3125 | 2.2351
[7 empty] | 5882 | 2 | 3.2007 | 2.1539
[7 empty] | 5883 | 3 | 3.1921 | 2.1476
[7 empty] | 5884 | 4 | 3.3297 | 2.2476
[7 empty] | 5885 | 5 | 3.3469 | 2.2601
[7 empty] | 5886 | 6 | 3.7857 | 2.5787
[7 empty] | 5887 | 7 | 4.5255 | 3.1159
[7 empty] | 5888 | 8 | 5.2137 | 3.6157
[7 empty] | 5889 | 9 | 5.1879 | 3.5969
[7 empty] | 5890 | 10 | 6.7449 | 4.7276
[7 empty] | 5891 | 11 | 8.8783 | 6.2768
[7 empty] | 5892 | 12 | 9.8676 | 6.9952
[7 empty] | 5893 | 13 | 10.2547 | 7.2763
[7 empty] | 5894 | 14 | 10.031 | 7.1139
[7 empty] | 5895 | 15 | 9.9364 | 7.0452
[7 empty] | 5896 | 16 | 11.1494 | 7.926
[7 empty] | 5897 | 17 | 12.5086 | 8.913
[7 empty] | 5898 | 18 | 12.2591 | 8.7319
[7 empty] | 5899 | 19 | 12.801 | 9.1254
[7 empty] | 5900 | 20 | 12.7322 | 9.0755
[7 empty] | 5901 | 21 | 13.3172 | 9.5002
[7 empty] | 5902 | 22 | 9.2568 | 6.5517
[7 empty] | 5903 | 23 | 5.3857 | 3.7406
[7 empty] | 5904 | 24 | 3.6704 | 2.495
[7 empty] | 5905 | 25 | 3.5706 | 2.4225
[7 empty] | 5906 | 26 | 3.4588 | 2.3413
[7 empty] | 5907 | 27 | 3.3555 | 2.2663
[7 empty] | 5908 | 28 | 3.4416 | 2.3288
[7 empty] | 5909 | 29 | 3.691 | 2.51
[7 empty] | 5910 | 30 | 3.9405 | 2.6911
[7 empty] | 5911 | 31 | 4.8093 | 3.3221
[7 empty] | 5912 | 32 | 5.1706 | 3.5844
[7 empty] | 5913 | 33 | 5.8502 | 4.0779
[7 empty] | 5914 | 34 | 6.7707 | 4.7464
[7 empty] | 5915 | 35 | 8.9987 | 6.3643
[7 empty] | 5916 | 36 | 10.0569 | 7.1327
[7 empty] | 5917 | 37 | 10.1343 | 7.1889
[7 empty] | 5918 | 38 | 10.2117 | 7.2451
[7 empty] | 5919 | 39 | 9.8762 | 7.0015
[7 empty] | 5920 | 40 | 10.9601 | 7.7886
[7 empty] | 5921 | 41 | 11.5279 | 8.2009
[7 empty] | 5922 | 42 | 11.5451 | 8.2134
[7 empty] | 5923 | 43 | 11.9236 | 8.4882
[7 empty] | 5924 | 44 | 13.1107 | 9.3503
[7 empty] | 5925 | 45 | 12.6978 | 9.0505
[7 empty] | 5926 | 46 | 9.8762 | 7.0015
[7 empty] | 5927 | 47 | 6.1771 | 4.3153
[7 empty] | 5928 | 48 | 4.6373 | 3.1971
[7 empty] | 5929 | 49 | 3.9577 | 2.7036
[7 empty] | 5930 | 50 | 3.6394 | 2.4725
[7 empty] | 5931 | 51 | 3.5276 | 2.3913
[7 empty] | 5932 | 52 | 3.562 | 2.4163
[7 empty] | 5933 | 53 | 3.5878 | 2.435
[7 empty] | 5934 | 54 | 4.1814 | 2.866
[7 empty] | 5935 | 55 | 5.3513 | 3.7156
[7 empty] | 5936 | 56 | 5.6008 | 3.8968
[7 empty] | 5937 | 57 | 6.5729 | 4.6027
[7 empty] | 5938 | 58 | 7.7084 | 5.4273
[7 empty] | 5939 | 59 | 8.9471 | 6.3268
[7 empty] | 5940 | 60 | 9.5923 | 6.7953
[7 empty] | 5941 | 61 | 10.2891 | 7.3013
[7 empty] | 5942 | 62 | 10.0827 | 7.1514
[7 empty] | 5943 | 63 | 10.6934 | 7.5949
[7 empty] | 5944 | 64 | 11.6655 | 8.3008
[7 empty] | 5945 | 65 | 12.3021 | 8.7631
[7 empty] | 5946 | 66 | 12.1989 | 8.6882
[7 empty] | 5947 | 67 | 12.9559 | 9.2379
[7 empty] | 5948 | 68 | 13.2054 | 9.419
[7 empty] | 5949 | 69 | 12.6806 | 9.038
[7 empty] | 5950 | 70 | 10.3235 | 7.3263
[7 empty] | 5951 | 71 | 5.6868 | 3.9592
[7 empty] | 5952 | 72 | 4.5734 | 3.1507
[7 empty] | 5953 | 73 | 3.8373 | 2.6162
[7 empty] | 5954 | 74 | 3.605 | 2.4475
[7 empty] | 5955 | 75 | 3.5018 | 2.3725
[7 empty] | 5956 | 76 | 3.4416 | 2.3288
[7 empty] | 5957 | 77 | 3.6222 | 2.46
[7 empty] | 5958 | 78 | 4.0351 | 2.7598
[7 empty] | 5959 | 79 | 5.1793 | 3.5907
[7 empty] | 5960 | 80 | 5.3599 | 3.7219
[7 empty] | 5961 | 81 | 6.5729 | 4.6027
[7 empty] | 5962 | 82 | 7.6912 | 5.4148
[7 empty] | 5963 | 83 | 8.4482 | 5.9645
[7 empty] | 5964 | 84 | 9.7214 | 6.889
[7 empty] | 5965 | 85 | 9.4117 | 6.6642
[7 empty] | 5966 | 86 | 8.8869 | 6.2831
[7 empty] | 5967 | 87 | 9.3428 | 6.6142
[7 empty] | 5968 | 88 | 10.0224 | 7.1077
[7 empty] | 5969 | 89 | 11.4074 | 8.1134
[7 empty] | 5970 | 90 | 10.8053 | 7.6762
[7 empty] | 5971 | 91 | 11.5107 | 8.1884
[7 empty] | 5972 | 92 | 10.8913 | 7.7386
[7 empty] | 5973 | 93 | 8.4138 | 5.9395
[7 empty] | 5974 | 94 | 7.4847 | 5.2648
[7 empty] | 5975 | 95 | 5.575 | 3.878
[7 empty] | 5976 | 96 | 4.5599 | 3.1409
[7 empty] | 5977 | 97 | 4.5083 | 3.1034
[7 empty] | 5978 | 98 | 4.2072 | 2.8848
[7 empty] | 5979 | 99 | 4.147 | 2.841
[7 empty] | 5980 | 100 | 3.7857 | 2.5787
[7 empty] | 5981 | 101 | 3.7254 | 2.5349
[7 empty] | 5982 | 102 | 3.9663 | 2.7099
[7 empty] | 5983 | 103 | 4.7319 | 3.2658
[7 empty] | 5984 | 104 | 4.99 | 3.4532
[7 empty] | 5985 | 105 | 5.4889 | 3.8156
[7 empty] | 5986 | 106 | 6.9858 | 4.9025
[7 empty] | 5987 | 107 | 7.3471 | 5.1649
[7 empty] | 5988 | 108 | 8.9643 | 6.3393
[7 empty] | 5989 | 109 | 8.2847 | 5.8458
[7 empty] | 5990 | 110 | 7.8202 | 5.5085
[7 empty] | 5991 | 111 | 7.6568 | 5.3898
[7 empty] | 5992 | 112 | 7.7256 | 5.4398
[7 empty] | 5993 | 113 | 7.3729 | 5.1836
[7 empty] | 5994 | 114 | 7.5449 | 5.3086
[7 empty] | 5995 | 115 | 7.0804 | 4.9712
[7 empty] | 5996 | 116 | 7.7772 | 5.4772
[7 empty] | 5997 | 117 | 7.3471 | 5.1649
[7 empty] | 5998 | 118 | 6.5556 | 4.5902
[7 empty] | 5999 | 119 | 4.9212 | 3.4033
[7 empty] | 6000 | 120 | 4.5954 | 3.1667
[7 empty] | 6001 | 121 | 3.8459 | 2.6224
[7 empty] | 6002 | 122 | 3.4243 | 2.3163
[7 empty] | 6003 | 123 | 3.3383 | 2.2538
[7 empty] | 6004 | 124 | 3.3039 | 2.2289
[7 empty] | 6005 | 125 | 3.2609 | 2.1976
[7 empty] | 6006 | 126 | 3.4071 | 2.3038
[7 empty] | 6007 | 127 | 4.9556 | 3.4283
[7 empty] | 6008 | 128 | 6.5556 | 4.5902
[7 empty] | 6009 | 129 | 7.2524 | 5.0962
[7 empty] | 6010 | 130 | 7.6998 | 5.421
[7 empty] | 6011 | 131 | 7.8632 | 5.5397
[7 empty] | 6012 | 132 | 7.6051 | 5.3523
[7 empty] | 6013 | 133 | 8.2589 | 5.8271
[7 empty] | 6014 | 134 | 8.5686 | 6.052
[7 empty] | 6015 | 135 | 8.6374 | 6.1019
[7 empty] | 6016 | 136 | 7.803 | 5.496
[7 empty] | 6017 | 137 | 7.6998 | 5.421
[7 empty] | 6018 | 138 | 7.6482 | 5.3835
[7 empty] | 6019 | 139 | 7.3041 | 5.1337
[7 empty] | 6020 | 140 | 7.3127 | 5.1399
[7 empty] | 6021 | 141 | 6.6417 | 4.6526
[7 empty] | 6022 | 142 | 5.9879 | 4.1779
[7 empty] | 6023 | 143 | 5.0846 | 3.522
[7 empty] | 6024 | 144 | 4.4566 | 3.0659
[7 empty] | 6025 | 145 | 3.9749 | 2.7161
[7 empty] | 6026 | 146 | 3.7598 | 2.5599
[7 empty] | 6027 | 147 | 3.691 | 2.51
[7 empty] | 6028 | 148 | 3.6824 | 2.5037
[7 empty] | 6029 | 149 | 3.6824 | 2.5037
[7 empty] | 6030 | 150 | 3.691 | 2.51
[7 empty] | 6031 | 151 | 4.8007 | 3.3158
[7 empty] | 6032 | 152 | 6.3664 | 4.4527
[7 empty] | 6033 | 153 | 6.9944 | 4.9088
[7 empty] | 6034 | 154 | 7.5707 | 5.3273
[7 empty] | 6035 | 155 | 7.4159 | 5.2149
[7 empty] | 6036 | 156 | 7.5879 | 5.3398
[7 empty] | 6037 | 157 | 8.3192 | 5.8708
[7 empty] | 6038 | 158 | 8.6546 | 6.1144
[7 empty] | 6039 | 159 | 8.9299 | 6.3143
[7 empty] | 6040 | 160 | 8.8009 | 6.2206
[7 empty] | 6041 | 161 | 9.5837 | 6.7891
[7 empty] | 6042 | 162 | 9.0762 | 6.4205
[7 empty] | 6043 | 163 | 9.4461 | 6.6891
[7 empty] | 6044 | 164 | 8.0611 | 5.6834
[7 empty] | 6045 | 165 | 11.2698 | 8.0135
[7 empty] | 6046 | 166 | 9.1708 | 6.4892
[7 empty] | 6047 | 167 | 5.4717 | 3.8031
[7 empty] | 6048 | 168 | 4.8093 | 3.3221
[7 empty] | 6049 | 1 | 3.3125 | 2.2351
[7 empty] | 6050 | 2 | 3.2007 | 2.1539
[7 empty] | 6051 | 3 | 3.1921 | 2.1476
[7 empty] | 6052 | 4 | 3.3297 | 2.2476
[7 empty] | 6053 | 5 | 3.3469 | 2.2601
[7 empty] | 6054 | 6 | 3.7857 | 2.5787
[7 empty] | 6055 | 7 | 4.5255 | 3.1159
[7 empty] | 6056 | 8 | 5.2137 | 3.6157
[7 empty] | 6057 | 9 | 5.1879 | 3.5969
[7 empty] | 6058 | 10 | 6.7449 | 4.7276
[7 empty] | 6059 | 11 | 8.8783 | 6.2768
[7 empty] | 6060 | 12 | 9.8676 | 6.9952
[7 empty] | 6061 | 13 | 10.2547 | 7.2763
[7 empty] | 6062 | 14 | 10.031 | 7.1139
[7 empty] | 6063 | 15 | 9.9364 | 7.0452
[7 empty] | 6064 | 16 | 11.1494 | 7.926
[7 empty] | 6065 | 17 | 12.5086 | 8.913
[7 empty] | 6066 | 18 | 12.2591 | 8.7319
[7 empty] | 6067 | 19 | 12.801 | 9.1254
[7 empty] | 6068 | 20 | 12.7322 | 9.0755
[7 empty] | 6069 | 21 | 13.3172 | 9.5002
[7 empty] | 6070 | 22 | 9.2568 | 6.5517
[7 empty] | 6071 | 23 | 5.3857 | 3.7406
[7 empty] | 6072 | 24 | 3.6704 | 2.495
[7 empty] | 6073 | 25 | 3.5706 | 2.4225
[7 empty] | 6074 | 26 | 3.4588 | 2.3413
[7 empty] | 6075 | 27 | 3.3555 | 2.2663
[7 empty] | 6076 | 28 | 3.4416 | 2.3288
[7 empty] | 6077 | 29 | 3.691 | 2.51
[7 empty] | 6078 | 30 | 3.9405 | 2.6911
[7 empty] | 6079 | 31 | 4.8093 | 3.3221
[7 empty] | 6080 | 32 | 5.1706 | 3.5844
[7 empty] | 6081 | 33 | 5.8502 | 4.0779
[7 empty] | 6082 | 34 | 6.7707 | 4.7464
[7 empty] | 6083 | 35 | 8.9987 | 6.3643
[7 empty] | 6084 | 36 | 10.0569 | 7.1327
[7 empty] | 6085 | 37 | 10.1343 | 7.1889
[7 empty] | 6086 | 38 | 10.2117 | 7.2451
[7 empty] | 6087 | 39 | 9.8762 | 7.0015
[7 empty] | 6088 | 40 | 10.9601 | 7.7886
[7 empty] | 6089 | 41 | 11.5279 | 8.2009
[7 empty] | 6090 | 42 | 11.5451 | 8.2134
[7 empty] | 6091 | 43 | 11.9236 | 8.4882
[7 empty] | 6092 | 44 | 13.1107 | 9.3503
[7 empty] | 6093 | 45 | 12.6978 | 9.0505
[7 empty] | 6094 | 46 | 9.8762 | 7.0015
[7 empty] | 6095 | 47 | 6.1771 | 4.3153
[7 empty] | 6096 | 48 | 4.6373 | 3.1971
[7 empty] | 6097 | 49 | 3.9577 | 2.7036
[7 empty] | 6098 | 50 | 3.6394 | 2.4725
[7 empty] | 6099 | 51 | 3.5276 | 2.3913
[7 empty] | 6100 | 52 | 3.562 | 2.4163
[7 empty] | 6101 | 53 | 3.5878 | 2.435
[7 empty] | 6102 | 54 | 4.1814 | 2.866
[7 empty] | 6103 | 55 | 5.3513 | 3.7156
[7 empty] | 6104 | 56 | 5.6008 | 3.8968
[7 empty] | 6105 | 57 | 6.5729 | 4.6027
[7 empty] | 6106 | 58 | 7.7084 | 5.4273
[7 empty] | 6107 | 59 | 8.9471 | 6.3268
[7 empty] | 6108 | 60 | 9.5923 | 6.7953
[7 empty] | 6109 | 61 | 10.2891 | 7.3013
[7 empty] | 6110 | 62 | 10.0827 | 7.1514
[7 empty] | 6111 | 63 | 10.6934 | 7.5949
[7 empty] | 6112 | 64 | 11.6655 | 8.3008
[7 empty] | 6113 | 65 | 12.3021 | 8.7631
[7 empty] | 6114 | 66 | 12.1989 | 8.6882
[7 empty] | 6115 | 67 | 12.9559 | 9.2379
[7 empty] | 6116 | 68 | 13.2054 | 9.419
[7 empty] | 6117 | 69 | 12.6806 | 9.038
[7 empty] | 6118 | 70 | 10.3235 | 7.3263
[7 empty] | 6119 | 71 | 5.6868 | 3.9592
[7 empty] | 6120 | 72 | 4.5734 | 3.1507
[7 empty] | 6121 | 73 | 3.8373 | 2.6162
[7 empty] | 6122 | 74 | 3.605 | 2.4475
[7 empty] | 6123 | 75 | 3.5018 | 2.3725
[7 empty] | 6124 | 76 | 3.4416 | 2.3288
[7 empty] | 6125 | 77 | 3.6222 | 2.46
[7 empty] | 6126 | 78 | 4.0351 | 2.7598
[7 empty] | 6127 | 79 | 5.1793 | 3.5907
[7 empty] | 6128 | 80 | 5.3599 | 3.7219
[7 empty] | 6129 | 81 | 6.5729 | 4.6027
[7 empty] | 6130 | 82 | 7.6912 | 5.4148
[7 empty] | 6131 | 83 | 8.4482 | 5.9645
[7 empty] | 6132 | 84 | 9.7214 | 6.889
[7 empty] | 6133 | 85 | 9.4117 | 6.6642
[7 empty] | 6134 | 86 | 8.8869 | 6.2831
[7 empty] | 6135 | 87 | 9.3428 | 6.6142
[7 empty] | 6136 | 88 | 10.0224 | 7.1077
[7 empty] | 6137 | 89 | 11.4074 | 8.1134
[7 empty] | 6138 | 90 | 10.8053 | 7.6762
[7 empty] | 6139 | 91 | 11.5107 | 8.1884
[7 empty] | 6140 | 92 | 10.8913 | 7.7386
[7 empty] | 6141 | 93 | 8.4138 | 5.9395
[7 empty] | 6142 | 94 | 7.4847 | 5.2648
[7 empty] | 6143 | 95 | 5.575 | 3.878
[7 empty] | 6144 | 96 | 4.5599 | 3.1409
[7 empty] | 6145 | 97 | 4.5083 | 3.1034
[7 empty] | 6146 | 98 | 4.2072 | 2.8848
[7 empty] | 6147 | 99 | 4.147 | 2.841
[7 empty] | 6148 | 100 | 3.7857 | 2.5787
[7 empty] | 6149 | 101 | 3.7254 | 2.5349
[7 empty] | 6150 | 102 | 3.9663 | 2.7099
[7 empty] | 6151 | 103 | 4.7319 | 3.2658
[7 empty] | 6152 | 104 | 4.99 | 3.4532
[7 empty] | 6153 | 105 | 5.4889 | 3.8156
[7 empty] | 6154 | 106 | 6.9858 | 4.9025
[7 empty] | 6155 | 107 | 7.3471 | 5.1649
[7 empty] | 6156 | 108 | 8.9643 | 6.3393
[7 empty] | 6157 | 109 | 8.2847 | 5.8458
[7 empty] | 6158 | 110 | 7.8202 | 5.5085
[7 empty] | 6159 | 111 | 7.6568 | 5.3898
[7 empty] | 6160 | 112 | 7.7256 | 5.4398
[7 empty] | 6161 | 113 | 7.3729 | 5.1836
[7 empty] | 6162 | 114 | 7.5449 | 5.3086
[7 empty] | 6163 | 115 | 7.0804 | 4.9712
[7 empty] | 6164 | 116 | 7.7772 | 5.4772
[7 empty] | 6165 | 117 | 7.3471 | 5.1649
[7 empty] | 6166 | 118 | 6.5556 | 4.5902
[7 empty] | 6167 | 119 | 4.9212 | 3.4033
[7 empty] | 6168 | 120 | 4.5954 | 3.1667
[7 empty] | 6169 | 121 | 3.8459 | 2.6224
[7 empty] | 6170 | 122 | 3.4243 | 2.3163
[7 empty] | 6171 | 123 | 3.3383 | 2.2538
[7 empty] | 6172 | 124 | 3.3039 | 2.2289
[7 empty] | 6173 | 125 | 3.2609 | 2.1976
[7 empty] | 6174 | 126 | 3.4071 | 2.3038
[7 empty] | 6175 | 127 | 4.9556 | 3.4283
[7 empty] | 6176 | 128 | 6.5556 | 4.5902
[7 empty] | 6177 | 129 | 7.2524 | 5.0962
[7 empty] | 6178 | 130 | 7.6998 | 5.421
[7 empty] | 6179 | 131 | 7.8632 | 5.5397
[7 empty] | 6180 | 132 | 7.6051 | 5.3523
[7 empty] | 6181 | 133 | 8.2589 | 5.8271
[7 empty] | 6182 | 134 | 8.5686 | 6.052
[7 empty] | 6183 | 135 | 8.6374 | 6.1019
[7 empty] | 6184 | 136 | 7.803 | 5.496
[7 empty] | 6185 | 137 | 7.6998 | 5.421
[7 empty] | 6186 | 138 | 7.6482 | 5.3835
[7 empty] | 6187 | 139 | 7.3041 | 5.1337
[7 empty] | 6188 | 140 | 7.3127 | 5.1399
[7 empty] | 6189 | 141 | 6.6417 | 4.6526
[7 empty] | 6190 | 142 | 5.9879 | 4.1779
[7 empty] | 6191 | 143 | 5.0846 | 3.522
[7 empty] | 6192 | 144 | 4.4566 | 3.0659
[7 empty] | 6193 | 145 | 3.9749 | 2.7161
[7 empty] | 6194 | 146 | 3.7598 | 2.5599
[7 empty] | 6195 | 147 | 3.691 | 2.51
[7 empty] | 6196 | 148 | 3.6824 | 2.5037
[7 empty] | 6197 | 149 | 3.6824 | 2.5037
[7 empty] | 6198 | 150 | 3.691 | 2.51
[7 empty] | 6199 | 151 | 4.8007 | 3.3158
[7 empty] | 6200 | 152 | 6.3664 | 4.4527
[7 empty] | 6201 | 153 | 6.9944 | 4.9088
[7 empty] | 6202 | 154 | 7.5707 | 5.3273
[7 empty] | 6203 | 155 | 7.4159 | 5.2149
[7 empty] | 6204 | 156 | 7.5879 | 5.3398
[7 empty] | 6205 | 157 | 8.3192 | 5.8708
[7 empty] | 6206 | 158 | 8.6546 | 6.1144
[7 empty] | 6207 | 159 | 8.9299 | 6.3143
[7 empty] | 6208 | 160 | 8.8009 | 6.2206
[7 empty] | 6209 | 161 | 9.5837 | 6.7891
[7 empty] | 6210 | 162 | 9.0762 | 6.4205
[7 empty] | 6211 | 163 | 9.4461 | 6.6891
[7 empty] | 6212 | 164 | 8.0611 | 5.6834
[7 empty] | 6213 | 165 | 11.2698 | 8.0135
[7 empty] | 6214 | 166 | 9.1708 | 6.4892
[7 empty] | 6215 | 167 | 5.4717 | 3.8031
[7 empty] | 6216 | 168 | 4.8093 | 3.3221
[7 empty] | 6217 | 1 | 3.3125 | 2.2351
[7 empty] | 6218 | 2 | 3.2007 | 2.1539
[7 empty] | 6219 | 3 | 3.1921 | 2.1476
[7 empty] | 6220 | 4 | 3.3297 | 2.2476
[7 empty] | 6221 | 5 | 3.3469 | 2.2601
[7 empty] | 6222 | 6 | 3.7857 | 2.5787
[7 empty] | 6223 | 7 | 4.5255 | 3.1159
[7 empty] | 6224 | 8 | 5.2137 | 3.6157
[7 empty] | 6225 | 9 | 5.1879 | 3.5969
[7 empty] | 6226 | 10 | 6.7449 | 4.7276
[7 empty] | 6227 | 11 | 8.8783 | 6.2768
[7 empty] | 6228 | 12 | 9.8676 | 6.9952
[7 empty] | 6229 | 13 | 10.2547 | 7.2763
[7 empty] | 6230 | 14 | 10.031 | 7.1139
[7 empty] | 6231 | 15 | 9.9364 | 7.0452
[7 empty] | 6232 | 16 | 11.1494 | 7.926
[7 empty] | 6233 | 17 | 12.5086 | 8.913
[7 empty] | 6234 | 18 | 12.2591 | 8.7319
[7 empty] | 6235 | 19 | 12.801 | 9.1254
[7 empty] | 6236 | 20 | 12.7322 | 9.0755
[7 empty] | 6237 | 21 | 13.3172 | 9.5002
[7 empty] | 6238 | 22 | 9.2568 | 6.5517
[7 empty] | 6239 | 23 | 5.3857 | 3.7406
[7 empty] | 6240 | 24 | 3.6704 | 2.495
[7 empty] | 6241 | 25 | 3.5706 | 2.4225
[7 empty] | 6242 | 26 | 3.4588 | 2.3413
[7 empty] | 6243 | 27 | 3.3555 | 2.2663
[7 empty] | 6244 | 28 | 3.4416 | 2.3288
[7 empty] | 6245 | 29 | 3.691 | 2.51
[7 empty] | 6246 | 30 | 3.9405 | 2.6911
[7 empty] | 6247 | 31 | 4.8093 | 3.3221
[7 empty] | 6248 | 32 | 5.1706 | 3.5844
[7 empty] | 6249 | 33 | 5.8502 | 4.0779
[7 empty] | 6250 | 34 | 6.7707 | 4.7464
[7 empty] | 6251 | 35 | 8.9987 | 6.3643
[7 empty] | 6252 | 36 | 10.0569 | 7.1327
[7 empty] | 6253 | 37 | 10.1343 | 7.1889
[7 empty] | 6254 | 38 | 10.2117 | 7.2451
[7 empty] | 6255 | 39 | 9.8762 | 7.0015
[7 empty] | 6256 | 40 | 10.9601 | 7.7886
[7 empty] | 6257 | 41 | 11.5279 | 8.2009
[7 empty] | 6258 | 42 | 11.5451 | 8.2134
[7 empty] | 6259 | 43 | 11.9236 | 8.4882
[7 empty] | 6260 | 44 | 13.1107 | 9.3503
[7 empty] | 6261 | 45 | 12.6978 | 9.0505
[7 empty] | 6262 | 46 | 9.8762 | 7.0015
[7 empty] | 6263 | 47 | 6.1771 | 4.3153
[7 empty] | 6264 | 48 | 4.6373 | 3.1971
[7 empty] | 6265 | 49 | 3.9577 | 2.7036
[7 empty] | 6266 | 50 | 3.6394 | 2.4725
[7 empty] | 6267 | 51 | 3.5276 | 2.3913
[7 empty] | 6268 | 52 | 3.562 | 2.4163
[7 empty] | 6269 | 53 | 3.5878 | 2.435
[7 empty] | 6270 | 54 | 4.1814 | 2.866
[7 empty] | 6271 | 55 | 5.3513 | 3.7156
[7 empty] | 6272 | 56 | 5.6008 | 3.8968
[7 empty] | 6273 | 57 | 6.5729 | 4.6027
[7 empty] | 6274 | 58 | 7.7084 | 5.4273
[7 empty] | 6275 | 59 | 8.9471 | 6.3268
[7 empty] | 6276 | 60 | 9.5923 | 6.7953
[7 empty] | 6277 | 61 | 10.2891 | 7.3013
[7 empty] | 6278 | 62 | 10.0827 | 7.1514
[7 empty] | 6279 | 63 | 10.6934 | 7.5949
[7 empty] | 6280 | 64 | 11.6655 | 8.3008
[7 empty] | 6281 | 65 | 12.3021 | 8.7631
[7 empty] | 6282 | 66 | 12.1989 | 8.6882
[7 empty] | 6283 | 67 | 12.9559 | 9.2379
[7 empty] | 6284 | 68 | 13.2054 | 9.419
[7 empty] | 6285 | 69 | 12.6806 | 9.038
[7 empty] | 6286 | 70 | 10.3235 | 7.3263
[7 empty] | 6287 | 71 | 5.6868 | 3.9592
[7 empty] | 6288 | 72 | 4.5734 | 3.1507
[7 empty] | 6289 | 73 | 3.8373 | 2.6162
[7 empty] | 6290 | 74 | 3.605 | 2.4475
[7 empty] | 6291 | 75 | 3.5018 | 2.3725
[7 empty] | 6292 | 76 | 3.4416 | 2.3288
[7 empty] | 6293 | 77 | 3.6222 | 2.46
[7 empty] | 6294 | 78 | 4.0351 | 2.7598
[7 empty] | 6295 | 79 | 5.1793 | 3.5907
[7 empty] | 6296 | 80 | 5.3599 | 3.7219
[7 empty] | 6297 | 81 | 6.5729 | 4.6027
[7 empty] | 6298 | 82 | 7.6912 | 5.4148
[7 empty] | 6299 | 83 | 8.4482 | 5.9645
[7 empty] | 6300 | 84 | 9.7214 | 6.889
[7 empty] | 6301 | 85 | 9.4117 | 6.6642
[7 empty] | 6302 | 86 | 8.8869 | 6.2831
[7 empty] | 6303 | 87 | 9.3428 | 6.6142
[7 empty] | 6304 | 88 | 10.0224 | 7.1077
[7 empty] | 6305 | 89 | 11.4074 | 8.1134
[7 empty] | 6306 | 90 | 10.8053 | 7.6762
[7 empty] | 6307 | 91 | 11.5107 | 8.1884
[7 empty] | 6308 | 92 | 10.8913 | 7.7386
[7 empty] | 6309 | 93 | 8.4138 | 5.9395
[7 empty] | 6310 | 94 | 7.4847 | 5.2648
[7 empty] | 6311 | 95 | 5.575 | 3.878
[7 empty] | 6312 | 96 | 4.5599 | 3.1409
[7 empty] | 6313 | 97 | 4.5083 | 3.1034
[7 empty] | 6314 | 98 | 4.2072 | 2.8848
[7 empty] | 6315 | 99 | 4.147 | 2.841
[7 empty] | 6316 | 100 | 3.7857 | 2.5787
[7 empty] | 6317 | 101 | 3.7254 | 2.5349
[7 empty] | 6318 | 102 | 3.9663 | 2.7099
[7 empty] | 6319 | 103 | 4.7319 | 3.2658
[7 empty] | 6320 | 104 | 4.99 | 3.4532
[7 empty] | 6321 | 105 | 5.4889 | 3.8156
[7 empty] | 6322 | 106 | 6.9858 | 4.9025
[7 empty] | 6323 | 107 | 7.3471 | 5.1649
[7 empty] | 6324 | 108 | 8.9643 | 6.3393
[7 empty] | 6325 | 109 | 8.2847 | 5.8458
[7 empty] | 6326 | 110 | 7.8202 | 5.5085
[7 empty] | 6327 | 111 | 7.6568 | 5.3898
[7 empty] | 6328 | 112 | 7.7256 | 5.4398
[7 empty] | 6329 | 113 | 7.3729 | 5.1836
[7 empty] | 6330 | 114 | 7.5449 | 5.3086
[7 empty] | 6331 | 115 | 7.0804 | 4.9712
[7 empty] | 6332 | 116 | 7.7772 | 5.4772
[7 empty] | 6333 | 117 | 7.3471 | 5.1649
[7 empty] | 6334 | 118 | 6.5556 | 4.5902
[7 empty] | 6335 | 119 | 4.9212 | 3.4033
[7 empty] | 6336 | 120 | 4.5954 | 3.1667
[7 empty] | 6337 | 121 | 3.8459 | 2.6224
[7 empty] | 6338 | 122 | 3.4243 | 2.3163
[7 empty] | 6339 | 123 | 3.3383 | 2.2538
[7 empty] | 6340 | 124 | 3.3039 | 2.2289
[7 empty] | 6341 | 125 | 3.2609 | 2.1976
[7 empty] | 6342 | 126 | 3.4071 | 2.3038
[7 empty] | 6343 | 127 | 4.9556 | 3.4283
[7 empty] | 6344 | 128 | 6.5556 | 4.5902
[7 empty] | 6345 | 129 | 7.2524 | 5.0962
[7 empty] | 6346 | 130 | 7.6998 | 5.421
[7 empty] | 6347 | 131 | 7.8632 | 5.5397
[7 empty] | 6348 | 132 | 7.6051 | 5.3523
[7 empty] | 6349 | 133 | 8.2589 | 5.8271
[7 empty] | 6350 | 134 | 8.5686 | 6.052
[7 empty] | 6351 | 135 | 8.6374 | 6.1019
[7 empty] | 6352 | 136 | 7.803 | 5.496
[7 empty] | 6353 | 137 | 7.6998 | 5.421
[7 empty] | 6354 | 138 | 7.6482 | 5.3835
[7 empty] | 6355 | 139 | 7.3041 | 5.1337
[7 empty] | 6356 | 140 | 7.3127 | 5.1399
[7 empty] | 6357 | 141 | 6.6417 | 4.6526
[7 empty] | 6358 | 142 | 5.9879 | 4.1779
[7 empty] | 6359 | 143 | 5.0846 | 3.522
[7 empty] | 6360 | 144 | 4.4566 | 3.0659
[7 empty] | 6361 | 145 | 3.9749 | 2.7161
[7 empty] | 6362 | 146 | 3.7598 | 2.5599
[7 empty] | 6363 | 147 | 3.691 | 2.51
[7 empty] | 6364 | 148 | 3.6824 | 2.5037
[7 empty] | 6365 | 149 | 3.6824 | 2.5037
[7 empty] | 6366 | 150 | 3.691 | 2.51
[7 empty] | 6367 | 151 | 4.8007 | 3.3158
[7 empty] | 6368 | 152 | 6.3664 | 4.4527
[7 empty] | 6369 | 153 | 6.9944 | 4.9088
[7 empty] | 6370 | 154 | 7.5707 | 5.3273
[7 empty] | 6371 | 155 | 7.4159 | 5.2149
[7 empty] | 6372 | 156 | 7.5879 | 5.3398
[7 empty] | 6373 | 157 | 8.3192 | 5.8708
[7 empty] | 6374 | 158 | 8.6546 | 6.1144
[7 empty] | 6375 | 159 | 8.9299 | 6.3143
[7 empty] | 6376 | 160 | 8.8009 | 6.2206
[7 empty] | 6377 | 161 | 9.5837 | 6.7891
[7 empty] | 6378 | 162 | 9.0762 | 6.4205
[7 empty] | 6379 | 163 | 9.4461 | 6.6891
[7 empty] | 6380 | 164 | 8.0611 | 5.6834
[7 empty] | 6381 | 165 | 11.2698 | 8.0135
[7 empty] | 6382 | 166 | 9.1708 | 6.4892
[7 empty] | 6383 | 167 | 5.4717 | 3.8031
[7 empty] | 6384 | 168 | 4.8093 | 3.3221
[7 empty] | 6385 | 1 | 3.3125 | 2.2351
[7 empty] | 6386 | 2 | 3.2007 | 2.1539
[7 empty] | 6387 | 3 | 3.1921 | 2.1476
[7 empty] | 6388 | 4 | 3.3297 | 2.2476
[7 empty] | 6389 | 5 | 3.3469 | 2.2601
[7 empty] | 6390 | 6 | 3.7857 | 2.5787
[7 empty] | 6391 | 7 | 4.5255 | 3.1159
[7 empty] | 6392 | 8 | 5.2137 | 3.6157
[7 empty] | 6393 | 9 | 5.1879 | 3.5969
[7 empty] | 6394 | 10 | 6.7449 | 4.7276
[7 empty] | 6395 | 11 | 8.8783 | 6.2768
[7 empty] | 6396 | 12 | 9.8676 | 6.9952
[7 empty] | 6397 | 13 | 10.2547 | 7.2763
[7 empty] | 6398 | 14 | 10.031 | 7.1139
[7 empty] | 6399 | 15 | 9.9364 | 7.0452
[7 empty] | 6400 | 16 | 11.1494 | 7.926
[7 empty] | 6401 | 17 | 12.5086 | 8.913
[7 empty] | 6402 | 18 | 12.2591 | 8.7319
[7 empty] | 6403 | 19 | 12.801 | 9.1254
[7 empty] | 6404 | 20 | 12.7322 | 9.0755
[7 empty] | 6405 | 21 | 13.3172 | 9.5002
[7 empty] | 6406 | 22 | 9.2568 | 6.5517
[7 empty] | 6407 | 23 | 5.3857 | 3.7406
[7 empty] | 6408 | 24 | 3.6704 | 2.495
[7 empty] | 6409 | 25 | 3.5706 | 2.4225
[7 empty] | 6410 | 26 | 3.4588 | 2.3413
[7 empty] | 6411 | 27 | 3.3555 | 2.2663
[7 empty] | 6412 | 28 | 3.4416 | 2.3288
[7 empty] | 6413 | 29 | 3.691 | 2.51
[7 empty] | 6414 | 30 | 3.9405 | 2.6911
[7 empty] | 6415 | 31 | 4.8093 | 3.3221
[7 empty] | 6416 | 32 | 5.1706 | 3.5844
[7 empty] | 6417 | 33 | 5.8502 | 4.0779
[7 empty] | 6418 | 34 | 6.7707 | 4.7464
[7 empty] | 6419 | 35 | 8.9987 | 6.3643
[7 empty] | 6420 | 36 | 10.0569 | 7.1327
[7 empty] | 6421 | 37 | 10.1343 | 7.1889
[7 empty] | 6422 | 38 | 10.2117 | 7.2451
[7 empty] | 6423 | 39 | 9.8762 | 7.0015
[7 empty] | 6424 | 40 | 10.9601 | 7.7886
[7 empty] | 6425 | 41 | 11.5279 | 8.2009
[7 empty] | 6426 | 42 | 11.5451 | 8.2134
[7 empty] | 6427 | 43 | 11.9236 | 8.4882
[7 empty] | 6428 | 44 | 13.1107 | 9.3503
[7 empty] | 6429 | 45 | 12.6978 | 9.0505
[7 empty] | 6430 | 46 | 9.8762 | 7.0015
[7 empty] | 6431 | 47 | 6.1771 | 4.3153
[7 empty] | 6432 | 48 | 4.6373 | 3.1971
[7 empty] | 6433 | 49 | 3.9577 | 2.7036
[7 empty] | 6434 | 50 | 3.6394 | 2.4725
[7 empty] | 6435 | 51 | 3.5276 | 2.3913
[7 empty] | 6436 | 52 | 3.562 | 2.4163
[7 empty] | 6437 | 53 | 3.5878 | 2.435
[7 empty] | 6438 | 54 | 4.1814 | 2.866
[7 empty] | 6439 | 55 | 5.3513 | 3.7156
[7 empty] | 6440 | 56 | 5.6008 | 3.8968
[7 empty] | 6441 | 57 | 6.5729 | 4.6027
[7 empty] | 6442 | 58 | 7.7084 | 5.4273
[7 empty] | 6443 | 59 | 8.9471 | 6.3268
[7 empty] | 6444 | 60 | 9.5923 | 6.7953
[7 empty] | 6445 | 61 | 10.2891 | 7.3013
[7 empty] | 6446 | 62 | 10.0827 | 7.1514
[7 empty] | 6447 | 63 | 10.6934 | 7.5949
[7 empty] | 6448 | 64 | 11.6655 | 8.3008
[7 empty] | 6449 | 65 | 12.3021 | 8.7631
[7 empty] | 6450 | 66 | 12.1989 | 8.6882
[7 empty] | 6451 | 67 | 12.9559 | 9.2379
[7 empty] | 6452 | 68 | 13.2054 | 9.419
[7 empty] | 6453 | 69 | 12.6806 | 9.038
[7 empty] | 6454 | 70 | 10.3235 | 7.3263
[7 empty] | 6455 | 71 | 5.6868 | 3.9592
[7 empty] | 6456 | 72 | 4.5734 | 3.1507
[7 empty] | 6457 | 73 | 3.8373 | 2.6162
[7 empty] | 6458 | 74 | 3.605 | 2.4475
[7 empty] | 6459 | 75 | 3.5018 | 2.3725
[7 empty] | 6460 | 76 | 3.4416 | 2.3288
[7 empty] | 6461 | 77 | 3.6222 | 2.46
[7 empty] | 6462 | 78 | 4.0351 | 2.7598
[7 empty] | 6463 | 79 | 5.1793 | 3.5907
[7 empty] | 6464 | 80 | 5.3599 | 3.7219
[7 empty] | 6465 | 81 | 6.5729 | 4.6027
[7 empty] | 6466 | 82 | 7.6912 | 5.4148
[7 empty] | 6467 | 83 | 8.4482 | 5.9645
[7 empty] | 6468 | 84 | 9.7214 | 6.889
[7 empty] | 6469 | 85 | 9.4117 | 6.6642
[7 empty] | 6470 | 86 | 8.8869 | 6.2831
[7 empty] | 6471 | 87 | 9.3428 | 6.6142
[7 empty] | 6472 | 88 | 10.0224 | 7.1077
[7 empty] | 6473 | 89 | 11.4074 | 8.1134
[7 empty] | 6474 | 90 | 10.8053 | 7.6762
[7 empty] | 6475 | 91 | 11.5107 | 8.1884
[7 empty] | 6476 | 92 | 10.8913 | 7.7386
[7 empty] | 6477 | 93 | 8.4138 | 5.9395
[7 empty] | 6478 | 94 | 7.4847 | 5.2648
[7 empty] | 6479 | 95 | 5.575 | 3.878
[7 empty] | 6480 | 96 | 4.5599 | 3.1409
[7 empty] | 6481 | 97 | 4.5083 | 3.1034
[7 empty] | 6482 | 98 | 4.2072 | 2.8848
[7 empty] | 6483 | 99 | 4.147 | 2.841
[7 empty] | 6484 | 100 | 3.7857 | 2.5787
[7 empty] | 6485 | 101 | 3.7254 | 2.5349
[7 empty] | 6486 | 102 | 3.9663 | 2.7099
[7 empty] | 6487 | 103 | 4.7319 | 3.2658
[7 empty] | 6488 | 104 | 4.99 | 3.4532
[7 empty] | 6489 | 105 | 5.4889 | 3.8156
[7 empty] | 6490 | 106 | 6.9858 | 4.9025
[7 empty] | 6491 | 107 | 7.3471 | 5.1649
[7 empty] | 6492 | 108 | 8.9643 | 6.3393
[7 empty] | 6493 | 109 | 8.2847 | 5.8458
[7 empty] | 6494 | 110 | 7.8202 | 5.5085
[7 empty] | 6495 | 111 | 7.6568 | 5.3898
[7 empty] | 6496 | 112 | 7.7256 | 5.4398
[7 empty] | 6497 | 113 | 7.3729 | 5.1836
[7 empty] | 6498 | 114 | 7.5449 | 5.3086
[7 empty] | 6499 | 115 | 7.0804 | 4.9712
[7 empty] | 6500 | 116 | 7.7772 | 5.4772
[7 empty] | 6501 | 117 | 7.3471 | 5.1649
[7 empty] | 6502 | 118 | 6.5556 | 4.5902
[7 empty] | 6503 | 119 | 4.9212 | 3.4033
[7 empty] | 6504 | 120 | 4.5954 | 3.1667
[7 empty] | 6505 | 121 | 3.8459 | 2.6224
[7 empty] | 6506 | 122 | 3.4243 | 2.3163
[7 empty] | 6507 | 123 | 3.3383 | 2.2538
[7 empty] | 6508 | 124 | 3.3039 | 2.2289
[7 empty] | 6509 | 125 | 3.2609 | 2.1976
[7 empty] | 6510 | 126 | 3.4071 | 2.3038
[7 empty] | 6511 | 127 | 4.9556 | 3.4283
[7 empty] | 6512 | 128 | 6.5556 | 4.5902
[7 empty] | 6513 | 129 | 7.2524 | 5.0962
[7 empty] | 6514 | 130 | 7.6998 | 5.421
[7 empty] | 6515 | 131 | 7.8632 | 5.5397
[7 empty] | 6516 | 132 | 7.6051 | 5.3523
[7 empty] | 6517 | 133 | 8.2589 | 5.8271
[7 empty] | 6518 | 134 | 8.5686 | 6.052
[7 empty] | 6519 | 135 | 8.6374 | 6.1019
[7 empty] | 6520 | 136 | 7.803 | 5.496
[7 empty] | 6521 | 137 | 7.6998 | 5.421
[7 empty] | 6522 | 138 | 7.6482 | 5.3835
[7 empty] | 6523 | 139 | 7.3041 | 5.1337
[7 empty] | 6524 | 140 | 7.3127 | 5.1399
[7 empty] | 6525 | 141 | 6.6417 | 4.6526
[7 empty] | 6526 | 142 | 5.9879 | 4.1779
[7 empty] | 6527 | 143 | 5.0846 | 3.522
[7 empty] | 6528 | 144 | 4.4566 | 3.0659
[7 empty] | 6529 | 145 | 3.9749 | 2.7161
[7 empty] | 6530 | 146 | 3.7598 | 2.5599
[7 empty] | 6531 | 147 | 3.691 | 2.51
[7 empty] | 6532 | 148 | 3.6824 | 2.5037
[7 empty] | 6533 | 149 | 3.6824 | 2.5037
[7 empty] | 6534 | 150 | 3.691 | 2.51
[7 empty] | 6535 | 151 | 4.8007 | 3.3158
[7 empty] | 6536 | 152 | 6.3664 | 4.4527
[7 empty] | 6537 | 153 | 6.9944 | 4.9088
[7 empty] | 6538 | 154 | 7.5707 | 5.3273
[7 empty] | 6539 | 155 | 7.4159 | 5.2149
[7 empty] | 6540 | 156 | 7.5879 | 5.3398
[7 empty] | 6541 | 157 | 8.3192 | 5.8708
[7 empty] | 6542 | 158 | 8.6546 | 6.1144
[7 empty] | 6543 | 159 | 8.9299 | 6.3143
[7 empty] | 6544 | 160 | 8.8009 | 6.2206
[7 empty] | 6545 | 161 | 9.5837 | 6.7891
[7 empty] | 6546 | 162 | 9.0762 | 6.4205
[7 empty] | 6547 | 163 | 9.4461 | 6.6891
[7 empty] | 6548 | 164 | 8.0611 | 5.6834
[7 empty] | 6549 | 165 | 11.2698 | 8.0135
[7 empty] | 6550 | 166 | 9.1708 | 6.4892
[7 empty] | 6551 | 167 | 5.4717 | 3.8031
[7 empty] | 6552 | 168 | 4.8093 | 3.3221
[7 empty] | 6553 | 1 | 3.3125 | 2.2351
[7 empty] | 6554 | 2 | 3.2007 | 2.1539
[7 empty] | 6555 | 3 | 3.1921 | 2.1476
[7 empty] | 6556 | 4 | 3.3297 | 2.2476
[7 empty] | 6557 | 5 | 3.3469 | 2.2601
[7 empty] | 6558 | 6 | 3.7857 | 2.5787
[7 empty] | 6559 | 7 | 4.5255 | 3.1159
[7 empty] | 6560 | 8 | 5.2137 | 3.6157
[7 empty] | 6561 | 9 | 5.1879 | 3.5969
[7 empty] | 6562 | 10 | 6.7449 | 4.7276
[7 empty] | 6563 | 11 | 8.8783 | 6.2768
[7 empty] | 6564 | 12 | 9.8676 | 6.9952
[7 empty] | 6565 | 13 | 10.2547 | 7.2763
[7 empty] | 6566 | 14 | 10.031 | 7.1139
[7 empty] | 6567 | 15 | 9.9364 | 7.0452
[7 empty] | 6568 | 16 | 11.1494 | 7.926
[7 empty] | 6569 | 17 | 12.5086 | 8.913
[7 empty] | 6570 | 18 | 12.2591 | 8.7319
[7 empty] | 6571 | 19 | 12.801 | 9.1254
[7 empty] | 6572 | 20 | 12.7322 | 9.0755
[7 empty] | 6573 | 21 | 13.3172 | 9.5002
[7 empty] | 6574 | 22 | 9.2568 | 6.5517
[7 empty] | 6575 | 23 | 5.3857 | 3.7406
[7 empty] | 6576 | 24 | 3.6704 | 2.495
[7 empty] | 6577 | 25 | 3.5706 | 2.4225
[7 empty] | 6578 | 26 | 3.4588 | 2.3413
[7 empty] | 6579 | 27 | 3.3555 | 2.2663
[7 empty] | 6580 | 28 | 3.4416 | 2.3288
[7 empty] | 6581 | 29 | 3.691 | 2.51
[7 empty] | 6582 | 30 | 3.9405 | 2.6911
[7 empty] | 6583 | 31 | 4.8093 | 3.3221
[7 empty] | 6584 | 32 | 5.1706 | 3.5844
[7 empty] | 6585 | 33 | 5.8502 | 4.0779
[7 empty] | 6586 | 34 | 6.7707 | 4.7464
[7 empty] | 6587 | 35 | 8.9987 | 6.3643
[7 empty] | 6588 | 36 | 10.0569 | 7.1327
[7 empty] | 6589 | 37 | 10.1343 | 7.1889
[7 empty] | 6590 | 38 | 10.2117 | 7.2451
[7 empty] | 6591 | 39 | 9.8762 | 7.0015
[7 empty] | 6592 | 40 | 10.9601 | 7.7886
[7 empty] | 6593 | 41 | 11.5279 | 8.2009
[7 empty] | 6594 | 42 | 11.5451 | 8.2134
[7 empty] | 6595 | 43 | 11.9236 | 8.4882
[7 empty] | 6596 | 44 | 13.1107 | 9.3503
[7 empty] | 6597 | 45 | 12.6978 | 9.0505
[7 empty] | 6598 | 46 | 9.8762 | 7.0015
[7 empty] | 6599 | 47 | 6.1771 | 4.3153
[7 empty] | 6600 | 48 | 4.6373 | 3.1971
[7 empty] | 6601 | 49 | 3.9577 | 2.7036
[7 empty] | 6602 | 50 | 3.6394 | 2.4725
[7 empty] | 6603 | 51 | 3.5276 | 2.3913
[7 empty] | 6604 | 52 | 3.562 | 2.4163
[7 empty] | 6605 | 53 | 3.5878 | 2.435
[7 empty] | 6606 | 54 | 4.1814 | 2.866
[7 empty] | 6607 | 55 | 5.3513 | 3.7156
[7 empty] | 6608 | 56 | 5.6008 | 3.8968
[7 empty] | 6609 | 57 | 6.5729 | 4.6027
[7 empty] | 6610 | 58 | 7.7084 | 5.4273
[7 empty] | 6611 | 59 | 8.9471 | 6.3268
[7 empty] | 6612 | 60 | 9.5923 | 6.7953
[7 empty] | 6613 | 61 | 10.2891 | 7.3013
[7 empty] | 6614 | 62 | 10.0827 | 7.1514
[7 empty] | 6615 | 63 | 10.6934 | 7.5949
[7 empty] | 6616 | 64 | 11.6655 | 8.3008
[7 empty] | 6617 | 65 | 12.3021 | 8.7631
[7 empty] | 6618 | 66 | 12.1989 | 8.6882
[7 empty] | 6619 | 67 | 12.9559 | 9.2379
[7 empty] | 6620 | 68 | 13.2054 | 9.419
[7 empty] | 6621 | 69 | 12.6806 | 9.038
[7 empty] | 6622 | 70 | 10.3235 | 7.3263
[7 empty] | 6623 | 71 | 5.6868 | 3.9592
[7 empty] | 6624 | 72 | 4.5734 | 3.1507
[7 empty] | 6625 | 73 | 3.8373 | 2.6162
[7 empty] | 6626 | 74 | 3.605 | 2.4475
[7 empty] | 6627 | 75 | 3.5018 | 2.3725
[7 empty] | 6628 | 76 | 3.4416 | 2.3288
[7 empty] | 6629 | 77 | 3.6222 | 2.46
[7 empty] | 6630 | 78 | 4.0351 | 2.7598
[7 empty] | 6631 | 79 | 5.1793 | 3.5907
[7 empty] | 6632 | 80 | 5.3599 | 3.7219
[7 empty] | 6633 | 81 | 6.5729 | 4.6027
[7 empty] | 6634 | 82 | 7.6912 | 5.4148
[7 empty] | 6635 | 83 | 8.4482 | 5.9645
[7 empty] | 6636 | 84 | 9.7214 | 6.889
[7 empty] | 6637 | 85 | 9.4117 | 6.6642
[7 empty] | 6638 | 86 | 8.8869 | 6.2831
[7 empty] | 6639 | 87 | 9.3428 | 6.6142
[7 empty] | 6640 | 88 | 10.0224 | 7.1077
[7 empty] | 6641 | 89 | 11.4074 | 8.1134
[7 empty] | 6642 | 90 | 10.8053 | 7.6762
[7 empty] | 6643 | 91 | 11.5107 | 8.1884
[7 empty] | 6644 | 92 | 10.8913 | 7.7386
[7 empty] | 6645 | 93 | 8.4138 | 5.9395
[7 empty] | 6646 | 94 | 7.4847 | 5.2648
[7 empty] | 6647 | 95 | 5.575 | 3.878
[7 empty] | 6648 | 96 | 4.5599 | 3.1409
[7 empty] | 6649 | 97 | 4.5083 | 3.1034
[7 empty] | 6650 | 98 | 4.2072 | 2.8848
[7 empty] | 6651 | 99 | 4.147 | 2.841
[7 empty] | 6652 | 100 | 3.7857 | 2.5787
[7 empty] | 6653 | 101 | 3.7254 | 2.5349
[7 empty] | 6654 | 102 | 3.9663 | 2.7099
[7 empty] | 6655 | 103 | 4.7319 | 3.2658
[7 empty] | 6656 | 104 | 4.99 | 3.4532
[7 empty] | 6657 | 105 | 5.4889 | 3.8156
[7 empty] | 6658 | 106 | 6.9858 | 4.9025
[7 empty] | 6659 | 107 | 7.3471 | 5.1649
[7 empty] | 6660 | 108 | 8.9643 | 6.3393
[7 empty] | 6661 | 109 | 8.2847 | 5.8458
[7 empty] | 6662 | 110 | 7.8202 | 5.5085
[7 empty] | 6663 | 111 | 7.6568 | 5.3898
[7 empty] | 6664 | 112 | 7.7256 | 5.4398
[7 empty] | 6665 | 113 | 7.3729 | 5.1836
[7 empty] | 6666 | 114 | 7.5449 | 5.3086
[7 empty] | 6667 | 115 | 7.0804 | 4.9712
[7 empty] | 6668 | 116 | 7.7772 | 5.4772
[7 empty] | 6669 | 117 | 7.3471 | 5.1649
[7 empty] | 6670 | 118 | 6.5556 | 4.5902
[7 empty] | 6671 | 119 | 4.9212 | 3.4033
[7 empty] | 6672 | 120 | 4.5954 | 3.1667
[7 empty] | 6673 | 121 | 3.8459 | 2.6224
[7 empty] | 6674 | 122 | 3.4243 | 2.3163
[7 empty] | 6675 | 123 | 3.3383 | 2.2538
[7 empty] | 6676 | 124 | 3.3039 | 2.2289
[7 empty] | 6677 | 125 | 3.2609 | 2.1976
[7 empty] | 6678 | 126 | 3.4071 | 2.3038
[7 empty] | 6679 | 127 | 4.9556 | 3.4283
[7 empty] | 6680 | 128 | 6.5556 | 4.5902
[7 empty] | 6681 | 129 | 7.2524 | 5.0962
[7 empty] | 6682 | 130 | 7.6998 | 5.421
[7 empty] | 6683 | 131 | 7.8632 | 5.5397
[7 empty] | 6684 | 132 | 7.6051 | 5.3523
[7 empty] | 6685 | 133 | 8.2589 | 5.8271
[7 empty] | 6686 | 134 | 8.5686 | 6.052
[7 empty] | 6687 | 135 | 8.6374 | 6.1019
[7 empty] | 6688 | 136 | 7.803 | 5.496
[7 empty] | 6689 | 137 | 7.6998 | 5.421
[7 empty] | 6690 | 138 | 7.6482 | 5.3835
[7 empty] | 6691 | 139 | 7.3041 | 5.1337
[7 empty] | 6692 | 140 | 7.3127 | 5.1399
[7 empty] | 6693 | 141 | 6.6417 | 4.6526
[7 empty] | 6694 | 142 | 5.9879 | 4.1779
[7 empty] | 6695 | 143 | 5.0846 | 3.522
[7 empty] | 6696 | 144 | 4.4566 | 3.0659
[7 empty] | 6697 | 145 | 3.9749 | 2.7161
[7 empty] | 6698 | 146 | 3.7598 | 2.5599
[7 empty] | 6699 | 147 | 3.691 | 2.51
[7 empty] | 6700 | 148 | 3.6824 | 2.5037
[7 empty] | 6701 | 149 | 3.6824 | 2.5037
[7 empty] | 6702 | 150 | 3.691 | 2.51
[7 empty] | 6703 | 151 | 4.8007 | 3.3158
[7 empty] | 6704 | 152 | 6.3664 | 4.4527
[7 empty] | 6705 | 153 | 6.9944 | 4.9088
[7 empty] | 6706 | 154 | 7.5707 | 5.3273
[7 empty] | 6707 | 155 | 7.4159 | 5.2149
[7 empty] | 6708 | 156 | 7.5879 | 5.3398
[7 empty] | 6709 | 157 | 8.3192 | 5.8708
[7 empty] | 6710 | 158 | 8.6546 | 6.1144
[7 empty] | 6711 | 159 | 8.9299 | 6.3143
[7 empty] | 6712 | 160 | 8.8009 | 6.2206
[7 empty] | 6713 | 161 | 9.5837 | 6.7891
[7 empty] | 6714 | 162 | 9.0762 | 6.4205
[7 empty] | 6715 | 163 | 9.4461 | 6.6891
[7 empty] | 6716 | 164 | 8.0611 | 5.6834
[7 empty] | 6717 | 165 | 11.2698 | 8.0135
[7 empty] | 6718 | 166 | 9.1708 | 6.4892
[7 empty] | 6719 | 167 | 5.4717 | 3.8031
[7 empty] | 6720 | 168 | 4.8093 | 3.3221
[7 empty] | 6721 | 1 | 3.3125 | 2.2351
[7 empty] | 6722 | 2 | 3.2007 | 2.1539
[7 empty] | 6723 | 3 | 3.1921 | 2.1476
[7 empty] | 6724 | 4 | 3.3297 | 2.2476
[7 empty] | 6725 | 5 | 3.3469 | 2.2601
[7 empty] | 6726 | 6 | 3.7857 | 2.5787
[7 empty] | 6727 | 7 | 4.5255 | 3.1159
[7 empty] | 6728 | 8 | 5.2137 | 3.6157
[7 empty] | 6729 | 9 | 5.1879 | 3.5969
[7 empty] | 6730 | 10 | 6.7449 | 4.7276
[7 empty] | 6731 | 11 | 8.8783 | 6.2768
[7 empty] | 6732 | 12 | 9.8676 | 6.9952
[7 empty] | 6733 | 13 | 10.2547 | 7.2763
[7 empty] | 6734 | 14 | 10.031 | 7.1139
[7 empty] | 6735 | 15 | 9.9364 | 7.0452
[7 empty] | 6736 | 16 | 11.1494 | 7.926
[7 empty] | 6737 | 17 | 12.5086 | 8.913
[7 empty] | 6738 | 18 | 12.2591 | 8.7319
[7 empty] | 6739 | 19 | 12.801 | 9.1254
[7 empty] | 6740 | 20 | 12.7322 | 9.0755
[7 empty] | 6741 | 21 | 13.3172 | 9.5002
[7 empty] | 6742 | 22 | 9.2568 | 6.5517
[7 empty] | 6743 | 23 | 5.3857 | 3.7406
[7 empty] | 6744 | 24 | 3.6704 | 2.495
[7 empty] | 6745 | 25 | 3.5706 | 2.4225
[7 empty] | 6746 | 26 | 3.4588 | 2.3413
[7 empty] | 6747 | 27 | 3.3555 | 2.2663
[7 empty] | 6748 | 28 | 3.4416 | 2.3288
[7 empty] | 6749 | 29 | 3.691 | 2.51
[7 empty] | 6750 | 30 | 3.9405 | 2.6911
[7 empty] | 6751 | 31 | 4.8093 | 3.3221
[7 empty] | 6752 | 32 | 5.1706 | 3.5844
[7 empty] | 6753 | 33 | 5.8502 | 4.0779
[7 empty] | 6754 | 34 | 6.7707 | 4.7464
[7 empty] | 6755 | 35 | 8.9987 | 6.3643
[7 empty] | 6756 | 36 | 10.0569 | 7.1327
[7 empty] | 6757 | 37 | 10.1343 | 7.1889
[7 empty] | 6758 | 38 | 10.2117 | 7.2451
[7 empty] | 6759 | 39 | 9.8762 | 7.0015
[7 empty] | 6760 | 40 | 10.9601 | 7.7886
[7 empty] | 6761 | 41 | 11.5279 | 8.2009
[7 empty] | 6762 | 42 | 11.5451 | 8.2134
[7 empty] | 6763 | 43 | 11.9236 | 8.4882
[7 empty] | 6764 | 44 | 13.1107 | 9.3503
[7 empty] | 6765 | 45 | 12.6978 | 9.0505
[7 empty] | 6766 | 46 | 9.8762 | 7.0015
[7 empty] | 6767 | 47 | 6.1771 | 4.3153
[7 empty] | 6768 | 48 | 4.6373 | 3.1971
[7 empty] | 6769 | 49 | 3.9577 | 2.7036
[7 empty] | 6770 | 50 | 3.6394 | 2.4725
[7 empty] | 6771 | 51 | 3.5276 | 2.3913
[7 empty] | 6772 | 52 | 3.562 | 2.4163
[7 empty] | 6773 | 53 | 3.5878 | 2.435
[7 empty] | 6774 | 54 | 4.1814 | 2.866
[7 empty] | 6775 | 55 | 5.3513 | 3.7156
[7 empty] | 6776 | 56 | 5.6008 | 3.8968
[7 empty] | 6777 | 57 | 6.5729 | 4.6027
[7 empty] | 6778 | 58 | 7.7084 | 5.4273
[7 empty] | 6779 | 59 | 8.9471 | 6.3268
[7 empty] | 6780 | 60 | 9.5923 | 6.7953
[7 empty] | 6781 | 61 | 10.2891 | 7.3013
[7 empty] | 6782 | 62 | 10.0827 | 7.1514
[7 empty] | 6783 | 63 | 10.6934 | 7.5949
[7 empty] | 6784 | 64 | 11.6655 | 8.3008
[7 empty] | 6785 | 65 | 12.3021 | 8.7631
[7 empty] | 6786 | 66 | 12.1989 | 8.6882
[7 empty] | 6787 | 67 | 12.9559 | 9.2379
[7 empty] | 6788 | 68 | 13.2054 | 9.419
[7 empty] | 6789 | 69 | 12.6806 | 9.038
[7 empty] | 6790 | 70 | 10.3235 | 7.3263
[7 empty] | 6791 | 71 | 5.6868 | 3.9592
[7 empty] | 6792 | 72 | 4.5734 | 3.1507
[7 empty] | 6793 | 73 | 3.8373 | 2.6162
[7 empty] | 6794 | 74 | 3.605 | 2.4475
[7 empty] | 6795 | 75 | 3.5018 | 2.3725
[7 empty] | 6796 | 76 | 3.4416 | 2.3288
[7 empty] | 6797 | 77 | 3.6222 | 2.46
[7 empty] | 6798 | 78 | 4.0351 | 2.7598
[7 empty] | 6799 | 79 | 5.1793 | 3.5907
[7 empty] | 6800 | 80 | 5.3599 | 3.7219
[7 empty] | 6801 | 81 | 6.5729 | 4.6027
[7 empty] | 6802 | 82 | 7.6912 | 5.4148
[7 empty] | 6803 | 83 | 8.4482 | 5.9645
[7 empty] | 6804 | 84 | 9.7214 | 6.889
[7 empty] | 6805 | 85 | 9.4117 | 6.6642
[7 empty] | 6806 | 86 | 8.8869 | 6.2831
[7 empty] | 6807 | 87 | 9.3428 | 6.6142
[7 empty] | 6808 | 88 | 10.0224 | 7.1077
[7 empty] | 6809 | 89 | 11.4074 | 8.1134
[7 empty] | 6810 | 90 | 10.8053 | 7.6762
[7 empty] | 6811 | 91 | 11.5107 | 8.1884
[7 empty] | 6812 | 92 | 10.8913 | 7.7386
[7 empty] | 6813 | 93 | 8.4138 | 5.9395
[7 empty] | 6814 | 94 | 7.4847 | 5.2648
[7 empty] | 6815 | 95 | 5.575 | 3.878
[7 empty] | 6816 | 96 | 4.5599 | 3.1409
[7 empty] | 6817 | 97 | 4.5083 | 3.1034
[7 empty] | 6818 | 98 | 4.2072 | 2.8848
[7 empty] | 6819 | 99 | 4.147 | 2.841
[7 empty] | 6820 | 100 | 3.7857 | 2.5787
[7 empty] | 6821 | 101 | 3.7254 | 2.5349
[7 empty] | 6822 | 102 | 3.9663 | 2.7099
[7 empty] | 6823 | 103 | 4.7319 | 3.2658
[7 empty] | 6824 | 104 | 4.99 | 3.4532
[7 empty] | 6825 | 105 | 5.4889 | 3.8156
[7 empty] | 6826 | 106 | 6.9858 | 4.9025
[7 empty] | 6827 | 107 | 7.3471 | 5.1649
[7 empty] | 6828 | 108 | 8.9643 | 6.3393
[7 empty] | 6829 | 109 | 8.2847 | 5.8458
[7 empty] | 6830 | 110 | 7.8202 | 5.5085
[7 empty] | 6831 | 111 | 7.6568 | 5.3898
[7 empty] | 6832 | 112 | 7.7256 | 5.4398
[7 empty] | 6833 | 113 | 7.3729 | 5.1836
[7 empty] | 6834 | 114 | 7.5449 | 5.3086
[7 empty] | 6835 | 115 | 7.0804 | 4.9712
[7 empty] | 6836 | 116 | 7.7772 | 5.4772
[7 empty] | 6837 | 117 | 7.3471 | 5.1649
[7 empty] | 6838 | 118 | 6.5556 | 4.5902
[7 empty] | 6839 | 119 | 4.9212 | 3.4033
[7 empty] | 6840 | 120 | 4.5954 | 3.1667
[7 empty] | 6841 | 121 | 3.8459 | 2.6224
[7 empty] | 6842 | 122 | 3.4243 | 2.3163
[7 empty] | 6843 | 123 | 3.3383 | 2.2538
[7 empty] | 6844 | 124 | 3.3039 | 2.2289
[7 empty] | 6845 | 125 | 3.2609 | 2.1976
[7 empty] | 6846 | 126 | 3.4071 | 2.3038
[7 empty] | 6847 | 127 | 4.9556 | 3.4283
[7 empty] | 6848 | 128 | 6.5556 | 4.5902
[7 empty] | 6849 | 129 | 7.2524 | 5.0962
[7 empty] | 6850 | 130 | 7.6998 | 5.421
[7 empty] | 6851 | 131 | 7.8632 | 5.5397
[7 empty] | 6852 | 132 | 7.6051 | 5.3523
[7 empty] | 6853 | 133 | 8.2589 | 5.8271
[7 empty] | 6854 | 134 | 8.5686 | 6.052
[7 empty] | 6855 | 135 | 8.6374 | 6.1019
[7 empty] | 6856 | 136 | 7.803 | 5.496
[7 empty] | 6857 | 137 | 7.6998 | 5.421
[7 empty] | 6858 | 138 | 7.6482 | 5.3835
[7 empty] | 6859 | 139 | 7.3041 | 5.1337
[7 empty] | 6860 | 140 | 7.3127 | 5.1399
[7 empty] | 6861 | 141 | 6.6417 | 4.6526
[7 empty] | 6862 | 142 | 5.9879 | 4.1779
[7 empty] | 6863 | 143 | 5.0846 | 3.522
[7 empty] | 6864 | 144 | 4.4566 | 3.0659
[7 empty] | 6865 | 145 | 3.9749 | 2.7161
[7 empty] | 6866 | 146 | 3.7598 | 2.5599
[7 empty] | 6867 | 147 | 3.691 | 2.51
[7 empty] | 6868 | 148 | 3.6824 | 2.5037
[7 empty] | 6869 | 149 | 3.6824 | 2.5037
[7 empty] | 6870 | 150 | 3.691 | 2.51
[7 empty] | 6871 | 151 | 4.8007 | 3.3158
[7 empty] | 6872 | 152 | 6.3664 | 4.4527
[7 empty] | 6873 | 153 | 6.9944 | 4.9088
[7 empty] | 6874 | 154 | 7.5707 | 5.3273
[7 empty] | 6875 | 155 | 7.4159 | 5.2149
[7 empty] | 6876 | 156 | 7.5879 | 5.3398
[7 empty] | 6877 | 157 | 8.3192 | 5.8708
[7 empty] | 6878 | 158 | 8.6546 | 6.1144
[7 empty] | 6879 | 159 | 8.9299 | 6.3143
[7 empty] | 6880 | 160 | 8.8009 | 6.2206
[7 empty] | 6881 | 161 | 9.5837 | 6.7891
[7 empty] | 6882 | 162 | 9.0762 | 6.4205
[7 empty] | 6883 | 163 | 9.4461 | 6.6891
[7 empty] | 6884 | 164 | 8.0611 | 5.6834
[7 empty] | 6885 | 165 | 11.2698 | 8.0135
[7 empty] | 6886 | 166 | 9.1708 | 6.4892
[7 empty] | 6887 | 167 | 5.4717 | 3.8031
[7 empty] | 6888 | 168 | 4.8093 | 3.3221
[7 empty] | 6889 | 1 | 3.3125 | 2.2351
[7 empty] | 6890 | 2 | 3.2007 | 2.1539
[7 empty] | 6891 | 3 | 3.1921 | 2.1476
[7 empty] | 6892 | 4 | 3.3297 | 2.2476
[7 empty] | 6893 | 5 | 3.3469 | 2.2601
[7 empty] | 6894 | 6 | 3.7857 | 2.5787
[7 empty] | 6895 | 7 | 4.5255 | 3.1159
[7 empty] | 6896 | 8 | 5.2137 | 3.6157
[7 empty] | 6897 | 9 | 5.1879 | 3.5969
[7 empty] | 6898 | 10 | 6.7449 | 4.7276
[7 empty] | 6899 | 11 | 8.8783 | 6.2768
[7 empty] | 6900 | 12 | 9.8676 | 6.9952
[7 empty] | 6901 | 13 | 10.2547 | 7.2763
[7 empty] | 6902 | 14 | 10.031 | 7.1139
[7 empty] | 6903 | 15 | 9.9364 | 7.0452
[7 empty] | 6904 | 16 | 11.1494 | 7.926
[7 empty] | 6905 | 17 | 12.5086 | 8.913
[7 empty] | 6906 | 18 | 12.2591 | 8.7319
[7 empty] | 6907 | 19 | 12.801 | 9.1254
[7 empty] | 6908 | 20 | 12.7322 | 9.0755
[7 empty] | 6909 | 21 | 13.3172 | 9.5002
[7 empty] | 6910 | 22 | 9.2568 | 6.5517
[7 empty] | 6911 | 23 | 5.3857 | 3.7406
[7 empty] | 6912 | 24 | 3.6704 | 2.495
[7 empty] | 6913 | 25 | 3.5706 | 2.4225
[7 empty] | 6914 | 26 | 3.4588 | 2.3413
[7 empty] | 6915 | 27 | 3.3555 | 2.2663
[7 empty] | 6916 | 28 | 3.4416 | 2.3288
[7 empty] | 6917 | 29 | 3.691 | 2.51
[7 empty] | 6918 | 30 | 3.9405 | 2.6911
[7 empty] | 6919 | 31 | 4.8093 | 3.3221
[7 empty] | 6920 | 32 | 5.1706 | 3.5844
[7 empty] | 6921 | 33 | 5.8502 | 4.0779
[7 empty] | 6922 | 34 | 6.7707 | 4.7464
[7 empty] | 6923 | 35 | 8.9987 | 6.3643
[7 empty] | 6924 | 36 | 10.0569 | 7.1327
[7 empty] | 6925 | 37 | 10.1343 | 7.1889
[7 empty] | 6926 | 38 | 10.2117 | 7.2451
[7 empty] | 6927 | 39 | 9.8762 | 7.0015
[7 empty] | 6928 | 40 | 10.9601 | 7.7886
[7 empty] | 6929 | 41 | 11.5279 | 8.2009
[7 empty] | 6930 | 42 | 11.5451 | 8.2134
[7 empty] | 6931 | 43 | 11.9236 | 8.4882
[7 empty] | 6932 | 44 | 13.1107 | 9.3503
[7 empty] | 6933 | 45 | 12.6978 | 9.0505
[7 empty] | 6934 | 46 | 9.8762 | 7.0015
[7 empty] | 6935 | 47 | 6.1771 | 4.3153
[7 empty] | 6936 | 48 | 4.6373 | 3.1971
[7 empty] | 6937 | 49 | 3.9577 | 2.7036
[7 empty] | 6938 | 50 | 3.6394 | 2.4725
[7 empty] | 6939 | 51 | 3.5276 | 2.3913
[7 empty] | 6940 | 52 | 3.562 | 2.4163
[7 empty] | 6941 | 53 | 3.5878 | 2.435
[7 empty] | 6942 | 54 | 4.1814 | 2.866
[7 empty] | 6943 | 55 | 5.3513 | 3.7156
[7 empty] | 6944 | 56 | 5.6008 | 3.8968
[7 empty] | 6945 | 57 | 6.5729 | 4.6027
[7 empty] | 6946 | 58 | 7.7084 | 5.4273
[7 empty] | 6947 | 59 | 8.9471 | 6.3268
[7 empty] | 6948 | 60 | 9.5923 | 6.7953
[7 empty] | 6949 | 61 | 10.2891 | 7.3013
[7 empty] | 6950 | 62 | 10.0827 | 7.1514
[7 empty] | 6951 | 63 | 10.6934 | 7.5949
[7 empty] | 6952 | 64 | 11.6655 | 8.3008
[7 empty] | 6953 | 65 | 12.3021 | 8.7631
[7 empty] | 6954 | 66 | 12.1989 | 8.6882
[7 empty] | 6955 | 67 | 12.9559 | 9.2379
[7 empty] | 6956 | 68 | 13.2054 | 9.419
[7 empty] | 6957 | 69 | 12.6806 | 9.038
[7 empty] | 6958 | 70 | 10.3235 | 7.3263
[7 empty] | 6959 | 71 | 5.6868 | 3.9592
[7 empty] | 6960 | 72 | 4.5734 | 3.1507
[7 empty] | 6961 | 73 | 3.8373 | 2.6162
[7 empty] | 6962 | 74 | 3.605 | 2.4475
[7 empty] | 6963 | 75 | 3.5018 | 2.3725
[7 empty] | 6964 | 76 | 3.4416 | 2.3288
[7 empty] | 6965 | 77 | 3.6222 | 2.46
[7 empty] | 6966 | 78 | 4.0351 | 2.7598
[7 empty] | 6967 | 79 | 5.1793 | 3.5907
[7 empty] | 6968 | 80 | 5.3599 | 3.7219
[7 empty] | 6969 | 81 | 6.5729 | 4.6027
[7 empty] | 6970 | 82 | 7.6912 | 5.4148
[7 empty] | 6971 | 83 | 8.4482 | 5.9645
[7 empty] | 6972 | 84 | 9.7214 | 6.889
[7 empty] | 6973 | 85 | 9.4117 | 6.6642
[7 empty] | 6974 | 86 | 8.8869 | 6.2831
[7 empty] | 6975 | 87 | 9.3428 | 6.6142
[7 empty] | 6976 | 88 | 10.0224 | 7.1077
[7 empty] | 6977 | 89 | 11.4074 | 8.1134
[7 empty] | 6978 | 90 | 10.8053 | 7.6762
[7 empty] | 6979 | 91 | 11.5107 | 8.1884
[7 empty] | 6980 | 92 | 10.8913 | 7.7386
[7 empty] | 6981 | 93 | 8.4138 | 5.9395
[7 empty] | 6982 | 94 | 7.4847 | 5.2648
[7 empty] | 6983 | 95 | 5.575 | 3.878
[7 empty] | 6984 | 96 | 4.5599 | 3.1409
[7 empty] | 6985 | 97 | 4.5083 | 3.1034
[7 empty] | 6986 | 98 | 4.2072 | 2.8848
[7 empty] | 6987 | 99 | 4.147 | 2.841
[7 empty] | 6988 | 100 | 3.7857 | 2.5787
[7 empty] | 6989 | 101 | 3.7254 | 2.5349
[7 empty] | 6990 | 102 | 3.9663 | 2.7099
[7 empty] | 6991 | 103 | 4.7319 | 3.2658
[7 empty] | 6992 | 104 | 4.99 | 3.4532
[7 empty] | 6993 | 105 | 5.4889 | 3.8156
[7 empty] | 6994 | 106 | 6.9858 | 4.9025
[7 empty] | 6995 | 107 | 7.3471 | 5.1649
[7 empty] | 6996 | 108 | 8.9643 | 6.3393
[7 empty] | 6997 | 109 | 8.2847 | 5.8458
[7 empty] | 6998 | 110 | 7.8202 | 5.5085
[7 empty] | 6999 | 111 | 7.6568 | 5.3898
[7 empty] | 7000 | 112 | 7.7256 | 5.4398
[7 empty] | 7001 | 113 | 7.3729 | 5.1836
[7 empty] | 7002 | 114 | 7.5449 | 5.3086
[7 empty] | 7003 | 115 | 7.0804 | 4.9712
[7 empty] | 7004 | 116 | 7.7772 | 5.4772
[7 empty] | 7005 | 117 | 7.3471 | 5.1649
[7 empty] | 7006 | 118 | 6.5556 | 4.5902
[7 empty] | 7007 | 119 | 4.9212 | 3.4033
[7 empty] | 7008 | 120 | 4.5954 | 3.1667
[7 empty] | 7009 | 121 | 3.8459 | 2.6224
[7 empty] | 7010 | 122 | 3.4243 | 2.3163
[7 empty] | 7011 | 123 | 3.3383 | 2.2538
[7 empty] | 7012 | 124 | 3.3039 | 2.2289
[7 empty] | 7013 | 125 | 3.2609 | 2.1976
[7 empty] | 7014 | 126 | 3.4071 | 2.3038
[7 empty] | 7015 | 127 | 4.9556 | 3.4283
[7 empty] | 7016 | 128 | 6.5556 | 4.5902
[7 empty] | 7017 | 129 | 7.2524 | 5.0962
[7 empty] | 7018 | 130 | 7.6998 | 5.421
[7 empty] | 7019 | 131 | 7.8632 | 5.5397
[7 empty] | 7020 | 132 | 7.6051 | 5.3523
[7 empty] | 7021 | 133 | 8.2589 | 5.8271
[7 empty] | 7022 | 134 | 8.5686 | 6.052
[7 empty] | 7023 | 135 | 8.6374 | 6.1019
[7 empty] | 7024 | 136 | 7.803 | 5.496
[7 empty] | 7025 | 137 | 7.6998 | 5.421
[7 empty] | 7026 | 138 | 7.6482 | 5.3835
[7 empty] | 7027 | 139 | 7.3041 | 5.1337
[7 empty] | 7028 | 140 | 7.3127 | 5.1399
[7 empty] | 7029 | 141 | 6.6417 | 4.6526
[7 empty] | 7030 | 142 | 5.9879 | 4.1779
[7 empty] | 7031 | 143 | 5.0846 | 3.522
[7 empty] | 7032 | 144 | 4.4566 | 3.0659
[7 empty] | 7033 | 145 | 3.9749 | 2.7161
[7 empty] | 7034 | 146 | 3.7598 | 2.5599
[7 empty] | 7035 | 147 | 3.691 | 2.51
[7 empty] | 7036 | 148 | 3.6824 | 2.5037
[7 empty] | 7037 | 149 | 3.6824 | 2.5037
[7 empty] | 7038 | 150 | 3.691 | 2.51
[7 empty] | 7039 | 151 | 4.8007 | 3.3158
[7 empty] | 7040 | 152 | 6.3664 | 4.4527
[7 empty] | 7041 | 153 | 6.9944 | 4.9088
[7 empty] | 7042 | 154 | 7.5707 | 5.3273
[7 empty] | 7043 | 155 | 7.4159 | 5.2149
[7 empty] | 7044 | 156 | 7.5879 | 5.3398
[7 empty] | 7045 | 157 | 8.3192 | 5.8708
[7 empty] | 7046 | 158 | 8.6546 | 6.1144
[7 empty] | 7047 | 159 | 8.9299 | 6.3143
[7 empty] | 7048 | 160 | 8.8009 | 6.2206
[7 empty] | 7049 | 161 | 9.5837 | 6.7891
[7 empty] | 7050 | 162 | 9.0762 | 6.4205
[7 empty] | 7051 | 163 | 9.4461 | 6.6891
[7 empty] | 7052 | 164 | 8.0611 | 5.6834
[7 empty] | 7053 | 165 | 11.2698 | 8.0135
[7 empty] | 7054 | 166 | 9.1708 | 6.4892
[7 empty] | 7055 | 167 | 5.4717 | 3.8031
[7 empty] | 7056 | 168 | 4.8093 | 3.3221
[7 empty] | 7057 | 1 | 3.3125 | 2.2351
[7 empty] | 7058 | 2 | 3.2007 | 2.1539
[7 empty] | 7059 | 3 | 3.1921 | 2.1476
[7 empty] | 7060 | 4 | 3.3297 | 2.2476
[7 empty] | 7061 | 5 | 3.3469 | 2.2601
[7 empty] | 7062 | 6 | 3.7857 | 2.5787
[7 empty] | 7063 | 7 | 4.5255 | 3.1159
[7 empty] | 7064 | 8 | 5.2137 | 3.6157
[7 empty] | 7065 | 9 | 5.1879 | 3.5969
[7 empty] | 7066 | 10 | 6.7449 | 4.7276
[7 empty] | 7067 | 11 | 8.8783 | 6.2768
[7 empty] | 7068 | 12 | 9.8676 | 6.9952
[7 empty] | 7069 | 13 | 10.2547 | 7.2763
[7 empty] | 7070 | 14 | 10.031 | 7.1139
[7 empty] | 7071 | 15 | 9.9364 | 7.0452
[7 empty] | 7072 | 16 | 11.1494 | 7.926
[7 empty] | 7073 | 17 | 12.5086 | 8.913
[7 empty] | 7074 | 18 | 12.2591 | 8.7319
[7 empty] | 7075 | 19 | 12.801 | 9.1254
[7 empty] | 7076 | 20 | 12.7322 | 9.0755
[7 empty] | 7077 | 21 | 13.3172 | 9.5002
[7 empty] | 7078 | 22 | 9.2568 | 6.5517
[7 empty] | 7079 | 23 | 5.3857 | 3.7406
[7 empty] | 7080 | 24 | 3.6704 | 2.495
[7 empty] | 7081 | 25 | 3.5706 | 2.4225
[7 empty] | 7082 | 26 | 3.4588 | 2.3413
[7 empty] | 7083 | 27 | 3.3555 | 2.2663
[7 empty] | 7084 | 28 | 3.4416 | 2.3288
[7 empty] | 7085 | 29 | 3.691 | 2.51
[7 empty] | 7086 | 30 | 3.9405 | 2.6911
[7 empty] | 7087 | 31 | 4.8093 | 3.3221
[7 empty] | 7088 | 32 | 5.1706 | 3.5844
[7 empty] | 7089 | 33 | 5.8502 | 4.0779
[7 empty] | 7090 | 34 | 6.7707 | 4.7464
[7 empty] | 7091 | 35 | 8.9987 | 6.3643
[7 empty] | 7092 | 36 | 10.0569 | 7.1327
[7 empty] | 7093 | 37 | 10.1343 | 7.1889
[7 empty] | 7094 | 38 | 10.2117 | 7.2451
[7 empty] | 7095 | 39 | 9.8762 | 7.0015
[7 empty] | 7096 | 40 | 10.9601 | 7.7886
[7 empty] | 7097 | 41 | 11.5279 | 8.2009
[7 empty] | 7098 | 42 | 11.5451 | 8.2134
[7 empty] | 7099 | 43 | 11.9236 | 8.4882
[7 empty] | 7100 | 44 | 13.1107 | 9.3503
[7 empty] | 7101 | 45 | 12.6978 | 9.0505
[7 empty] | 7102 | 46 | 9.8762 | 7.0015
[7 empty] | 7103 | 47 | 6.1771 | 4.3153
[7 empty] | 7104 | 48 | 4.6373 | 3.1971
[7 empty] | 7105 | 49 | 3.9577 | 2.7036
[7 empty] | 7106 | 50 | 3.6394 | 2.4725
[7 empty] | 7107 | 51 | 3.5276 | 2.3913
[7 empty] | 7108 | 52 | 3.562 | 2.4163
[7 empty] | 7109 | 53 | 3.5878 | 2.435
[7 empty] | 7110 | 54 | 4.1814 | 2.866
[7 empty] | 7111 | 55 | 5.3513 | 3.7156
[7 empty] | 7112 | 56 | 5.6008 | 3.8968
[7 empty] | 7113 | 57 | 6.5729 | 4.6027
[7 empty] | 7114 | 58 | 7.7084 | 5.4273
[7 empty] | 7115 | 59 | 8.9471 | 6.3268
[7 empty] | 7116 | 60 | 9.5923 | 6.7953
[7 empty] | 7117 | 61 | 10.2891 | 7.3013
[7 empty] | 7118 | 62 | 10.0827 | 7.1514
[7 empty] | 7119 | 63 | 10.6934 | 7.5949
[7 empty] | 7120 | 64 | 11.6655 | 8.3008
[7 empty] | 7121 | 65 | 12.3021 | 8.7631
[7 empty] | 7122 | 66 | 12.1989 | 8.6882
[7 empty] | 7123 | 67 | 12.9559 | 9.2379
[7 empty] | 7124 | 68 | 13.2054 | 9.419
[7 empty] | 7125 | 69 | 12.6806 | 9.038
[7 empty] | 7126 | 70 | 10.3235 | 7.3263
[7 empty] | 7127 | 71 | 5.6868 | 3.9592
[7 empty] | 7128 | 72 | 4.5734 | 3.1507
[7 empty] | 7129 | 73 | 3.8373 | 2.6162
[7 empty] | 7130 | 74 | 3.605 | 2.4475
[7 empty] | 7131 | 75 | 3.5018 | 2.3725
[7 empty] | 7132 | 76 | 3.4416 | 2.3288
[7 empty] | 7133 | 77 | 3.6222 | 2.46
[7 empty] | 7134 | 78 | 4.0351 | 2.7598
[7 empty] | 7135 | 79 | 5.1793 | 3.5907
[7 empty] | 7136 | 80 | 5.3599 | 3.7219
[7 empty] | 7137 | 81 | 6.5729 | 4.6027
[7 empty] | 7138 | 82 | 7.6912 | 5.4148
[7 empty] | 7139 | 83 | 8.4482 | 5.9645
[7 empty] | 7140 | 84 | 9.7214 | 6.889
[7 empty] | 7141 | 85 | 9.4117 | 6.6642
[7 empty] | 7142 | 86 | 8.8869 | 6.2831
[7 empty] | 7143 | 87 | 9.3428 | 6.6142
[7 empty] | 7144 | 88 | 10.0224 | 7.1077
[7 empty] | 7145 | 89 | 11.4074 | 8.1134
[7 empty] | 7146 | 90 | 10.8053 | 7.6762
[7 empty] | 7147 | 91 | 11.5107 | 8.1884
[7 empty] | 7148 | 92 | 10.8913 | 7.7386
[7 empty] | 7149 | 93 | 8.4138 | 5.9395
[7 empty] | 7150 | 94 | 7.4847 | 5.2648
[7 empty] | 7151 | 95 | 5.575 | 3.878
[7 empty] | 7152 | 96 | 4.5599 | 3.1409
[7 empty] | 7153 | 97 | 4.5083 | 3.1034
[7 empty] | 7154 | 98 | 4.2072 | 2.8848
[7 empty] | 7155 | 99 | 4.147 | 2.841
[7 empty] | 7156 | 100 | 3.7857 | 2.5787
[7 empty] | 7157 | 101 | 3.7254 | 2.5349
[7 empty] | 7158 | 102 | 3.9663 | 2.7099
[7 empty] | 7159 | 103 | 4.7319 | 3.2658
[7 empty] | 7160 | 104 | 4.99 | 3.4532
[7 empty] | 7161 | 105 | 5.4889 | 3.8156
[7 empty] | 7162 | 106 | 6.9858 | 4.9025
[7 empty] | 7163 | 107 | 7.3471 | 5.1649
[7 empty] | 7164 | 108 | 8.9643 | 6.3393
[7 empty] | 7165 | 109 | 8.2847 | 5.8458
[7 empty] | 7166 | 110 | 7.8202 | 5.5085
[7 empty] | 7167 | 111 | 7.6568 | 5.3898
[7 empty] | 7168 | 112 | 7.7256 | 5.4398
[7 empty] | 7169 | 113 | 7.3729 | 5.1836
[7 empty] | 7170 | 114 | 7.5449 | 5.3086
[7 empty] | 7171 | 115 | 7.0804 | 4.9712
[7 empty] | 7172 | 116 | 7.7772 | 5.4772
[7 empty] | 7173 | 117 | 7.3471 | 5.1649
[7 empty] | 7174 | 118 | 6.5556 | 4.5902
[7 empty] | 7175 | 119 | 4.9212 | 3.4033
[7 empty] | 7176 | 120 | 4.5954 | 3.1667
[7 empty] | 7177 | 121 | 3.8459 | 2.6224
[7 empty] | 7178 | 122 | 3.4243 | 2.3163
[7 empty] | 7179 | 123 | 3.3383 | 2.2538
[7 empty] | 7180 | 124 | 3.3039 | 2.2289
[7 empty] | 7181 | 125 | 3.2609 | 2.1976
[7 empty] | 7182 | 126 | 3.4071 | 2.3038
[7 empty] | 7183 | 127 | 4.9556 | 3.4283
[7 empty] | 7184 | 128 | 6.5556 | 4.5902
[7 empty] | 7185 | 129 | 7.2524 | 5.0962
[7 empty] | 7186 | 130 | 7.6998 | 5.421
[7 empty] | 7187 | 131 | 7.8632 | 5.5397
[7 empty] | 7188 | 132 | 7.6051 | 5.3523
[7 empty] | 7189 | 133 | 8.2589 | 5.8271
[7 empty] | 7190 | 134 | 8.5686 | 6.052
[7 empty] | 7191 | 135 | 8.6374 | 6.1019
[7 empty] | 7192 | 136 | 7.803 | 5.496
[7 empty] | 7193 | 137 | 7.6998 | 5.421
[7 empty] | 7194 | 138 | 7.6482 | 5.3835
[7 empty] | 7195 | 139 | 7.3041 | 5.1337
[7 empty] | 7196 | 140 | 7.3127 | 5.1399
[7 empty] | 7197 | 141 | 6.6417 | 4.6526
[7 empty] | 7198 | 142 | 5.9879 | 4.1779
[7 empty] | 7199 | 143 | 5.0846 | 3.522
[7 empty] | 7200 | 144 | 4.4566 | 3.0659
[7 empty] | 7201 | 145 | 3.9749 | 2.7161
[7 empty] | 7202 | 146 | 3.7598 | 2.5599
[7 empty] | 7203 | 147 | 3.691 | 2.51
[7 empty] | 7204 | 148 | 3.6824 | 2.5037
[7 empty] | 7205 | 149 | 3.6824 | 2.5037
[7 empty] | 7206 | 150 | 3.691 | 2.51
[7 empty] | 7207 | 151 | 4.8007 | 3.3158
[7 empty] | 7208 | 152 | 6.3664 | 4.4527
[7 empty] | 7209 | 153 | 6.9944 | 4.9088
[7 empty] | 7210 | 154 | 7.5707 | 5.3273
[7 empty] | 7211 | 155 | 7.4159 | 5.2149
[7 empty] | 7212 | 156 | 7.5879 | 5.3398
[7 empty] | 7213 | 157 | 8.3192 | 5.8708
[7 empty] | 7214 | 158 | 8.6546 | 6.1144
[7 empty] | 7215 | 159 | 8.9299 | 6.3143
[7 empty] | 7216 | 160 | 8.8009 | 6.2206
[7 empty] | 7217 | 161 | 9.5837 | 6.7891
[7 empty] | 7218 | 162 | 9.0762 | 6.4205
[7 empty] | 7219 | 163 | 9.4461 | 6.6891
[7 empty] | 7220 | 164 | 8.0611 | 5.6834
[7 empty] | 7221 | 165 | 11.2698 | 8.0135
[7 empty] | 7222 | 166 | 9.1708 | 6.4892
[7 empty] | 7223 | 167 | 5.4717 | 3.8031
[7 empty] | 7224 | 168 | 4.8093 | 3.3221
[7 empty] | 7225 | 1 | 3.3125 | 2.2351
[7 empty] | 7226 | 2 | 3.2007 | 2.1539
[7 empty] | 7227 | 3 | 3.1921 | 2.1476
[7 empty] | 7228 | 4 | 3.3297 | 2.2476
[7 empty] | 7229 | 5 | 3.3469 | 2.2601
[7 empty] | 7230 | 6 | 3.7857 | 2.5787
[7 empty] | 7231 | 7 | 4.5255 | 3.1159
[7 empty] | 7232 | 8 | 5.2137 | 3.6157
[7 empty] | 7233 | 9 | 5.1879 | 3.5969
[7 empty] | 7234 | 10 | 6.7449 | 4.7276
[7 empty] | 7235 | 11 | 8.8783 | 6.2768
[7 empty] | 7236 | 12 | 9.8676 | 6.9952
[7 empty] | 7237 | 13 | 10.2547 | 7.2763
[7 empty] | 7238 | 14 | 10.031 | 7.1139
[7 empty] | 7239 | 15 | 9.9364 | 7.0452
[7 empty] | 7240 | 16 | 11.1494 | 7.926
[7 empty] | 7241 | 17 | 12.5086 | 8.913
[7 empty] | 7242 | 18 | 12.2591 | 8.7319
[7 empty] | 7243 | 19 | 12.801 | 9.1254
[7 empty] | 7244 | 20 | 12.7322 | 9.0755
[7 empty] | 7245 | 21 | 13.3172 | 9.5002
[7 empty] | 7246 | 22 | 9.2568 | 6.5517
[7 empty] | 7247 | 23 | 5.3857 | 3.7406
[7 empty] | 7248 | 24 | 3.6704 | 2.495
[7 empty] | 7249 | 25 | 3.5706 | 2.4225
[7 empty] | 7250 | 26 | 3.4588 | 2.3413
[7 empty] | 7251 | 27 | 3.3555 | 2.2663
[7 empty] | 7252 | 28 | 3.4416 | 2.3288
[7 empty] | 7253 | 29 | 3.691 | 2.51
[7 empty] | 7254 | 30 | 3.9405 | 2.6911
[7 empty] | 7255 | 31 | 4.8093 | 3.3221
[7 empty] | 7256 | 32 | 5.1706 | 3.5844
[7 empty] | 7257 | 33 | 5.8502 | 4.0779
[7 empty] | 7258 | 34 | 6.7707 | 4.7464
[7 empty] | 7259 | 35 | 8.9987 | 6.3643
[7 empty] | 7260 | 36 | 10.0569 | 7.1327
[7 empty] | 7261 | 37 | 10.1343 | 7.1889
[7 empty] | 7262 | 38 | 10.2117 | 7.2451
[7 empty] | 7263 | 39 | 9.8762 | 7.0015
[7 empty] | 7264 | 40 | 10.9601 | 7.7886
[7 empty] | 7265 | 41 | 11.5279 | 8.2009
[7 empty] | 7266 | 42 | 11.5451 | 8.2134
[7 empty] | 7267 | 43 | 11.9236 | 8.4882
[7 empty] | 7268 | 44 | 13.1107 | 9.3503
[7 empty] | 7269 | 45 | 12.6978 | 9.0505
[7 empty] | 7270 | 46 | 9.8762 | 7.0015
[7 empty] | 7271 | 47 | 6.1771 | 4.3153
[7 empty] | 7272 | 48 | 4.6373 | 3.1971
[7 empty] | 7273 | 49 | 3.9577 | 2.7036
[7 empty] | 7274 | 50 | 3.6394 | 2.4725
[7 empty] | 7275 | 51 | 3.5276 | 2.3913
[7 empty] | 7276 | 52 | 3.562 | 2.4163
[7 empty] | 7277 | 53 | 3.5878 | 2.435
[7 empty] | 7278 | 54 | 4.1814 | 2.866
[7 empty] | 7279 | 55 | 5.3513 | 3.7156
[7 empty] | 7280 | 56 | 5.6008 | 3.8968
[7 empty] | 7281 | 57 | 6.5729 | 4.6027
[7 empty] | 7282 | 58 | 7.7084 | 5.4273
[7 empty] | 7283 | 59 | 8.9471 | 6.3268
[7 empty] | 7284 | 60 | 9.5923 | 6.7953
[7 empty] | 7285 | 61 | 10.2891 | 7.3013
[7 empty] | 7286 | 62 | 10.0827 | 7.1514
[7 empty] | 7287 | 63 | 10.6934 | 7.5949
[7 empty] | 7288 | 64 | 11.6655 | 8.3008
[7 empty] | 7289 | 65 | 12.3021 | 8.7631
[7 empty] | 7290 | 66 | 12.1989 | 8.6882
[7 empty] | 7291 | 67 | 12.9559 | 9.2379
[7 empty] | 7292 | 68 | 13.2054 | 9.419
[7 empty] | 7293 | 69 | 12.6806 | 9.038
[7 empty] | 7294 | 70 | 10.3235 | 7.3263
[7 empty] | 7295 | 71 | 5.6868 | 3.9592
[7 empty] | 7296 | 72 | 4.5734 | 3.1507
[7 empty] | 7297 | 73 | 3.8373 | 2.6162
[7 empty] | 7298 | 74 | 3.605 | 2.4475
[7 empty] | 7299 | 75 | 3.5018 | 2.3725
[7 empty] | 7300 | 76 | 3.4416 | 2.3288
[7 empty] | 7301 | 77 | 3.6222 | 2.46
[7 empty] | 7302 | 78 | 4.0351 | 2.7598
[7 empty] | 7303 | 79 | 5.1793 | 3.5907
[7 empty] | 7304 | 80 | 5.3599 | 3.7219
[7 empty] | 7305 | 81 | 6.5729 | 4.6027
[7 empty] | 7306 | 82 | 7.6912 | 5.4148
[7 empty] | 7307 | 83 | 8.4482 | 5.9645
[7 empty] | 7308 | 84 | 9.7214 | 6.889
[7 empty] | 7309 | 85 | 9.4117 | 6.6642
[7 empty] | 7310 | 86 | 8.8869 | 6.2831
[7 empty] | 7311 | 87 | 9.3428 | 6.6142
[7 empty] | 7312 | 88 | 10.0224 | 7.1077
[7 empty] | 7313 | 89 | 11.4074 | 8.1134
[7 empty] | 7314 | 90 | 10.8053 | 7.6762
[7 empty] | 7315 | 91 | 11.5107 | 8.1884
[7 empty] | 7316 | 92 | 10.8913 | 7.7386
[7 empty] | 7317 | 93 | 8.4138 | 5.9395
[7 empty] | 7318 | 94 | 7.4847 | 5.2648
[7 empty] | 7319 | 95 | 5.575 | 3.878
[7 empty] | 7320 | 96 | 4.5599 | 3.1409
[7 empty] | 7321 | 97 | 4.5083 | 3.1034
[7 empty] | 7322 | 98 | 4.2072 | 2.8848
[7 empty] | 7323 | 99 | 4.147 | 2.841
[7 empty] | 7324 | 100 | 3.7857 | 2.5787
[7 empty] | 7325 | 101 | 3.7254 | 2.5349
[7 empty] | 7326 | 102 | 3.9663 | 2.7099
[7 empty] | 7327 | 103 | 4.7319 | 3.2658
[7 empty] | 7328 | 104 | 4.99 | 3.4532
[7 empty] | 7329 | 105 | 5.4889 | 3.8156
[7 empty] | 7330 | 106 | 6.9858 | 4.9025
[7 empty] | 7331 | 107 | 7.3471 | 5.1649
[7 empty] | 7332 | 108 | 8.9643 | 6.3393
[7 empty] | 7333 | 109 | 8.2847 | 5.8458
[7 empty] | 7334 | 110 | 7.8202 | 5.5085
[7 empty] | 7335 | 111 | 7.6568 | 5.3898
[7 empty] | 7336 | 112 | 7.7256 | 5.4398
[7 empty] | 7337 | 113 | 7.3729 | 5.1836
[7 empty] | 7338 | 114 | 7.5449 | 5.3086
[7 empty] | 7339 | 115 | 7.0804 | 4.9712
[7 empty] | 7340 | 116 | 7.7772 | 5.4772
[7 empty] | 7341 | 117 | 7.3471 | 5.1649
[7 empty] | 7342 | 118 | 6.5556 | 4.5902
[7 empty] | 7343 | 119 | 4.9212 | 3.4033
[7 empty] | 7344 | 120 | 4.5954 | 3.1667
[7 empty] | 7345 | 121 | 3.8459 | 2.6224
[7 empty] | 7346 | 122 | 3.4243 | 2.3163
[7 empty] | 7347 | 123 | 3.3383 | 2.2538
[7 empty] | 7348 | 124 | 3.3039 | 2.2289
[7 empty] | 7349 | 125 | 3.2609 | 2.1976
[7 empty] | 7350 | 126 | 3.4071 | 2.3038
[7 empty] | 7351 | 127 | 4.9556 | 3.4283
[7 empty] | 7352 | 128 | 6.5556 | 4.5902
[7 empty] | 7353 | 129 | 7.2524 | 5.0962
[7 empty] | 7354 | 130 | 7.6998 | 5.421
[7 empty] | 7355 | 131 | 7.8632 | 5.5397
[7 empty] | 7356 | 132 | 7.6051 | 5.3523
[7 empty] | 7357 | 133 | 8.2589 | 5.8271
[7 empty] | 7358 | 134 | 8.5686 | 6.052
[7 empty] | 7359 | 135 | 8.6374 | 6.1019
[7 empty] | 7360 | 136 | 7.803 | 5.496
[7 empty] | 7361 | 137 | 7.6998 | 5.421
[7 empty] | 7362 | 138 | 7.6482 | 5.3835
[7 empty] | 7363 | 139 | 7.3041 | 5.1337
[7 empty] | 7364 | 140 | 7.3127 | 5.1399
[7 empty] | 7365 | 141 | 6.6417 | 4.6526
[7 empty] | 7366 | 142 | 5.9879 | 4.1779
[7 empty] | 7367 | 143 | 5.0846 | 3.522
[7 empty] | 7368 | 144 | 4.4566 | 3.0659
[7 empty] | 7369 | 145 | 3.9749 | 2.7161
[7 empty] | 7370 | 146 | 3.7598 | 2.5599
[7 empty] | 7371 | 147 | 3.691 | 2.51
[7 empty] | 7372 | 148 | 3.6824 | 2.5037
[7 empty] | 7373 | 149 | 3.6824 | 2.5037
[7 empty] | 7374 | 150 | 3.691 | 2.51
[7 empty] | 7375 | 151 | 4.8007 | 3.3158
[7 empty] | 7376 | 152 | 6.3664 | 4.4527
[7 empty] | 7377 | 153 | 6.9944 | 4.9088
[7 empty] | 7378 | 154 | 7.5707 | 5.3273
[7 empty] | 7379 | 155 | 7.4159 | 5.2149
[7 empty] | 7380 | 156 | 7.5879 | 5.3398
[7 empty] | 7381 | 157 | 8.3192 | 5.8708
[7 empty] | 7382 | 158 | 8.6546 | 6.1144
[7 empty] | 7383 | 159 | 8.9299 | 6.3143
[7 empty] | 7384 | 160 | 8.8009 | 6.2206
[7 empty] | 7385 | 161 | 9.5837 | 6.7891
[7 empty] | 7386 | 162 | 9.0762 | 6.4205
[7 empty] | 7387 | 163 | 9.4461 | 6.6891
[7 empty] | 7388 | 164 | 8.0611 | 5.6834
[7 empty] | 7389 | 165 | 11.2698 | 8.0135
[7 empty] | 7390 | 166 | 9.1708 | 6.4892
[7 empty] | 7391 | 167 | 5.4717 | 3.8031
[7 empty] | 7392 | 168 | 4.8093 | 3.3221
[7 empty] | 7393 | 1 | 3.3125 | 2.2351
[7 empty] | 7394 | 2 | 3.2007 | 2.1539
[7 empty] | 7395 | 3 | 3.1921 | 2.1476
[7 empty] | 7396 | 4 | 3.3297 | 2.2476
[7 empty] | 7397 | 5 | 3.3469 | 2.2601
[7 empty] | 7398 | 6 | 3.7857 | 2.5787
[7 empty] | 7399 | 7 | 4.5255 | 3.1159
[7 empty] | 7400 | 8 | 5.2137 | 3.6157
[7 empty] | 7401 | 9 | 5.1879 | 3.5969
[7 empty] | 7402 | 10 | 6.7449 | 4.7276
[7 empty] | 7403 | 11 | 8.8783 | 6.2768
[7 empty] | 7404 | 12 | 9.8676 | 6.9952
[7 empty] | 7405 | 13 | 10.2547 | 7.2763
[7 empty] | 7406 | 14 | 10.031 | 7.1139
[7 empty] | 7407 | 15 | 9.9364 | 7.0452
[7 empty] | 7408 | 16 | 11.1494 | 7.926
[7 empty] | 7409 | 17 | 12.5086 | 8.913
[7 empty] | 7410 | 18 | 12.2591 | 8.7319
[7 empty] | 7411 | 19 | 12.801 | 9.1254
[7 empty] | 7412 | 20 | 12.7322 | 9.0755
[7 empty] | 7413 | 21 | 13.3172 | 9.5002
[7 empty] | 7414 | 22 | 9.2568 | 6.5517
[7 empty] | 7415 | 23 | 5.3857 | 3.7406
[7 empty] | 7416 | 24 | 3.6704 | 2.495
[7 empty] | 7417 | 25 | 3.5706 | 2.4225
[7 empty] | 7418 | 26 | 3.4588 | 2.3413
[7 empty] | 7419 | 27 | 3.3555 | 2.2663
[7 empty] | 7420 | 28 | 3.4416 | 2.3288
[7 empty] | 7421 | 29 | 3.691 | 2.51
[7 empty] | 7422 | 30 | 3.9405 | 2.6911
[7 empty] | 7423 | 31 | 4.8093 | 3.3221
[7 empty] | 7424 | 32 | 5.1706 | 3.5844
[7 empty] | 7425 | 33 | 5.8502 | 4.0779
[7 empty] | 7426 | 34 | 6.7707 | 4.7464
[7 empty] | 7427 | 35 | 8.9987 | 6.3643
[7 empty] | 7428 | 36 | 10.0569 | 7.1327
[7 empty] | 7429 | 37 | 10.1343 | 7.1889
[7 empty] | 7430 | 38 | 10.2117 | 7.2451
[7 empty] | 7431 | 39 | 9.8762 | 7.0015
[7 empty] | 7432 | 40 | 10.9601 | 7.7886
[7 empty] | 7433 | 41 | 11.5279 | 8.2009
[7 empty] | 7434 | 42 | 11.5451 | 8.2134
[7 empty] | 7435 | 43 | 11.9236 | 8.4882
[7 empty] | 7436 | 44 | 13.1107 | 9.3503
[7 empty] | 7437 | 45 | 12.6978 | 9.0505
[7 empty] | 7438 | 46 | 9.8762 | 7.0015
[7 empty] | 7439 | 47 | 6.1771 | 4.3153
[7 empty] | 7440 | 48 | 4.6373 | 3.1971
[7 empty] | 7441 | 49 | 3.9577 | 2.7036
[7 empty] | 7442 | 50 | 3.6394 | 2.4725
[7 empty] | 7443 | 51 | 3.5276 | 2.3913
[7 empty] | 7444 | 52 | 3.562 | 2.4163
[7 empty] | 7445 | 53 | 3.5878 | 2.435
[7 empty] | 7446 | 54 | 4.1814 | 2.866
[7 empty] | 7447 | 55 | 5.3513 | 3.7156
[7 empty] | 7448 | 56 | 5.6008 | 3.8968
[7 empty] | 7449 | 57 | 6.5729 | 4.6027
[7 empty] | 7450 | 58 | 7.7084 | 5.4273
[7 empty] | 7451 | 59 | 8.9471 | 6.3268
[7 empty] | 7452 | 60 | 9.5923 | 6.7953
[7 empty] | 7453 | 61 | 10.2891 | 7.3013
[7 empty] | 7454 | 62 | 10.0827 | 7.1514
[7 empty] | 7455 | 63 | 10.6934 | 7.5949
[7 empty] | 7456 | 64 | 11.6655 | 8.3008
[7 empty] | 7457 | 65 | 12.3021 | 8.7631
[7 empty] | 7458 | 66 | 12.1989 | 8.6882
[7 empty] | 7459 | 67 | 12.9559 | 9.2379
[7 empty] | 7460 | 68 | 13.2054 | 9.419
[7 empty] | 7461 | 69 | 12.6806 | 9.038
[7 empty] | 7462 | 70 | 10.3235 | 7.3263
[7 empty] | 7463 | 71 | 5.6868 | 3.9592
[7 empty] | 7464 | 72 | 4.5734 | 3.1507
[7 empty] | 7465 | 73 | 3.8373 | 2.6162
[7 empty] | 7466 | 74 | 3.605 | 2.4475
[7 empty] | 7467 | 75 | 3.5018 | 2.3725
[7 empty] | 7468 | 76 | 3.4416 | 2.3288
[7 empty] | 7469 | 77 | 3.6222 | 2.46
[7 empty] | 7470 | 78 | 4.0351 | 2.7598
[7 empty] | 7471 | 79 | 5.1793 | 3.5907
[7 empty] | 7472 | 80 | 5.3599 | 3.7219
[7 empty] | 7473 | 81 | 6.5729 | 4.6027
[7 empty] | 7474 | 82 | 7.6912 | 5.4148
[7 empty] | 7475 | 83 | 8.4482 | 5.9645
[7 empty] | 7476 | 84 | 9.7214 | 6.889
[7 empty] | 7477 | 85 | 9.4117 | 6.6642
[7 empty] | 7478 | 86 | 8.8869 | 6.2831
[7 empty] | 7479 | 87 | 9.3428 | 6.6142
[7 empty] | 7480 | 88 | 10.0224 | 7.1077
[7 empty] | 7481 | 89 | 11.4074 | 8.1134
[7 empty] | 7482 | 90 | 10.8053 | 7.6762
[7 empty] | 7483 | 91 | 11.5107 | 8.1884
[7 empty] | 7484 | 92 | 10.8913 | 7.7386
[7 empty] | 7485 | 93 | 8.4138 | 5.9395
[7 empty] | 7486 | 94 | 7.4847 | 5.2648
[7 empty] | 7487 | 95 | 5.575 | 3.878
[7 empty] | 7488 | 96 | 4.5599 | 3.1409
[7 empty] | 7489 | 97 | 4.5083 | 3.1034
[7 empty] | 7490 | 98 | 4.2072 | 2.8848
[7 empty] | 7491 | 99 | 4.147 | 2.841
[7 empty] | 7492 | 100 | 3.7857 | 2.5787
[7 empty] | 7493 | 101 | 3.7254 | 2.5349
[7 empty] | 7494 | 102 | 3.9663 | 2.7099
[7 empty] | 7495 | 103 | 4.7319 | 3.2658
[7 empty] | 7496 | 104 | 4.99 | 3.4532
[7 empty] | 7497 | 105 | 5.4889 | 3.8156
[7 empty] | 7498 | 106 | 6.9858 | 4.9025
[7 empty] | 7499 | 107 | 7.3471 | 5.1649
[7 empty] | 7500 | 108 | 8.9643 | 6.3393
[7 empty] | 7501 | 109 | 8.2847 | 5.8458
[7 empty] | 7502 | 110 | 7.8202 | 5.5085
[7 empty] | 7503 | 111 | 7.6568 | 5.3898
[7 empty] | 7504 | 112 | 7.7256 | 5.4398
[7 empty] | 7505 | 113 | 7.3729 | 5.1836
[7 empty] | 7506 | 114 | 7.5449 | 5.3086
[7 empty] | 7507 | 115 | 7.0804 | 4.9712
[7 empty] | 7508 | 116 | 7.7772 | 5.4772
[7 empty] | 7509 | 117 | 7.3471 | 5.1649
[7 empty] | 7510 | 118 | 6.5556 | 4.5902
[7 empty] | 7511 | 119 | 4.9212 | 3.4033
[7 empty] | 7512 | 120 | 4.5954 | 3.1667
[7 empty] | 7513 | 121 | 3.8459 | 2.6224
[7 empty] | 7514 | 122 | 3.4243 | 2.3163
[7 empty] | 7515 | 123 | 3.3383 | 2.2538
[7 empty] | 7516 | 124 | 3.3039 | 2.2289
[7 empty] | 7517 | 125 | 3.2609 | 2.1976
[7 empty] | 7518 | 126 | 3.4071 | 2.3038
[7 empty] | 7519 | 127 | 4.9556 | 3.4283
[7 empty] | 7520 | 128 | 6.5556 | 4.5902
[7 empty] | 7521 | 129 | 7.2524 | 5.0962
[7 empty] | 7522 | 130 | 7.6998 | 5.421
[7 empty] | 7523 | 131 | 7.8632 | 5.5397
[7 empty] | 7524 | 132 | 7.6051 | 5.3523
[7 empty] | 7525 | 133 | 8.2589 | 5.8271
[7 empty] | 7526 | 134 | 8.5686 | 6.052
[7 empty] | 7527 | 135 | 8.6374 | 6.1019
[7 empty] | 7528 | 136 | 7.803 | 5.496
[7 empty] | 7529 | 137 | 7.6998 | 5.421
[7 empty] | 7530 | 138 | 7.6482 | 5.3835
[7 empty] | 7531 | 139 | 7.3041 | 5.1337
[7 empty] | 7532 | 140 | 7.3127 | 5.1399
[7 empty] | 7533 | 141 | 6.6417 | 4.6526
[7 empty] | 7534 | 142 | 5.9879 | 4.1779
[7 empty] | 7535 | 143 | 5.0846 | 3.522
[7 empty] | 7536 | 144 | 4.4566 | 3.0659
[7 empty] | 7537 | 145 | 3.9749 | 2.7161
[7 empty] | 7538 | 146 | 3.7598 | 2.5599
[7 empty] | 7539 | 147 | 3.691 | 2.51
[7 empty] | 7540 | 148 | 3.6824 | 2.5037
[7 empty] | 7541 | 149 | 3.6824 | 2.5037
[7 empty] | 7542 | 150 | 3.691 | 2.51
[7 empty] | 7543 | 151 | 4.8007 | 3.3158
[7 empty] | 7544 | 152 | 6.3664 | 4.4527
[7 empty] | 7545 | 153 | 6.9944 | 4.9088
[7 empty] | 7546 | 154 | 7.5707 | 5.3273
[7 empty] | 7547 | 155 | 7.4159 | 5.2149
[7 empty] | 7548 | 156 | 7.5879 | 5.3398
[7 empty] | 7549 | 157 | 8.3192 | 5.8708
[7 empty] | 7550 | 158 | 8.6546 | 6.1144
[7 empty] | 7551 | 159 | 8.9299 | 6.3143
[7 empty] | 7552 | 160 | 8.8009 | 6.2206
[7 empty] | 7553 | 161 | 9.5837 | 6.7891
[7 empty] | 7554 | 162 | 9.0762 | 6.4205
[7 empty] | 7555 | 163 | 9.4461 | 6.6891
[7 empty] | 7556 | 164 | 8.0611 | 5.6834
[7 empty] | 7557 | 165 | 11.2698 | 8.0135
[7 empty] | 7558 | 166 | 9.1708 | 6.4892
[7 empty] | 7559 | 167 | 5.4717 | 3.8031
[7 empty] | 7560 | 168 | 4.8093 | 3.3221
[7 empty] | 7561 | 1 | 3.3125 | 2.2351
[7 empty] | 7562 | 2 | 3.2007 | 2.1539
[7 empty] | 7563 | 3 | 3.1921 | 2.1476
[7 empty] | 7564 | 4 | 3.3297 | 2.2476
[7 empty] | 7565 | 5 | 3.3469 | 2.2601
[7 empty] | 7566 | 6 | 3.7857 | 2.5787
[7 empty] | 7567 | 7 | 4.5255 | 3.1159
[7 empty] | 7568 | 8 | 5.2137 | 3.6157
[7 empty] | 7569 | 9 | 5.1879 | 3.5969
[7 empty] | 7570 | 10 | 6.7449 | 4.7276
[7 empty] | 7571 | 11 | 8.8783 | 6.2768
[7 empty] | 7572 | 12 | 9.8676 | 6.9952
[7 empty] | 7573 | 13 | 10.2547 | 7.2763
[7 empty] | 7574 | 14 | 10.031 | 7.1139
[7 empty] | 7575 | 15 | 9.9364 | 7.0452
[7 empty] | 7576 | 16 | 11.1494 | 7.926
[7 empty] | 7577 | 17 | 12.5086 | 8.913
[7 empty] | 7578 | 18 | 12.2591 | 8.7319
[7 empty] | 7579 | 19 | 12.801 | 9.1254
[7 empty] | 7580 | 20 | 12.7322 | 9.0755
[7 empty] | 7581 | 21 | 13.3172 | 9.5002
[7 empty] | 7582 | 22 | 9.2568 | 6.5517
[7 empty] | 7583 | 23 | 5.3857 | 3.7406
[7 empty] | 7584 | 24 | 3.6704 | 2.495
[7 empty] | 7585 | 25 | 3.5706 | 2.4225
[7 empty] | 7586 | 26 | 3.4588 | 2.3413
[7 empty] | 7587 | 27 | 3.3555 | 2.2663
[7 empty] | 7588 | 28 | 3.4416 | 2.3288
[7 empty] | 7589 | 29 | 3.691 | 2.51
[7 empty] | 7590 | 30 | 3.9405 | 2.6911
[7 empty] | 7591 | 31 | 4.8093 | 3.3221
[7 empty] | 7592 | 32 | 5.1706 | 3.5844
[7 empty] | 7593 | 33 | 5.8502 | 4.0779
[7 empty] | 7594 | 34 | 6.7707 | 4.7464
[7 empty] | 7595 | 35 | 8.9987 | 6.3643
[7 empty] | 7596 | 36 | 10.0569 | 7.1327
[7 empty] | 7597 | 37 | 10.1343 | 7.1889
[7 empty] | 7598 | 38 | 10.2117 | 7.2451
[7 empty] | 7599 | 39 | 9.8762 | 7.0015
[7 empty] | 7600 | 40 | 10.9601 | 7.7886
[7 empty] | 7601 | 41 | 11.5279 | 8.2009
[7 empty] | 7602 | 42 | 11.5451 | 8.2134
[7 empty] | 7603 | 43 | 11.9236 | 8.4882
[7 empty] | 7604 | 44 | 13.1107 | 9.3503
[7 empty] | 7605 | 45 | 12.6978 | 9.0505
[7 empty] | 7606 | 46 | 9.8762 | 7.0015
[7 empty] | 7607 | 47 | 6.1771 | 4.3153
[7 empty] | 7608 | 48 | 4.6373 | 3.1971
[7 empty] | 7609 | 49 | 3.9577 | 2.7036
[7 empty] | 7610 | 50 | 3.6394 | 2.4725
[7 empty] | 7611 | 51 | 3.5276 | 2.3913
[7 empty] | 7612 | 52 | 3.562 | 2.4163
[7 empty] | 7613 | 53 | 3.5878 | 2.435
[7 empty] | 7614 | 54 | 4.1814 | 2.866
[7 empty] | 7615 | 55 | 5.3513 | 3.7156
[7 empty] | 7616 | 56 | 5.6008 | 3.8968
[7 empty] | 7617 | 57 | 6.5729 | 4.6027
[7 empty] | 7618 | 58 | 7.7084 | 5.4273
[7 empty] | 7619 | 59 | 8.9471 | 6.3268
[7 empty] | 7620 | 60 | 9.5923 | 6.7953
[7 empty] | 7621 | 61 | 10.2891 | 7.3013
[7 empty] | 7622 | 62 | 10.0827 | 7.1514
[7 empty] | 7623 | 63 | 10.6934 | 7.5949
[7 empty] | 7624 | 64 | 11.6655 | 8.3008
[7 empty] | 7625 | 65 | 12.3021 | 8.7631
[7 empty] | 7626 | 66 | 12.1989 | 8.6882
[7 empty] | 7627 | 67 | 12.9559 | 9.2379
[7 empty] | 7628 | 68 | 13.2054 | 9.419
[7 empty] | 7629 | 69 | 12.6806 | 9.038
[7 empty] | 7630 | 70 | 10.3235 | 7.3263
[7 empty] | 7631 | 71 | 5.6868 | 3.9592
[7 empty] | 7632 | 72 | 4.5734 | 3.1507
[7 empty] | 7633 | 73 | 3.8373 | 2.6162
[7 empty] | 7634 | 74 | 3.605 | 2.4475
[7 empty] | 7635 | 75 | 3.5018 | 2.3725
[7 empty] | 7636 | 76 | 3.4416 | 2.3288
[7 empty] | 7637 | 77 | 3.6222 | 2.46
[7 empty] | 7638 | 78 | 4.0351 | 2.7598
[7 empty] | 7639 | 79 | 5.1793 | 3.5907
[7 empty] | 7640 | 80 | 5.3599 | 3.7219
[7 empty] | 7641 | 81 | 6.5729 | 4.6027
[7 empty] | 7642 | 82 | 7.6912 | 5.4148
[7 empty] | 7643 | 83 | 8.4482 | 5.9645
[7 empty] | 7644 | 84 | 9.7214 | 6.889
[7 empty] | 7645 | 85 | 9.4117 | 6.6642
[7 empty] | 7646 | 86 | 8.8869 | 6.2831
[7 empty] | 7647 | 87 | 9.3428 | 6.6142
[7 empty] | 7648 | 88 | 10.0224 | 7.1077
[7 empty] | 7649 | 89 | 11.4074 | 8.1134
[7 empty] | 7650 | 90 | 10.8053 | 7.6762
[7 empty] | 7651 | 91 | 11.5107 | 8.1884
[7 empty] | 7652 | 92 | 10.8913 | 7.7386
[7 empty] | 7653 | 93 | 8.4138 | 5.9395
[7 empty] | 7654 | 94 | 7.4847 | 5.2648
[7 empty] | 7655 | 95 | 5.575 | 3.878
[7 empty] | 7656 | 96 | 4.5599 | 3.1409
[7 empty] | 7657 | 97 | 4.5083 | 3.1034
[7 empty] | 7658 | 98 | 4.2072 | 2.8848
[7 empty] | 7659 | 99 | 4.147 | 2.841
[7 empty] | 7660 | 100 | 3.7857 | 2.5787
[7 empty] | 7661 | 101 | 3.7254 | 2.5349
[7 empty] | 7662 | 102 | 3.9663 | 2.7099
[7 empty] | 7663 | 103 | 4.7319 | 3.2658
[7 empty] | 7664 | 104 | 4.99 | 3.4532
[7 empty] | 7665 | 105 | 5.4889 | 3.8156
[7 empty] | 7666 | 106 | 6.9858 | 4.9025
[7 empty] | 7667 | 107 | 7.3471 | 5.1649
[7 empty] | 7668 | 108 | 8.9643 | 6.3393
[7 empty] | 7669 | 109 | 8.2847 | 5.8458
[7 empty] | 7670 | 110 | 7.8202 | 5.5085
[7 empty] | 7671 | 111 | 7.6568 | 5.3898
[7 empty] | 7672 | 112 | 7.7256 | 5.4398
[7 empty] | 7673 | 113 | 7.3729 | 5.1836
[7 empty] | 7674 | 114 | 7.5449 | 5.3086
[7 empty] | 7675 | 115 | 7.0804 | 4.9712
[7 empty] | 7676 | 116 | 7.7772 | 5.4772
[7 empty] | 7677 | 117 | 7.3471 | 5.1649
[7 empty] | 7678 | 118 | 6.5556 | 4.5902
[7 empty] | 7679 | 119 | 4.9212 | 3.4033
[7 empty] | 7680 | 120 | 4.5954 | 3.1667
[7 empty] | 7681 | 121 | 3.8459 | 2.6224
[7 empty] | 7682 | 122 | 3.4243 | 2.3163
[7 empty] | 7683 | 123 | 3.3383 | 2.2538
[7 empty] | 7684 | 124 | 3.3039 | 2.2289
[7 empty] | 7685 | 125 | 3.2609 | 2.1976
[7 empty] | 7686 | 126 | 3.4071 | 2.3038
[7 empty] | 7687 | 127 | 4.9556 | 3.4283
[7 empty] | 7688 | 128 | 6.5556 | 4.5902
[7 empty] | 7689 | 129 | 7.2524 | 5.0962
[7 empty] | 7690 | 130 | 7.6998 | 5.421
[7 empty] | 7691 | 131 | 7.8632 | 5.5397
[7 empty] | 7692 | 132 | 7.6051 | 5.3523
[7 empty] | 7693 | 133 | 8.2589 | 5.8271
[7 empty] | 7694 | 134 | 8.5686 | 6.052
[7 empty] | 7695 | 135 | 8.6374 | 6.1019
[7 empty] | 7696 | 136 | 7.803 | 5.496
[7 empty] | 7697 | 137 | 7.6998 | 5.421
[7 empty] | 7698 | 138 | 7.6482 | 5.3835
[7 empty] | 7699 | 139 | 7.3041 | 5.1337
[7 empty] | 7700 | 140 | 7.3127 | 5.1399
[7 empty] | 7701 | 141 | 6.6417 | 4.6526
[7 empty] | 7702 | 142 | 5.9879 | 4.1779
[7 empty] | 7703 | 143 | 5.0846 | 3.522
[7 empty] | 7704 | 144 | 4.4566 | 3.0659
[7 empty] | 7705 | 145 | 3.9749 | 2.7161
[7 empty] | 7706 | 146 | 3.7598 | 2.5599
[7 empty] | 7707 | 147 | 3.691 | 2.51
[7 empty] | 7708 | 148 | 3.6824 | 2.5037
[7 empty] | 7709 | 149 | 3.6824 | 2.5037
[7 empty] | 7710 | 150 | 3.691 | 2.51
[7 empty] | 7711 | 151 | 4.8007 | 3.3158
[7 empty] | 7712 | 152 | 6.3664 | 4.4527
[7 empty] | 7713 | 153 | 6.9944 | 4.9088
[7 empty] | 7714 | 154 | 7.5707 | 5.3273
[7 empty] | 7715 | 155 | 7.4159 | 5.2149
[7 empty] | 7716 | 156 | 7.5879 | 5.3398
[7 empty] | 7717 | 157 | 8.3192 | 5.8708
[7 empty] | 7718 | 158 | 8.6546 | 6.1144
[7 empty] | 7719 | 159 | 8.9299 | 6.3143
[7 empty] | 7720 | 160 | 8.8009 | 6.2206
[7 empty] | 7721 | 161 | 9.5837 | 6.7891
[7 empty] | 7722 | 162 | 9.0762 | 6.4205
[7 empty] | 7723 | 163 | 9.4461 | 6.6891
[7 empty] | 7724 | 164 | 8.0611 | 5.6834
[7 empty] | 7725 | 165 | 11.2698 | 8.0135
[7 empty] | 7726 | 166 | 9.1708 | 6.4892
[7 empty] | 7727 | 167 | 5.4717 | 3.8031
[7 empty] | 7728 | 168 | 4.8093 | 3.3221
[7 empty] | 7729 | 1 | 3.3125 | 2.2351
[7 empty] | 7730 | 2 | 3.2007 | 2.1539
[7 empty] | 7731 | 3 | 3.1921 | 2.1476
[7 empty] | 7732 | 4 | 3.3297 | 2.2476
[7 empty] | 7733 | 5 | 3.3469 | 2.2601
[7 empty] | 7734 | 6 | 3.7857 | 2.5787
[7 empty] | 7735 | 7 | 4.5255 | 3.1159
[7 empty] | 7736 | 8 | 5.2137 | 3.6157
[7 empty] | 7737 | 9 | 5.1879 | 3.5969
[7 empty] | 7738 | 10 | 6.7449 | 4.7276
[7 empty] | 7739 | 11 | 8.8783 | 6.2768
[7 empty] | 7740 | 12 | 9.8676 | 6.9952
[7 empty] | 7741 | 13 | 10.2547 | 7.2763
[7 empty] | 7742 | 14 | 10.031 | 7.1139
[7 empty] | 7743 | 15 | 9.9364 | 7.0452
[7 empty] | 7744 | 16 | 11.1494 | 7.926
[7 empty] | 7745 | 17 | 12.5086 | 8.913
[7 empty] | 7746 | 18 | 12.2591 | 8.7319
[7 empty] | 7747 | 19 | 12.801 | 9.1254
[7 empty] | 7748 | 20 | 12.7322 | 9.0755
[7 empty] | 7749 | 21 | 13.3172 | 9.5002
[7 empty] | 7750 | 22 | 9.2568 | 6.5517
[7 empty] | 7751 | 23 | 5.3857 | 3.7406
[7 empty] | 7752 | 24 | 3.6704 | 2.495
[7 empty] | 7753 | 25 | 3.5706 | 2.4225
[7 empty] | 7754 | 26 | 3.4588 | 2.3413
[7 empty] | 7755 | 27 | 3.3555 | 2.2663
[7 empty] | 7756 | 28 | 3.4416 | 2.3288
[7 empty] | 7757 | 29 | 3.691 | 2.51
[7 empty] | 7758 | 30 | 3.9405 | 2.6911
[7 empty] | 7759 | 31 | 4.8093 | 3.3221
[7 empty] | 7760 | 32 | 5.1706 | 3.5844
[7 empty] | 7761 | 33 | 5.8502 | 4.0779
[7 empty] | 7762 | 34 | 6.7707 | 4.7464
[7 empty] | 7763 | 35 | 8.9987 | 6.3643
[7 empty] | 7764 | 36 | 10.0569 | 7.1327
[7 empty] | 7765 | 37 | 10.1343 | 7.1889
[7 empty] | 7766 | 38 | 10.2117 | 7.2451
[7 empty] | 7767 | 39 | 9.8762 | 7.0015
[7 empty] | 7768 | 40 | 10.9601 | 7.7886
[7 empty] | 7769 | 41 | 11.5279 | 8.2009
[7 empty] | 7770 | 42 | 11.5451 | 8.2134
[7 empty] | 7771 | 43 | 11.9236 | 8.4882
[7 empty] | 7772 | 44 | 13.1107 | 9.3503
[7 empty] | 7773 | 45 | 12.6978 | 9.0505
[7 empty] | 7774 | 46 | 9.8762 | 7.0015
[7 empty] | 7775 | 47 | 6.1771 | 4.3153
[7 empty] | 7776 | 48 | 4.6373 | 3.1971
[7 empty] | 7777 | 49 | 3.9577 | 2.7036
[7 empty] | 7778 | 50 | 3.6394 | 2.4725
[7 empty] | 7779 | 51 | 3.5276 | 2.3913
[7 empty] | 7780 | 52 | 3.562 | 2.4163
[7 empty] | 7781 | 53 | 3.5878 | 2.435
[7 empty] | 7782 | 54 | 4.1814 | 2.866
[7 empty] | 7783 | 55 | 5.3513 | 3.7156
[7 empty] | 7784 | 56 | 5.6008 | 3.8968
[7 empty] | 7785 | 57 | 6.5729 | 4.6027
[7 empty] | 7786 | 58 | 7.7084 | 5.4273
[7 empty] | 7787 | 59 | 8.9471 | 6.3268
[7 empty] | 7788 | 60 | 9.5923 | 6.7953
[7 empty] | 7789 | 61 | 10.2891 | 7.3013
[7 empty] | 7790 | 62 | 10.0827 | 7.1514
[7 empty] | 7791 | 63 | 10.6934 | 7.5949
[7 empty] | 7792 | 64 | 11.6655 | 8.3008
[7 empty] | 7793 | 65 | 12.3021 | 8.7631
[7 empty] | 7794 | 66 | 12.1989 | 8.6882
[7 empty] | 7795 | 67 | 12.9559 | 9.2379
[7 empty] | 7796 | 68 | 13.2054 | 9.419
[7 empty] | 7797 | 69 | 12.6806 | 9.038
[7 empty] | 7798 | 70 | 10.3235 | 7.3263
[7 empty] | 7799 | 71 | 5.6868 | 3.9592
[7 empty] | 7800 | 72 | 4.5734 | 3.1507
[7 empty] | 7801 | 73 | 3.8373 | 2.6162
[7 empty] | 7802 | 74 | 3.605 | 2.4475
[7 empty] | 7803 | 75 | 3.5018 | 2.3725
[7 empty] | 7804 | 76 | 3.4416 | 2.3288
[7 empty] | 7805 | 77 | 3.6222 | 2.46
[7 empty] | 7806 | 78 | 4.0351 | 2.7598
[7 empty] | 7807 | 79 | 5.1793 | 3.5907
[7 empty] | 7808 | 80 | 5.3599 | 3.7219
[7 empty] | 7809 | 81 | 6.5729 | 4.6027
[7 empty] | 7810 | 82 | 7.6912 | 5.4148
[7 empty] | 7811 | 83 | 8.4482 | 5.9645
[7 empty] | 7812 | 84 | 9.7214 | 6.889
[7 empty] | 7813 | 85 | 9.4117 | 6.6642
[7 empty] | 7814 | 86 | 8.8869 | 6.2831
[7 empty] | 7815 | 87 | 9.3428 | 6.6142
[7 empty] | 7816 | 88 | 10.0224 | 7.1077
[7 empty] | 7817 | 89 | 11.4074 | 8.1134
[7 empty] | 7818 | 90 | 10.8053 | 7.6762
[7 empty] | 7819 | 91 | 11.5107 | 8.1884
[7 empty] | 7820 | 92 | 10.8913 | 7.7386
[7 empty] | 7821 | 93 | 8.4138 | 5.9395
[7 empty] | 7822 | 94 | 7.4847 | 5.2648
[7 empty] | 7823 | 95 | 5.575 | 3.878
[7 empty] | 7824 | 96 | 4.5599 | 3.1409
[7 empty] | 7825 | 97 | 4.5083 | 3.1034
[7 empty] | 7826 | 98 | 4.2072 | 2.8848
[7 empty] | 7827 | 99 | 4.147 | 2.841
[7 empty] | 7828 | 100 | 3.7857 | 2.5787
[7 empty] | 7829 | 101 | 3.7254 | 2.5349
[7 empty] | 7830 | 102 | 3.9663 | 2.7099
[7 empty] | 7831 | 103 | 4.7319 | 3.2658
[7 empty] | 7832 | 104 | 4.99 | 3.4532
[7 empty] | 7833 | 105 | 5.4889 | 3.8156
[7 empty] | 7834 | 106 | 6.9858 | 4.9025
[7 empty] | 7835 | 107 | 7.3471 | 5.1649
[7 empty] | 7836 | 108 | 8.9643 | 6.3393
[7 empty] | 7837 | 109 | 8.2847 | 5.8458
[7 empty] | 7838 | 110 | 7.8202 | 5.5085
[7 empty] | 7839 | 111 | 7.6568 | 5.3898
[7 empty] | 7840 | 112 | 7.7256 | 5.4398
[7 empty] | 7841 | 113 | 7.3729 | 5.1836
[7 empty] | 7842 | 114 | 7.5449 | 5.3086
[7 empty] | 7843 | 115 | 7.0804 | 4.9712
[7 empty] | 7844 | 116 | 7.7772 | 5.4772
[7 empty] | 7845 | 117 | 7.3471 | 5.1649
[7 empty] | 7846 | 118 | 6.5556 | 4.5902
[7 empty] | 7847 | 119 | 4.9212 | 3.4033
[7 empty] | 7848 | 120 | 4.5954 | 3.1667
[7 empty] | 7849 | 121 | 3.8459 | 2.6224
[7 empty] | 7850 | 122 | 3.4243 | 2.3163
[7 empty] | 7851 | 123 | 3.3383 | 2.2538
[7 empty] | 7852 | 124 | 3.3039 | 2.2289
[7 empty] | 7853 | 125 | 3.2609 | 2.1976
[7 empty] | 7854 | 126 | 3.4071 | 2.3038
[7 empty] | 7855 | 127 | 4.9556 | 3.4283
[7 empty] | 7856 | 128 | 6.5556 | 4.5902
[7 empty] | 7857 | 129 | 7.2524 | 5.0962
[7 empty] | 7858 | 130 | 7.6998 | 5.421
[7 empty] | 7859 | 131 | 7.8632 | 5.5397
[7 empty] | 7860 | 132 | 7.6051 | 5.3523
[7 empty] | 7861 | 133 | 8.2589 | 5.8271
[7 empty] | 7862 | 134 | 8.5686 | 6.052
[7 empty] | 7863 | 135 | 8.6374 | 6.1019
[7 empty] | 7864 | 136 | 7.803 | 5.496
[7 empty] | 7865 | 137 | 7.6998 | 5.421
[7 empty] | 7866 | 138 | 7.6482 | 5.3835
[7 empty] | 7867 | 139 | 7.3041 | 5.1337
[7 empty] | 7868 | 140 | 7.3127 | 5.1399
[7 empty] | 7869 | 141 | 6.6417 | 4.6526
[7 empty] | 7870 | 142 | 5.9879 | 4.1779
[7 empty] | 7871 | 143 | 5.0846 | 3.522
[7 empty] | 7872 | 144 | 4.4566 | 3.0659
[7 empty] | 7873 | 145 | 3.9749 | 2.7161
[7 empty] | 7874 | 146 | 3.7598 | 2.5599
[7 empty] | 7875 | 147 | 3.691 | 2.51
[7 empty] | 7876 | 148 | 3.6824 | 2.5037
[7 empty] | 7877 | 149 | 3.6824 | 2.5037
[7 empty] | 7878 | 150 | 3.691 | 2.51
[7 empty] | 7879 | 151 | 4.8007 | 3.3158
[7 empty] | 7880 | 152 | 6.3664 | 4.4527
[7 empty] | 7881 | 153 | 6.9944 | 4.9088
[7 empty] | 7882 | 154 | 7.5707 | 5.3273
[7 empty] | 7883 | 155 | 7.4159 | 5.2149
[7 empty] | 7884 | 156 | 7.5879 | 5.3398
[7 empty] | 7885 | 157 | 8.3192 | 5.8708
[7 empty] | 7886 | 158 | 8.6546 | 6.1144
[7 empty] | 7887 | 159 | 8.9299 | 6.3143
[7 empty] | 7888 | 160 | 8.8009 | 6.2206
[7 empty] | 7889 | 161 | 9.5837 | 6.7891
[7 empty] | 7890 | 162 | 9.0762 | 6.4205
[7 empty] | 7891 | 163 | 9.4461 | 6.6891
[7 empty] | 7892 | 164 | 8.0611 | 5.6834
[7 empty] | 7893 | 165 | 11.2698 | 8.0135
[7 empty] | 7894 | 166 | 9.1708 | 6.4892
[7 empty] | 7895 | 167 | 5.4717 | 3.8031
[7 empty] | 7896 | 168 | 4.8093 | 3.3221
[7 empty] | 7897 | 1 | 3.3125 | 2.2351
[7 empty] | 7898 | 2 | 3.2007 | 2.1539
[7 empty] | 7899 | 3 | 3.1921 | 2.1476
[7 empty] | 7900 | 4 | 3.3297 | 2.2476
[7 empty] | 7901 | 5 | 3.3469 | 2.2601
[7 empty] | 7902 | 6 | 3.7857 | 2.5787
[7 empty] | 7903 | 7 | 4.5255 | 3.1159
[7 empty] | 7904 | 8 | 5.2137 | 3.6157
[7 empty] | 7905 | 9 | 5.1879 | 3.5969
[7 empty] | 7906 | 10 | 6.7449 | 4.7276
[7 empty] | 7907 | 11 | 8.8783 | 6.2768
[7 empty] | 7908 | 12 | 9.8676 | 6.9952
[7 empty] | 7909 | 13 | 10.2547 | 7.2763
[7 empty] | 7910 | 14 | 10.031 | 7.1139
[7 empty] | 7911 | 15 | 9.9364 | 7.0452
[7 empty] | 7912 | 16 | 11.1494 | 7.926
[7 empty] | 7913 | 17 | 12.5086 | 8.913
[7 empty] | 7914 | 18 | 12.2591 | 8.7319
[7 empty] | 7915 | 19 | 12.801 | 9.1254
[7 empty] | 7916 | 20 | 12.7322 | 9.0755
[7 empty] | 7917 | 21 | 13.3172 | 9.5002
[7 empty] | 7918 | 22 | 9.2568 | 6.5517
[7 empty] | 7919 | 23 | 5.3857 | 3.7406
[7 empty] | 7920 | 24 | 3.6704 | 2.495
[7 empty] | 7921 | 25 | 3.5706 | 2.4225
[7 empty] | 7922 | 26 | 3.4588 | 2.3413
[7 empty] | 7923 | 27 | 3.3555 | 2.2663
[7 empty] | 7924 | 28 | 3.4416 | 2.3288
[7 empty] | 7925 | 29 | 3.691 | 2.51
[7 empty] | 7926 | 30 | 3.9405 | 2.6911
[7 empty] | 7927 | 31 | 4.8093 | 3.3221
[7 empty] | 7928 | 32 | 5.1706 | 3.5844
[7 empty] | 7929 | 33 | 5.8502 | 4.0779
[7 empty] | 7930 | 34 | 6.7707 | 4.7464
[7 empty] | 7931 | 35 | 8.9987 | 6.3643
[7 empty] | 7932 | 36 | 10.0569 | 7.1327
[7 empty] | 7933 | 37 | 10.1343 | 7.1889
[7 empty] | 7934 | 38 | 10.2117 | 7.2451
[7 empty] | 7935 | 39 | 9.8762 | 7.0015
[7 empty] | 7936 | 40 | 10.9601 | 7.7886
[7 empty] | 7937 | 41 | 11.5279 | 8.2009
[7 empty] | 7938 | 42 | 11.5451 | 8.2134
[7 empty] | 7939 | 43 | 11.9236 | 8.4882
[7 empty] | 7940 | 44 | 13.1107 | 9.3503
[7 empty] | 7941 | 45 | 12.6978 | 9.0505
[7 empty] | 7942 | 46 | 9.8762 | 7.0015
[7 empty] | 7943 | 47 | 6.1771 | 4.3153
[7 empty] | 7944 | 48 | 4.6373 | 3.1971
[7 empty] | 7945 | 49 | 3.9577 | 2.7036
[7 empty] | 7946 | 50 | 3.6394 | 2.4725
[7 empty] | 7947 | 51 | 3.5276 | 2.3913
[7 empty] | 7948 | 52 | 3.562 | 2.4163
[7 empty] | 7949 | 53 | 3.5878 | 2.435
[7 empty] | 7950 | 54 | 4.1814 | 2.866
[7 empty] | 7951 | 55 | 5.3513 | 3.7156
[7 empty] | 7952 | 56 | 5.6008 | 3.8968
[7 empty] | 7953 | 57 | 6.5729 | 4.6027
[7 empty] | 7954 | 58 | 7.7084 | 5.4273
[7 empty] | 7955 | 59 | 8.9471 | 6.3268
[7 empty] | 7956 | 60 | 9.5923 | 6.7953
[7 empty] | 7957 | 61 | 10.2891 | 7.3013
[7 empty] | 7958 | 62 | 10.0827 | 7.1514
[7 empty] | 7959 | 63 | 10.6934 | 7.5949
[7 empty] | 7960 | 64 | 11.6655 | 8.3008
[7 empty] | 7961 | 65 | 12.3021 | 8.7631
[7 empty] | 7962 | 66 | 12.1989 | 8.6882
[7 empty] | 7963 | 67 | 12.9559 | 9.2379
[7 empty] | 7964 | 68 | 13.2054 | 9.419
[7 empty] | 7965 | 69 | 12.6806 | 9.038
[7 empty] | 7966 | 70 | 10.3235 | 7.3263
[7 empty] | 7967 | 71 | 5.6868 | 3.9592
[7 empty] | 7968 | 72 | 4.5734 | 3.1507
[7 empty] | 7969 | 73 | 3.8373 | 2.6162
[7 empty] | 7970 | 74 | 3.605 | 2.4475
[7 empty] | 7971 | 75 | 3.5018 | 2.3725
[7 empty] | 7972 | 76 | 3.4416 | 2.3288
[7 empty] | 7973 | 77 | 3.6222 | 2.46
[7 empty] | 7974 | 78 | 4.0351 | 2.7598
[7 empty] | 7975 | 79 | 5.1793 | 3.5907
[7 empty] | 7976 | 80 | 5.3599 | 3.7219
[7 empty] | 7977 | 81 | 6.5729 | 4.6027
[7 empty] | 7978 | 82 | 7.6912 | 5.4148
[7 empty] | 7979 | 83 | 8.4482 | 5.9645
[7 empty] | 7980 | 84 | 9.7214 | 6.889
[7 empty] | 7981 | 85 | 9.4117 | 6.6642
[7 empty] | 7982 | 86 | 8.8869 | 6.2831
[7 empty] | 7983 | 87 | 9.3428 | 6.6142
[7 empty] | 7984 | 88 | 10.0224 | 7.1077
[7 empty] | 7985 | 89 | 11.4074 | 8.1134
[7 empty] | 7986 | 90 | 10.8053 | 7.6762
[7 empty] | 7987 | 91 | 11.5107 | 8.1884
[7 empty] | 7988 | 92 | 10.8913 | 7.7386
[7 empty] | 7989 | 93 | 8.4138 | 5.9395
[7 empty] | 7990 | 94 | 7.4847 | 5.2648
[7 empty] | 7991 | 95 | 5.575 | 3.878
[7 empty] | 7992 | 96 | 4.5599 | 3.1409
[7 empty] | 7993 | 97 | 4.5083 | 3.1034
[7 empty] | 7994 | 98 | 4.2072 | 2.8848
[7 empty] | 7995 | 99 | 4.147 | 2.841
[7 empty] | 7996 | 100 | 3.7857 | 2.5787
[7 empty] | 7997 | 101 | 3.7254 | 2.5349
[7 empty] | 7998 | 102 | 3.9663 | 2.7099
[7 empty] | 7999 | 103 | 4.7319 | 3.2658
[7 empty] | 8000 | 104 | 4.99 | 3.4532
[7 empty] | 8001 | 105 | 5.4889 | 3.8156
[7 empty] | 8002 | 106 | 6.9858 | 4.9025
[7 empty] | 8003 | 107 | 7.3471 | 5.1649
[7 empty] | 8004 | 108 | 8.9643 | 6.3393
[7 empty] | 8005 | 109 | 8.2847 | 5.8458
[7 empty] | 8006 | 110 | 7.8202 | 5.5085
[7 empty] | 8007 | 111 | 7.6568 | 5.3898
[7 empty] | 8008 | 112 | 7.7256 | 5.4398
[7 empty] | 8009 | 113 | 7.3729 | 5.1836
[7 empty] | 8010 | 114 | 7.5449 | 5.3086
[7 empty] | 8011 | 115 | 7.0804 | 4.9712
[7 empty] | 8012 | 116 | 7.7772 | 5.4772
[7 empty] | 8013 | 117 | 7.3471 | 5.1649
[7 empty] | 8014 | 118 | 6.5556 | 4.5902
[7 empty] | 8015 | 119 | 4.9212 | 3.4033
[7 empty] | 8016 | 120 | 4.5954 | 3.1667
[7 empty] | 8017 | 121 | 3.8459 | 2.6224
[7 empty] | 8018 | 122 | 3.4243 | 2.3163
[7 empty] | 8019 | 123 | 3.3383 | 2.2538
[7 empty] | 8020 | 124 | 3.3039 | 2.2289
[7 empty] | 8021 | 125 | 3.2609 | 2.1976
[7 empty] | 8022 | 126 | 3.4071 | 2.3038
[7 empty] | 8023 | 127 | 4.9556 | 3.4283
[7 empty] | 8024 | 128 | 6.5556 | 4.5902
[7 empty] | 8025 | 129 | 7.2524 | 5.0962
[7 empty] | 8026 | 130 | 7.6998 | 5.421
[7 empty] | 8027 | 131 | 7.8632 | 5.5397
[7 empty] | 8028 | 132 | 7.6051 | 5.3523
[7 empty] | 8029 | 133 | 8.2589 | 5.8271
[7 empty] | 8030 | 134 | 8.5686 | 6.052
[7 empty] | 8031 | 135 | 8.6374 | 6.1019
[7 empty] | 8032 | 136 | 7.803 | 5.496
[7 empty] | 8033 | 137 | 7.6998 | 5.421
[7 empty] | 8034 | 138 | 7.6482 | 5.3835
[7 empty] | 8035 | 139 | 7.3041 | 5.1337
[7 empty] | 8036 | 140 | 7.3127 | 5.1399
[7 empty] | 8037 | 141 | 6.6417 | 4.6526
[7 empty] | 8038 | 142 | 5.9879 | 4.1779
[7 empty] | 8039 | 143 | 5.0846 | 3.522
[7 empty] | 8040 | 144 | 4.4566 | 3.0659
[7 empty] | 8041 | 145 | 3.9749 | 2.7161
[7 empty] | 8042 | 146 | 3.7598 | 2.5599
[7 empty] | 8043 | 147 | 3.691 | 2.51
[7 empty] | 8044 | 148 | 3.6824 | 2.5037
[7 empty] | 8045 | 149 | 3.6824 | 2.5037
[7 empty] | 8046 | 150 | 3.691 | 2.51
[7 empty] | 8047 | 151 | 4.8007 | 3.3158
[7 empty] | 8048 | 152 | 6.3664 | 4.4527
[7 empty] | 8049 | 153 | 6.9944 | 4.9088
[7 empty] | 8050 | 154 | 7.5707 | 5.3273
[7 empty] | 8051 | 155 | 7.4159 | 5.2149
[7 empty] | 8052 | 156 | 7.5879 | 5.3398
[7 empty] | 8053 | 157 | 8.3192 | 5.8708
[7 empty] | 8054 | 158 | 8.6546 | 6.1144
[7 empty] | 8055 | 159 | 8.9299 | 6.3143
[7 empty] | 8056 | 160 | 8.8009 | 6.2206
[7 empty] | 8057 | 161 | 9.5837 | 6.7891
[7 empty] | 8058 | 162 | 9.0762 | 6.4205
[7 empty] | 8059 | 163 | 9.4461 | 6.6891
[7 empty] | 8060 | 164 | 8.0611 | 5.6834
[7 empty] | 8061 | 165 | 11.2698 | 8.0135
[7 empty] | 8062 | 166 | 9.1708 | 6.4892
[7 empty] | 8063 | 167 | 5.4717 | 3.8031
[7 empty] | 8064 | 168 | 4.8093 | 3.3221
[7 empty] | 8065 | 1 | 3.3125 | 2.2351
[7 empty] | 8066 | 2 | 3.2007 | 2.1539
[7 empty] | 8067 | 3 | 3.1921 | 2.1476
[7 empty] | 8068 | 4 | 3.3297 | 2.2476
[7 empty] | 8069 | 5 | 3.3469 | 2.2601
[7 empty] | 8070 | 6 | 3.7857 | 2.5787
[7 empty] | 8071 | 7 | 4.5255 | 3.1159
[7 empty] | 8072 | 8 | 5.2137 | 3.6157
[7 empty] | 8073 | 9 | 5.1879 | 3.5969
[7 empty] | 8074 | 10 | 6.7449 | 4.7276
[7 empty] | 8075 | 11 | 8.8783 | 6.2768
[7 empty] | 8076 | 12 | 9.8676 | 6.9952
[7 empty] | 8077 | 13 | 10.2547 | 7.2763
[7 empty] | 8078 | 14 | 10.031 | 7.1139
[7 empty] | 8079 | 15 | 9.9364 | 7.0452
[7 empty] | 8080 | 16 | 11.1494 | 7.926
[7 empty] | 8081 | 17 | 12.5086 | 8.913
[7 empty] | 8082 | 18 | 12.2591 | 8.7319
[7 empty] | 8083 | 19 | 12.801 | 9.1254
[7 empty] | 8084 | 20 | 12.7322 | 9.0755
[7 empty] | 8085 | 21 | 13.3172 | 9.5002
[7 empty] | 8086 | 22 | 9.2568 | 6.5517
[7 empty] | 8087 | 23 | 5.3857 | 3.7406
[7 empty] | 8088 | 24 | 3.6704 | 2.495
[7 empty] | 8089 | 25 | 3.5706 | 2.4225
[7 empty] | 8090 | 26 | 3.4588 | 2.3413
[7 empty] | 8091 | 27 | 3.3555 | 2.2663
[7 empty] | 8092 | 28 | 3.4416 | 2.3288
[7 empty] | 8093 | 29 | 3.691 | 2.51
[7 empty] | 8094 | 30 | 3.9405 | 2.6911
[7 empty] | 8095 | 31 | 4.8093 | 3.3221
[7 empty] | 8096 | 32 | 5.1706 | 3.5844
[7 empty] | 8097 | 33 | 5.8502 | 4.0779
[7 empty] | 8098 | 34 | 6.7707 | 4.7464
[7 empty] | 8099 | 35 | 8.9987 | 6.3643
[7 empty] | 8100 | 36 | 10.0569 | 7.1327
[7 empty] | 8101 | 37 | 10.1343 | 7.1889
[7 empty] | 8102 | 38 | 10.2117 | 7.2451
[7 empty] | 8103 | 39 | 9.8762 | 7.0015
[7 empty] | 8104 | 40 | 10.9601 | 7.7886
[7 empty] | 8105 | 41 | 11.5279 | 8.2009
[7 empty] | 8106 | 42 | 11.5451 | 8.2134
[7 empty] | 8107 | 43 | 11.9236 | 8.4882
[7 empty] | 8108 | 44 | 13.1107 | 9.3503
[7 empty] | 8109 | 45 | 12.6978 | 9.0505
[7 empty] | 8110 | 46 | 9.8762 | 7.0015
[7 empty] | 8111 | 47 | 6.1771 | 4.3153
[7 empty] | 8112 | 48 | 4.6373 | 3.1971
[7 empty] | 8113 | 49 | 3.9577 | 2.7036
[7 empty] | 8114 | 50 | 3.6394 | 2.4725
[7 empty] | 8115 | 51 | 3.5276 | 2.3913
[7 empty] | 8116 | 52 | 3.562 | 2.4163
[7 empty] | 8117 | 53 | 3.5878 | 2.435
[7 empty] | 8118 | 54 | 4.1814 | 2.866
[7 empty] | 8119 | 55 | 5.3513 | 3.7156
[7 empty] | 8120 | 56 | 5.6008 | 3.8968
[7 empty] | 8121 | 57 | 6.5729 | 4.6027
[7 empty] | 8122 | 58 | 7.7084 | 5.4273
[7 empty] | 8123 | 59 | 8.9471 | 6.3268
[7 empty] | 8124 | 60 | 9.5923 | 6.7953
[7 empty] | 8125 | 61 | 10.2891 | 7.3013
[7 empty] | 8126 | 62 | 10.0827 | 7.1514
[7 empty] | 8127 | 63 | 10.6934 | 7.5949
[7 empty] | 8128 | 64 | 11.6655 | 8.3008
[7 empty] | 8129 | 65 | 12.3021 | 8.7631
[7 empty] | 8130 | 66 | 12.1989 | 8.6882
[7 empty] | 8131 | 67 | 12.9559 | 9.2379
[7 empty] | 8132 | 68 | 13.2054 | 9.419
[7 empty] | 8133 | 69 | 12.6806 | 9.038
[7 empty] | 8134 | 70 | 10.3235 | 7.3263
[7 empty] | 8135 | 71 | 5.6868 | 3.9592
[7 empty] | 8136 | 72 | 4.5734 | 3.1507
[7 empty] | 8137 | 73 | 3.8373 | 2.6162
[7 empty] | 8138 | 74 | 3.605 | 2.4475
[7 empty] | 8139 | 75 | 3.5018 | 2.3725
[7 empty] | 8140 | 76 | 3.4416 | 2.3288
[7 empty] | 8141 | 77 | 3.6222 | 2.46
[7 empty] | 8142 | 78 | 4.0351 | 2.7598
[7 empty] | 8143 | 79 | 5.1793 | 3.5907
[7 empty] | 8144 | 80 | 5.3599 | 3.7219
[7 empty] | 8145 | 81 | 6.5729 | 4.6027
[7 empty] | 8146 | 82 | 7.6912 | 5.4148
[7 empty] | 8147 | 83 | 8.4482 | 5.9645
[7 empty] | 8148 | 84 | 9.7214 | 6.889
[7 empty] | 8149 | 85 | 9.4117 | 6.6642
[7 empty] | 8150 | 86 | 8.8869 | 6.2831
[7 empty] | 8151 | 87 | 9.3428 | 6.6142
[7 empty] | 8152 | 88 | 10.0224 | 7.1077
[7 empty] | 8153 | 89 | 11.4074 | 8.1134
[7 empty] | 8154 | 90 | 10.8053 | 7.6762
[7 empty] | 8155 | 91 | 11.5107 | 8.1884
[7 empty] | 8156 | 92 | 10.8913 | 7.7386
[7 empty] | 8157 | 93 | 8.4138 | 5.9395
[7 empty] | 8158 | 94 | 7.4847 | 5.2648
[7 empty] | 8159 | 95 | 5.575 | 3.878
[7 empty] | 8160 | 96 | 4.5599 | 3.1409
[7 empty] | 8161 | 97 | 4.5083 | 3.1034
[7 empty] | 8162 | 98 | 4.2072 | 2.8848
[7 empty] | 8163 | 99 | 4.147 | 2.841
[7 empty] | 8164 | 100 | 3.7857 | 2.5787
[7 empty] | 8165 | 101 | 3.7254 | 2.5349
[7 empty] | 8166 | 102 | 3.9663 | 2.7099
[7 empty] | 8167 | 103 | 4.7319 | 3.2658
[7 empty] | 8168 | 104 | 4.99 | 3.4532
[7 empty] | 8169 | 105 | 5.4889 | 3.8156
[7 empty] | 8170 | 106 | 6.9858 | 4.9025
[7 empty] | 8171 | 107 | 7.3471 | 5.1649
[7 empty] | 8172 | 108 | 8.9643 | 6.3393
[7 empty] | 8173 | 109 | 8.2847 | 5.8458
[7 empty] | 8174 | 110 | 7.8202 | 5.5085
[7 empty] | 8175 | 111 | 7.6568 | 5.3898
[7 empty] | 8176 | 112 | 7.7256 | 5.4398
[7 empty] | 8177 | 113 | 7.3729 | 5.1836
[7 empty] | 8178 | 114 | 7.5449 | 5.3086
[7 empty] | 8179 | 115 | 7.0804 | 4.9712
[7 empty] | 8180 | 116 | 7.7772 | 5.4772
[7 empty] | 8181 | 117 | 7.3471 | 5.1649
[7 empty] | 8182 | 118 | 6.5556 | 4.5902
[7 empty] | 8183 | 119 | 4.9212 | 3.4033
[7 empty] | 8184 | 120 | 4.5954 | 3.1667
[7 empty] | 8185 | 121 | 3.8459 | 2.6224
[7 empty] | 8186 | 122 | 3.4243 | 2.3163
[7 empty] | 8187 | 123 | 3.3383 | 2.2538
[7 empty] | 8188 | 124 | 3.3039 | 2.2289
[7 empty] | 8189 | 125 | 3.2609 | 2.1976
[7 empty] | 8190 | 126 | 3.4071 | 2.3038
[7 empty] | 8191 | 127 | 4.9556 | 3.4283
[7 empty] | 8192 | 128 | 6.5556 | 4.5902
[7 empty] | 8193 | 129 | 7.2524 | 5.0962
[7 empty] | 8194 | 130 | 7.6998 | 5.421
[7 empty] | 8195 | 131 | 7.8632 | 5.5397
[7 empty] | 8196 | 132 | 7.6051 | 5.3523
[7 empty] | 8197 | 133 | 8.2589 | 5.8271
[7 empty] | 8198 | 134 | 8.5686 | 6.052
[7 empty] | 8199 | 135 | 8.6374 | 6.1019
[7 empty] | 8200 | 136 | 7.803 | 5.496
[7 empty] | 8201 | 137 | 7.6998 | 5.421
[7 empty] | 8202 | 138 | 7.6482 | 5.3835
[7 empty] | 8203 | 139 | 7.3041 | 5.1337
[7 empty] | 8204 | 140 | 7.3127 | 5.1399
[7 empty] | 8205 | 141 | 6.6417 | 4.6526
[7 empty] | 8206 | 142 | 5.9879 | 4.1779
[7 empty] | 8207 | 143 | 5.0846 | 3.522
[7 empty] | 8208 | 144 | 4.4566 | 3.0659
[7 empty] | 8209 | 145 | 3.9749 | 2.7161
[7 empty] | 8210 | 146 | 3.7598 | 2.5599
[7 empty] | 8211 | 147 | 3.691 | 2.51
[7 empty] | 8212 | 148 | 3.6824 | 2.5037
[7 empty] | 8213 | 149 | 3.6824 | 2.5037
[7 empty] | 8214 | 150 | 3.691 | 2.51
[7 empty] | 8215 | 151 | 4.8007 | 3.3158
[7 empty] | 8216 | 152 | 6.3664 | 4.4527
[7 empty] | 8217 | 153 | 6.9944 | 4.9088
[7 empty] | 8218 | 154 | 7.5707 | 5.3273
[7 empty] | 8219 | 155 | 7.4159 | 5.2149
[7 empty] | 8220 | 156 | 7.5879 | 5.3398
[7 empty] | 8221 | 157 | 8.3192 | 5.8708
[7 empty] | 8222 | 158 | 8.6546 | 6.1144
[7 empty] | 8223 | 159 | 8.9299 | 6.3143
[7 empty] | 8224 | 160 | 8.8009 | 6.2206
[7 empty] | 8225 | 161 | 9.5837 | 6.7891
[7 empty] | 8226 | 162 | 9.0762 | 6.4205
[7 empty] | 8227 | 163 | 9.4461 | 6.6891
[7 empty] | 8228 | 164 | 8.0611 | 5.6834
[7 empty] | 8229 | 165 | 11.2698 | 8.0135
[7 empty] | 8230 | 166 | 9.1708 | 6.4892
[7 empty] | 8231 | 167 | 5.4717 | 3.8031
[7 empty] | 8232 | 168 | 4.8093 | 3.3221
[7 empty] | 8233 | 1 | 3.3125 | 2.2351
[7 empty] | 8234 | 2 | 3.2007 | 2.1539
[7 empty] | 8235 | 3 | 3.1921 | 2.1476
[7 empty] | 8236 | 4 | 3.3297 | 2.2476
[7 empty] | 8237 | 5 | 3.3469 | 2.2601
[7 empty] | 8238 | 6 | 3.7857 | 2.5787
[7 empty] | 8239 | 7 | 4.5255 | 3.1159
[7 empty] | 8240 | 8 | 5.2137 | 3.6157
[7 empty] | 8241 | 9 | 5.1879 | 3.5969
[7 empty] | 8242 | 10 | 6.7449 | 4.7276
[7 empty] | 8243 | 11 | 8.8783 | 6.2768
[7 empty] | 8244 | 12 | 9.8676 | 6.9952
[7 empty] | 8245 | 13 | 10.2547 | 7.2763
[7 empty] | 8246 | 14 | 10.031 | 7.1139
[7 empty] | 8247 | 15 | 9.9364 | 7.0452
[7 empty] | 8248 | 16 | 11.1494 | 7.926
[7 empty] | 8249 | 17 | 12.5086 | 8.913
[7 empty] | 8250 | 18 | 12.2591 | 8.7319
[7 empty] | 8251 | 19 | 12.801 | 9.1254
[7 empty] | 8252 | 20 | 12.7322 | 9.0755
[7 empty] | 8253 | 21 | 13.3172 | 9.5002
[7 empty] | 8254 | 22 | 9.2568 | 6.5517
[7 empty] | 8255 | 23 | 5.3857 | 3.7406
[7 empty] | 8256 | 24 | 3.6704 | 2.495
[7 empty] | 8257 | 25 | 3.5706 | 2.4225
[7 empty] | 8258 | 26 | 3.4588 | 2.3413
[7 empty] | 8259 | 27 | 3.3555 | 2.2663
[7 empty] | 8260 | 28 | 3.4416 | 2.3288
[7 empty] | 8261 | 29 | 3.691 | 2.51
[7 empty] | 8262 | 30 | 3.9405 | 2.6911
[7 empty] | 8263 | 31 | 4.8093 | 3.3221
[7 empty] | 8264 | 32 | 5.1706 | 3.5844
[7 empty] | 8265 | 33 | 5.8502 | 4.0779
[7 empty] | 8266 | 34 | 6.7707 | 4.7464
[7 empty] | 8267 | 35 | 8.9987 | 6.3643
[7 empty] | 8268 | 36 | 10.0569 | 7.1327
[7 empty] | 8269 | 37 | 10.1343 | 7.1889
[7 empty] | 8270 | 38 | 10.2117 | 7.2451
[7 empty] | 8271 | 39 | 9.8762 | 7.0015
[7 empty] | 8272 | 40 | 10.9601 | 7.7886
[7 empty] | 8273 | 41 | 11.5279 | 8.2009
[7 empty] | 8274 | 42 | 11.5451 | 8.2134
[7 empty] | 8275 | 43 | 11.9236 | 8.4882
[7 empty] | 8276 | 44 | 13.1107 | 9.3503
[7 empty] | 8277 | 45 | 12.6978 | 9.0505
[7 empty] | 8278 | 46 | 9.8762 | 7.0015
[7 empty] | 8279 | 47 | 6.1771 | 4.3153
[7 empty] | 8280 | 48 | 4.6373 | 3.1971
[7 empty] | 8281 | 49 | 3.9577 | 2.7036
[7 empty] | 8282 | 50 | 3.6394 | 2.4725
[7 empty] | 8283 | 51 | 3.5276 | 2.3913
[7 empty] | 8284 | 52 | 3.562 | 2.4163
[7 empty] | 8285 | 53 | 3.5878 | 2.435
[7 empty] | 8286 | 54 | 4.1814 | 2.866
[7 empty] | 8287 | 55 | 5.3513 | 3.7156
[7 empty] | 8288 | 56 | 5.6008 | 3.8968
[7 empty] | 8289 | 57 | 6.5729 | 4.6027
[7 empty] | 8290 | 58 | 7.7084 | 5.4273
[7 empty] | 8291 | 59 | 8.9471 | 6.3268
[7 empty] | 8292 | 60 | 9.5923 | 6.7953
[7 empty] | 8293 | 61 | 10.2891 | 7.3013
[7 empty] | 8294 | 62 | 10.0827 | 7.1514
[7 empty] | 8295 | 63 | 10.6934 | 7.5949
[7 empty] | 8296 | 64 | 11.6655 | 8.3008
[7 empty] | 8297 | 65 | 12.3021 | 8.7631
[7 empty] | 8298 | 66 | 12.1989 | 8.6882
[7 empty] | 8299 | 67 | 12.9559 | 9.2379
[7 empty] | 8300 | 68 | 13.2054 | 9.419
[7 empty] | 8301 | 69 | 12.6806 | 9.038
[7 empty] | 8302 | 70 | 10.3235 | 7.3263
[7 empty] | 8303 | 71 | 5.6868 | 3.9592
[7 empty] | 8304 | 72 | 4.5734 | 3.1507
[7 empty] | 8305 | 73 | 3.8373 | 2.6162
[7 empty] | 8306 | 74 | 3.605 | 2.4475
[7 empty] | 8307 | 75 | 3.5018 | 2.3725
[7 empty] | 8308 | 76 | 3.4416 | 2.3288
[7 empty] | 8309 | 77 | 3.6222 | 2.46
[7 empty] | 8310 | 78 | 4.0351 | 2.7598
[7 empty] | 8311 | 79 | 5.1793 | 3.5907
[7 empty] | 8312 | 80 | 5.3599 | 3.7219
[7 empty] | 8313 | 81 | 6.5729 | 4.6027
[7 empty] | 8314 | 82 | 7.6912 | 5.4148
[7 empty] | 8315 | 83 | 8.4482 | 5.9645
[7 empty] | 8316 | 84 | 9.7214 | 6.889
[7 empty] | 8317 | 85 | 9.4117 | 6.6642
[7 empty] | 8318 | 86 | 8.8869 | 6.2831
[7 empty] | 8319 | 87 | 9.3428 | 6.6142
[7 empty] | 8320 | 88 | 10.0224 | 7.1077
[7 empty] | 8321 | 89 | 11.4074 | 8.1134
[7 empty] | 8322 | 90 | 10.8053 | 7.6762
[7 empty] | 8323 | 91 | 11.5107 | 8.1884
[7 empty] | 8324 | 92 | 10.8913 | 7.7386
[7 empty] | 8325 | 93 | 8.4138 | 5.9395
[7 empty] | 8326 | 94 | 7.4847 | 5.2648
[7 empty] | 8327 | 95 | 5.575 | 3.878
[7 empty] | 8328 | 96 | 4.5599 | 3.1409
[7 empty] | 8329 | 97 | 4.5083 | 3.1034
[7 empty] | 8330 | 98 | 4.2072 | 2.8848
[7 empty] | 8331 | 99 | 4.147 | 2.841
[7 empty] | 8332 | 100 | 3.7857 | 2.5787
[7 empty] | 8333 | 101 | 3.7254 | 2.5349
[7 empty] | 8334 | 102 | 3.9663 | 2.7099
[7 empty] | 8335 | 103 | 4.7319 | 3.2658
[7 empty] | 8336 | 104 | 4.99 | 3.4532
[7 empty] | 8337 | 105 | 5.4889 | 3.8156
[7 empty] | 8338 | 106 | 6.9858 | 4.9025
[7 empty] | 8339 | 107 | 7.3471 | 5.1649
[7 empty] | 8340 | 108 | 8.9643 | 6.3393
[7 empty] | 8341 | 109 | 8.2847 | 5.8458
[7 empty] | 8342 | 110 | 7.8202 | 5.5085
[7 empty] | 8343 | 111 | 7.6568 | 5.3898
[7 empty] | 8344 | 112 | 7.7256 | 5.4398
[7 empty] | 8345 | 113 | 7.3729 | 5.1836
[7 empty] | 8346 | 114 | 7.5449 | 5.3086
[7 empty] | 8347 | 115 | 7.0804 | 4.9712
[7 empty] | 8348 | 116 | 7.7772 | 5.4772
[7 empty] | 8349 | 117 | 7.3471 | 5.1649
[7 empty] | 8350 | 118 | 6.5556 | 4.5902
[7 empty] | 8351 | 119 | 4.9212 | 3.4033
[7 empty] | 8352 | 120 | 4.5954 | 3.1667
[7 empty] | 8353 | 121 | 3.8459 | 2.6224
[7 empty] | 8354 | 122 | 3.4243 | 2.3163
[7 empty] | 8355 | 123 | 3.3383 | 2.2538
[7 empty] | 8356 | 124 | 3.3039 | 2.2289
[7 empty] | 8357 | 125 | 3.2609 | 2.1976
[7 empty] | 8358 | 126 | 3.4071 | 2.3038
[7 empty] | 8359 | 127 | 4.9556 | 3.4283
[7 empty] | 8360 | 128 | 6.5556 | 4.5902
[7 empty] | 8361 | 129 | 7.2524 | 5.0962
[7 empty] | 8362 | 130 | 7.6998 | 5.421
[7 empty] | 8363 | 131 | 7.8632 | 5.5397
[7 empty] | 8364 | 132 | 7.6051 | 5.3523
[7 empty] | 8365 | 133 | 8.2589 | 5.8271
[7 empty] | 8366 | 134 | 8.5686 | 6.052
[7 empty] | 8367 | 135 | 8.6374 | 6.1019
[7 empty] | 8368 | 136 | 7.803 | 5.496
[7 empty] | 8369 | 137 | 7.6998 | 5.421
[7 empty] | 8370 | 138 | 7.6482 | 5.3835
[7 empty] | 8371 | 139 | 7.3041 | 5.1337
[7 empty] | 8372 | 140 | 7.3127 | 5.1399
[7 empty] | 8373 | 141 | 6.6417 | 4.6526
[7 empty] | 8374 | 142 | 5.9879 | 4.1779
[7 empty] | 8375 | 143 | 5.0846 | 3.522
[7 empty] | 8376 | 144 | 4.4566 | 3.0659
[7 empty] | 8377 | 145 | 3.9749 | 2.7161
[7 empty] | 8378 | 146 | 3.7598 | 2.5599
[7 empty] | 8379 | 147 | 3.691 | 2.51
[7 empty] | 8380 | 148 | 3.6824 | 2.5037
[7 empty] | 8381 | 149 | 3.6824 | 2.5037
[7 empty] | 8382 | 150 | 3.691 | 2.51
[7 empty] | 8383 | 151 | 4.8007 | 3.3158
[7 empty] | 8384 | 152 | 6.3664 | 4.4527
[7 empty] | 8385 | 153 | 6.9944 | 4.9088
[7 empty] | 8386 | 154 | 7.5707 | 5.3273
[7 empty] | 8387 | 155 | 7.4159 | 5.2149
[7 empty] | 8388 | 156 | 7.5879 | 5.3398
[7 empty] | 8389 | 157 | 8.3192 | 5.8708
[7 empty] | 8390 | 158 | 8.6546 | 6.1144
[7 empty] | 8391 | 159 | 8.9299 | 6.3143
[7 empty] | 8392 | 160 | 8.8009 | 6.2206
[7 empty] | 8393 | 161 | 9.5837 | 6.7891
[7 empty] | 8394 | 162 | 9.0762 | 6.4205
[7 empty] | 8395 | 163 | 9.4461 | 6.6891
[7 empty] | 8396 | 164 | 8.0611 | 5.6834
[7 empty] | 8397 | 165 | 11.2698 | 8.0135
[7 empty] | 8398 | 166 | 9.1708 | 6.4892
[7 empty] | 8399 | 167 | 5.4717 | 3.8031
[7 empty] | 8400 | 168 | 4.8093 | 3.3221
[7 empty] | 8401 | 1 | 3.3125 | 2.2351
[7 empty] | 8402 | 2 | 3.2007 | 2.1539
[7 empty] | 8403 | 3 | 3.1921 | 2.1476
[7 empty] | 8404 | 4 | 3.3297 | 2.2476
[7 empty] | 8405 | 5 | 3.3469 | 2.2601
[7 empty] | 8406 | 6 | 3.7857 | 2.5787
[7 empty] | 8407 | 7 | 4.5255 | 3.1159
[7 empty] | 8408 | 8 | 5.2137 | 3.6157
[7 empty] | 8409 | 9 | 5.1879 | 3.5969
[7 empty] | 8410 | 10 | 6.7449 | 4.7276
[7 empty] | 8411 | 11 | 8.8783 | 6.2768
[7 empty] | 8412 | 12 | 9.8676 | 6.9952
[7 empty] | 8413 | 13 | 10.2547 | 7.2763
[7 empty] | 8414 | 14 | 10.031 | 7.1139
[7 empty] | 8415 | 15 | 9.9364 | 7.0452
[7 empty] | 8416 | 16 | 11.1494 | 7.926
[7 empty] | 8417 | 17 | 12.5086 | 8.913
[7 empty] | 8418 | 18 | 12.2591 | 8.7319
[7 empty] | 8419 | 19 | 12.801 | 9.1254
[7 empty] | 8420 | 20 | 12.7322 | 9.0755
[7 empty] | 8421 | 21 | 13.3172 | 9.5002
[7 empty] | 8422 | 22 | 9.2568 | 6.5517
[7 empty] | 8423 | 23 | 5.3857 | 3.7406
[7 empty] | 8424 | 24 | 3.6704 | 2.495
[7 empty] | 8425 | 25 | 3.5706 | 2.4225
[7 empty] | 8426 | 26 | 3.4588 | 2.3413
[7 empty] | 8427 | 27 | 3.3555 | 2.2663
[7 empty] | 8428 | 28 | 3.4416 | 2.3288
[7 empty] | 8429 | 29 | 3.691 | 2.51
[7 empty] | 8430 | 30 | 3.9405 | 2.6911
[7 empty] | 8431 | 31 | 4.8093 | 3.3221
[7 empty] | 8432 | 32 | 5.1706 | 3.5844
[7 empty] | 8433 | 33 | 5.8502 | 4.0779
[7 empty] | 8434 | 34 | 6.7707 | 4.7464
[7 empty] | 8435 | 35 | 8.9987 | 6.3643
[7 empty] | 8436 | 36 | 10.0569 | 7.1327
[7 empty] | 8437 | 37 | 10.1343 | 7.1889
[7 empty] | 8438 | 38 | 10.2117 | 7.2451
[7 empty] | 8439 | 39 | 9.8762 | 7.0015
[7 empty] | 8440 | 40 | 10.9601 | 7.7886
[7 empty] | 8441 | 41 | 11.5279 | 8.2009
[7 empty] | 8442 | 42 | 11.5451 | 8.2134
[7 empty] | 8443 | 43 | 11.9236 | 8.4882
[7 empty] | 8444 | 44 | 13.1107 | 9.3503
[7 empty] | 8445 | 45 | 12.6978 | 9.0505
[7 empty] | 8446 | 46 | 9.8762 | 7.0015
[7 empty] | 8447 | 47 | 6.1771 | 4.3153
[7 empty] | 8448 | 48 | 4.6373 | 3.1971
[7 empty] | 8449 | 49 | 3.9577 | 2.7036
[7 empty] | 8450 | 50 | 3.6394 | 2.4725
[7 empty] | 8451 | 51 | 3.5276 | 2.3913
[7 empty] | 8452 | 52 | 3.562 | 2.4163
[7 empty] | 8453 | 53 | 3.5878 | 2.435
[7 empty] | 8454 | 54 | 4.1814 | 2.866
[7 empty] | 8455 | 55 | 5.3513 | 3.7156
[7 empty] | 8456 | 56 | 5.6008 | 3.8968
[7 empty] | 8457 | 57 | 6.5729 | 4.6027
[7 empty] | 8458 | 58 | 7.7084 | 5.4273
[7 empty] | 8459 | 59 | 8.9471 | 6.3268
[7 empty] | 8460 | 60 | 9.5923 | 6.7953
[7 empty] | 8461 | 61 | 10.2891 | 7.3013
[7 empty] | 8462 | 62 | 10.0827 | 7.1514
[7 empty] | 8463 | 63 | 10.6934 | 7.5949
[7 empty] | 8464 | 64 | 11.6655 | 8.3008
[7 empty] | 8465 | 65 | 12.3021 | 8.7631
[7 empty] | 8466 | 66 | 12.1989 | 8.6882
[7 empty] | 8467 | 67 | 12.9559 | 9.2379
[7 empty] | 8468 | 68 | 13.2054 | 9.419
[7 empty] | 8469 | 69 | 12.6806 | 9.038
[7 empty] | 8470 | 70 | 10.3235 | 7.3263
[7 empty] | 8471 | 71 | 5.6868 | 3.9592
[7 empty] | 8472 | 72 | 4.5734 | 3.1507
[7 empty] | 8473 | 73 | 3.8373 | 2.6162
[7 empty] | 8474 | 74 | 3.605 | 2.4475
[7 empty] | 8475 | 75 | 3.5018 | 2.3725
[7 empty] | 8476 | 76 | 3.4416 | 2.3288
[7 empty] | 8477 | 77 | 3.6222 | 2.46
[7 empty] | 8478 | 78 | 4.0351 | 2.7598
[7 empty] | 8479 | 79 | 5.1793 | 3.5907
[7 empty] | 8480 | 80 | 5.3599 | 3.7219
[7 empty] | 8481 | 81 | 6.5729 | 4.6027
[7 empty] | 8482 | 82 | 7.6912 | 5.4148
[7 empty] | 8483 | 83 | 8.4482 | 5.9645
[7 empty] | 8484 | 84 | 9.7214 | 6.889
[7 empty] | 8485 | 85 | 9.4117 | 6.6642
[7 empty] | 8486 | 86 | 8.8869 | 6.2831
[7 empty] | 8487 | 87 | 9.3428 | 6.6142
[7 empty] | 8488 | 88 | 10.0224 | 7.1077
[7 empty] | 8489 | 89 | 11.4074 | 8.1134
[7 empty] | 8490 | 90 | 10.8053 | 7.6762
[7 empty] | 8491 | 91 | 11.5107 | 8.1884
[7 empty] | 8492 | 92 | 10.8913 | 7.7386
[7 empty] | 8493 | 93 | 8.4138 | 5.9395
[7 empty] | 8494 | 94 | 7.4847 | 5.2648
[7 empty] | 8495 | 95 | 5.575 | 3.878
[7 empty] | 8496 | 96 | 4.5599 | 3.1409
[7 empty] | 8497 | 97 | 4.5083 | 3.1034
[7 empty] | 8498 | 98 | 4.2072 | 2.8848
[7 empty] | 8499 | 99 | 4.147 | 2.841
[7 empty] | 8500 | 100 | 3.7857 | 2.5787
[7 empty] | 8501 | 101 | 3.7254 | 2.5349
[7 empty] | 8502 | 102 | 3.9663 | 2.7099
[7 empty] | 8503 | 103 | 4.7319 | 3.2658
[7 empty] | 8504 | 104 | 4.99 | 3.4532
[7 empty] | 8505 | 105 | 5.4889 | 3.8156
[7 empty] | 8506 | 106 | 6.9858 | 4.9025
[7 empty] | 8507 | 107 | 7.3471 | 5.1649
[7 empty] | 8508 | 108 | 8.9643 | 6.3393
[7 empty] | 8509 | 109 | 8.2847 | 5.8458
[7 empty] | 8510 | 110 | 7.8202 | 5.5085
[7 empty] | 8511 | 111 | 7.6568 | 5.3898
[7 empty] | 8512 | 112 | 7.7256 | 5.4398
[7 empty] | 8513 | 113 | 7.3729 | 5.1836
[7 empty] | 8514 | 114 | 7.5449 | 5.3086
[7 empty] | 8515 | 115 | 7.0804 | 4.9712
[7 empty] | 8516 | 116 | 7.7772 | 5.4772
[7 empty] | 8517 | 117 | 7.3471 | 5.1649
[7 empty] | 8518 | 118 | 6.5556 | 4.5902
[7 empty] | 8519 | 119 | 4.9212 | 3.4033
[7 empty] | 8520 | 120 | 4.5954 | 3.1667
[7 empty] | 8521 | 121 | 3.8459 | 2.6224
[7 empty] | 8522 | 122 | 3.4243 | 2.3163
[7 empty] | 8523 | 123 | 3.3383 | 2.2538
[7 empty] | 8524 | 124 | 3.3039 | 2.2289
[7 empty] | 8525 | 125 | 3.2609 | 2.1976
[7 empty] | 8526 | 126 | 3.4071 | 2.3038
[7 empty] | 8527 | 127 | 4.9556 | 3.4283
[7 empty] | 8528 | 128 | 6.5556 | 4.5902
[7 empty] | 8529 | 129 | 7.2524 | 5.0962
[7 empty] | 8530 | 130 | 7.6998 | 5.421
[7 empty] | 8531 | 131 | 7.8632 | 5.5397
[7 empty] | 8532 | 132 | 7.6051 | 5.3523
[7 empty] | 8533 | 133 | 8.2589 | 5.8271
[7 empty] | 8534 | 134 | 8.5686 | 6.052
[7 empty] | 8535 | 135 | 8.6374 | 6.1019
[7 empty] | 8536 | 136 | 7.803 | 5.496
[7 empty] | 8537 | 137 | 7.6998 | 5.421
[7 empty] | 8538 | 138 | 7.6482 | 5.3835
[7 empty] | 8539 | 139 | 7.3041 | 5.1337
[7 empty] | 8540 | 140 | 7.3127 | 5.1399
[7 empty] | 8541 | 141 | 6.6417 | 4.6526
[7 empty] | 8542 | 142 | 5.9879 | 4.1779
[7 empty] | 8543 | 143 | 5.0846 | 3.522
[7 empty] | 8544 | 144 | 4.4566 | 3.0659
[7 empty] | 8545 | 145 | 3.9749 | 2.7161
[7 empty] | 8546 | 146 | 3.7598 | 2.5599
[7 empty] | 8547 | 147 | 3.691 | 2.51
[7 empty] | 8548 | 148 | 3.6824 | 2.5037
[7 empty] | 8549 | 149 | 3.6824 | 2.5037
[7 empty] | 8550 | 150 | 3.691 | 2.51
[7 empty] | 8551 | 151 | 4.8007 | 3.3158
[7 empty] | 8552 | 152 | 6.3664 | 4.4527
[7 empty] | 8553 | 153 | 6.9944 | 4.9088
[7 empty] | 8554 | 154 | 7.5707 | 5.3273
[7 empty] | 8555 | 155 | 7.4159 | 5.2149
[7 empty] | 8556 | 156 | 7.5879 | 5.3398
[7 empty] | 8557 | 157 | 8.3192 | 5.8708
[7 empty] | 8558 | 158 | 8.6546 | 6.1144
[7 empty] | 8559 | 159 | 8.9299 | 6.3143
[7 empty] | 8560 | 160 | 8.8009 | 6.2206
[7 empty] | 8561 | 161 | 9.5837 | 6.7891
[7 empty] | 8562 | 162 | 9.0762 | 6.4205
[7 empty] | 8563 | 163 | 9.4461 | 6.6891
[7 empty] | 8564 | 164 | 8.0611 | 5.6834
[7 empty] | 8565 | 165 | 11.2698 | 8.0135
[7 empty] | 8566 | 166 | 9.1708 | 6.4892
[7 empty] | 8567 | 167 | 5.4717 | 3.8031
[7 empty] | 8568 | 168 | 4.8093 | 3.3221
[7 empty] | 8569 | 1 | 3.3125 | 2.2351
[7 empty] | 8570 | 2 | 3.2007 | 2.1539
[7 empty] | 8571 | 3 | 3.1921 | 2.1476
[7 empty] | 8572 | 4 | 3.3297 | 2.2476
[7 empty] | 8573 | 5 | 3.3469 | 2.2601
[7 empty] | 8574 | 6 | 3.7857 | 2.5787
[7 empty] | 8575 | 7 | 4.5255 | 3.1159
[7 empty] | 8576 | 8 | 5.2137 | 3.6157
[7 empty] | 8577 | 9 | 5.1879 | 3.5969
[7 empty] | 8578 | 10 | 6.7449 | 4.7276
[7 empty] | 8579 | 11 | 8.8783 | 6.2768
[7 empty] | 8580 | 12 | 9.8676 | 6.9952
[7 empty] | 8581 | 13 | 10.2547 | 7.2763
[7 empty] | 8582 | 14 | 10.031 | 7.1139
[7 empty] | 8583 | 15 | 9.9364 | 7.0452
[7 empty] | 8584 | 16 | 11.1494 | 7.926
[7 empty] | 8585 | 17 | 12.5086 | 8.913
[7 empty] | 8586 | 18 | 12.2591 | 8.7319
[7 empty] | 8587 | 19 | 12.801 | 9.1254
[7 empty] | 8588 | 20 | 12.7322 | 9.0755
[7 empty] | 8589 | 21 | 13.3172 | 9.5002
[7 empty] | 8590 | 22 | 9.2568 | 6.5517
[7 empty] | 8591 | 23 | 5.3857 | 3.7406
[7 empty] | 8592 | 24 | 3.6704 | 2.495
[7 empty] | 8593 | 25 | 3.5706 | 2.4225
[7 empty] | 8594 | 26 | 3.4588 | 2.3413
[7 empty] | 8595 | 27 | 3.3555 | 2.2663
[7 empty] | 8596 | 28 | 3.4416 | 2.3288
[7 empty] | 8597 | 29 | 3.691 | 2.51
[7 empty] | 8598 | 30 | 3.9405 | 2.6911
[7 empty] | 8599 | 31 | 4.8093 | 3.3221
[7 empty] | 8600 | 32 | 5.1706 | 3.5844
[7 empty] | 8601 | 33 | 5.8502 | 4.0779
[7 empty] | 8602 | 34 | 6.7707 | 4.7464
[7 empty] | 8603 | 35 | 8.9987 | 6.3643
[7 empty] | 8604 | 36 | 10.0569 | 7.1327
[7 empty] | 8605 | 37 | 10.1343 | 7.1889
[7 empty] | 8606 | 38 | 10.2117 | 7.2451
[7 empty] | 8607 | 39 | 9.8762 | 7.0015
[7 empty] | 8608 | 40 | 10.9601 | 7.7886
[7 empty] | 8609 | 41 | 11.5279 | 8.2009
[7 empty] | 8610 | 42 | 11.5451 | 8.2134
[7 empty] | 8611 | 43 | 11.9236 | 8.4882
[7 empty] | 8612 | 44 | 13.1107 | 9.3503
[7 empty] | 8613 | 45 | 12.6978 | 9.0505
[7 empty] | 8614 | 46 | 9.8762 | 7.0015
[7 empty] | 8615 | 47 | 6.1771 | 4.3153
[7 empty] | 8616 | 48 | 4.6373 | 3.1971
[7 empty] | 8617 | 49 | 3.9577 | 2.7036
[7 empty] | 8618 | 50 | 3.6394 | 2.4725
[7 empty] | 8619 | 51 | 3.5276 | 2.3913
[7 empty] | 8620 | 52 | 3.562 | 2.4163
[7 empty] | 8621 | 53 | 3.5878 | 2.435
[7 empty] | 8622 | 54 | 4.1814 | 2.866
[7 empty] | 8623 | 55 | 5.3513 | 3.7156
[7 empty] | 8624 | 56 | 5.6008 | 3.8968
[7 empty] | 8625 | 57 | 6.5729 | 4.6027
[7 empty] | 8626 | 58 | 7.7084 | 5.4273
[7 empty] | 8627 | 59 | 8.9471 | 6.3268
[7 empty] | 8628 | 60 | 9.5923 | 6.7953
[7 empty] | 8629 | 61 | 10.2891 | 7.3013
[7 empty] | 8630 | 62 | 10.0827 | 7.1514
[7 empty] | 8631 | 63 | 10.6934 | 7.5949
[7 empty] | 8632 | 64 | 11.6655 | 8.3008
[7 empty] | 8633 | 65 | 12.3021 | 8.7631
[7 empty] | 8634 | 66 | 12.1989 | 8.6882
[7 empty] | 8635 | 67 | 12.9559 | 9.2379
[7 empty] | 8636 | 68 | 13.2054 | 9.419
[7 empty] | 8637 | 69 | 12.6806 | 9.038
[7 empty] | 8638 | 70 | 10.3235 | 7.3263
[7 empty] | 8639 | 71 | 5.6868 | 3.9592
[7 empty] | 8640 | 72 | 4.5734 | 3.1507
[7 empty] | 8641 | 73 | 3.8373 | 2.6162
[7 empty] | 8642 | 74 | 3.605 | 2.4475
[7 empty] | 8643 | 75 | 3.5018 | 2.3725
[7 empty] | 8644 | 76 | 3.4416 | 2.3288
[7 empty] | 8645 | 77 | 3.6222 | 2.46
[7 empty] | 8646 | 78 | 4.0351 | 2.7598
[7 empty] | 8647 | 79 | 5.1793 | 3.5907
[7 empty] | 8648 | 80 | 5.3599 | 3.7219
[7 empty] | 8649 | 81 | 6.5729 | 4.6027
[7 empty] | 8650 | 82 | 7.6912 | 5.4148
[7 empty] | 8651 | 83 | 8.4482 | 5.9645
[7 empty] | 8652 | 84 | 9.7214 | 6.889
[7 empty] | 8653 | 85 | 9.4117 | 6.6642
[7 empty] | 8654 | 86 | 8.8869 | 6.2831
[7 empty] | 8655 | 87 | 9.3428 | 6.6142
[7 empty] | 8656 | 88 | 10.0224 | 7.1077
[7 empty] | 8657 | 89 | 11.4074 | 8.1134
[7 empty] | 8658 | 90 | 10.8053 | 7.6762
[7 empty] | 8659 | 91 | 11.5107 | 8.1884
[7 empty] | 8660 | 92 | 10.8913 | 7.7386
[7 empty] | 8661 | 93 | 8.4138 | 5.9395
[7 empty] | 8662 | 94 | 7.4847 | 5.2648
[7 empty] | 8663 | 95 | 5.575 | 3.878
[7 empty] | 8664 | 96 | 4.5599 | 3.1409
[7 empty] | 8665 | 97 | 4.5083 | 3.1034
[7 empty] | 8666 | 98 | 4.2072 | 2.8848
[7 empty] | 8667 | 99 | 4.147 | 2.841
[7 empty] | 8668 | 100 | 3.7857 | 2.5787
[7 empty] | 8669 | 101 | 3.7254 | 2.5349
[7 empty] | 8670 | 102 | 3.9663 | 2.7099
[7 empty] | 8671 | 103 | 4.7319 | 3.2658
[7 empty] | 8672 | 104 | 4.99 | 3.4532
[7 empty] | 8673 | 105 | 5.4889 | 3.8156
[7 empty] | 8674 | 106 | 6.9858 | 4.9025
[7 empty] | 8675 | 107 | 7.3471 | 5.1649
[7 empty] | 8676 | 108 | 8.9643 | 6.3393
[7 empty] | 8677 | 109 | 8.2847 | 5.8458
[7 empty] | 8678 | 110 | 7.8202 | 5.5085
[7 empty] | 8679 | 111 | 7.6568 | 5.3898
[7 empty] | 8680 | 112 | 7.7256 | 5.4398
[7 empty] | 8681 | 113 | 7.3729 | 5.1836
[7 empty] | 8682 | 114 | 7.5449 | 5.3086
[7 empty] | 8683 | 115 | 7.0804 | 4.9712
[7 empty] | 8684 | 116 | 7.7772 | 5.4772
[7 empty] | 8685 | 117 | 7.3471 | 5.1649
[7 empty] | 8686 | 118 | 6.5556 | 4.5902
[7 empty] | 8687 | 119 | 4.9212 | 3.4033
[7 empty] | 8688 | 120 | 4.5954 | 3.1667
[7 empty] | 8689 | 121 | 3.8459 | 2.6224
[7 empty] | 8690 | 122 | 3.4243 | 2.3163
[7 empty] | 8691 | 123 | 3.3383 | 2.2538
[7 empty] | 8692 | 124 | 3.3039 | 2.2289
[7 empty] | 8693 | 125 | 3.2609 | 2.1976
[7 empty] | 8694 | 126 | 3.4071 | 2.3038
[7 empty] | 8695 | 127 | 4.9556 | 3.4283
[7 empty] | 8696 | 128 | 6.5556 | 4.5902
[7 empty] | 8697 | 129 | 7.2524 | 5.0962
[7 empty] | 8698 | 130 | 7.6998 | 5.421
[7 empty] | 8699 | 131 | 7.8632 | 5.5397
[7 empty] | 8700 | 132 | 7.6051 | 5.3523
[7 empty] | 8701 | 133 | 8.2589 | 5.8271
[7 empty] | 8702 | 134 | 8.5686 | 6.052
[7 empty] | 8703 | 135 | 8.6374 | 6.1019
[7 empty] | 8704 | 136 | 7.803 | 5.496
[7 empty] | 8705 | 137 | 7.6998 | 5.421
[7 empty] | 8706 | 138 | 7.6482 | 5.3835
[7 empty] | 8707 | 139 | 7.3041 | 5.1337
[7 empty] | 8708 | 140 | 7.3127 | 5.1399
[7 empty] | 8709 | 141 | 6.6417 | 4.6526
[7 empty] | 8710 | 142 | 5.9879 | 4.1779
[7 empty] | 8711 | 143 | 5.0846 | 3.522
[7 empty] | 8712 | 144 | 4.4566 | 3.0659
[7 empty] | 8713 | 145 | 3.9749 | 2.7161
[7 empty] | 8714 | 146 | 3.7598 | 2.5599
[7 empty] | 8715 | 147 | 3.691 | 2.51
[7 empty] | 8716 | 148 | 3.6824 | 2.5037
[7 empty] | 8717 | 149 | 3.6824 | 2.5037
[7 empty] | 8718 | 150 | 3.691 | 2.51
[7 empty] | 8719 | 151 | 4.8007 | 3.3158
[7 empty] | 8720 | 152 | 6.3664 | 4.4527
[7 empty] | 8721 | 153 | 6.9944 | 4.9088
[7 empty] | 8722 | 154 | 7.5707 | 5.3273
[7 empty] | 8723 | 155 | 7.4159 | 5.2149
[7 empty] | 8724 | 156 | 7.5879 | 5.3398
[7 empty] | 8725 | 157 | 8.3192 | 5.8708
[7 empty] | 8726 | 158 | 8.6546 | 6.1144
[7 empty] | 8727 | 159 | 8.9299 | 6.3143
[7 empty] | 8728 | 160 | 8.8009 | 6.2206
[7 empty] | 8729 | 161 | 9.5837 | 6.7891
[7 empty] | 8730 | 162 | 9.0762 | 6.4205
[7 empty] | 8731 | 163 | 9.4461 | 6.6891
[7 empty] | 8732 | 164 | 8.0611 | 5.6834
[7 empty] | 8733 | 165 | 11.2698 | 8.0135
[7 empty] | 8734 | 166 | 9.1708 | 6.4892
[7 empty] | 8735 | 167 | 5.4717 | 3.8031
[7 empty] | 8736 | 168 | 4.8093 | 3.3221
[7 empty] | 8737 | 1 | 3.3125 | 2.2351
[7 empty] | 8738 | 2 | 3.2007 | 2.1539
[7 empty] | 8739 | 3 | 3.1921 | 2.1476
[7 empty] | 8740 | 4 | 3.3297 | 2.2476
[7 empty] | 8741 | 5 | 3.3469 | 2.2601
[7 empty] | 8742 | 6 | 3.7857 | 2.5787
[7 empty] | 8743 | 7 | 4.5255 | 3.1159
[7 empty] | 8744 | 8 | 5.2137 | 3.6157
[7 empty] | 8745 | 9 | 5.1879 | 3.5969
[7 empty] | 8746 | 10 | 6.7449 | 4.7276
[7 empty] | 8747 | 11 | 8.8783 | 6.2768
[7 empty] | 8748 | 12 | 9.8676 | 6.9952
[7 empty] | 8749 | 13 | 10.2547 | 7.2763
[7 empty] | 8750 | 14 | 10.031 | 7.1139
[7 empty] | 8751 | 15 | 9.9364 | 7.0452
[7 empty] | 8752 | 16 | 11.1494 | 7.926
[7 empty] | 8753 | 17 | 12.5086 | 8.913
[7 empty] | 8754 | 18 | 12.2591 | 8.7319
[7 empty] | 8755 | 19 | 12.801 | 9.1254
[7 empty] | 8756 | 20 | 12.7322 | 9.0755
[7 empty] | 8757 | 21 | 13.3172 | 9.5002
[7 empty] | 8758 | 22 | 9.2568 | 6.5517
[7 empty] | 8759 | 23 | 5.3857 | 3.7406
[7 empty] | 8760 | 24 | 3.6704 | 2.495

## DC_2017
Hour | Server | Non-server | Total | Unit: MW | PUE | PUE-Max | Hour-year | Hour-week | Total (MWh) | Server (MWh)
1 | 2.048 | 0.94978 | 2.9978 |  | 1.383 | 1.3546 | 1 | 1 | 2.9978 | 2.048
2 | 1.9648 | 0.92279 | 2.8876 |  |  |  | 2 | 2 | 2.8876 | 1.9648
3 | 1.9584 | 0.92071 | 2.8791 |  | Server-Max | Total-Max | 3 | 3 | 2.8791 | 1.9584
4 | 2.0608 | 0.95393 | 3.0147 |  | 9.4882 | 12.853 | 4 | 4 | 3.0147 | 2.0608
5 | 2.0736 | 0.95809 | 3.0317 |  |  |  | 5 | 5 | 3.0317 | 2.0736
6 | 2.3999 | 1.064 | 3.4638 |  | Assumed max utilization rate (UR) |  | 6 | 6 | 3.4638 | 2.3999
7 | 2.95 | 1.2426 | 4.1926 |  | 65% |  | 7 | 7 | 4.1926 | 2.95
8 | 3.4618 | 1.4087 | 4.8705 |  |  |  | 8 | 8 | 4.8705 | 3.4618
9 | 3.4426 | 1.4025 | 4.8451 |  | Servers energy at max UR | Total energy at max UR | 9 | 9 | 4.8451 | 3.4426
10 | 4.6006 | 1.7783 | 6.3789 |  | 7.025 | 9.5902 | 10 | 10 | 6.3789 | 4.6006
11 | 6.1871 | 2.2933 | 8.4804 |  |  |  | 11 | 11 | 8.4804 | 6.1871
12 | 6.9228 | 2.5321 | 9.4549 |  | Non-server power linear model scaling factor |  | 12 | 12 | 9.4549 | 6.9228
13 | 7.2107 | 2.6255 | 9.8362 |  | 0.3028 |  | 13 | 13 | 9.8362 | 7.2107
14 | 7.0444 | 2.5715 | 9.6159 |  |  |  | 14 | 14 | 9.6159 | 7.0444
15 | 6.974 | 2.5487 | 9.5227 |  |  |  | 15 | 15 | 9.5227 | 6.974
16 | 7.8761 | 2.8415 | 10.7175 |  |  |  | 16 | 16 | 10.7175 | 7.8761
17 | 8.8868 | 3.1696 | 12.0564 |  |  |  | 17 | 17 | 12.0564 | 8.8868
18 | 8.7013 | 3.1094 | 11.8107 |  |  |  | 18 | 18 | 11.8107 | 8.7013
19 | 9.1044 | 3.2402 | 12.3445 |  |  |  | 19 | 19 | 12.3445 | 9.1044
20 | 9.0532 | 3.2236 | 12.2767 |  |  |  | 20 | 20 | 12.2767 | 9.0532
21 | 9.4882 | 3.3648 | 12.853 |  |  |  | 21 | 21 | 12.853 | 9.4882
22 | 6.4686 | 2.3847 | 8.8533 |  |  |  | 22 | 22 | 8.8533 | 6.4686
23 | 3.5898 | 1.4502 | 5.04 |  |  |  | 23 | 23 | 5.04 | 3.5898
24 | 2.3142 | 1.0362 | 3.3504 |  |  |  | 24 | 24 | 3.3504 | 2.3142
25 | 2.2399 | 1.0121 | 3.252 |  |  |  | 25 | 25 | 3.252 | 2.2399
26 | 2.1567 | 0.98508 | 3.1418 |  |  |  | 26 | 26 | 3.1418 | 2.1567
27 | 2.08 | 0.96016 | 3.0401 |  |  |  | 27 | 27 | 3.0401 | 2.08
28 | 2.144 | 0.98093 | 3.1249 |  |  |  | 28 | 28 | 3.1249 | 2.144
29 | 2.3295 | 1.0411 | 3.3706 |  |  |  | 29 | 29 | 3.3706 | 2.3295
30 | 2.515 | 1.1014 | 3.6164 |  |  |  | 30 | 30 | 3.6164 | 2.515
31 | 3.1611 | 1.3111 | 4.4722 |  |  |  | 31 | 31 | 4.4722 | 3.1611
32 | 3.4298 | 1.3983 | 4.8281 |  |  |  | 32 | 32 | 4.8281 | 3.4298
33 | 3.9352 | 1.5624 | 5.4976 |  |  |  | 33 | 33 | 5.4976 | 3.9352
34 | 4.6198 | 1.7845 | 6.4043 |  |  |  | 34 | 34 | 6.4043 | 4.6198
35 | 6.2767 | 2.3224 | 8.5991 |  |  |  | 35 | 35 | 8.5991 | 6.2767
36 | 7.0636 | 2.5778 | 9.6413 |  |  |  | 36 | 36 | 9.6413 | 7.0636
37 | 7.1212 | 2.5965 | 9.7176 |  |  |  | 37 | 37 | 9.7176 | 7.1212
38 | 7.1787 | 2.6151 | 9.7939 |  |  |  | 38 | 38 | 9.7939 | 7.1787
39 | 6.9292 | 2.5342 | 9.4634 |  |  |  | 39 | 39 | 9.4634 | 6.9292
40 | 7.7353 | 2.7958 | 10.5311 |  |  |  | 40 | 40 | 10.5311 | 7.7353
41 | 8.1575 | 2.9329 | 11.0904 |  |  |  | 41 | 41 | 11.0904 | 8.1575
42 | 8.1703 | 2.937 | 11.1073 |  |  |  | 42 | 42 | 11.1073 | 8.1703
43 | 8.4518 | 3.0284 | 11.4802 |  |  |  | 43 | 43 | 11.4802 | 8.4518
44 | 9.3347 | 3.3149 | 12.6496 |  |  |  | 44 | 44 | 12.6496 | 9.3347
45 | 9.0276 | 3.2153 | 12.2428 |  |  |  | 45 | 45 | 12.2428 | 9.0276
46 | 6.9292 | 2.5342 | 9.4634 |  |  |  | 46 | 46 | 9.4634 | 6.9292
47 | 4.1783 | 1.6413 | 5.8196 |  |  |  | 47 | 47 | 5.8196 | 4.1783
48 | 3.0332 | 1.2696 | 4.3028 |  |  |  | 48 | 48 | 4.3028 | 3.0332
49 | 2.5278 | 1.1055 | 3.6333 |  |  |  | 49 | 49 | 3.6333 | 2.5278
50 | 2.2911 | 1.0287 | 3.3198 |  |  |  | 50 | 50 | 3.3198 | 2.2911
51 | 2.2079 | 1.0017 | 3.2096 |  |  |  | 51 | 51 | 3.2096 | 2.2079
52 | 2.2335 | 1.01 | 3.2435 |  |  |  | 52 | 52 | 3.2435 | 2.2335
53 | 2.2527 | 1.0162 | 3.2689 |  |  |  | 53 | 53 | 3.2689 | 2.2527
54 | 2.6941 | 1.1595 | 3.8536 |  |  |  | 54 | 54 | 3.8536 | 2.6941
55 | 3.5642 | 1.4419 | 5.0061 |  |  |  | 55 | 55 | 5.0061 | 3.5642
56 | 3.7497 | 1.5021 | 5.2518 |  |  |  | 56 | 56 | 5.2518 | 3.7497
57 | 4.4726 | 1.7368 | 6.2094 |  |  |  | 57 | 57 | 6.2094 | 4.4726
58 | 5.3171 | 2.0109 | 7.328 |  |  |  | 58 | 58 | 7.328 | 5.3171
59 | 6.2383 | 2.3099 | 8.5482 |  |  |  | 59 | 59 | 8.5482 | 6.2383
60 | 6.7181 | 2.4656 | 9.1838 |  |  |  | 60 | 60 | 9.1838 | 6.7181
61 | 7.2363 | 2.6338 | 9.8701 |  |  |  | 61 | 61 | 9.8701 | 7.2363
62 | 7.0828 | 2.584 | 9.6668 |  |  |  | 62 | 62 | 9.6668 | 7.0828
63 | 7.537 | 2.7314 | 10.2684 |  |  |  | 63 | 63 | 10.2684 | 7.537
64 | 8.2599 | 2.9661 | 11.226 |  |  |  | 64 | 64 | 11.226 | 8.2599
65 | 8.7333 | 3.1197 | 11.853 |  |  |  | 65 | 65 | 11.853 | 8.7333
66 | 8.6565 | 3.0948 | 11.7514 |  |  |  | 66 | 66 | 11.7514 | 8.6565
67 | 9.2195 | 3.2776 | 12.4971 |  |  |  | 67 | 67 | 12.4971 | 9.2195
68 | 9.405 | 3.3378 | 12.7428 |  |  |  | 68 | 68 | 12.7428 | 9.405
69 | 9.0148 | 3.2111 | 12.2259 |  |  |  | 69 | 69 | 12.2259 | 9.0148
70 | 7.2619 | 2.6421 | 9.904 |  |  |  | 70 | 70 | 9.904 | 7.2619
71 | 3.8137 | 1.5229 | 5.3366 |  |  |  | 71 | 71 | 5.3366 | 3.8137
72 | 2.9857 | 1.2541 | 4.2398 |  |  |  | 72 | 72 | 4.2398 | 2.9857
73 | 2.4382 | 1.0764 | 3.5147 |  |  |  | 73 | 73 | 3.5147 | 2.4382
74 | 2.2655 | 1.0204 | 3.2859 |  |  |  | 74 | 74 | 3.2859 | 2.2655
75 | 2.1887 | 0.99546 | 3.1842 |  |  |  | 75 | 75 | 3.1842 | 2.1887
76 | 2.144 | 0.98093 | 3.1249 |  |  |  | 76 | 76 | 3.1249 | 2.144
77 | 2.2783 | 1.0245 | 3.3028 |  |  |  | 77 | 77 | 3.3028 | 2.2783
78 | 2.5854 | 1.1242 | 3.7096 |  |  |  | 78 | 78 | 3.7096 | 2.5854
79 | 3.4362 | 1.4004 | 4.8366 |  |  |  | 79 | 79 | 4.8366 | 3.4362
80 | 3.5706 | 1.444 | 5.0146 |  |  |  | 80 | 80 | 5.0146 | 3.5706
81 | 4.4726 | 1.7368 | 6.2094 |  |  |  | 81 | 81 | 6.2094 | 4.4726
82 | 5.3043 | 2.0067 | 7.311 |  |  |  | 82 | 82 | 7.311 | 5.3043
83 | 5.8673 | 2.1895 | 8.0567 |  |  |  | 83 | 83 | 8.0567 | 5.8673
84 | 6.8141 | 2.4968 | 9.3109 |  |  |  | 84 | 84 | 9.3109 | 6.8141
85 | 6.5838 | 2.422 | 9.0058 |  |  |  | 85 | 85 | 9.0058 | 6.5838
86 | 6.1935 | 2.2954 | 8.4889 |  |  |  | 86 | 86 | 8.4889 | 6.1935
87 | 6.5326 | 2.4054 | 8.938 |  |  |  | 87 | 87 | 8.938 | 6.5326
88 | 7.038 | 2.5695 | 9.6075 |  |  |  | 88 | 88 | 9.6075 | 7.038
89 | 8.068 | 2.9038 | 10.9718 |  |  |  | 89 | 89 | 10.9718 | 8.068
90 | 7.6202 | 2.7584 | 10.3786 |  |  |  | 90 | 90 | 10.3786 | 7.6202
91 | 8.1447 | 2.9287 | 11.0734 |  |  |  | 91 | 91 | 11.0734 | 8.1447
92 | 7.6841 | 2.7792 | 10.4633 |  |  |  | 92 | 92 | 10.4633 | 7.6841
93 | 5.8417 | 2.1812 | 8.0228 |  |  |  | 93 | 93 | 8.0228 | 5.8417
94 | 5.1507 | 1.9569 | 7.1076 |  |  |  | 94 | 94 | 7.1076 | 5.1507
95 | 3.7305 | 1.4959 | 5.2264 |  |  |  | 95 | 95 | 5.2264 | 3.7305
96 | 2.9756 | 1.2509 | 4.2265 |  |  |  | 96 | 96 | 4.2265 | 2.9756
97 | 2.9372 | 1.2384 | 4.1757 |  |  |  | 97 | 97 | 4.1757 | 2.9372
98 | 2.7133 | 1.1657 | 3.8791 |  |  |  | 98 | 98 | 3.8791 | 2.7133
99 | 2.6685 | 1.1512 | 3.8197 |  |  |  | 99 | 99 | 3.8197 | 2.6685
100 | 2.3999 | 1.064 | 3.4638 |  |  |  | 100 | 100 | 3.4638 | 2.3999
101 | 2.3551 | 1.0495 | 3.4045 |  |  |  | 101 | 101 | 3.4045 | 2.3551
102 | 2.5342 | 1.1076 | 3.6418 |  |  |  | 102 | 102 | 3.6418 | 2.5342
103 | 3.1036 | 1.2924 | 4.396 |  |  |  | 103 | 103 | 4.396 | 3.1036
104 | 3.2955 | 1.3547 | 4.6502 |  |  |  | 104 | 104 | 4.6502 | 3.2955
105 | 3.6665 | 1.4751 | 5.1417 |  |  |  | 105 | 105 | 5.1417 | 3.6665
106 | 4.7797 | 1.8365 | 6.6161 |  |  |  | 106 | 106 | 6.6161 | 4.7797
107 | 5.0484 | 1.9237 | 6.9721 |  |  |  | 107 | 107 | 6.9721 | 5.0484
108 | 6.2511 | 2.3141 | 8.5652 |  |  |  | 108 | 108 | 8.5652 | 6.2511
109 | 5.7457 | 2.15 | 7.8957 |  |  |  | 109 | 109 | 7.8957 | 5.7457
110 | 5.4002 | 2.0379 | 7.4381 |  |  |  | 110 | 110 | 7.4381 | 5.4002
111 | 5.2787 | 1.9984 | 7.2771 |  |  |  | 111 | 111 | 7.2771 | 5.2787
112 | 5.3299 | 2.015 | 7.3449 |  |  |  | 112 | 112 | 7.3449 | 5.3299
113 | 5.0676 | 1.9299 | 6.9975 |  |  |  | 113 | 113 | 6.9975 | 5.0676
114 | 5.1955 | 1.9714 | 7.167 |  |  |  | 114 | 114 | 7.167 | 5.1955
115 | 4.8501 | 1.8593 | 6.7094 |  |  |  | 115 | 115 | 6.7094 | 4.8501
116 | 5.3683 | 2.0275 | 7.3958 |  |  |  | 116 | 116 | 7.3958 | 5.3683
117 | 5.0484 | 1.9237 | 6.9721 |  |  |  | 117 | 117 | 6.9721 | 5.0484
118 | 4.4598 | 1.7326 | 6.1924 |  |  |  | 118 | 118 | 6.1924 | 4.4598
119 | 3.2443 | 1.3381 | 4.5824 |  |  |  | 119 | 119 | 4.5824 | 3.2443
120 | 3.0021 | 1.2595 | 4.2615 |  |  |  | 120 | 120 | 4.2615 | 3.0021
121 | 2.4446 | 1.0785 | 3.5232 |  |  |  | 121 | 121 | 3.5232 | 2.4446
122 | 2.1312 | 0.97678 | 3.1079 |  |  |  | 122 | 122 | 3.1079 | 2.1312
123 | 2.0672 | 0.95601 | 3.0232 |  |  |  | 123 | 123 | 3.0232 | 2.0672
124 | 2.0416 | 0.9477 | 2.9893 |  |  |  | 124 | 124 | 2.9893 | 2.0416
125 | 2.0096 | 0.93732 | 2.9469 |  |  |  | 125 | 125 | 2.9469 | 2.0096
126 | 2.1184 | 0.97262 | 3.091 |  |  |  | 126 | 126 | 3.091 | 2.1184
127 | 3.2699 | 1.3464 | 4.6163 |  |  |  | 127 | 127 | 4.6163 | 3.2699
128 | 4.4598 | 1.7326 | 6.1924 |  |  |  | 128 | 128 | 6.1924 | 4.4598
129 | 4.978 | 1.9008 | 6.8788 |  |  |  | 129 | 129 | 6.8788 | 4.978
130 | 5.3107 | 2.0088 | 7.3195 |  |  |  | 130 | 130 | 7.3195 | 5.3107
131 | 5.4322 | 2.0483 | 7.4805 |  |  |  | 131 | 131 | 7.4805 | 5.4322
132 | 5.2403 | 1.986 | 7.2263 |  |  |  | 132 | 132 | 7.2263 | 5.2403
133 | 5.7265 | 2.1438 | 7.8703 |  |  |  | 133 | 133 | 7.8703 | 5.7265
134 | 5.9568 | 2.2185 | 8.1754 |  |  |  | 134 | 134 | 8.1754 | 5.9568
135 | 6.008 | 2.2351 | 8.2431 |  |  |  | 135 | 135 | 8.2431 | 6.008
136 | 5.3875 | 2.0337 | 7.4212 |  |  |  | 136 | 136 | 7.4212 | 5.3875
137 | 5.3107 | 2.0088 | 7.3195 |  |  |  | 137 | 137 | 7.3195 | 5.3107
138 | 5.2723 | 1.9963 | 7.2686 |  |  |  | 138 | 138 | 7.2686 | 5.2723
139 | 5.0164 | 1.9133 | 6.9297 |  |  |  | 139 | 139 | 6.9297 | 5.0164
140 | 5.0228 | 1.9154 | 6.9382 |  |  |  | 140 | 140 | 6.9382 | 5.0228
141 | 4.5238 | 1.7534 | 6.2772 |  |  |  | 141 | 141 | 6.2772 | 4.5238
142 | 4.0376 | 1.5956 | 5.6332 |  |  |  | 142 | 142 | 5.6332 | 4.0376
143 | 3.3659 | 1.3775 | 4.7434 |  |  |  | 143 | 143 | 4.7434 | 3.3659
144 | 2.8989 | 1.226 | 4.1248 |  |  |  | 144 | 144 | 4.1248 | 2.8989
145 | 2.5406 | 1.1097 | 3.6503 |  |  |  | 145 | 145 | 3.6503 | 2.5406
146 | 2.3807 | 1.0578 | 3.4384 |  |  |  | 146 | 146 | 3.4384 | 2.3807
147 | 2.3295 | 1.0411 | 3.3706 |  |  |  | 147 | 147 | 3.3706 | 2.3295
148 | 2.3231 | 1.0391 | 3.3622 |  |  |  | 148 | 148 | 3.3622 | 2.3231
149 | 2.3231 | 1.0391 | 3.3622 |  |  |  | 149 | 149 | 3.3622 | 2.3231
150 | 2.3295 | 1.0411 | 3.3706 |  |  |  | 150 | 150 | 3.3706 | 2.3295
151 | 3.1547 | 1.309 | 4.4638 |  |  |  | 151 | 151 | 4.4638 | 3.1547
152 | 4.3191 | 1.6869 | 6.006 |  |  |  | 152 | 152 | 6.006 | 4.3191
153 | 4.7861 | 1.8385 | 6.6246 |  |  |  | 153 | 153 | 6.6246 | 4.7861
154 | 5.2147 | 1.9777 | 7.1924 |  |  |  | 154 | 154 | 7.1924 | 5.2147
155 | 5.0996 | 1.9403 | 7.0398 |  |  |  | 155 | 155 | 7.0398 | 5.0996
156 | 5.2275 | 1.9818 | 7.2093 |  |  |  | 156 | 156 | 7.2093 | 5.2275
157 | 5.7713 | 2.1583 | 7.9296 |  |  |  | 157 | 157 | 7.9296 | 5.7713
158 | 6.0208 | 2.2393 | 8.2601 |  |  |  | 158 | 158 | 8.2601 | 6.0208
159 | 6.2255 | 2.3057 | 8.5313 |  |  |  | 159 | 159 | 8.5313 | 6.2255
160 | 6.1296 | 2.2746 | 8.4041 |  |  |  | 160 | 160 | 8.4041 | 6.1296
161 | 6.7117 | 2.4636 | 9.1753 |  |  |  | 161 | 161 | 9.1753 | 6.7117
162 | 6.3343 | 2.341 | 8.6753 |  |  |  | 162 | 162 | 8.6753 | 6.3343
163 | 6.6094 | 2.4303 | 9.0397 |  |  |  | 163 | 163 | 9.0397 | 6.6094
164 | 5.5794 | 2.096 | 7.6754 |  |  |  | 164 | 164 | 7.6754 | 5.5794
165 | 7.9656 | 2.8706 | 10.8362 |  |  |  | 165 | 165 | 10.8362 | 7.9656
166 | 6.4046 | 2.3639 | 8.7685 |  |  |  | 166 | 166 | 8.7685 | 6.4046
167 | 3.6537 | 1.471 | 5.1247 |  |  |  | 167 | 167 | 5.1247 | 3.6537
168 | 3.1611 | 1.3111 | 4.4722 |  |  |  | 168 | 168 | 4.4722 | 3.1611
[7 empty] | 169 | 1 | 2.9978 | 2.048
[7 empty] | 170 | 2 | 2.8876 | 1.9648
[7 empty] | 171 | 3 | 2.8791 | 1.9584
[7 empty] | 172 | 4 | 3.0147 | 2.0608
[7 empty] | 173 | 5 | 3.0317 | 2.0736
[7 empty] | 174 | 6 | 3.4638 | 2.3999
[7 empty] | 175 | 7 | 4.1926 | 2.95
[7 empty] | 176 | 8 | 4.8705 | 3.4618
[7 empty] | 177 | 9 | 4.8451 | 3.4426
[7 empty] | 178 | 10 | 6.3789 | 4.6006
[7 empty] | 179 | 11 | 8.4804 | 6.1871
[7 empty] | 180 | 12 | 9.4549 | 6.9228
[7 empty] | 181 | 13 | 9.8362 | 7.2107
[7 empty] | 182 | 14 | 9.6159 | 7.0444
[7 empty] | 183 | 15 | 9.5227 | 6.974
[7 empty] | 184 | 16 | 10.7175 | 7.8761
[7 empty] | 185 | 17 | 12.0564 | 8.8868
[7 empty] | 186 | 18 | 11.8107 | 8.7013
[7 empty] | 187 | 19 | 12.3445 | 9.1044
[7 empty] | 188 | 20 | 12.2767 | 9.0532
[7 empty] | 189 | 21 | 12.853 | 9.4882
[7 empty] | 190 | 22 | 8.8533 | 6.4686
[7 empty] | 191 | 23 | 5.04 | 3.5898
[7 empty] | 192 | 24 | 3.3504 | 2.3142
[7 empty] | 193 | 25 | 3.252 | 2.2399
[7 empty] | 194 | 26 | 3.1418 | 2.1567
[7 empty] | 195 | 27 | 3.0401 | 2.08
[7 empty] | 196 | 28 | 3.1249 | 2.144
[7 empty] | 197 | 29 | 3.3706 | 2.3295
[7 empty] | 198 | 30 | 3.6164 | 2.515
[7 empty] | 199 | 31 | 4.4722 | 3.1611
[7 empty] | 200 | 32 | 4.8281 | 3.4298
[7 empty] | 201 | 33 | 5.4976 | 3.9352
[7 empty] | 202 | 34 | 6.4043 | 4.6198
[7 empty] | 203 | 35 | 8.5991 | 6.2767
[7 empty] | 204 | 36 | 9.6413 | 7.0636
[7 empty] | 205 | 37 | 9.7176 | 7.1212
[7 empty] | 206 | 38 | 9.7939 | 7.1787
[7 empty] | 207 | 39 | 9.4634 | 6.9292
[7 empty] | 208 | 40 | 10.5311 | 7.7353
[7 empty] | 209 | 41 | 11.0904 | 8.1575
[7 empty] | 210 | 42 | 11.1073 | 8.1703
[7 empty] | 211 | 43 | 11.4802 | 8.4518
[7 empty] | 212 | 44 | 12.6496 | 9.3347
[7 empty] | 213 | 45 | 12.2428 | 9.0276
[7 empty] | 214 | 46 | 9.4634 | 6.9292
[7 empty] | 215 | 47 | 5.8196 | 4.1783
[7 empty] | 216 | 48 | 4.3028 | 3.0332
[7 empty] | 217 | 49 | 3.6333 | 2.5278
[7 empty] | 218 | 50 | 3.3198 | 2.2911
[7 empty] | 219 | 51 | 3.2096 | 2.2079
[7 empty] | 220 | 52 | 3.2435 | 2.2335
[7 empty] | 221 | 53 | 3.2689 | 2.2527
[7 empty] | 222 | 54 | 3.8536 | 2.6941
[7 empty] | 223 | 55 | 5.0061 | 3.5642
[7 empty] | 224 | 56 | 5.2518 | 3.7497
[7 empty] | 225 | 57 | 6.2094 | 4.4726
[7 empty] | 226 | 58 | 7.328 | 5.3171
[7 empty] | 227 | 59 | 8.5482 | 6.2383
[7 empty] | 228 | 60 | 9.1838 | 6.7181
[7 empty] | 229 | 61 | 9.8701 | 7.2363
[7 empty] | 230 | 62 | 9.6668 | 7.0828
[7 empty] | 231 | 63 | 10.2684 | 7.537
[7 empty] | 232 | 64 | 11.226 | 8.2599
[7 empty] | 233 | 65 | 11.853 | 8.7333
[7 empty] | 234 | 66 | 11.7514 | 8.6565
[7 empty] | 235 | 67 | 12.4971 | 9.2195
[7 empty] | 236 | 68 | 12.7428 | 9.405
[7 empty] | 237 | 69 | 12.2259 | 9.0148
[7 empty] | 238 | 70 | 9.904 | 7.2619
[7 empty] | 239 | 71 | 5.3366 | 3.8137
[7 empty] | 240 | 72 | 4.2398 | 2.9857
[7 empty] | 241 | 73 | 3.5147 | 2.4382
[7 empty] | 242 | 74 | 3.2859 | 2.2655
[7 empty] | 243 | 75 | 3.1842 | 2.1887
[7 empty] | 244 | 76 | 3.1249 | 2.144
[7 empty] | 245 | 77 | 3.3028 | 2.2783
[7 empty] | 246 | 78 | 3.7096 | 2.5854
[7 empty] | 247 | 79 | 4.8366 | 3.4362
[7 empty] | 248 | 80 | 5.0146 | 3.5706
[7 empty] | 249 | 81 | 6.2094 | 4.4726
[7 empty] | 250 | 82 | 7.311 | 5.3043
[7 empty] | 251 | 83 | 8.0567 | 5.8673
[7 empty] | 252 | 84 | 9.3109 | 6.8141
[7 empty] | 253 | 85 | 9.0058 | 6.5838
[7 empty] | 254 | 86 | 8.4889 | 6.1935
[7 empty] | 255 | 87 | 8.938 | 6.5326
[7 empty] | 256 | 88 | 9.6075 | 7.038
[7 empty] | 257 | 89 | 10.9718 | 8.068
[7 empty] | 258 | 90 | 10.3786 | 7.6202
[7 empty] | 259 | 91 | 11.0734 | 8.1447
[7 empty] | 260 | 92 | 10.4633 | 7.6841
[7 empty] | 261 | 93 | 8.0228 | 5.8417
[7 empty] | 262 | 94 | 7.1076 | 5.1507
[7 empty] | 263 | 95 | 5.2264 | 3.7305
[7 empty] | 264 | 96 | 4.2265 | 2.9756
[7 empty] | 265 | 97 | 4.1757 | 2.9372
[7 empty] | 266 | 98 | 3.8791 | 2.7133
[7 empty] | 267 | 99 | 3.8197 | 2.6685
[7 empty] | 268 | 100 | 3.4638 | 2.3999
[7 empty] | 269 | 101 | 3.4045 | 2.3551
[7 empty] | 270 | 102 | 3.6418 | 2.5342
[7 empty] | 271 | 103 | 4.396 | 3.1036
[7 empty] | 272 | 104 | 4.6502 | 3.2955
[7 empty] | 273 | 105 | 5.1417 | 3.6665
[7 empty] | 274 | 106 | 6.6161 | 4.7797
[7 empty] | 275 | 107 | 6.9721 | 5.0484
[7 empty] | 276 | 108 | 8.5652 | 6.2511
[7 empty] | 277 | 109 | 7.8957 | 5.7457
[7 empty] | 278 | 110 | 7.4381 | 5.4002
[7 empty] | 279 | 111 | 7.2771 | 5.2787
[7 empty] | 280 | 112 | 7.3449 | 5.3299
[7 empty] | 281 | 113 | 6.9975 | 5.0676
[7 empty] | 282 | 114 | 7.167 | 5.1955
[7 empty] | 283 | 115 | 6.7094 | 4.8501
[7 empty] | 284 | 116 | 7.3958 | 5.3683
[7 empty] | 285 | 117 | 6.9721 | 5.0484
[7 empty] | 286 | 118 | 6.1924 | 4.4598
[7 empty] | 287 | 119 | 4.5824 | 3.2443
[7 empty] | 288 | 120 | 4.2615 | 3.0021
[7 empty] | 289 | 121 | 3.5232 | 2.4446
[7 empty] | 290 | 122 | 3.1079 | 2.1312
[7 empty] | 291 | 123 | 3.0232 | 2.0672
[7 empty] | 292 | 124 | 2.9893 | 2.0416
[7 empty] | 293 | 125 | 2.9469 | 2.0096
[7 empty] | 294 | 126 | 3.091 | 2.1184
[7 empty] | 295 | 127 | 4.6163 | 3.2699
[7 empty] | 296 | 128 | 6.1924 | 4.4598
[7 empty] | 297 | 129 | 6.8788 | 4.978
[7 empty] | 298 | 130 | 7.3195 | 5.3107
[7 empty] | 299 | 131 | 7.4805 | 5.4322
[7 empty] | 300 | 132 | 7.2263 | 5.2403
[7 empty] | 301 | 133 | 7.8703 | 5.7265
[7 empty] | 302 | 134 | 8.1754 | 5.9568
[7 empty] | 303 | 135 | 8.2431 | 6.008
[7 empty] | 304 | 136 | 7.4212 | 5.3875
[7 empty] | 305 | 137 | 7.3195 | 5.3107
[7 empty] | 306 | 138 | 7.2686 | 5.2723
[7 empty] | 307 | 139 | 6.9297 | 5.0164
[7 empty] | 308 | 140 | 6.9382 | 5.0228
[7 empty] | 309 | 141 | 6.2772 | 4.5238
[7 empty] | 310 | 142 | 5.6332 | 4.0376
[7 empty] | 311 | 143 | 4.7434 | 3.3659
[7 empty] | 312 | 144 | 4.1248 | 2.8989
[7 empty] | 313 | 145 | 3.6503 | 2.5406
[7 empty] | 314 | 146 | 3.4384 | 2.3807
[7 empty] | 315 | 147 | 3.3706 | 2.3295
[7 empty] | 316 | 148 | 3.3622 | 2.3231
[7 empty] | 317 | 149 | 3.3622 | 2.3231
[7 empty] | 318 | 150 | 3.3706 | 2.3295
[7 empty] | 319 | 151 | 4.4638 | 3.1547
[7 empty] | 320 | 152 | 6.006 | 4.3191
[7 empty] | 321 | 153 | 6.6246 | 4.7861
[7 empty] | 322 | 154 | 7.1924 | 5.2147
[7 empty] | 323 | 155 | 7.0398 | 5.0996
[7 empty] | 324 | 156 | 7.2093 | 5.2275
[7 empty] | 325 | 157 | 7.9296 | 5.7713
[7 empty] | 326 | 158 | 8.2601 | 6.0208
[7 empty] | 327 | 159 | 8.5313 | 6.2255
[7 empty] | 328 | 160 | 8.4041 | 6.1296
[7 empty] | 329 | 161 | 9.1753 | 6.7117
[7 empty] | 330 | 162 | 8.6753 | 6.3343
[7 empty] | 331 | 163 | 9.0397 | 6.6094
[7 empty] | 332 | 164 | 7.6754 | 5.5794
[7 empty] | 333 | 165 | 10.8362 | 7.9656
[7 empty] | 334 | 166 | 8.7685 | 6.4046
[7 empty] | 335 | 167 | 5.1247 | 3.6537
[7 empty] | 336 | 168 | 4.4722 | 3.1611
[7 empty] | 337 | 1 | 2.9978 | 2.048
[7 empty] | 338 | 2 | 2.8876 | 1.9648
[7 empty] | 339 | 3 | 2.8791 | 1.9584
[7 empty] | 340 | 4 | 3.0147 | 2.0608
[7 empty] | 341 | 5 | 3.0317 | 2.0736
[7 empty] | 342 | 6 | 3.4638 | 2.3999
[7 empty] | 343 | 7 | 4.1926 | 2.95
[7 empty] | 344 | 8 | 4.8705 | 3.4618
[7 empty] | 345 | 9 | 4.8451 | 3.4426
[7 empty] | 346 | 10 | 6.3789 | 4.6006
[7 empty] | 347 | 11 | 8.4804 | 6.1871
[7 empty] | 348 | 12 | 9.4549 | 6.9228
[7 empty] | 349 | 13 | 9.8362 | 7.2107
[7 empty] | 350 | 14 | 9.6159 | 7.0444
[7 empty] | 351 | 15 | 9.5227 | 6.974
[7 empty] | 352 | 16 | 10.7175 | 7.8761
[7 empty] | 353 | 17 | 12.0564 | 8.8868
[7 empty] | 354 | 18 | 11.8107 | 8.7013
[7 empty] | 355 | 19 | 12.3445 | 9.1044
[7 empty] | 356 | 20 | 12.2767 | 9.0532
[7 empty] | 357 | 21 | 12.853 | 9.4882
[7 empty] | 358 | 22 | 8.8533 | 6.4686
[7 empty] | 359 | 23 | 5.04 | 3.5898
[7 empty] | 360 | 24 | 3.3504 | 2.3142
[7 empty] | 361 | 25 | 3.252 | 2.2399
[7 empty] | 362 | 26 | 3.1418 | 2.1567
[7 empty] | 363 | 27 | 3.0401 | 2.08
[7 empty] | 364 | 28 | 3.1249 | 2.144
[7 empty] | 365 | 29 | 3.3706 | 2.3295
[7 empty] | 366 | 30 | 3.6164 | 2.515
[7 empty] | 367 | 31 | 4.4722 | 3.1611
[7 empty] | 368 | 32 | 4.8281 | 3.4298
[7 empty] | 369 | 33 | 5.4976 | 3.9352
[7 empty] | 370 | 34 | 6.4043 | 4.6198
[7 empty] | 371 | 35 | 8.5991 | 6.2767
[7 empty] | 372 | 36 | 9.6413 | 7.0636
[7 empty] | 373 | 37 | 9.7176 | 7.1212
[7 empty] | 374 | 38 | 9.7939 | 7.1787
[7 empty] | 375 | 39 | 9.4634 | 6.9292
[7 empty] | 376 | 40 | 10.5311 | 7.7353
[7 empty] | 377 | 41 | 11.0904 | 8.1575
[7 empty] | 378 | 42 | 11.1073 | 8.1703
[7 empty] | 379 | 43 | 11.4802 | 8.4518
[7 empty] | 380 | 44 | 12.6496 | 9.3347
[7 empty] | 381 | 45 | 12.2428 | 9.0276
[7 empty] | 382 | 46 | 9.4634 | 6.9292
[7 empty] | 383 | 47 | 5.8196 | 4.1783
[7 empty] | 384 | 48 | 4.3028 | 3.0332
[7 empty] | 385 | 49 | 3.6333 | 2.5278
[7 empty] | 386 | 50 | 3.3198 | 2.2911
[7 empty] | 387 | 51 | 3.2096 | 2.2079
[7 empty] | 388 | 52 | 3.2435 | 2.2335
[7 empty] | 389 | 53 | 3.2689 | 2.2527
[7 empty] | 390 | 54 | 3.8536 | 2.6941
[7 empty] | 391 | 55 | 5.0061 | 3.5642
[7 empty] | 392 | 56 | 5.2518 | 3.7497
[7 empty] | 393 | 57 | 6.2094 | 4.4726
[7 empty] | 394 | 58 | 7.328 | 5.3171
[7 empty] | 395 | 59 | 8.5482 | 6.2383
[7 empty] | 396 | 60 | 9.1838 | 6.7181
[7 empty] | 397 | 61 | 9.8701 | 7.2363
[7 empty] | 398 | 62 | 9.6668 | 7.0828
[7 empty] | 399 | 63 | 10.2684 | 7.537
[7 empty] | 400 | 64 | 11.226 | 8.2599
[7 empty] | 401 | 65 | 11.853 | 8.7333
[7 empty] | 402 | 66 | 11.7514 | 8.6565
[7 empty] | 403 | 67 | 12.4971 | 9.2195
[7 empty] | 404 | 68 | 12.7428 | 9.405
[7 empty] | 405 | 69 | 12.2259 | 9.0148
[7 empty] | 406 | 70 | 9.904 | 7.2619
[7 empty] | 407 | 71 | 5.3366 | 3.8137
[7 empty] | 408 | 72 | 4.2398 | 2.9857
[7 empty] | 409 | 73 | 3.5147 | 2.4382
[7 empty] | 410 | 74 | 3.2859 | 2.2655
[7 empty] | 411 | 75 | 3.1842 | 2.1887
[7 empty] | 412 | 76 | 3.1249 | 2.144
[7 empty] | 413 | 77 | 3.3028 | 2.2783
[7 empty] | 414 | 78 | 3.7096 | 2.5854
[7 empty] | 415 | 79 | 4.8366 | 3.4362
[7 empty] | 416 | 80 | 5.0146 | 3.5706
[7 empty] | 417 | 81 | 6.2094 | 4.4726
[7 empty] | 418 | 82 | 7.311 | 5.3043
[7 empty] | 419 | 83 | 8.0567 | 5.8673
[7 empty] | 420 | 84 | 9.3109 | 6.8141
[7 empty] | 421 | 85 | 9.0058 | 6.5838
[7 empty] | 422 | 86 | 8.4889 | 6.1935
[7 empty] | 423 | 87 | 8.938 | 6.5326
[7 empty] | 424 | 88 | 9.6075 | 7.038
[7 empty] | 425 | 89 | 10.9718 | 8.068
[7 empty] | 426 | 90 | 10.3786 | 7.6202
[7 empty] | 427 | 91 | 11.0734 | 8.1447
[7 empty] | 428 | 92 | 10.4633 | 7.6841
[7 empty] | 429 | 93 | 8.0228 | 5.8417
[7 empty] | 430 | 94 | 7.1076 | 5.1507
[7 empty] | 431 | 95 | 5.2264 | 3.7305
[7 empty] | 432 | 96 | 4.2265 | 2.9756
[7 empty] | 433 | 97 | 4.1757 | 2.9372
[7 empty] | 434 | 98 | 3.8791 | 2.7133
[7 empty] | 435 | 99 | 3.8197 | 2.6685
[7 empty] | 436 | 100 | 3.4638 | 2.3999
[7 empty] | 437 | 101 | 3.4045 | 2.3551
[7 empty] | 438 | 102 | 3.6418 | 2.5342
[7 empty] | 439 | 103 | 4.396 | 3.1036
[7 empty] | 440 | 104 | 4.6502 | 3.2955
[7 empty] | 441 | 105 | 5.1417 | 3.6665
[7 empty] | 442 | 106 | 6.6161 | 4.7797
[7 empty] | 443 | 107 | 6.9721 | 5.0484
[7 empty] | 444 | 108 | 8.5652 | 6.2511
[7 empty] | 445 | 109 | 7.8957 | 5.7457
[7 empty] | 446 | 110 | 7.4381 | 5.4002
[7 empty] | 447 | 111 | 7.2771 | 5.2787
[7 empty] | 448 | 112 | 7.3449 | 5.3299
[7 empty] | 449 | 113 | 6.9975 | 5.0676
[7 empty] | 450 | 114 | 7.167 | 5.1955
[7 empty] | 451 | 115 | 6.7094 | 4.8501
[7 empty] | 452 | 116 | 7.3958 | 5.3683
[7 empty] | 453 | 117 | 6.9721 | 5.0484
[7 empty] | 454 | 118 | 6.1924 | 4.4598
[7 empty] | 455 | 119 | 4.5824 | 3.2443
[7 empty] | 456 | 120 | 4.2615 | 3.0021
[7 empty] | 457 | 121 | 3.5232 | 2.4446
[7 empty] | 458 | 122 | 3.1079 | 2.1312
[7 empty] | 459 | 123 | 3.0232 | 2.0672
[7 empty] | 460 | 124 | 2.9893 | 2.0416
[7 empty] | 461 | 125 | 2.9469 | 2.0096
[7 empty] | 462 | 126 | 3.091 | 2.1184
[7 empty] | 463 | 127 | 4.6163 | 3.2699
[7 empty] | 464 | 128 | 6.1924 | 4.4598
[7 empty] | 465 | 129 | 6.8788 | 4.978
[7 empty] | 466 | 130 | 7.3195 | 5.3107
[7 empty] | 467 | 131 | 7.4805 | 5.4322
[7 empty] | 468 | 132 | 7.2263 | 5.2403
[7 empty] | 469 | 133 | 7.8703 | 5.7265
[7 empty] | 470 | 134 | 8.1754 | 5.9568
[7 empty] | 471 | 135 | 8.2431 | 6.008
[7 empty] | 472 | 136 | 7.4212 | 5.3875
[7 empty] | 473 | 137 | 7.3195 | 5.3107
[7 empty] | 474 | 138 | 7.2686 | 5.2723
[7 empty] | 475 | 139 | 6.9297 | 5.0164
[7 empty] | 476 | 140 | 6.9382 | 5.0228
[7 empty] | 477 | 141 | 6.2772 | 4.5238
[7 empty] | 478 | 142 | 5.6332 | 4.0376
[7 empty] | 479 | 143 | 4.7434 | 3.3659
[7 empty] | 480 | 144 | 4.1248 | 2.8989
[7 empty] | 481 | 145 | 3.6503 | 2.5406
[7 empty] | 482 | 146 | 3.4384 | 2.3807
[7 empty] | 483 | 147 | 3.3706 | 2.3295
[7 empty] | 484 | 148 | 3.3622 | 2.3231
[7 empty] | 485 | 149 | 3.3622 | 2.3231
[7 empty] | 486 | 150 | 3.3706 | 2.3295
[7 empty] | 487 | 151 | 4.4638 | 3.1547
[7 empty] | 488 | 152 | 6.006 | 4.3191
[7 empty] | 489 | 153 | 6.6246 | 4.7861
[7 empty] | 490 | 154 | 7.1924 | 5.2147
[7 empty] | 491 | 155 | 7.0398 | 5.0996
[7 empty] | 492 | 156 | 7.2093 | 5.2275
[7 empty] | 493 | 157 | 7.9296 | 5.7713
[7 empty] | 494 | 158 | 8.2601 | 6.0208
[7 empty] | 495 | 159 | 8.5313 | 6.2255
[7 empty] | 496 | 160 | 8.4041 | 6.1296
[7 empty] | 497 | 161 | 9.1753 | 6.7117
[7 empty] | 498 | 162 | 8.6753 | 6.3343
[7 empty] | 499 | 163 | 9.0397 | 6.6094
[7 empty] | 500 | 164 | 7.6754 | 5.5794
[7 empty] | 501 | 165 | 10.8362 | 7.9656
[7 empty] | 502 | 166 | 8.7685 | 6.4046
[7 empty] | 503 | 167 | 5.1247 | 3.6537
[7 empty] | 504 | 168 | 4.4722 | 3.1611
[7 empty] | 505 | 1 | 2.9978 | 2.048
[7 empty] | 506 | 2 | 2.8876 | 1.9648
[7 empty] | 507 | 3 | 2.8791 | 1.9584
[7 empty] | 508 | 4 | 3.0147 | 2.0608
[7 empty] | 509 | 5 | 3.0317 | 2.0736
[7 empty] | 510 | 6 | 3.4638 | 2.3999
[7 empty] | 511 | 7 | 4.1926 | 2.95
[7 empty] | 512 | 8 | 4.8705 | 3.4618
[7 empty] | 513 | 9 | 4.8451 | 3.4426
[7 empty] | 514 | 10 | 6.3789 | 4.6006
[7 empty] | 515 | 11 | 8.4804 | 6.1871
[7 empty] | 516 | 12 | 9.4549 | 6.9228
[7 empty] | 517 | 13 | 9.8362 | 7.2107
[7 empty] | 518 | 14 | 9.6159 | 7.0444
[7 empty] | 519 | 15 | 9.5227 | 6.974
[7 empty] | 520 | 16 | 10.7175 | 7.8761
[7 empty] | 521 | 17 | 12.0564 | 8.8868
[7 empty] | 522 | 18 | 11.8107 | 8.7013
[7 empty] | 523 | 19 | 12.3445 | 9.1044
[7 empty] | 524 | 20 | 12.2767 | 9.0532
[7 empty] | 525 | 21 | 12.853 | 9.4882
[7 empty] | 526 | 22 | 8.8533 | 6.4686
[7 empty] | 527 | 23 | 5.04 | 3.5898
[7 empty] | 528 | 24 | 3.3504 | 2.3142
[7 empty] | 529 | 25 | 3.252 | 2.2399
[7 empty] | 530 | 26 | 3.1418 | 2.1567
[7 empty] | 531 | 27 | 3.0401 | 2.08
[7 empty] | 532 | 28 | 3.1249 | 2.144
[7 empty] | 533 | 29 | 3.3706 | 2.3295
[7 empty] | 534 | 30 | 3.6164 | 2.515
[7 empty] | 535 | 31 | 4.4722 | 3.1611
[7 empty] | 536 | 32 | 4.8281 | 3.4298
[7 empty] | 537 | 33 | 5.4976 | 3.9352
[7 empty] | 538 | 34 | 6.4043 | 4.6198
[7 empty] | 539 | 35 | 8.5991 | 6.2767
[7 empty] | 540 | 36 | 9.6413 | 7.0636
[7 empty] | 541 | 37 | 9.7176 | 7.1212
[7 empty] | 542 | 38 | 9.7939 | 7.1787
[7 empty] | 543 | 39 | 9.4634 | 6.9292
[7 empty] | 544 | 40 | 10.5311 | 7.7353
[7 empty] | 545 | 41 | 11.0904 | 8.1575
[7 empty] | 546 | 42 | 11.1073 | 8.1703
[7 empty] | 547 | 43 | 11.4802 | 8.4518
[7 empty] | 548 | 44 | 12.6496 | 9.3347
[7 empty] | 549 | 45 | 12.2428 | 9.0276
[7 empty] | 550 | 46 | 9.4634 | 6.9292
[7 empty] | 551 | 47 | 5.8196 | 4.1783
[7 empty] | 552 | 48 | 4.3028 | 3.0332
[7 empty] | 553 | 49 | 3.6333 | 2.5278
[7 empty] | 554 | 50 | 3.3198 | 2.2911
[7 empty] | 555 | 51 | 3.2096 | 2.2079
[7 empty] | 556 | 52 | 3.2435 | 2.2335
[7 empty] | 557 | 53 | 3.2689 | 2.2527
[7 empty] | 558 | 54 | 3.8536 | 2.6941
[7 empty] | 559 | 55 | 5.0061 | 3.5642
[7 empty] | 560 | 56 | 5.2518 | 3.7497
[7 empty] | 561 | 57 | 6.2094 | 4.4726
[7 empty] | 562 | 58 | 7.328 | 5.3171
[7 empty] | 563 | 59 | 8.5482 | 6.2383
[7 empty] | 564 | 60 | 9.1838 | 6.7181
[7 empty] | 565 | 61 | 9.8701 | 7.2363
[7 empty] | 566 | 62 | 9.6668 | 7.0828
[7 empty] | 567 | 63 | 10.2684 | 7.537
[7 empty] | 568 | 64 | 11.226 | 8.2599
[7 empty] | 569 | 65 | 11.853 | 8.7333
[7 empty] | 570 | 66 | 11.7514 | 8.6565
[7 empty] | 571 | 67 | 12.4971 | 9.2195
[7 empty] | 572 | 68 | 12.7428 | 9.405
[7 empty] | 573 | 69 | 12.2259 | 9.0148
[7 empty] | 574 | 70 | 9.904 | 7.2619
[7 empty] | 575 | 71 | 5.3366 | 3.8137
[7 empty] | 576 | 72 | 4.2398 | 2.9857
[7 empty] | 577 | 73 | 3.5147 | 2.4382
[7 empty] | 578 | 74 | 3.2859 | 2.2655
[7 empty] | 579 | 75 | 3.1842 | 2.1887
[7 empty] | 580 | 76 | 3.1249 | 2.144
[7 empty] | 581 | 77 | 3.3028 | 2.2783
[7 empty] | 582 | 78 | 3.7096 | 2.5854
[7 empty] | 583 | 79 | 4.8366 | 3.4362
[7 empty] | 584 | 80 | 5.0146 | 3.5706
[7 empty] | 585 | 81 | 6.2094 | 4.4726
[7 empty] | 586 | 82 | 7.311 | 5.3043
[7 empty] | 587 | 83 | 8.0567 | 5.8673
[7 empty] | 588 | 84 | 9.3109 | 6.8141
[7 empty] | 589 | 85 | 9.0058 | 6.5838
[7 empty] | 590 | 86 | 8.4889 | 6.1935
[7 empty] | 591 | 87 | 8.938 | 6.5326
[7 empty] | 592 | 88 | 9.6075 | 7.038
[7 empty] | 593 | 89 | 10.9718 | 8.068
[7 empty] | 594 | 90 | 10.3786 | 7.6202
[7 empty] | 595 | 91 | 11.0734 | 8.1447
[7 empty] | 596 | 92 | 10.4633 | 7.6841
[7 empty] | 597 | 93 | 8.0228 | 5.8417
[7 empty] | 598 | 94 | 7.1076 | 5.1507
[7 empty] | 599 | 95 | 5.2264 | 3.7305
[7 empty] | 600 | 96 | 4.2265 | 2.9756
[7 empty] | 601 | 97 | 4.1757 | 2.9372
[7 empty] | 602 | 98 | 3.8791 | 2.7133
[7 empty] | 603 | 99 | 3.8197 | 2.6685
[7 empty] | 604 | 100 | 3.4638 | 2.3999
[7 empty] | 605 | 101 | 3.4045 | 2.3551
[7 empty] | 606 | 102 | 3.6418 | 2.5342
[7 empty] | 607 | 103 | 4.396 | 3.1036
[7 empty] | 608 | 104 | 4.6502 | 3.2955
[7 empty] | 609 | 105 | 5.1417 | 3.6665
[7 empty] | 610 | 106 | 6.6161 | 4.7797
[7 empty] | 611 | 107 | 6.9721 | 5.0484
[7 empty] | 612 | 108 | 8.5652 | 6.2511
[7 empty] | 613 | 109 | 7.8957 | 5.7457
[7 empty] | 614 | 110 | 7.4381 | 5.4002
[7 empty] | 615 | 111 | 7.2771 | 5.2787
[7 empty] | 616 | 112 | 7.3449 | 5.3299
[7 empty] | 617 | 113 | 6.9975 | 5.0676
[7 empty] | 618 | 114 | 7.167 | 5.1955
[7 empty] | 619 | 115 | 6.7094 | 4.8501
[7 empty] | 620 | 116 | 7.3958 | 5.3683
[7 empty] | 621 | 117 | 6.9721 | 5.0484
[7 empty] | 622 | 118 | 6.1924 | 4.4598
[7 empty] | 623 | 119 | 4.5824 | 3.2443
[7 empty] | 624 | 120 | 4.2615 | 3.0021
[7 empty] | 625 | 121 | 3.5232 | 2.4446
[7 empty] | 626 | 122 | 3.1079 | 2.1312
[7 empty] | 627 | 123 | 3.0232 | 2.0672
[7 empty] | 628 | 124 | 2.9893 | 2.0416
[7 empty] | 629 | 125 | 2.9469 | 2.0096
[7 empty] | 630 | 126 | 3.091 | 2.1184
[7 empty] | 631 | 127 | 4.6163 | 3.2699
[7 empty] | 632 | 128 | 6.1924 | 4.4598
[7 empty] | 633 | 129 | 6.8788 | 4.978
[7 empty] | 634 | 130 | 7.3195 | 5.3107
[7 empty] | 635 | 131 | 7.4805 | 5.4322
[7 empty] | 636 | 132 | 7.2263 | 5.2403
[7 empty] | 637 | 133 | 7.8703 | 5.7265
[7 empty] | 638 | 134 | 8.1754 | 5.9568
[7 empty] | 639 | 135 | 8.2431 | 6.008
[7 empty] | 640 | 136 | 7.4212 | 5.3875
[7 empty] | 641 | 137 | 7.3195 | 5.3107
[7 empty] | 642 | 138 | 7.2686 | 5.2723
[7 empty] | 643 | 139 | 6.9297 | 5.0164
[7 empty] | 644 | 140 | 6.9382 | 5.0228
[7 empty] | 645 | 141 | 6.2772 | 4.5238
[7 empty] | 646 | 142 | 5.6332 | 4.0376
[7 empty] | 647 | 143 | 4.7434 | 3.3659
[7 empty] | 648 | 144 | 4.1248 | 2.8989
[7 empty] | 649 | 145 | 3.6503 | 2.5406
[7 empty] | 650 | 146 | 3.4384 | 2.3807
[7 empty] | 651 | 147 | 3.3706 | 2.3295
[7 empty] | 652 | 148 | 3.3622 | 2.3231
[7 empty] | 653 | 149 | 3.3622 | 2.3231
[7 empty] | 654 | 150 | 3.3706 | 2.3295
[7 empty] | 655 | 151 | 4.4638 | 3.1547
[7 empty] | 656 | 152 | 6.006 | 4.3191
[7 empty] | 657 | 153 | 6.6246 | 4.7861
[7 empty] | 658 | 154 | 7.1924 | 5.2147
[7 empty] | 659 | 155 | 7.0398 | 5.0996
[7 empty] | 660 | 156 | 7.2093 | 5.2275
[7 empty] | 661 | 157 | 7.9296 | 5.7713
[7 empty] | 662 | 158 | 8.2601 | 6.0208
[7 empty] | 663 | 159 | 8.5313 | 6.2255
[7 empty] | 664 | 160 | 8.4041 | 6.1296
[7 empty] | 665 | 161 | 9.1753 | 6.7117
[7 empty] | 666 | 162 | 8.6753 | 6.3343
[7 empty] | 667 | 163 | 9.0397 | 6.6094
[7 empty] | 668 | 164 | 7.6754 | 5.5794
[7 empty] | 669 | 165 | 10.8362 | 7.9656
[7 empty] | 670 | 166 | 8.7685 | 6.4046
[7 empty] | 671 | 167 | 5.1247 | 3.6537
[7 empty] | 672 | 168 | 4.4722 | 3.1611
[7 empty] | 673 | 1 | 2.9978 | 2.048
[7 empty] | 674 | 2 | 2.8876 | 1.9648
[7 empty] | 675 | 3 | 2.8791 | 1.9584
[7 empty] | 676 | 4 | 3.0147 | 2.0608
[7 empty] | 677 | 5 | 3.0317 | 2.0736
[7 empty] | 678 | 6 | 3.4638 | 2.3999
[7 empty] | 679 | 7 | 4.1926 | 2.95
[7 empty] | 680 | 8 | 4.8705 | 3.4618
[7 empty] | 681 | 9 | 4.8451 | 3.4426
[7 empty] | 682 | 10 | 6.3789 | 4.6006
[7 empty] | 683 | 11 | 8.4804 | 6.1871
[7 empty] | 684 | 12 | 9.4549 | 6.9228
[7 empty] | 685 | 13 | 9.8362 | 7.2107
[7 empty] | 686 | 14 | 9.6159 | 7.0444
[7 empty] | 687 | 15 | 9.5227 | 6.974
[7 empty] | 688 | 16 | 10.7175 | 7.8761
[7 empty] | 689 | 17 | 12.0564 | 8.8868
[7 empty] | 690 | 18 | 11.8107 | 8.7013
[7 empty] | 691 | 19 | 12.3445 | 9.1044
[7 empty] | 692 | 20 | 12.2767 | 9.0532
[7 empty] | 693 | 21 | 12.853 | 9.4882
[7 empty] | 694 | 22 | 8.8533 | 6.4686
[7 empty] | 695 | 23 | 5.04 | 3.5898
[7 empty] | 696 | 24 | 3.3504 | 2.3142
[7 empty] | 697 | 25 | 3.252 | 2.2399
[7 empty] | 698 | 26 | 3.1418 | 2.1567
[7 empty] | 699 | 27 | 3.0401 | 2.08
[7 empty] | 700 | 28 | 3.1249 | 2.144
[7 empty] | 701 | 29 | 3.3706 | 2.3295
[7 empty] | 702 | 30 | 3.6164 | 2.515
[7 empty] | 703 | 31 | 4.4722 | 3.1611
[7 empty] | 704 | 32 | 4.8281 | 3.4298
[7 empty] | 705 | 33 | 5.4976 | 3.9352
[7 empty] | 706 | 34 | 6.4043 | 4.6198
[7 empty] | 707 | 35 | 8.5991 | 6.2767
[7 empty] | 708 | 36 | 9.6413 | 7.0636
[7 empty] | 709 | 37 | 9.7176 | 7.1212
[7 empty] | 710 | 38 | 9.7939 | 7.1787
[7 empty] | 711 | 39 | 9.4634 | 6.9292
[7 empty] | 712 | 40 | 10.5311 | 7.7353
[7 empty] | 713 | 41 | 11.0904 | 8.1575
[7 empty] | 714 | 42 | 11.1073 | 8.1703
[7 empty] | 715 | 43 | 11.4802 | 8.4518
[7 empty] | 716 | 44 | 12.6496 | 9.3347
[7 empty] | 717 | 45 | 12.2428 | 9.0276
[7 empty] | 718 | 46 | 9.4634 | 6.9292
[7 empty] | 719 | 47 | 5.8196 | 4.1783
[7 empty] | 720 | 48 | 4.3028 | 3.0332
[7 empty] | 721 | 49 | 3.6333 | 2.5278
[7 empty] | 722 | 50 | 3.3198 | 2.2911
[7 empty] | 723 | 51 | 3.2096 | 2.2079
[7 empty] | 724 | 52 | 3.2435 | 2.2335
[7 empty] | 725 | 53 | 3.2689 | 2.2527
[7 empty] | 726 | 54 | 3.8536 | 2.6941
[7 empty] | 727 | 55 | 5.0061 | 3.5642
[7 empty] | 728 | 56 | 5.2518 | 3.7497
[7 empty] | 729 | 57 | 6.2094 | 4.4726
[7 empty] | 730 | 58 | 7.328 | 5.3171
[7 empty] | 731 | 59 | 8.5482 | 6.2383
[7 empty] | 732 | 60 | 9.1838 | 6.7181
[7 empty] | 733 | 61 | 9.8701 | 7.2363
[7 empty] | 734 | 62 | 9.6668 | 7.0828
[7 empty] | 735 | 63 | 10.2684 | 7.537
[7 empty] | 736 | 64 | 11.226 | 8.2599
[7 empty] | 737 | 65 | 11.853 | 8.7333
[7 empty] | 738 | 66 | 11.7514 | 8.6565
[7 empty] | 739 | 67 | 12.4971 | 9.2195
[7 empty] | 740 | 68 | 12.7428 | 9.405
[7 empty] | 741 | 69 | 12.2259 | 9.0148
[7 empty] | 742 | 70 | 9.904 | 7.2619
[7 empty] | 743 | 71 | 5.3366 | 3.8137
[7 empty] | 744 | 72 | 4.2398 | 2.9857
[7 empty] | 745 | 73 | 3.5147 | 2.4382
[7 empty] | 746 | 74 | 3.2859 | 2.2655
[7 empty] | 747 | 75 | 3.1842 | 2.1887
[7 empty] | 748 | 76 | 3.1249 | 2.144
[7 empty] | 749 | 77 | 3.3028 | 2.2783
[7 empty] | 750 | 78 | 3.7096 | 2.5854
[7 empty] | 751 | 79 | 4.8366 | 3.4362
[7 empty] | 752 | 80 | 5.0146 | 3.5706
[7 empty] | 753 | 81 | 6.2094 | 4.4726
[7 empty] | 754 | 82 | 7.311 | 5.3043
[7 empty] | 755 | 83 | 8.0567 | 5.8673
[7 empty] | 756 | 84 | 9.3109 | 6.8141
[7 empty] | 757 | 85 | 9.0058 | 6.5838
[7 empty] | 758 | 86 | 8.4889 | 6.1935
[7 empty] | 759 | 87 | 8.938 | 6.5326
[7 empty] | 760 | 88 | 9.6075 | 7.038
[7 empty] | 761 | 89 | 10.9718 | 8.068
[7 empty] | 762 | 90 | 10.3786 | 7.6202
[7 empty] | 763 | 91 | 11.0734 | 8.1447
[7 empty] | 764 | 92 | 10.4633 | 7.6841
[7 empty] | 765 | 93 | 8.0228 | 5.8417
[7 empty] | 766 | 94 | 7.1076 | 5.1507
[7 empty] | 767 | 95 | 5.2264 | 3.7305
[7 empty] | 768 | 96 | 4.2265 | 2.9756
[7 empty] | 769 | 97 | 4.1757 | 2.9372
[7 empty] | 770 | 98 | 3.8791 | 2.7133
[7 empty] | 771 | 99 | 3.8197 | 2.6685
[7 empty] | 772 | 100 | 3.4638 | 2.3999
[7 empty] | 773 | 101 | 3.4045 | 2.3551
[7 empty] | 774 | 102 | 3.6418 | 2.5342
[7 empty] | 775 | 103 | 4.396 | 3.1036
[7 empty] | 776 | 104 | 4.6502 | 3.2955
[7 empty] | 777 | 105 | 5.1417 | 3.6665
[7 empty] | 778 | 106 | 6.6161 | 4.7797
[7 empty] | 779 | 107 | 6.9721 | 5.0484
[7 empty] | 780 | 108 | 8.5652 | 6.2511
[7 empty] | 781 | 109 | 7.8957 | 5.7457
[7 empty] | 782 | 110 | 7.4381 | 5.4002
[7 empty] | 783 | 111 | 7.2771 | 5.2787
[7 empty] | 784 | 112 | 7.3449 | 5.3299
[7 empty] | 785 | 113 | 6.9975 | 5.0676
[7 empty] | 786 | 114 | 7.167 | 5.1955
[7 empty] | 787 | 115 | 6.7094 | 4.8501
[7 empty] | 788 | 116 | 7.3958 | 5.3683
[7 empty] | 789 | 117 | 6.9721 | 5.0484
[7 empty] | 790 | 118 | 6.1924 | 4.4598
[7 empty] | 791 | 119 | 4.5824 | 3.2443
[7 empty] | 792 | 120 | 4.2615 | 3.0021
[7 empty] | 793 | 121 | 3.5232 | 2.4446
[7 empty] | 794 | 122 | 3.1079 | 2.1312
[7 empty] | 795 | 123 | 3.0232 | 2.0672
[7 empty] | 796 | 124 | 2.9893 | 2.0416
[7 empty] | 797 | 125 | 2.9469 | 2.0096
[7 empty] | 798 | 126 | 3.091 | 2.1184
[7 empty] | 799 | 127 | 4.6163 | 3.2699
[7 empty] | 800 | 128 | 6.1924 | 4.4598
[7 empty] | 801 | 129 | 6.8788 | 4.978
[7 empty] | 802 | 130 | 7.3195 | 5.3107
[7 empty] | 803 | 131 | 7.4805 | 5.4322
[7 empty] | 804 | 132 | 7.2263 | 5.2403
[7 empty] | 805 | 133 | 7.8703 | 5.7265
[7 empty] | 806 | 134 | 8.1754 | 5.9568
[7 empty] | 807 | 135 | 8.2431 | 6.008
[7 empty] | 808 | 136 | 7.4212 | 5.3875
[7 empty] | 809 | 137 | 7.3195 | 5.3107
[7 empty] | 810 | 138 | 7.2686 | 5.2723
[7 empty] | 811 | 139 | 6.9297 | 5.0164
[7 empty] | 812 | 140 | 6.9382 | 5.0228
[7 empty] | 813 | 141 | 6.2772 | 4.5238
[7 empty] | 814 | 142 | 5.6332 | 4.0376
[7 empty] | 815 | 143 | 4.7434 | 3.3659
[7 empty] | 816 | 144 | 4.1248 | 2.8989
[7 empty] | 817 | 145 | 3.6503 | 2.5406
[7 empty] | 818 | 146 | 3.4384 | 2.3807
[7 empty] | 819 | 147 | 3.3706 | 2.3295
[7 empty] | 820 | 148 | 3.3622 | 2.3231
[7 empty] | 821 | 149 | 3.3622 | 2.3231
[7 empty] | 822 | 150 | 3.3706 | 2.3295
[7 empty] | 823 | 151 | 4.4638 | 3.1547
[7 empty] | 824 | 152 | 6.006 | 4.3191
[7 empty] | 825 | 153 | 6.6246 | 4.7861
[7 empty] | 826 | 154 | 7.1924 | 5.2147
[7 empty] | 827 | 155 | 7.0398 | 5.0996
[7 empty] | 828 | 156 | 7.2093 | 5.2275
[7 empty] | 829 | 157 | 7.9296 | 5.7713
[7 empty] | 830 | 158 | 8.2601 | 6.0208
[7 empty] | 831 | 159 | 8.5313 | 6.2255
[7 empty] | 832 | 160 | 8.4041 | 6.1296
[7 empty] | 833 | 161 | 9.1753 | 6.7117
[7 empty] | 834 | 162 | 8.6753 | 6.3343
[7 empty] | 835 | 163 | 9.0397 | 6.6094
[7 empty] | 836 | 164 | 7.6754 | 5.5794
[7 empty] | 837 | 165 | 10.8362 | 7.9656
[7 empty] | 838 | 166 | 8.7685 | 6.4046
[7 empty] | 839 | 167 | 5.1247 | 3.6537
[7 empty] | 840 | 168 | 4.4722 | 3.1611
[7 empty] | 841 | 1 | 2.9978 | 2.048
[7 empty] | 842 | 2 | 2.8876 | 1.9648
[7 empty] | 843 | 3 | 2.8791 | 1.9584
[7 empty] | 844 | 4 | 3.0147 | 2.0608
[7 empty] | 845 | 5 | 3.0317 | 2.0736
[7 empty] | 846 | 6 | 3.4638 | 2.3999
[7 empty] | 847 | 7 | 4.1926 | 2.95
[7 empty] | 848 | 8 | 4.8705 | 3.4618
[7 empty] | 849 | 9 | 4.8451 | 3.4426
[7 empty] | 850 | 10 | 6.3789 | 4.6006
[7 empty] | 851 | 11 | 8.4804 | 6.1871
[7 empty] | 852 | 12 | 9.4549 | 6.9228
[7 empty] | 853 | 13 | 9.8362 | 7.2107
[7 empty] | 854 | 14 | 9.6159 | 7.0444
[7 empty] | 855 | 15 | 9.5227 | 6.974
[7 empty] | 856 | 16 | 10.7175 | 7.8761
[7 empty] | 857 | 17 | 12.0564 | 8.8868
[7 empty] | 858 | 18 | 11.8107 | 8.7013
[7 empty] | 859 | 19 | 12.3445 | 9.1044
[7 empty] | 860 | 20 | 12.2767 | 9.0532
[7 empty] | 861 | 21 | 12.853 | 9.4882
[7 empty] | 862 | 22 | 8.8533 | 6.4686
[7 empty] | 863 | 23 | 5.04 | 3.5898
[7 empty] | 864 | 24 | 3.3504 | 2.3142
[7 empty] | 865 | 25 | 3.252 | 2.2399
[7 empty] | 866 | 26 | 3.1418 | 2.1567
[7 empty] | 867 | 27 | 3.0401 | 2.08
[7 empty] | 868 | 28 | 3.1249 | 2.144
[7 empty] | 869 | 29 | 3.3706 | 2.3295
[7 empty] | 870 | 30 | 3.6164 | 2.515
[7 empty] | 871 | 31 | 4.4722 | 3.1611
[7 empty] | 872 | 32 | 4.8281 | 3.4298
[7 empty] | 873 | 33 | 5.4976 | 3.9352
[7 empty] | 874 | 34 | 6.4043 | 4.6198
[7 empty] | 875 | 35 | 8.5991 | 6.2767
[7 empty] | 876 | 36 | 9.6413 | 7.0636
[7 empty] | 877 | 37 | 9.7176 | 7.1212
[7 empty] | 878 | 38 | 9.7939 | 7.1787
[7 empty] | 879 | 39 | 9.4634 | 6.9292
[7 empty] | 880 | 40 | 10.5311 | 7.7353
[7 empty] | 881 | 41 | 11.0904 | 8.1575
[7 empty] | 882 | 42 | 11.1073 | 8.1703
[7 empty] | 883 | 43 | 11.4802 | 8.4518
[7 empty] | 884 | 44 | 12.6496 | 9.3347
[7 empty] | 885 | 45 | 12.2428 | 9.0276
[7 empty] | 886 | 46 | 9.4634 | 6.9292
[7 empty] | 887 | 47 | 5.8196 | 4.1783
[7 empty] | 888 | 48 | 4.3028 | 3.0332
[7 empty] | 889 | 49 | 3.6333 | 2.5278
[7 empty] | 890 | 50 | 3.3198 | 2.2911
[7 empty] | 891 | 51 | 3.2096 | 2.2079
[7 empty] | 892 | 52 | 3.2435 | 2.2335
[7 empty] | 893 | 53 | 3.2689 | 2.2527
[7 empty] | 894 | 54 | 3.8536 | 2.6941
[7 empty] | 895 | 55 | 5.0061 | 3.5642
[7 empty] | 896 | 56 | 5.2518 | 3.7497
[7 empty] | 897 | 57 | 6.2094 | 4.4726
[7 empty] | 898 | 58 | 7.328 | 5.3171
[7 empty] | 899 | 59 | 8.5482 | 6.2383
[7 empty] | 900 | 60 | 9.1838 | 6.7181
[7 empty] | 901 | 61 | 9.8701 | 7.2363
[7 empty] | 902 | 62 | 9.6668 | 7.0828
[7 empty] | 903 | 63 | 10.2684 | 7.537
[7 empty] | 904 | 64 | 11.226 | 8.2599
[7 empty] | 905 | 65 | 11.853 | 8.7333
[7 empty] | 906 | 66 | 11.7514 | 8.6565
[7 empty] | 907 | 67 | 12.4971 | 9.2195
[7 empty] | 908 | 68 | 12.7428 | 9.405
[7 empty] | 909 | 69 | 12.2259 | 9.0148
[7 empty] | 910 | 70 | 9.904 | 7.2619
[7 empty] | 911 | 71 | 5.3366 | 3.8137
[7 empty] | 912 | 72 | 4.2398 | 2.9857
[7 empty] | 913 | 73 | 3.5147 | 2.4382
[7 empty] | 914 | 74 | 3.2859 | 2.2655
[7 empty] | 915 | 75 | 3.1842 | 2.1887
[7 empty] | 916 | 76 | 3.1249 | 2.144
[7 empty] | 917 | 77 | 3.3028 | 2.2783
[7 empty] | 918 | 78 | 3.7096 | 2.5854
[7 empty] | 919 | 79 | 4.8366 | 3.4362
[7 empty] | 920 | 80 | 5.0146 | 3.5706
[7 empty] | 921 | 81 | 6.2094 | 4.4726
[7 empty] | 922 | 82 | 7.311 | 5.3043
[7 empty] | 923 | 83 | 8.0567 | 5.8673
[7 empty] | 924 | 84 | 9.3109 | 6.8141
[7 empty] | 925 | 85 | 9.0058 | 6.5838
[7 empty] | 926 | 86 | 8.4889 | 6.1935
[7 empty] | 927 | 87 | 8.938 | 6.5326
[7 empty] | 928 | 88 | 9.6075 | 7.038
[7 empty] | 929 | 89 | 10.9718 | 8.068
[7 empty] | 930 | 90 | 10.3786 | 7.6202
[7 empty] | 931 | 91 | 11.0734 | 8.1447
[7 empty] | 932 | 92 | 10.4633 | 7.6841
[7 empty] | 933 | 93 | 8.0228 | 5.8417
[7 empty] | 934 | 94 | 7.1076 | 5.1507
[7 empty] | 935 | 95 | 5.2264 | 3.7305
[7 empty] | 936 | 96 | 4.2265 | 2.9756
[7 empty] | 937 | 97 | 4.1757 | 2.9372
[7 empty] | 938 | 98 | 3.8791 | 2.7133
[7 empty] | 939 | 99 | 3.8197 | 2.6685
[7 empty] | 940 | 100 | 3.4638 | 2.3999
[7 empty] | 941 | 101 | 3.4045 | 2.3551
[7 empty] | 942 | 102 | 3.6418 | 2.5342
[7 empty] | 943 | 103 | 4.396 | 3.1036
[7 empty] | 944 | 104 | 4.6502 | 3.2955
[7 empty] | 945 | 105 | 5.1417 | 3.6665
[7 empty] | 946 | 106 | 6.6161 | 4.7797
[7 empty] | 947 | 107 | 6.9721 | 5.0484
[7 empty] | 948 | 108 | 8.5652 | 6.2511
[7 empty] | 949 | 109 | 7.8957 | 5.7457
[7 empty] | 950 | 110 | 7.4381 | 5.4002
[7 empty] | 951 | 111 | 7.2771 | 5.2787
[7 empty] | 952 | 112 | 7.3449 | 5.3299
[7 empty] | 953 | 113 | 6.9975 | 5.0676
[7 empty] | 954 | 114 | 7.167 | 5.1955
[7 empty] | 955 | 115 | 6.7094 | 4.8501
[7 empty] | 956 | 116 | 7.3958 | 5.3683
[7 empty] | 957 | 117 | 6.9721 | 5.0484
[7 empty] | 958 | 118 | 6.1924 | 4.4598
[7 empty] | 959 | 119 | 4.5824 | 3.2443
[7 empty] | 960 | 120 | 4.2615 | 3.0021
[7 empty] | 961 | 121 | 3.5232 | 2.4446
[7 empty] | 962 | 122 | 3.1079 | 2.1312
[7 empty] | 963 | 123 | 3.0232 | 2.0672
[7 empty] | 964 | 124 | 2.9893 | 2.0416
[7 empty] | 965 | 125 | 2.9469 | 2.0096
[7 empty] | 966 | 126 | 3.091 | 2.1184
[7 empty] | 967 | 127 | 4.6163 | 3.2699
[7 empty] | 968 | 128 | 6.1924 | 4.4598
[7 empty] | 969 | 129 | 6.8788 | 4.978
[7 empty] | 970 | 130 | 7.3195 | 5.3107
[7 empty] | 971 | 131 | 7.4805 | 5.4322
[7 empty] | 972 | 132 | 7.2263 | 5.2403
[7 empty] | 973 | 133 | 7.8703 | 5.7265
[7 empty] | 974 | 134 | 8.1754 | 5.9568
[7 empty] | 975 | 135 | 8.2431 | 6.008
[7 empty] | 976 | 136 | 7.4212 | 5.3875
[7 empty] | 977 | 137 | 7.3195 | 5.3107
[7 empty] | 978 | 138 | 7.2686 | 5.2723
[7 empty] | 979 | 139 | 6.9297 | 5.0164
[7 empty] | 980 | 140 | 6.9382 | 5.0228
[7 empty] | 981 | 141 | 6.2772 | 4.5238
[7 empty] | 982 | 142 | 5.6332 | 4.0376
[7 empty] | 983 | 143 | 4.7434 | 3.3659
[7 empty] | 984 | 144 | 4.1248 | 2.8989
[7 empty] | 985 | 145 | 3.6503 | 2.5406
[7 empty] | 986 | 146 | 3.4384 | 2.3807
[7 empty] | 987 | 147 | 3.3706 | 2.3295
[7 empty] | 988 | 148 | 3.3622 | 2.3231
[7 empty] | 989 | 149 | 3.3622 | 2.3231
[7 empty] | 990 | 150 | 3.3706 | 2.3295
[7 empty] | 991 | 151 | 4.4638 | 3.1547
[7 empty] | 992 | 152 | 6.006 | 4.3191
[7 empty] | 993 | 153 | 6.6246 | 4.7861
[7 empty] | 994 | 154 | 7.1924 | 5.2147
[7 empty] | 995 | 155 | 7.0398 | 5.0996
[7 empty] | 996 | 156 | 7.2093 | 5.2275
[7 empty] | 997 | 157 | 7.9296 | 5.7713
[7 empty] | 998 | 158 | 8.2601 | 6.0208
[7 empty] | 999 | 159 | 8.5313 | 6.2255
[7 empty] | 1000 | 160 | 8.4041 | 6.1296
[7 empty] | 1001 | 161 | 9.1753 | 6.7117
[7 empty] | 1002 | 162 | 8.6753 | 6.3343
[7 empty] | 1003 | 163 | 9.0397 | 6.6094
[7 empty] | 1004 | 164 | 7.6754 | 5.5794
[7 empty] | 1005 | 165 | 10.8362 | 7.9656
[7 empty] | 1006 | 166 | 8.7685 | 6.4046
[7 empty] | 1007 | 167 | 5.1247 | 3.6537
[7 empty] | 1008 | 168 | 4.4722 | 3.1611
[7 empty] | 1009 | 1 | 2.9978 | 2.048
[7 empty] | 1010 | 2 | 2.8876 | 1.9648
[7 empty] | 1011 | 3 | 2.8791 | 1.9584
[7 empty] | 1012 | 4 | 3.0147 | 2.0608
[7 empty] | 1013 | 5 | 3.0317 | 2.0736
[7 empty] | 1014 | 6 | 3.4638 | 2.3999
[7 empty] | 1015 | 7 | 4.1926 | 2.95
[7 empty] | 1016 | 8 | 4.8705 | 3.4618
[7 empty] | 1017 | 9 | 4.8451 | 3.4426
[7 empty] | 1018 | 10 | 6.3789 | 4.6006
[7 empty] | 1019 | 11 | 8.4804 | 6.1871
[7 empty] | 1020 | 12 | 9.4549 | 6.9228
[7 empty] | 1021 | 13 | 9.8362 | 7.2107
[7 empty] | 1022 | 14 | 9.6159 | 7.0444
[7 empty] | 1023 | 15 | 9.5227 | 6.974
[7 empty] | 1024 | 16 | 10.7175 | 7.8761
[7 empty] | 1025 | 17 | 12.0564 | 8.8868
[7 empty] | 1026 | 18 | 11.8107 | 8.7013
[7 empty] | 1027 | 19 | 12.3445 | 9.1044
[7 empty] | 1028 | 20 | 12.2767 | 9.0532
[7 empty] | 1029 | 21 | 12.853 | 9.4882
[7 empty] | 1030 | 22 | 8.8533 | 6.4686
[7 empty] | 1031 | 23 | 5.04 | 3.5898
[7 empty] | 1032 | 24 | 3.3504 | 2.3142
[7 empty] | 1033 | 25 | 3.252 | 2.2399
[7 empty] | 1034 | 26 | 3.1418 | 2.1567
[7 empty] | 1035 | 27 | 3.0401 | 2.08
[7 empty] | 1036 | 28 | 3.1249 | 2.144
[7 empty] | 1037 | 29 | 3.3706 | 2.3295
[7 empty] | 1038 | 30 | 3.6164 | 2.515
[7 empty] | 1039 | 31 | 4.4722 | 3.1611
[7 empty] | 1040 | 32 | 4.8281 | 3.4298
[7 empty] | 1041 | 33 | 5.4976 | 3.9352
[7 empty] | 1042 | 34 | 6.4043 | 4.6198
[7 empty] | 1043 | 35 | 8.5991 | 6.2767
[7 empty] | 1044 | 36 | 9.6413 | 7.0636
[7 empty] | 1045 | 37 | 9.7176 | 7.1212
[7 empty] | 1046 | 38 | 9.7939 | 7.1787
[7 empty] | 1047 | 39 | 9.4634 | 6.9292
[7 empty] | 1048 | 40 | 10.5311 | 7.7353
[7 empty] | 1049 | 41 | 11.0904 | 8.1575
[7 empty] | 1050 | 42 | 11.1073 | 8.1703
[7 empty] | 1051 | 43 | 11.4802 | 8.4518
[7 empty] | 1052 | 44 | 12.6496 | 9.3347
[7 empty] | 1053 | 45 | 12.2428 | 9.0276
[7 empty] | 1054 | 46 | 9.4634 | 6.9292
[7 empty] | 1055 | 47 | 5.8196 | 4.1783
[7 empty] | 1056 | 48 | 4.3028 | 3.0332
[7 empty] | 1057 | 49 | 3.6333 | 2.5278
[7 empty] | 1058 | 50 | 3.3198 | 2.2911
[7 empty] | 1059 | 51 | 3.2096 | 2.2079
[7 empty] | 1060 | 52 | 3.2435 | 2.2335
[7 empty] | 1061 | 53 | 3.2689 | 2.2527
[7 empty] | 1062 | 54 | 3.8536 | 2.6941
[7 empty] | 1063 | 55 | 5.0061 | 3.5642
[7 empty] | 1064 | 56 | 5.2518 | 3.7497
[7 empty] | 1065 | 57 | 6.2094 | 4.4726
[7 empty] | 1066 | 58 | 7.328 | 5.3171
[7 empty] | 1067 | 59 | 8.5482 | 6.2383
[7 empty] | 1068 | 60 | 9.1838 | 6.7181
[7 empty] | 1069 | 61 | 9.8701 | 7.2363
[7 empty] | 1070 | 62 | 9.6668 | 7.0828
[7 empty] | 1071 | 63 | 10.2684 | 7.537
[7 empty] | 1072 | 64 | 11.226 | 8.2599
[7 empty] | 1073 | 65 | 11.853 | 8.7333
[7 empty] | 1074 | 66 | 11.7514 | 8.6565
[7 empty] | 1075 | 67 | 12.4971 | 9.2195
[7 empty] | 1076 | 68 | 12.7428 | 9.405
[7 empty] | 1077 | 69 | 12.2259 | 9.0148
[7 empty] | 1078 | 70 | 9.904 | 7.2619
[7 empty] | 1079 | 71 | 5.3366 | 3.8137
[7 empty] | 1080 | 72 | 4.2398 | 2.9857
[7 empty] | 1081 | 73 | 3.5147 | 2.4382
[7 empty] | 1082 | 74 | 3.2859 | 2.2655
[7 empty] | 1083 | 75 | 3.1842 | 2.1887
[7 empty] | 1084 | 76 | 3.1249 | 2.144
[7 empty] | 1085 | 77 | 3.3028 | 2.2783
[7 empty] | 1086 | 78 | 3.7096 | 2.5854
[7 empty] | 1087 | 79 | 4.8366 | 3.4362
[7 empty] | 1088 | 80 | 5.0146 | 3.5706
[7 empty] | 1089 | 81 | 6.2094 | 4.4726
[7 empty] | 1090 | 82 | 7.311 | 5.3043
[7 empty] | 1091 | 83 | 8.0567 | 5.8673
[7 empty] | 1092 | 84 | 9.3109 | 6.8141
[7 empty] | 1093 | 85 | 9.0058 | 6.5838
[7 empty] | 1094 | 86 | 8.4889 | 6.1935
[7 empty] | 1095 | 87 | 8.938 | 6.5326
[7 empty] | 1096 | 88 | 9.6075 | 7.038
[7 empty] | 1097 | 89 | 10.9718 | 8.068
[7 empty] | 1098 | 90 | 10.3786 | 7.6202
[7 empty] | 1099 | 91 | 11.0734 | 8.1447
[7 empty] | 1100 | 92 | 10.4633 | 7.6841
[7 empty] | 1101 | 93 | 8.0228 | 5.8417
[7 empty] | 1102 | 94 | 7.1076 | 5.1507
[7 empty] | 1103 | 95 | 5.2264 | 3.7305
[7 empty] | 1104 | 96 | 4.2265 | 2.9756
[7 empty] | 1105 | 97 | 4.1757 | 2.9372
[7 empty] | 1106 | 98 | 3.8791 | 2.7133
[7 empty] | 1107 | 99 | 3.8197 | 2.6685
[7 empty] | 1108 | 100 | 3.4638 | 2.3999
[7 empty] | 1109 | 101 | 3.4045 | 2.3551
[7 empty] | 1110 | 102 | 3.6418 | 2.5342
[7 empty] | 1111 | 103 | 4.396 | 3.1036
[7 empty] | 1112 | 104 | 4.6502 | 3.2955
[7 empty] | 1113 | 105 | 5.1417 | 3.6665
[7 empty] | 1114 | 106 | 6.6161 | 4.7797
[7 empty] | 1115 | 107 | 6.9721 | 5.0484
[7 empty] | 1116 | 108 | 8.5652 | 6.2511
[7 empty] | 1117 | 109 | 7.8957 | 5.7457
[7 empty] | 1118 | 110 | 7.4381 | 5.4002
[7 empty] | 1119 | 111 | 7.2771 | 5.2787
[7 empty] | 1120 | 112 | 7.3449 | 5.3299
[7 empty] | 1121 | 113 | 6.9975 | 5.0676
[7 empty] | 1122 | 114 | 7.167 | 5.1955
[7 empty] | 1123 | 115 | 6.7094 | 4.8501
[7 empty] | 1124 | 116 | 7.3958 | 5.3683
[7 empty] | 1125 | 117 | 6.9721 | 5.0484
[7 empty] | 1126 | 118 | 6.1924 | 4.4598
[7 empty] | 1127 | 119 | 4.5824 | 3.2443
[7 empty] | 1128 | 120 | 4.2615 | 3.0021
[7 empty] | 1129 | 121 | 3.5232 | 2.4446
[7 empty] | 1130 | 122 | 3.1079 | 2.1312
[7 empty] | 1131 | 123 | 3.0232 | 2.0672
[7 empty] | 1132 | 124 | 2.9893 | 2.0416
[7 empty] | 1133 | 125 | 2.9469 | 2.0096
[7 empty] | 1134 | 126 | 3.091 | 2.1184
[7 empty] | 1135 | 127 | 4.6163 | 3.2699
[7 empty] | 1136 | 128 | 6.1924 | 4.4598
[7 empty] | 1137 | 129 | 6.8788 | 4.978
[7 empty] | 1138 | 130 | 7.3195 | 5.3107
[7 empty] | 1139 | 131 | 7.4805 | 5.4322
[7 empty] | 1140 | 132 | 7.2263 | 5.2403
[7 empty] | 1141 | 133 | 7.8703 | 5.7265
[7 empty] | 1142 | 134 | 8.1754 | 5.9568
[7 empty] | 1143 | 135 | 8.2431 | 6.008
[7 empty] | 1144 | 136 | 7.4212 | 5.3875
[7 empty] | 1145 | 137 | 7.3195 | 5.3107
[7 empty] | 1146 | 138 | 7.2686 | 5.2723
[7 empty] | 1147 | 139 | 6.9297 | 5.0164
[7 empty] | 1148 | 140 | 6.9382 | 5.0228
[7 empty] | 1149 | 141 | 6.2772 | 4.5238
[7 empty] | 1150 | 142 | 5.6332 | 4.0376
[7 empty] | 1151 | 143 | 4.7434 | 3.3659
[7 empty] | 1152 | 144 | 4.1248 | 2.8989
[7 empty] | 1153 | 145 | 3.6503 | 2.5406
[7 empty] | 1154 | 146 | 3.4384 | 2.3807
[7 empty] | 1155 | 147 | 3.3706 | 2.3295
[7 empty] | 1156 | 148 | 3.3622 | 2.3231
[7 empty] | 1157 | 149 | 3.3622 | 2.3231
[7 empty] | 1158 | 150 | 3.3706 | 2.3295
[7 empty] | 1159 | 151 | 4.4638 | 3.1547
[7 empty] | 1160 | 152 | 6.006 | 4.3191
[7 empty] | 1161 | 153 | 6.6246 | 4.7861
[7 empty] | 1162 | 154 | 7.1924 | 5.2147
[7 empty] | 1163 | 155 | 7.0398 | 5.0996
[7 empty] | 1164 | 156 | 7.2093 | 5.2275
[7 empty] | 1165 | 157 | 7.9296 | 5.7713
[7 empty] | 1166 | 158 | 8.2601 | 6.0208
[7 empty] | 1167 | 159 | 8.5313 | 6.2255
[7 empty] | 1168 | 160 | 8.4041 | 6.1296
[7 empty] | 1169 | 161 | 9.1753 | 6.7117
[7 empty] | 1170 | 162 | 8.6753 | 6.3343
[7 empty] | 1171 | 163 | 9.0397 | 6.6094
[7 empty] | 1172 | 164 | 7.6754 | 5.5794
[7 empty] | 1173 | 165 | 10.8362 | 7.9656
[7 empty] | 1174 | 166 | 8.7685 | 6.4046
[7 empty] | 1175 | 167 | 5.1247 | 3.6537
[7 empty] | 1176 | 168 | 4.4722 | 3.1611
[7 empty] | 1177 | 1 | 2.9978 | 2.048
[7 empty] | 1178 | 2 | 2.8876 | 1.9648
[7 empty] | 1179 | 3 | 2.8791 | 1.9584
[7 empty] | 1180 | 4 | 3.0147 | 2.0608
[7 empty] | 1181 | 5 | 3.0317 | 2.0736
[7 empty] | 1182 | 6 | 3.4638 | 2.3999
[7 empty] | 1183 | 7 | 4.1926 | 2.95
[7 empty] | 1184 | 8 | 4.8705 | 3.4618
[7 empty] | 1185 | 9 | 4.8451 | 3.4426
[7 empty] | 1186 | 10 | 6.3789 | 4.6006
[7 empty] | 1187 | 11 | 8.4804 | 6.1871
[7 empty] | 1188 | 12 | 9.4549 | 6.9228
[7 empty] | 1189 | 13 | 9.8362 | 7.2107
[7 empty] | 1190 | 14 | 9.6159 | 7.0444
[7 empty] | 1191 | 15 | 9.5227 | 6.974
[7 empty] | 1192 | 16 | 10.7175 | 7.8761
[7 empty] | 1193 | 17 | 12.0564 | 8.8868
[7 empty] | 1194 | 18 | 11.8107 | 8.7013
[7 empty] | 1195 | 19 | 12.3445 | 9.1044
[7 empty] | 1196 | 20 | 12.2767 | 9.0532
[7 empty] | 1197 | 21 | 12.853 | 9.4882
[7 empty] | 1198 | 22 | 8.8533 | 6.4686
[7 empty] | 1199 | 23 | 5.04 | 3.5898
[7 empty] | 1200 | 24 | 3.3504 | 2.3142
[7 empty] | 1201 | 25 | 3.252 | 2.2399
[7 empty] | 1202 | 26 | 3.1418 | 2.1567
[7 empty] | 1203 | 27 | 3.0401 | 2.08
[7 empty] | 1204 | 28 | 3.1249 | 2.144
[7 empty] | 1205 | 29 | 3.3706 | 2.3295
[7 empty] | 1206 | 30 | 3.6164 | 2.515
[7 empty] | 1207 | 31 | 4.4722 | 3.1611
[7 empty] | 1208 | 32 | 4.8281 | 3.4298
[7 empty] | 1209 | 33 | 5.4976 | 3.9352
[7 empty] | 1210 | 34 | 6.4043 | 4.6198
[7 empty] | 1211 | 35 | 8.5991 | 6.2767
[7 empty] | 1212 | 36 | 9.6413 | 7.0636
[7 empty] | 1213 | 37 | 9.7176 | 7.1212
[7 empty] | 1214 | 38 | 9.7939 | 7.1787
[7 empty] | 1215 | 39 | 9.4634 | 6.9292
[7 empty] | 1216 | 40 | 10.5311 | 7.7353
[7 empty] | 1217 | 41 | 11.0904 | 8.1575
[7 empty] | 1218 | 42 | 11.1073 | 8.1703
[7 empty] | 1219 | 43 | 11.4802 | 8.4518
[7 empty] | 1220 | 44 | 12.6496 | 9.3347
[7 empty] | 1221 | 45 | 12.2428 | 9.0276
[7 empty] | 1222 | 46 | 9.4634 | 6.9292
[7 empty] | 1223 | 47 | 5.8196 | 4.1783
[7 empty] | 1224 | 48 | 4.3028 | 3.0332
[7 empty] | 1225 | 49 | 3.6333 | 2.5278
[7 empty] | 1226 | 50 | 3.3198 | 2.2911
[7 empty] | 1227 | 51 | 3.2096 | 2.2079
[7 empty] | 1228 | 52 | 3.2435 | 2.2335
[7 empty] | 1229 | 53 | 3.2689 | 2.2527
[7 empty] | 1230 | 54 | 3.8536 | 2.6941
[7 empty] | 1231 | 55 | 5.0061 | 3.5642
[7 empty] | 1232 | 56 | 5.2518 | 3.7497
[7 empty] | 1233 | 57 | 6.2094 | 4.4726
[7 empty] | 1234 | 58 | 7.328 | 5.3171
[7 empty] | 1235 | 59 | 8.5482 | 6.2383
[7 empty] | 1236 | 60 | 9.1838 | 6.7181
[7 empty] | 1237 | 61 | 9.8701 | 7.2363
[7 empty] | 1238 | 62 | 9.6668 | 7.0828
[7 empty] | 1239 | 63 | 10.2684 | 7.537
[7 empty] | 1240 | 64 | 11.226 | 8.2599
[7 empty] | 1241 | 65 | 11.853 | 8.7333
[7 empty] | 1242 | 66 | 11.7514 | 8.6565
[7 empty] | 1243 | 67 | 12.4971 | 9.2195
[7 empty] | 1244 | 68 | 12.7428 | 9.405
[7 empty] | 1245 | 69 | 12.2259 | 9.0148
[7 empty] | 1246 | 70 | 9.904 | 7.2619
[7 empty] | 1247 | 71 | 5.3366 | 3.8137
[7 empty] | 1248 | 72 | 4.2398 | 2.9857
[7 empty] | 1249 | 73 | 3.5147 | 2.4382
[7 empty] | 1250 | 74 | 3.2859 | 2.2655
[7 empty] | 1251 | 75 | 3.1842 | 2.1887
[7 empty] | 1252 | 76 | 3.1249 | 2.144
[7 empty] | 1253 | 77 | 3.3028 | 2.2783
[7 empty] | 1254 | 78 | 3.7096 | 2.5854
[7 empty] | 1255 | 79 | 4.8366 | 3.4362
[7 empty] | 1256 | 80 | 5.0146 | 3.5706
[7 empty] | 1257 | 81 | 6.2094 | 4.4726
[7 empty] | 1258 | 82 | 7.311 | 5.3043
[7 empty] | 1259 | 83 | 8.0567 | 5.8673
[7 empty] | 1260 | 84 | 9.3109 | 6.8141
[7 empty] | 1261 | 85 | 9.0058 | 6.5838
[7 empty] | 1262 | 86 | 8.4889 | 6.1935
[7 empty] | 1263 | 87 | 8.938 | 6.5326
[7 empty] | 1264 | 88 | 9.6075 | 7.038
[7 empty] | 1265 | 89 | 10.9718 | 8.068
[7 empty] | 1266 | 90 | 10.3786 | 7.6202
[7 empty] | 1267 | 91 | 11.0734 | 8.1447
[7 empty] | 1268 | 92 | 10.4633 | 7.6841
[7 empty] | 1269 | 93 | 8.0228 | 5.8417
[7 empty] | 1270 | 94 | 7.1076 | 5.1507
[7 empty] | 1271 | 95 | 5.2264 | 3.7305
[7 empty] | 1272 | 96 | 4.2265 | 2.9756
[7 empty] | 1273 | 97 | 4.1757 | 2.9372
[7 empty] | 1274 | 98 | 3.8791 | 2.7133
[7 empty] | 1275 | 99 | 3.8197 | 2.6685
[7 empty] | 1276 | 100 | 3.4638 | 2.3999
[7 empty] | 1277 | 101 | 3.4045 | 2.3551
[7 empty] | 1278 | 102 | 3.6418 | 2.5342
[7 empty] | 1279 | 103 | 4.396 | 3.1036
[7 empty] | 1280 | 104 | 4.6502 | 3.2955
[7 empty] | 1281 | 105 | 5.1417 | 3.6665
[7 empty] | 1282 | 106 | 6.6161 | 4.7797
[7 empty] | 1283 | 107 | 6.9721 | 5.0484
[7 empty] | 1284 | 108 | 8.5652 | 6.2511
[7 empty] | 1285 | 109 | 7.8957 | 5.7457
[7 empty] | 1286 | 110 | 7.4381 | 5.4002
[7 empty] | 1287 | 111 | 7.2771 | 5.2787
[7 empty] | 1288 | 112 | 7.3449 | 5.3299
[7 empty] | 1289 | 113 | 6.9975 | 5.0676
[7 empty] | 1290 | 114 | 7.167 | 5.1955
[7 empty] | 1291 | 115 | 6.7094 | 4.8501
[7 empty] | 1292 | 116 | 7.3958 | 5.3683
[7 empty] | 1293 | 117 | 6.9721 | 5.0484
[7 empty] | 1294 | 118 | 6.1924 | 4.4598
[7 empty] | 1295 | 119 | 4.5824 | 3.2443
[7 empty] | 1296 | 120 | 4.2615 | 3.0021
[7 empty] | 1297 | 121 | 3.5232 | 2.4446
[7 empty] | 1298 | 122 | 3.1079 | 2.1312
[7 empty] | 1299 | 123 | 3.0232 | 2.0672
[7 empty] | 1300 | 124 | 2.9893 | 2.0416
[7 empty] | 1301 | 125 | 2.9469 | 2.0096
[7 empty] | 1302 | 126 | 3.091 | 2.1184
[7 empty] | 1303 | 127 | 4.6163 | 3.2699
[7 empty] | 1304 | 128 | 6.1924 | 4.4598
[7 empty] | 1305 | 129 | 6.8788 | 4.978
[7 empty] | 1306 | 130 | 7.3195 | 5.3107
[7 empty] | 1307 | 131 | 7.4805 | 5.4322
[7 empty] | 1308 | 132 | 7.2263 | 5.2403
[7 empty] | 1309 | 133 | 7.8703 | 5.7265
[7 empty] | 1310 | 134 | 8.1754 | 5.9568
[7 empty] | 1311 | 135 | 8.2431 | 6.008
[7 empty] | 1312 | 136 | 7.4212 | 5.3875
[7 empty] | 1313 | 137 | 7.3195 | 5.3107
[7 empty] | 1314 | 138 | 7.2686 | 5.2723
[7 empty] | 1315 | 139 | 6.9297 | 5.0164
[7 empty] | 1316 | 140 | 6.9382 | 5.0228
[7 empty] | 1317 | 141 | 6.2772 | 4.5238
[7 empty] | 1318 | 142 | 5.6332 | 4.0376
[7 empty] | 1319 | 143 | 4.7434 | 3.3659
[7 empty] | 1320 | 144 | 4.1248 | 2.8989
[7 empty] | 1321 | 145 | 3.6503 | 2.5406
[7 empty] | 1322 | 146 | 3.4384 | 2.3807
[7 empty] | 1323 | 147 | 3.3706 | 2.3295
[7 empty] | 1324 | 148 | 3.3622 | 2.3231
[7 empty] | 1325 | 149 | 3.3622 | 2.3231
[7 empty] | 1326 | 150 | 3.3706 | 2.3295
[7 empty] | 1327 | 151 | 4.4638 | 3.1547
[7 empty] | 1328 | 152 | 6.006 | 4.3191
[7 empty] | 1329 | 153 | 6.6246 | 4.7861
[7 empty] | 1330 | 154 | 7.1924 | 5.2147
[7 empty] | 1331 | 155 | 7.0398 | 5.0996
[7 empty] | 1332 | 156 | 7.2093 | 5.2275
[7 empty] | 1333 | 157 | 7.9296 | 5.7713
[7 empty] | 1334 | 158 | 8.2601 | 6.0208
[7 empty] | 1335 | 159 | 8.5313 | 6.2255
[7 empty] | 1336 | 160 | 8.4041 | 6.1296
[7 empty] | 1337 | 161 | 9.1753 | 6.7117
[7 empty] | 1338 | 162 | 8.6753 | 6.3343
[7 empty] | 1339 | 163 | 9.0397 | 6.6094
[7 empty] | 1340 | 164 | 7.6754 | 5.5794
[7 empty] | 1341 | 165 | 10.8362 | 7.9656
[7 empty] | 1342 | 166 | 8.7685 | 6.4046
[7 empty] | 1343 | 167 | 5.1247 | 3.6537
[7 empty] | 1344 | 168 | 4.4722 | 3.1611
[7 empty] | 1345 | 1 | 2.9978 | 2.048
[7 empty] | 1346 | 2 | 2.8876 | 1.9648
[7 empty] | 1347 | 3 | 2.8791 | 1.9584
[7 empty] | 1348 | 4 | 3.0147 | 2.0608
[7 empty] | 1349 | 5 | 3.0317 | 2.0736
[7 empty] | 1350 | 6 | 3.4638 | 2.3999
[7 empty] | 1351 | 7 | 4.1926 | 2.95
[7 empty] | 1352 | 8 | 4.8705 | 3.4618
[7 empty] | 1353 | 9 | 4.8451 | 3.4426
[7 empty] | 1354 | 10 | 6.3789 | 4.6006
[7 empty] | 1355 | 11 | 8.4804 | 6.1871
[7 empty] | 1356 | 12 | 9.4549 | 6.9228
[7 empty] | 1357 | 13 | 9.8362 | 7.2107
[7 empty] | 1358 | 14 | 9.6159 | 7.0444
[7 empty] | 1359 | 15 | 9.5227 | 6.974
[7 empty] | 1360 | 16 | 10.7175 | 7.8761
[7 empty] | 1361 | 17 | 12.0564 | 8.8868
[7 empty] | 1362 | 18 | 11.8107 | 8.7013
[7 empty] | 1363 | 19 | 12.3445 | 9.1044
[7 empty] | 1364 | 20 | 12.2767 | 9.0532
[7 empty] | 1365 | 21 | 12.853 | 9.4882
[7 empty] | 1366 | 22 | 8.8533 | 6.4686
[7 empty] | 1367 | 23 | 5.04 | 3.5898
[7 empty] | 1368 | 24 | 3.3504 | 2.3142
[7 empty] | 1369 | 25 | 3.252 | 2.2399
[7 empty] | 1370 | 26 | 3.1418 | 2.1567
[7 empty] | 1371 | 27 | 3.0401 | 2.08
[7 empty] | 1372 | 28 | 3.1249 | 2.144
[7 empty] | 1373 | 29 | 3.3706 | 2.3295
[7 empty] | 1374 | 30 | 3.6164 | 2.515
[7 empty] | 1375 | 31 | 4.4722 | 3.1611
[7 empty] | 1376 | 32 | 4.8281 | 3.4298
[7 empty] | 1377 | 33 | 5.4976 | 3.9352
[7 empty] | 1378 | 34 | 6.4043 | 4.6198
[7 empty] | 1379 | 35 | 8.5991 | 6.2767
[7 empty] | 1380 | 36 | 9.6413 | 7.0636
[7 empty] | 1381 | 37 | 9.7176 | 7.1212
[7 empty] | 1382 | 38 | 9.7939 | 7.1787
[7 empty] | 1383 | 39 | 9.4634 | 6.9292
[7 empty] | 1384 | 40 | 10.5311 | 7.7353
[7 empty] | 1385 | 41 | 11.0904 | 8.1575
[7 empty] | 1386 | 42 | 11.1073 | 8.1703
[7 empty] | 1387 | 43 | 11.4802 | 8.4518
[7 empty] | 1388 | 44 | 12.6496 | 9.3347
[7 empty] | 1389 | 45 | 12.2428 | 9.0276
[7 empty] | 1390 | 46 | 9.4634 | 6.9292
[7 empty] | 1391 | 47 | 5.8196 | 4.1783
[7 empty] | 1392 | 48 | 4.3028 | 3.0332
[7 empty] | 1393 | 49 | 3.6333 | 2.5278
[7 empty] | 1394 | 50 | 3.3198 | 2.2911
[7 empty] | 1395 | 51 | 3.2096 | 2.2079
[7 empty] | 1396 | 52 | 3.2435 | 2.2335
[7 empty] | 1397 | 53 | 3.2689 | 2.2527
[7 empty] | 1398 | 54 | 3.8536 | 2.6941
[7 empty] | 1399 | 55 | 5.0061 | 3.5642
[7 empty] | 1400 | 56 | 5.2518 | 3.7497
[7 empty] | 1401 | 57 | 6.2094 | 4.4726
[7 empty] | 1402 | 58 | 7.328 | 5.3171
[7 empty] | 1403 | 59 | 8.5482 | 6.2383
[7 empty] | 1404 | 60 | 9.1838 | 6.7181
[7 empty] | 1405 | 61 | 9.8701 | 7.2363
[7 empty] | 1406 | 62 | 9.6668 | 7.0828
[7 empty] | 1407 | 63 | 10.2684 | 7.537
[7 empty] | 1408 | 64 | 11.226 | 8.2599
[7 empty] | 1409 | 65 | 11.853 | 8.7333
[7 empty] | 1410 | 66 | 11.7514 | 8.6565
[7 empty] | 1411 | 67 | 12.4971 | 9.2195
[7 empty] | 1412 | 68 | 12.7428 | 9.405
[7 empty] | 1413 | 69 | 12.2259 | 9.0148
[7 empty] | 1414 | 70 | 9.904 | 7.2619
[7 empty] | 1415 | 71 | 5.3366 | 3.8137
[7 empty] | 1416 | 72 | 4.2398 | 2.9857
[7 empty] | 1417 | 73 | 3.5147 | 2.4382
[7 empty] | 1418 | 74 | 3.2859 | 2.2655
[7 empty] | 1419 | 75 | 3.1842 | 2.1887
[7 empty] | 1420 | 76 | 3.1249 | 2.144
[7 empty] | 1421 | 77 | 3.3028 | 2.2783
[7 empty] | 1422 | 78 | 3.7096 | 2.5854
[7 empty] | 1423 | 79 | 4.8366 | 3.4362
[7 empty] | 1424 | 80 | 5.0146 | 3.5706
[7 empty] | 1425 | 81 | 6.2094 | 4.4726
[7 empty] | 1426 | 82 | 7.311 | 5.3043
[7 empty] | 1427 | 83 | 8.0567 | 5.8673
[7 empty] | 1428 | 84 | 9.3109 | 6.8141
[7 empty] | 1429 | 85 | 9.0058 | 6.5838
[7 empty] | 1430 | 86 | 8.4889 | 6.1935
[7 empty] | 1431 | 87 | 8.938 | 6.5326
[7 empty] | 1432 | 88 | 9.6075 | 7.038
[7 empty] | 1433 | 89 | 10.9718 | 8.068
[7 empty] | 1434 | 90 | 10.3786 | 7.6202
[7 empty] | 1435 | 91 | 11.0734 | 8.1447
[7 empty] | 1436 | 92 | 10.4633 | 7.6841
[7 empty] | 1437 | 93 | 8.0228 | 5.8417
[7 empty] | 1438 | 94 | 7.1076 | 5.1507
[7 empty] | 1439 | 95 | 5.2264 | 3.7305
[7 empty] | 1440 | 96 | 4.2265 | 2.9756
[7 empty] | 1441 | 97 | 4.1757 | 2.9372
[7 empty] | 1442 | 98 | 3.8791 | 2.7133
[7 empty] | 1443 | 99 | 3.8197 | 2.6685
[7 empty] | 1444 | 100 | 3.4638 | 2.3999
[7 empty] | 1445 | 101 | 3.4045 | 2.3551
[7 empty] | 1446 | 102 | 3.6418 | 2.5342
[7 empty] | 1447 | 103 | 4.396 | 3.1036
[7 empty] | 1448 | 104 | 4.6502 | 3.2955
[7 empty] | 1449 | 105 | 5.1417 | 3.6665
[7 empty] | 1450 | 106 | 6.6161 | 4.7797
[7 empty] | 1451 | 107 | 6.9721 | 5.0484
[7 empty] | 1452 | 108 | 8.5652 | 6.2511
[7 empty] | 1453 | 109 | 7.8957 | 5.7457
[7 empty] | 1454 | 110 | 7.4381 | 5.4002
[7 empty] | 1455 | 111 | 7.2771 | 5.2787
[7 empty] | 1456 | 112 | 7.3449 | 5.3299
[7 empty] | 1457 | 113 | 6.9975 | 5.0676
[7 empty] | 1458 | 114 | 7.167 | 5.1955
[7 empty] | 1459 | 115 | 6.7094 | 4.8501
[7 empty] | 1460 | 116 | 7.3958 | 5.3683
[7 empty] | 1461 | 117 | 6.9721 | 5.0484
[7 empty] | 1462 | 118 | 6.1924 | 4.4598
[7 empty] | 1463 | 119 | 4.5824 | 3.2443
[7 empty] | 1464 | 120 | 4.2615 | 3.0021
[7 empty] | 1465 | 121 | 3.5232 | 2.4446
[7 empty] | 1466 | 122 | 3.1079 | 2.1312
[7 empty] | 1467 | 123 | 3.0232 | 2.0672
[7 empty] | 1468 | 124 | 2.9893 | 2.0416
[7 empty] | 1469 | 125 | 2.9469 | 2.0096
[7 empty] | 1470 | 126 | 3.091 | 2.1184
[7 empty] | 1471 | 127 | 4.6163 | 3.2699
[7 empty] | 1472 | 128 | 6.1924 | 4.4598
[7 empty] | 1473 | 129 | 6.8788 | 4.978
[7 empty] | 1474 | 130 | 7.3195 | 5.3107
[7 empty] | 1475 | 131 | 7.4805 | 5.4322
[7 empty] | 1476 | 132 | 7.2263 | 5.2403
[7 empty] | 1477 | 133 | 7.8703 | 5.7265
[7 empty] | 1478 | 134 | 8.1754 | 5.9568
[7 empty] | 1479 | 135 | 8.2431 | 6.008
[7 empty] | 1480 | 136 | 7.4212 | 5.3875
[7 empty] | 1481 | 137 | 7.3195 | 5.3107
[7 empty] | 1482 | 138 | 7.2686 | 5.2723
[7 empty] | 1483 | 139 | 6.9297 | 5.0164
[7 empty] | 1484 | 140 | 6.9382 | 5.0228
[7 empty] | 1485 | 141 | 6.2772 | 4.5238
[7 empty] | 1486 | 142 | 5.6332 | 4.0376
[7 empty] | 1487 | 143 | 4.7434 | 3.3659
[7 empty] | 1488 | 144 | 4.1248 | 2.8989
[7 empty] | 1489 | 145 | 3.6503 | 2.5406
[7 empty] | 1490 | 146 | 3.4384 | 2.3807
[7 empty] | 1491 | 147 | 3.3706 | 2.3295
[7 empty] | 1492 | 148 | 3.3622 | 2.3231
[7 empty] | 1493 | 149 | 3.3622 | 2.3231
[7 empty] | 1494 | 150 | 3.3706 | 2.3295
[7 empty] | 1495 | 151 | 4.4638 | 3.1547
[7 empty] | 1496 | 152 | 6.006 | 4.3191
[7 empty] | 1497 | 153 | 6.6246 | 4.7861
[7 empty] | 1498 | 154 | 7.1924 | 5.2147
[7 empty] | 1499 | 155 | 7.0398 | 5.0996
[7 empty] | 1500 | 156 | 7.2093 | 5.2275
[7 empty] | 1501 | 157 | 7.9296 | 5.7713
[7 empty] | 1502 | 158 | 8.2601 | 6.0208
[7 empty] | 1503 | 159 | 8.5313 | 6.2255
[7 empty] | 1504 | 160 | 8.4041 | 6.1296
[7 empty] | 1505 | 161 | 9.1753 | 6.7117
[7 empty] | 1506 | 162 | 8.6753 | 6.3343
[7 empty] | 1507 | 163 | 9.0397 | 6.6094
[7 empty] | 1508 | 164 | 7.6754 | 5.5794
[7 empty] | 1509 | 165 | 10.8362 | 7.9656
[7 empty] | 1510 | 166 | 8.7685 | 6.4046
[7 empty] | 1511 | 167 | 5.1247 | 3.6537
[7 empty] | 1512 | 168 | 4.4722 | 3.1611
[7 empty] | 1513 | 1 | 2.9978 | 2.048
[7 empty] | 1514 | 2 | 2.8876 | 1.9648
[7 empty] | 1515 | 3 | 2.8791 | 1.9584
[7 empty] | 1516 | 4 | 3.0147 | 2.0608
[7 empty] | 1517 | 5 | 3.0317 | 2.0736
[7 empty] | 1518 | 6 | 3.4638 | 2.3999
[7 empty] | 1519 | 7 | 4.1926 | 2.95
[7 empty] | 1520 | 8 | 4.8705 | 3.4618
[7 empty] | 1521 | 9 | 4.8451 | 3.4426
[7 empty] | 1522 | 10 | 6.3789 | 4.6006
[7 empty] | 1523 | 11 | 8.4804 | 6.1871
[7 empty] | 1524 | 12 | 9.4549 | 6.9228
[7 empty] | 1525 | 13 | 9.8362 | 7.2107
[7 empty] | 1526 | 14 | 9.6159 | 7.0444
[7 empty] | 1527 | 15 | 9.5227 | 6.974
[7 empty] | 1528 | 16 | 10.7175 | 7.8761
[7 empty] | 1529 | 17 | 12.0564 | 8.8868
[7 empty] | 1530 | 18 | 11.8107 | 8.7013
[7 empty] | 1531 | 19 | 12.3445 | 9.1044
[7 empty] | 1532 | 20 | 12.2767 | 9.0532
[7 empty] | 1533 | 21 | 12.853 | 9.4882
[7 empty] | 1534 | 22 | 8.8533 | 6.4686
[7 empty] | 1535 | 23 | 5.04 | 3.5898
[7 empty] | 1536 | 24 | 3.3504 | 2.3142
[7 empty] | 1537 | 25 | 3.252 | 2.2399
[7 empty] | 1538 | 26 | 3.1418 | 2.1567
[7 empty] | 1539 | 27 | 3.0401 | 2.08
[7 empty] | 1540 | 28 | 3.1249 | 2.144
[7 empty] | 1541 | 29 | 3.3706 | 2.3295
[7 empty] | 1542 | 30 | 3.6164 | 2.515
[7 empty] | 1543 | 31 | 4.4722 | 3.1611
[7 empty] | 1544 | 32 | 4.8281 | 3.4298
[7 empty] | 1545 | 33 | 5.4976 | 3.9352
[7 empty] | 1546 | 34 | 6.4043 | 4.6198
[7 empty] | 1547 | 35 | 8.5991 | 6.2767
[7 empty] | 1548 | 36 | 9.6413 | 7.0636
[7 empty] | 1549 | 37 | 9.7176 | 7.1212
[7 empty] | 1550 | 38 | 9.7939 | 7.1787
[7 empty] | 1551 | 39 | 9.4634 | 6.9292
[7 empty] | 1552 | 40 | 10.5311 | 7.7353
[7 empty] | 1553 | 41 | 11.0904 | 8.1575
[7 empty] | 1554 | 42 | 11.1073 | 8.1703
[7 empty] | 1555 | 43 | 11.4802 | 8.4518
[7 empty] | 1556 | 44 | 12.6496 | 9.3347
[7 empty] | 1557 | 45 | 12.2428 | 9.0276
[7 empty] | 1558 | 46 | 9.4634 | 6.9292
[7 empty] | 1559 | 47 | 5.8196 | 4.1783
[7 empty] | 1560 | 48 | 4.3028 | 3.0332
[7 empty] | 1561 | 49 | 3.6333 | 2.5278
[7 empty] | 1562 | 50 | 3.3198 | 2.2911
[7 empty] | 1563 | 51 | 3.2096 | 2.2079
[7 empty] | 1564 | 52 | 3.2435 | 2.2335
[7 empty] | 1565 | 53 | 3.2689 | 2.2527
[7 empty] | 1566 | 54 | 3.8536 | 2.6941
[7 empty] | 1567 | 55 | 5.0061 | 3.5642
[7 empty] | 1568 | 56 | 5.2518 | 3.7497
[7 empty] | 1569 | 57 | 6.2094 | 4.4726
[7 empty] | 1570 | 58 | 7.328 | 5.3171
[7 empty] | 1571 | 59 | 8.5482 | 6.2383
[7 empty] | 1572 | 60 | 9.1838 | 6.7181
[7 empty] | 1573 | 61 | 9.8701 | 7.2363
[7 empty] | 1574 | 62 | 9.6668 | 7.0828
[7 empty] | 1575 | 63 | 10.2684 | 7.537
[7 empty] | 1576 | 64 | 11.226 | 8.2599
[7 empty] | 1577 | 65 | 11.853 | 8.7333
[7 empty] | 1578 | 66 | 11.7514 | 8.6565
[7 empty] | 1579 | 67 | 12.4971 | 9.2195
[7 empty] | 1580 | 68 | 12.7428 | 9.405
[7 empty] | 1581 | 69 | 12.2259 | 9.0148
[7 empty] | 1582 | 70 | 9.904 | 7.2619
[7 empty] | 1583 | 71 | 5.3366 | 3.8137
[7 empty] | 1584 | 72 | 4.2398 | 2.9857
[7 empty] | 1585 | 73 | 3.5147 | 2.4382
[7 empty] | 1586 | 74 | 3.2859 | 2.2655
[7 empty] | 1587 | 75 | 3.1842 | 2.1887
[7 empty] | 1588 | 76 | 3.1249 | 2.144
[7 empty] | 1589 | 77 | 3.3028 | 2.2783
[7 empty] | 1590 | 78 | 3.7096 | 2.5854
[7 empty] | 1591 | 79 | 4.8366 | 3.4362
[7 empty] | 1592 | 80 | 5.0146 | 3.5706
[7 empty] | 1593 | 81 | 6.2094 | 4.4726
[7 empty] | 1594 | 82 | 7.311 | 5.3043
[7 empty] | 1595 | 83 | 8.0567 | 5.8673
[7 empty] | 1596 | 84 | 9.3109 | 6.8141
[7 empty] | 1597 | 85 | 9.0058 | 6.5838
[7 empty] | 1598 | 86 | 8.4889 | 6.1935
[7 empty] | 1599 | 87 | 8.938 | 6.5326
[7 empty] | 1600 | 88 | 9.6075 | 7.038
[7 empty] | 1601 | 89 | 10.9718 | 8.068
[7 empty] | 1602 | 90 | 10.3786 | 7.6202
[7 empty] | 1603 | 91 | 11.0734 | 8.1447
[7 empty] | 1604 | 92 | 10.4633 | 7.6841
[7 empty] | 1605 | 93 | 8.0228 | 5.8417
[7 empty] | 1606 | 94 | 7.1076 | 5.1507
[7 empty] | 1607 | 95 | 5.2264 | 3.7305
[7 empty] | 1608 | 96 | 4.2265 | 2.9756
[7 empty] | 1609 | 97 | 4.1757 | 2.9372
[7 empty] | 1610 | 98 | 3.8791 | 2.7133
[7 empty] | 1611 | 99 | 3.8197 | 2.6685
[7 empty] | 1612 | 100 | 3.4638 | 2.3999
[7 empty] | 1613 | 101 | 3.4045 | 2.3551
[7 empty] | 1614 | 102 | 3.6418 | 2.5342
[7 empty] | 1615 | 103 | 4.396 | 3.1036
[7 empty] | 1616 | 104 | 4.6502 | 3.2955
[7 empty] | 1617 | 105 | 5.1417 | 3.6665
[7 empty] | 1618 | 106 | 6.6161 | 4.7797
[7 empty] | 1619 | 107 | 6.9721 | 5.0484
[7 empty] | 1620 | 108 | 8.5652 | 6.2511
[7 empty] | 1621 | 109 | 7.8957 | 5.7457
[7 empty] | 1622 | 110 | 7.4381 | 5.4002
[7 empty] | 1623 | 111 | 7.2771 | 5.2787
[7 empty] | 1624 | 112 | 7.3449 | 5.3299
[7 empty] | 1625 | 113 | 6.9975 | 5.0676
[7 empty] | 1626 | 114 | 7.167 | 5.1955
[7 empty] | 1627 | 115 | 6.7094 | 4.8501
[7 empty] | 1628 | 116 | 7.3958 | 5.3683
[7 empty] | 1629 | 117 | 6.9721 | 5.0484
[7 empty] | 1630 | 118 | 6.1924 | 4.4598
[7 empty] | 1631 | 119 | 4.5824 | 3.2443
[7 empty] | 1632 | 120 | 4.2615 | 3.0021
[7 empty] | 1633 | 121 | 3.5232 | 2.4446
[7 empty] | 1634 | 122 | 3.1079 | 2.1312
[7 empty] | 1635 | 123 | 3.0232 | 2.0672
[7 empty] | 1636 | 124 | 2.9893 | 2.0416
[7 empty] | 1637 | 125 | 2.9469 | 2.0096
[7 empty] | 1638 | 126 | 3.091 | 2.1184
[7 empty] | 1639 | 127 | 4.6163 | 3.2699
[7 empty] | 1640 | 128 | 6.1924 | 4.4598
[7 empty] | 1641 | 129 | 6.8788 | 4.978
[7 empty] | 1642 | 130 | 7.3195 | 5.3107
[7 empty] | 1643 | 131 | 7.4805 | 5.4322
[7 empty] | 1644 | 132 | 7.2263 | 5.2403
[7 empty] | 1645 | 133 | 7.8703 | 5.7265
[7 empty] | 1646 | 134 | 8.1754 | 5.9568
[7 empty] | 1647 | 135 | 8.2431 | 6.008
[7 empty] | 1648 | 136 | 7.4212 | 5.3875
[7 empty] | 1649 | 137 | 7.3195 | 5.3107
[7 empty] | 1650 | 138 | 7.2686 | 5.2723
[7 empty] | 1651 | 139 | 6.9297 | 5.0164
[7 empty] | 1652 | 140 | 6.9382 | 5.0228
[7 empty] | 1653 | 141 | 6.2772 | 4.5238
[7 empty] | 1654 | 142 | 5.6332 | 4.0376
[7 empty] | 1655 | 143 | 4.7434 | 3.3659
[7 empty] | 1656 | 144 | 4.1248 | 2.8989
[7 empty] | 1657 | 145 | 3.6503 | 2.5406
[7 empty] | 1658 | 146 | 3.4384 | 2.3807
[7 empty] | 1659 | 147 | 3.3706 | 2.3295
[7 empty] | 1660 | 148 | 3.3622 | 2.3231
[7 empty] | 1661 | 149 | 3.3622 | 2.3231
[7 empty] | 1662 | 150 | 3.3706 | 2.3295
[7 empty] | 1663 | 151 | 4.4638 | 3.1547
[7 empty] | 1664 | 152 | 6.006 | 4.3191
[7 empty] | 1665 | 153 | 6.6246 | 4.7861
[7 empty] | 1666 | 154 | 7.1924 | 5.2147
[7 empty] | 1667 | 155 | 7.0398 | 5.0996
[7 empty] | 1668 | 156 | 7.2093 | 5.2275
[7 empty] | 1669 | 157 | 7.9296 | 5.7713
[7 empty] | 1670 | 158 | 8.2601 | 6.0208
[7 empty] | 1671 | 159 | 8.5313 | 6.2255
[7 empty] | 1672 | 160 | 8.4041 | 6.1296
[7 empty] | 1673 | 161 | 9.1753 | 6.7117
[7 empty] | 1674 | 162 | 8.6753 | 6.3343
[7 empty] | 1675 | 163 | 9.0397 | 6.6094
[7 empty] | 1676 | 164 | 7.6754 | 5.5794
[7 empty] | 1677 | 165 | 10.8362 | 7.9656
[7 empty] | 1678 | 166 | 8.7685 | 6.4046
[7 empty] | 1679 | 167 | 5.1247 | 3.6537
[7 empty] | 1680 | 168 | 4.4722 | 3.1611
[7 empty] | 1681 | 1 | 2.9978 | 2.048
[7 empty] | 1682 | 2 | 2.8876 | 1.9648
[7 empty] | 1683 | 3 | 2.8791 | 1.9584
[7 empty] | 1684 | 4 | 3.0147 | 2.0608
[7 empty] | 1685 | 5 | 3.0317 | 2.0736
[7 empty] | 1686 | 6 | 3.4638 | 2.3999
[7 empty] | 1687 | 7 | 4.1926 | 2.95
[7 empty] | 1688 | 8 | 4.8705 | 3.4618
[7 empty] | 1689 | 9 | 4.8451 | 3.4426
[7 empty] | 1690 | 10 | 6.3789 | 4.6006
[7 empty] | 1691 | 11 | 8.4804 | 6.1871
[7 empty] | 1692 | 12 | 9.4549 | 6.9228
[7 empty] | 1693 | 13 | 9.8362 | 7.2107
[7 empty] | 1694 | 14 | 9.6159 | 7.0444
[7 empty] | 1695 | 15 | 9.5227 | 6.974
[7 empty] | 1696 | 16 | 10.7175 | 7.8761
[7 empty] | 1697 | 17 | 12.0564 | 8.8868
[7 empty] | 1698 | 18 | 11.8107 | 8.7013
[7 empty] | 1699 | 19 | 12.3445 | 9.1044
[7 empty] | 1700 | 20 | 12.2767 | 9.0532
[7 empty] | 1701 | 21 | 12.853 | 9.4882
[7 empty] | 1702 | 22 | 8.8533 | 6.4686
[7 empty] | 1703 | 23 | 5.04 | 3.5898
[7 empty] | 1704 | 24 | 3.3504 | 2.3142
[7 empty] | 1705 | 25 | 3.252 | 2.2399
[7 empty] | 1706 | 26 | 3.1418 | 2.1567
[7 empty] | 1707 | 27 | 3.0401 | 2.08
[7 empty] | 1708 | 28 | 3.1249 | 2.144
[7 empty] | 1709 | 29 | 3.3706 | 2.3295
[7 empty] | 1710 | 30 | 3.6164 | 2.515
[7 empty] | 1711 | 31 | 4.4722 | 3.1611
[7 empty] | 1712 | 32 | 4.8281 | 3.4298
[7 empty] | 1713 | 33 | 5.4976 | 3.9352
[7 empty] | 1714 | 34 | 6.4043 | 4.6198
[7 empty] | 1715 | 35 | 8.5991 | 6.2767
[7 empty] | 1716 | 36 | 9.6413 | 7.0636
[7 empty] | 1717 | 37 | 9.7176 | 7.1212
[7 empty] | 1718 | 38 | 9.7939 | 7.1787
[7 empty] | 1719 | 39 | 9.4634 | 6.9292
[7 empty] | 1720 | 40 | 10.5311 | 7.7353
[7 empty] | 1721 | 41 | 11.0904 | 8.1575
[7 empty] | 1722 | 42 | 11.1073 | 8.1703
[7 empty] | 1723 | 43 | 11.4802 | 8.4518
[7 empty] | 1724 | 44 | 12.6496 | 9.3347
[7 empty] | 1725 | 45 | 12.2428 | 9.0276
[7 empty] | 1726 | 46 | 9.4634 | 6.9292
[7 empty] | 1727 | 47 | 5.8196 | 4.1783
[7 empty] | 1728 | 48 | 4.3028 | 3.0332
[7 empty] | 1729 | 49 | 3.6333 | 2.5278
[7 empty] | 1730 | 50 | 3.3198 | 2.2911
[7 empty] | 1731 | 51 | 3.2096 | 2.2079
[7 empty] | 1732 | 52 | 3.2435 | 2.2335
[7 empty] | 1733 | 53 | 3.2689 | 2.2527
[7 empty] | 1734 | 54 | 3.8536 | 2.6941
[7 empty] | 1735 | 55 | 5.0061 | 3.5642
[7 empty] | 1736 | 56 | 5.2518 | 3.7497
[7 empty] | 1737 | 57 | 6.2094 | 4.4726
[7 empty] | 1738 | 58 | 7.328 | 5.3171
[7 empty] | 1739 | 59 | 8.5482 | 6.2383
[7 empty] | 1740 | 60 | 9.1838 | 6.7181
[7 empty] | 1741 | 61 | 9.8701 | 7.2363
[7 empty] | 1742 | 62 | 9.6668 | 7.0828
[7 empty] | 1743 | 63 | 10.2684 | 7.537
[7 empty] | 1744 | 64 | 11.226 | 8.2599
[7 empty] | 1745 | 65 | 11.853 | 8.7333
[7 empty] | 1746 | 66 | 11.7514 | 8.6565
[7 empty] | 1747 | 67 | 12.4971 | 9.2195
[7 empty] | 1748 | 68 | 12.7428 | 9.405
[7 empty] | 1749 | 69 | 12.2259 | 9.0148
[7 empty] | 1750 | 70 | 9.904 | 7.2619
[7 empty] | 1751 | 71 | 5.3366 | 3.8137
[7 empty] | 1752 | 72 | 4.2398 | 2.9857
[7 empty] | 1753 | 73 | 3.5147 | 2.4382
[7 empty] | 1754 | 74 | 3.2859 | 2.2655
[7 empty] | 1755 | 75 | 3.1842 | 2.1887
[7 empty] | 1756 | 76 | 3.1249 | 2.144
[7 empty] | 1757 | 77 | 3.3028 | 2.2783
[7 empty] | 1758 | 78 | 3.7096 | 2.5854
[7 empty] | 1759 | 79 | 4.8366 | 3.4362
[7 empty] | 1760 | 80 | 5.0146 | 3.5706
[7 empty] | 1761 | 81 | 6.2094 | 4.4726
[7 empty] | 1762 | 82 | 7.311 | 5.3043
[7 empty] | 1763 | 83 | 8.0567 | 5.8673
[7 empty] | 1764 | 84 | 9.3109 | 6.8141
[7 empty] | 1765 | 85 | 9.0058 | 6.5838
[7 empty] | 1766 | 86 | 8.4889 | 6.1935
[7 empty] | 1767 | 87 | 8.938 | 6.5326
[7 empty] | 1768 | 88 | 9.6075 | 7.038
[7 empty] | 1769 | 89 | 10.9718 | 8.068
[7 empty] | 1770 | 90 | 10.3786 | 7.6202
[7 empty] | 1771 | 91 | 11.0734 | 8.1447
[7 empty] | 1772 | 92 | 10.4633 | 7.6841
[7 empty] | 1773 | 93 | 8.0228 | 5.8417
[7 empty] | 1774 | 94 | 7.1076 | 5.1507
[7 empty] | 1775 | 95 | 5.2264 | 3.7305
[7 empty] | 1776 | 96 | 4.2265 | 2.9756
[7 empty] | 1777 | 97 | 4.1757 | 2.9372
[7 empty] | 1778 | 98 | 3.8791 | 2.7133
[7 empty] | 1779 | 99 | 3.8197 | 2.6685
[7 empty] | 1780 | 100 | 3.4638 | 2.3999
[7 empty] | 1781 | 101 | 3.4045 | 2.3551
[7 empty] | 1782 | 102 | 3.6418 | 2.5342
[7 empty] | 1783 | 103 | 4.396 | 3.1036
[7 empty] | 1784 | 104 | 4.6502 | 3.2955
[7 empty] | 1785 | 105 | 5.1417 | 3.6665
[7 empty] | 1786 | 106 | 6.6161 | 4.7797
[7 empty] | 1787 | 107 | 6.9721 | 5.0484
[7 empty] | 1788 | 108 | 8.5652 | 6.2511
[7 empty] | 1789 | 109 | 7.8957 | 5.7457
[7 empty] | 1790 | 110 | 7.4381 | 5.4002
[7 empty] | 1791 | 111 | 7.2771 | 5.2787
[7 empty] | 1792 | 112 | 7.3449 | 5.3299
[7 empty] | 1793 | 113 | 6.9975 | 5.0676
[7 empty] | 1794 | 114 | 7.167 | 5.1955
[7 empty] | 1795 | 115 | 6.7094 | 4.8501
[7 empty] | 1796 | 116 | 7.3958 | 5.3683
[7 empty] | 1797 | 117 | 6.9721 | 5.0484
[7 empty] | 1798 | 118 | 6.1924 | 4.4598
[7 empty] | 1799 | 119 | 4.5824 | 3.2443
[7 empty] | 1800 | 120 | 4.2615 | 3.0021
[7 empty] | 1801 | 121 | 3.5232 | 2.4446
[7 empty] | 1802 | 122 | 3.1079 | 2.1312
[7 empty] | 1803 | 123 | 3.0232 | 2.0672
[7 empty] | 1804 | 124 | 2.9893 | 2.0416
[7 empty] | 1805 | 125 | 2.9469 | 2.0096
[7 empty] | 1806 | 126 | 3.091 | 2.1184
[7 empty] | 1807 | 127 | 4.6163 | 3.2699
[7 empty] | 1808 | 128 | 6.1924 | 4.4598
[7 empty] | 1809 | 129 | 6.8788 | 4.978
[7 empty] | 1810 | 130 | 7.3195 | 5.3107
[7 empty] | 1811 | 131 | 7.4805 | 5.4322
[7 empty] | 1812 | 132 | 7.2263 | 5.2403
[7 empty] | 1813 | 133 | 7.8703 | 5.7265
[7 empty] | 1814 | 134 | 8.1754 | 5.9568
[7 empty] | 1815 | 135 | 8.2431 | 6.008
[7 empty] | 1816 | 136 | 7.4212 | 5.3875
[7 empty] | 1817 | 137 | 7.3195 | 5.3107
[7 empty] | 1818 | 138 | 7.2686 | 5.2723
[7 empty] | 1819 | 139 | 6.9297 | 5.0164
[7 empty] | 1820 | 140 | 6.9382 | 5.0228
[7 empty] | 1821 | 141 | 6.2772 | 4.5238
[7 empty] | 1822 | 142 | 5.6332 | 4.0376
[7 empty] | 1823 | 143 | 4.7434 | 3.3659
[7 empty] | 1824 | 144 | 4.1248 | 2.8989
[7 empty] | 1825 | 145 | 3.6503 | 2.5406
[7 empty] | 1826 | 146 | 3.4384 | 2.3807
[7 empty] | 1827 | 147 | 3.3706 | 2.3295
[7 empty] | 1828 | 148 | 3.3622 | 2.3231
[7 empty] | 1829 | 149 | 3.3622 | 2.3231
[7 empty] | 1830 | 150 | 3.3706 | 2.3295
[7 empty] | 1831 | 151 | 4.4638 | 3.1547
[7 empty] | 1832 | 152 | 6.006 | 4.3191
[7 empty] | 1833 | 153 | 6.6246 | 4.7861
[7 empty] | 1834 | 154 | 7.1924 | 5.2147
[7 empty] | 1835 | 155 | 7.0398 | 5.0996
[7 empty] | 1836 | 156 | 7.2093 | 5.2275
[7 empty] | 1837 | 157 | 7.9296 | 5.7713
[7 empty] | 1838 | 158 | 8.2601 | 6.0208
[7 empty] | 1839 | 159 | 8.5313 | 6.2255
[7 empty] | 1840 | 160 | 8.4041 | 6.1296
[7 empty] | 1841 | 161 | 9.1753 | 6.7117
[7 empty] | 1842 | 162 | 8.6753 | 6.3343
[7 empty] | 1843 | 163 | 9.0397 | 6.6094
[7 empty] | 1844 | 164 | 7.6754 | 5.5794
[7 empty] | 1845 | 165 | 10.8362 | 7.9656
[7 empty] | 1846 | 166 | 8.7685 | 6.4046
[7 empty] | 1847 | 167 | 5.1247 | 3.6537
[7 empty] | 1848 | 168 | 4.4722 | 3.1611
[7 empty] | 1849 | 1 | 2.9978 | 2.048
[7 empty] | 1850 | 2 | 2.8876 | 1.9648
[7 empty] | 1851 | 3 | 2.8791 | 1.9584
[7 empty] | 1852 | 4 | 3.0147 | 2.0608
[7 empty] | 1853 | 5 | 3.0317 | 2.0736
[7 empty] | 1854 | 6 | 3.4638 | 2.3999
[7 empty] | 1855 | 7 | 4.1926 | 2.95
[7 empty] | 1856 | 8 | 4.8705 | 3.4618
[7 empty] | 1857 | 9 | 4.8451 | 3.4426
[7 empty] | 1858 | 10 | 6.3789 | 4.6006
[7 empty] | 1859 | 11 | 8.4804 | 6.1871
[7 empty] | 1860 | 12 | 9.4549 | 6.9228
[7 empty] | 1861 | 13 | 9.8362 | 7.2107
[7 empty] | 1862 | 14 | 9.6159 | 7.0444
[7 empty] | 1863 | 15 | 9.5227 | 6.974
[7 empty] | 1864 | 16 | 10.7175 | 7.8761
[7 empty] | 1865 | 17 | 12.0564 | 8.8868
[7 empty] | 1866 | 18 | 11.8107 | 8.7013
[7 empty] | 1867 | 19 | 12.3445 | 9.1044
[7 empty] | 1868 | 20 | 12.2767 | 9.0532
[7 empty] | 1869 | 21 | 12.853 | 9.4882
[7 empty] | 1870 | 22 | 8.8533 | 6.4686
[7 empty] | 1871 | 23 | 5.04 | 3.5898
[7 empty] | 1872 | 24 | 3.3504 | 2.3142
[7 empty] | 1873 | 25 | 3.252 | 2.2399
[7 empty] | 1874 | 26 | 3.1418 | 2.1567
[7 empty] | 1875 | 27 | 3.0401 | 2.08
[7 empty] | 1876 | 28 | 3.1249 | 2.144
[7 empty] | 1877 | 29 | 3.3706 | 2.3295
[7 empty] | 1878 | 30 | 3.6164 | 2.515
[7 empty] | 1879 | 31 | 4.4722 | 3.1611
[7 empty] | 1880 | 32 | 4.8281 | 3.4298
[7 empty] | 1881 | 33 | 5.4976 | 3.9352
[7 empty] | 1882 | 34 | 6.4043 | 4.6198
[7 empty] | 1883 | 35 | 8.5991 | 6.2767
[7 empty] | 1884 | 36 | 9.6413 | 7.0636
[7 empty] | 1885 | 37 | 9.7176 | 7.1212
[7 empty] | 1886 | 38 | 9.7939 | 7.1787
[7 empty] | 1887 | 39 | 9.4634 | 6.9292
[7 empty] | 1888 | 40 | 10.5311 | 7.7353
[7 empty] | 1889 | 41 | 11.0904 | 8.1575
[7 empty] | 1890 | 42 | 11.1073 | 8.1703
[7 empty] | 1891 | 43 | 11.4802 | 8.4518
[7 empty] | 1892 | 44 | 12.6496 | 9.3347
[7 empty] | 1893 | 45 | 12.2428 | 9.0276
[7 empty] | 1894 | 46 | 9.4634 | 6.9292
[7 empty] | 1895 | 47 | 5.8196 | 4.1783
[7 empty] | 1896 | 48 | 4.3028 | 3.0332
[7 empty] | 1897 | 49 | 3.6333 | 2.5278
[7 empty] | 1898 | 50 | 3.3198 | 2.2911
[7 empty] | 1899 | 51 | 3.2096 | 2.2079
[7 empty] | 1900 | 52 | 3.2435 | 2.2335
[7 empty] | 1901 | 53 | 3.2689 | 2.2527
[7 empty] | 1902 | 54 | 3.8536 | 2.6941
[7 empty] | 1903 | 55 | 5.0061 | 3.5642
[7 empty] | 1904 | 56 | 5.2518 | 3.7497
[7 empty] | 1905 | 57 | 6.2094 | 4.4726
[7 empty] | 1906 | 58 | 7.328 | 5.3171
[7 empty] | 1907 | 59 | 8.5482 | 6.2383
[7 empty] | 1908 | 60 | 9.1838 | 6.7181
[7 empty] | 1909 | 61 | 9.8701 | 7.2363
[7 empty] | 1910 | 62 | 9.6668 | 7.0828
[7 empty] | 1911 | 63 | 10.2684 | 7.537
[7 empty] | 1912 | 64 | 11.226 | 8.2599
[7 empty] | 1913 | 65 | 11.853 | 8.7333
[7 empty] | 1914 | 66 | 11.7514 | 8.6565
[7 empty] | 1915 | 67 | 12.4971 | 9.2195
[7 empty] | 1916 | 68 | 12.7428 | 9.405
[7 empty] | 1917 | 69 | 12.2259 | 9.0148
[7 empty] | 1918 | 70 | 9.904 | 7.2619
[7 empty] | 1919 | 71 | 5.3366 | 3.8137
[7 empty] | 1920 | 72 | 4.2398 | 2.9857
[7 empty] | 1921 | 73 | 3.5147 | 2.4382
[7 empty] | 1922 | 74 | 3.2859 | 2.2655
[7 empty] | 1923 | 75 | 3.1842 | 2.1887
[7 empty] | 1924 | 76 | 3.1249 | 2.144
[7 empty] | 1925 | 77 | 3.3028 | 2.2783
[7 empty] | 1926 | 78 | 3.7096 | 2.5854
[7 empty] | 1927 | 79 | 4.8366 | 3.4362
[7 empty] | 1928 | 80 | 5.0146 | 3.5706
[7 empty] | 1929 | 81 | 6.2094 | 4.4726
[7 empty] | 1930 | 82 | 7.311 | 5.3043
[7 empty] | 1931 | 83 | 8.0567 | 5.8673
[7 empty] | 1932 | 84 | 9.3109 | 6.8141
[7 empty] | 1933 | 85 | 9.0058 | 6.5838
[7 empty] | 1934 | 86 | 8.4889 | 6.1935
[7 empty] | 1935 | 87 | 8.938 | 6.5326
[7 empty] | 1936 | 88 | 9.6075 | 7.038
[7 empty] | 1937 | 89 | 10.9718 | 8.068
[7 empty] | 1938 | 90 | 10.3786 | 7.6202
[7 empty] | 1939 | 91 | 11.0734 | 8.1447
[7 empty] | 1940 | 92 | 10.4633 | 7.6841
[7 empty] | 1941 | 93 | 8.0228 | 5.8417
[7 empty] | 1942 | 94 | 7.1076 | 5.1507
[7 empty] | 1943 | 95 | 5.2264 | 3.7305
[7 empty] | 1944 | 96 | 4.2265 | 2.9756
[7 empty] | 1945 | 97 | 4.1757 | 2.9372
[7 empty] | 1946 | 98 | 3.8791 | 2.7133
[7 empty] | 1947 | 99 | 3.8197 | 2.6685
[7 empty] | 1948 | 100 | 3.4638 | 2.3999
[7 empty] | 1949 | 101 | 3.4045 | 2.3551
[7 empty] | 1950 | 102 | 3.6418 | 2.5342
[7 empty] | 1951 | 103 | 4.396 | 3.1036
[7 empty] | 1952 | 104 | 4.6502 | 3.2955
[7 empty] | 1953 | 105 | 5.1417 | 3.6665
[7 empty] | 1954 | 106 | 6.6161 | 4.7797
[7 empty] | 1955 | 107 | 6.9721 | 5.0484
[7 empty] | 1956 | 108 | 8.5652 | 6.2511
[7 empty] | 1957 | 109 | 7.8957 | 5.7457
[7 empty] | 1958 | 110 | 7.4381 | 5.4002
[7 empty] | 1959 | 111 | 7.2771 | 5.2787
[7 empty] | 1960 | 112 | 7.3449 | 5.3299
[7 empty] | 1961 | 113 | 6.9975 | 5.0676
[7 empty] | 1962 | 114 | 7.167 | 5.1955
[7 empty] | 1963 | 115 | 6.7094 | 4.8501
[7 empty] | 1964 | 116 | 7.3958 | 5.3683
[7 empty] | 1965 | 117 | 6.9721 | 5.0484
[7 empty] | 1966 | 118 | 6.1924 | 4.4598
[7 empty] | 1967 | 119 | 4.5824 | 3.2443
[7 empty] | 1968 | 120 | 4.2615 | 3.0021
[7 empty] | 1969 | 121 | 3.5232 | 2.4446
[7 empty] | 1970 | 122 | 3.1079 | 2.1312
[7 empty] | 1971 | 123 | 3.0232 | 2.0672
[7 empty] | 1972 | 124 | 2.9893 | 2.0416
[7 empty] | 1973 | 125 | 2.9469 | 2.0096
[7 empty] | 1974 | 126 | 3.091 | 2.1184
[7 empty] | 1975 | 127 | 4.6163 | 3.2699
[7 empty] | 1976 | 128 | 6.1924 | 4.4598
[7 empty] | 1977 | 129 | 6.8788 | 4.978
[7 empty] | 1978 | 130 | 7.3195 | 5.3107
[7 empty] | 1979 | 131 | 7.4805 | 5.4322
[7 empty] | 1980 | 132 | 7.2263 | 5.2403
[7 empty] | 1981 | 133 | 7.8703 | 5.7265
[7 empty] | 1982 | 134 | 8.1754 | 5.9568
[7 empty] | 1983 | 135 | 8.2431 | 6.008
[7 empty] | 1984 | 136 | 7.4212 | 5.3875
[7 empty] | 1985 | 137 | 7.3195 | 5.3107
[7 empty] | 1986 | 138 | 7.2686 | 5.2723
[7 empty] | 1987 | 139 | 6.9297 | 5.0164
[7 empty] | 1988 | 140 | 6.9382 | 5.0228
[7 empty] | 1989 | 141 | 6.2772 | 4.5238
[7 empty] | 1990 | 142 | 5.6332 | 4.0376
[7 empty] | 1991 | 143 | 4.7434 | 3.3659
[7 empty] | 1992 | 144 | 4.1248 | 2.8989
[7 empty] | 1993 | 145 | 3.6503 | 2.5406
[7 empty] | 1994 | 146 | 3.4384 | 2.3807
[7 empty] | 1995 | 147 | 3.3706 | 2.3295
[7 empty] | 1996 | 148 | 3.3622 | 2.3231
[7 empty] | 1997 | 149 | 3.3622 | 2.3231
[7 empty] | 1998 | 150 | 3.3706 | 2.3295
[7 empty] | 1999 | 151 | 4.4638 | 3.1547
[7 empty] | 2000 | 152 | 6.006 | 4.3191
[7 empty] | 2001 | 153 | 6.6246 | 4.7861
[7 empty] | 2002 | 154 | 7.1924 | 5.2147
[7 empty] | 2003 | 155 | 7.0398 | 5.0996
[7 empty] | 2004 | 156 | 7.2093 | 5.2275
[7 empty] | 2005 | 157 | 7.9296 | 5.7713
[7 empty] | 2006 | 158 | 8.2601 | 6.0208
[7 empty] | 2007 | 159 | 8.5313 | 6.2255
[7 empty] | 2008 | 160 | 8.4041 | 6.1296
[7 empty] | 2009 | 161 | 9.1753 | 6.7117
[7 empty] | 2010 | 162 | 8.6753 | 6.3343
[7 empty] | 2011 | 163 | 9.0397 | 6.6094
[7 empty] | 2012 | 164 | 7.6754 | 5.5794
[7 empty] | 2013 | 165 | 10.8362 | 7.9656
[7 empty] | 2014 | 166 | 8.7685 | 6.4046
[7 empty] | 2015 | 167 | 5.1247 | 3.6537
[7 empty] | 2016 | 168 | 4.4722 | 3.1611
[7 empty] | 2017 | 1 | 2.9978 | 2.048
[7 empty] | 2018 | 2 | 2.8876 | 1.9648
[7 empty] | 2019 | 3 | 2.8791 | 1.9584
[7 empty] | 2020 | 4 | 3.0147 | 2.0608
[7 empty] | 2021 | 5 | 3.0317 | 2.0736
[7 empty] | 2022 | 6 | 3.4638 | 2.3999
[7 empty] | 2023 | 7 | 4.1926 | 2.95
[7 empty] | 2024 | 8 | 4.8705 | 3.4618
[7 empty] | 2025 | 9 | 4.8451 | 3.4426
[7 empty] | 2026 | 10 | 6.3789 | 4.6006
[7 empty] | 2027 | 11 | 8.4804 | 6.1871
[7 empty] | 2028 | 12 | 9.4549 | 6.9228
[7 empty] | 2029 | 13 | 9.8362 | 7.2107
[7 empty] | 2030 | 14 | 9.6159 | 7.0444
[7 empty] | 2031 | 15 | 9.5227 | 6.974
[7 empty] | 2032 | 16 | 10.7175 | 7.8761
[7 empty] | 2033 | 17 | 12.0564 | 8.8868
[7 empty] | 2034 | 18 | 11.8107 | 8.7013
[7 empty] | 2035 | 19 | 12.3445 | 9.1044
[7 empty] | 2036 | 20 | 12.2767 | 9.0532
[7 empty] | 2037 | 21 | 12.853 | 9.4882
[7 empty] | 2038 | 22 | 8.8533 | 6.4686
[7 empty] | 2039 | 23 | 5.04 | 3.5898
[7 empty] | 2040 | 24 | 3.3504 | 2.3142
[7 empty] | 2041 | 25 | 3.252 | 2.2399
[7 empty] | 2042 | 26 | 3.1418 | 2.1567
[7 empty] | 2043 | 27 | 3.0401 | 2.08
[7 empty] | 2044 | 28 | 3.1249 | 2.144
[7 empty] | 2045 | 29 | 3.3706 | 2.3295
[7 empty] | 2046 | 30 | 3.6164 | 2.515
[7 empty] | 2047 | 31 | 4.4722 | 3.1611
[7 empty] | 2048 | 32 | 4.8281 | 3.4298
[7 empty] | 2049 | 33 | 5.4976 | 3.9352
[7 empty] | 2050 | 34 | 6.4043 | 4.6198
[7 empty] | 2051 | 35 | 8.5991 | 6.2767
[7 empty] | 2052 | 36 | 9.6413 | 7.0636
[7 empty] | 2053 | 37 | 9.7176 | 7.1212
[7 empty] | 2054 | 38 | 9.7939 | 7.1787
[7 empty] | 2055 | 39 | 9.4634 | 6.9292
[7 empty] | 2056 | 40 | 10.5311 | 7.7353
[7 empty] | 2057 | 41 | 11.0904 | 8.1575
[7 empty] | 2058 | 42 | 11.1073 | 8.1703
[7 empty] | 2059 | 43 | 11.4802 | 8.4518
[7 empty] | 2060 | 44 | 12.6496 | 9.3347
[7 empty] | 2061 | 45 | 12.2428 | 9.0276
[7 empty] | 2062 | 46 | 9.4634 | 6.9292
[7 empty] | 2063 | 47 | 5.8196 | 4.1783
[7 empty] | 2064 | 48 | 4.3028 | 3.0332
[7 empty] | 2065 | 49 | 3.6333 | 2.5278
[7 empty] | 2066 | 50 | 3.3198 | 2.2911
[7 empty] | 2067 | 51 | 3.2096 | 2.2079
[7 empty] | 2068 | 52 | 3.2435 | 2.2335
[7 empty] | 2069 | 53 | 3.2689 | 2.2527
[7 empty] | 2070 | 54 | 3.8536 | 2.6941
[7 empty] | 2071 | 55 | 5.0061 | 3.5642
[7 empty] | 2072 | 56 | 5.2518 | 3.7497
[7 empty] | 2073 | 57 | 6.2094 | 4.4726
[7 empty] | 2074 | 58 | 7.328 | 5.3171
[7 empty] | 2075 | 59 | 8.5482 | 6.2383
[7 empty] | 2076 | 60 | 9.1838 | 6.7181
[7 empty] | 2077 | 61 | 9.8701 | 7.2363
[7 empty] | 2078 | 62 | 9.6668 | 7.0828
[7 empty] | 2079 | 63 | 10.2684 | 7.537
[7 empty] | 2080 | 64 | 11.226 | 8.2599
[7 empty] | 2081 | 65 | 11.853 | 8.7333
[7 empty] | 2082 | 66 | 11.7514 | 8.6565
[7 empty] | 2083 | 67 | 12.4971 | 9.2195
[7 empty] | 2084 | 68 | 12.7428 | 9.405
[7 empty] | 2085 | 69 | 12.2259 | 9.0148
[7 empty] | 2086 | 70 | 9.904 | 7.2619
[7 empty] | 2087 | 71 | 5.3366 | 3.8137
[7 empty] | 2088 | 72 | 4.2398 | 2.9857
[7 empty] | 2089 | 73 | 3.5147 | 2.4382
[7 empty] | 2090 | 74 | 3.2859 | 2.2655
[7 empty] | 2091 | 75 | 3.1842 | 2.1887
[7 empty] | 2092 | 76 | 3.1249 | 2.144
[7 empty] | 2093 | 77 | 3.3028 | 2.2783
[7 empty] | 2094 | 78 | 3.7096 | 2.5854
[7 empty] | 2095 | 79 | 4.8366 | 3.4362
[7 empty] | 2096 | 80 | 5.0146 | 3.5706
[7 empty] | 2097 | 81 | 6.2094 | 4.4726
[7 empty] | 2098 | 82 | 7.311 | 5.3043
[7 empty] | 2099 | 83 | 8.0567 | 5.8673
[7 empty] | 2100 | 84 | 9.3109 | 6.8141
[7 empty] | 2101 | 85 | 9.0058 | 6.5838
[7 empty] | 2102 | 86 | 8.4889 | 6.1935
[7 empty] | 2103 | 87 | 8.938 | 6.5326
[7 empty] | 2104 | 88 | 9.6075 | 7.038
[7 empty] | 2105 | 89 | 10.9718 | 8.068
[7 empty] | 2106 | 90 | 10.3786 | 7.6202
[7 empty] | 2107 | 91 | 11.0734 | 8.1447
[7 empty] | 2108 | 92 | 10.4633 | 7.6841
[7 empty] | 2109 | 93 | 8.0228 | 5.8417
[7 empty] | 2110 | 94 | 7.1076 | 5.1507
[7 empty] | 2111 | 95 | 5.2264 | 3.7305
[7 empty] | 2112 | 96 | 4.2265 | 2.9756
[7 empty] | 2113 | 97 | 4.1757 | 2.9372
[7 empty] | 2114 | 98 | 3.8791 | 2.7133
[7 empty] | 2115 | 99 | 3.8197 | 2.6685
[7 empty] | 2116 | 100 | 3.4638 | 2.3999
[7 empty] | 2117 | 101 | 3.4045 | 2.3551
[7 empty] | 2118 | 102 | 3.6418 | 2.5342
[7 empty] | 2119 | 103 | 4.396 | 3.1036
[7 empty] | 2120 | 104 | 4.6502 | 3.2955
[7 empty] | 2121 | 105 | 5.1417 | 3.6665
[7 empty] | 2122 | 106 | 6.6161 | 4.7797
[7 empty] | 2123 | 107 | 6.9721 | 5.0484
[7 empty] | 2124 | 108 | 8.5652 | 6.2511
[7 empty] | 2125 | 109 | 7.8957 | 5.7457
[7 empty] | 2126 | 110 | 7.4381 | 5.4002
[7 empty] | 2127 | 111 | 7.2771 | 5.2787
[7 empty] | 2128 | 112 | 7.3449 | 5.3299
[7 empty] | 2129 | 113 | 6.9975 | 5.0676
[7 empty] | 2130 | 114 | 7.167 | 5.1955
[7 empty] | 2131 | 115 | 6.7094 | 4.8501
[7 empty] | 2132 | 116 | 7.3958 | 5.3683
[7 empty] | 2133 | 117 | 6.9721 | 5.0484
[7 empty] | 2134 | 118 | 6.1924 | 4.4598
[7 empty] | 2135 | 119 | 4.5824 | 3.2443
[7 empty] | 2136 | 120 | 4.2615 | 3.0021
[7 empty] | 2137 | 121 | 3.5232 | 2.4446
[7 empty] | 2138 | 122 | 3.1079 | 2.1312
[7 empty] | 2139 | 123 | 3.0232 | 2.0672
[7 empty] | 2140 | 124 | 2.9893 | 2.0416
[7 empty] | 2141 | 125 | 2.9469 | 2.0096
[7 empty] | 2142 | 126 | 3.091 | 2.1184
[7 empty] | 2143 | 127 | 4.6163 | 3.2699
[7 empty] | 2144 | 128 | 6.1924 | 4.4598
[7 empty] | 2145 | 129 | 6.8788 | 4.978
[7 empty] | 2146 | 130 | 7.3195 | 5.3107
[7 empty] | 2147 | 131 | 7.4805 | 5.4322
[7 empty] | 2148 | 132 | 7.2263 | 5.2403
[7 empty] | 2149 | 133 | 7.8703 | 5.7265
[7 empty] | 2150 | 134 | 8.1754 | 5.9568
[7 empty] | 2151 | 135 | 8.2431 | 6.008
[7 empty] | 2152 | 136 | 7.4212 | 5.3875
[7 empty] | 2153 | 137 | 7.3195 | 5.3107
[7 empty] | 2154 | 138 | 7.2686 | 5.2723
[7 empty] | 2155 | 139 | 6.9297 | 5.0164
[7 empty] | 2156 | 140 | 6.9382 | 5.0228
[7 empty] | 2157 | 141 | 6.2772 | 4.5238
[7 empty] | 2158 | 142 | 5.6332 | 4.0376
[7 empty] | 2159 | 143 | 4.7434 | 3.3659
[7 empty] | 2160 | 144 | 4.1248 | 2.8989
[7 empty] | 2161 | 145 | 3.6503 | 2.5406
[7 empty] | 2162 | 146 | 3.4384 | 2.3807
[7 empty] | 2163 | 147 | 3.3706 | 2.3295
[7 empty] | 2164 | 148 | 3.3622 | 2.3231
[7 empty] | 2165 | 149 | 3.3622 | 2.3231
[7 empty] | 2166 | 150 | 3.3706 | 2.3295
[7 empty] | 2167 | 151 | 4.4638 | 3.1547
[7 empty] | 2168 | 152 | 6.006 | 4.3191
[7 empty] | 2169 | 153 | 6.6246 | 4.7861
[7 empty] | 2170 | 154 | 7.1924 | 5.2147
[7 empty] | 2171 | 155 | 7.0398 | 5.0996
[7 empty] | 2172 | 156 | 7.2093 | 5.2275
[7 empty] | 2173 | 157 | 7.9296 | 5.7713
[7 empty] | 2174 | 158 | 8.2601 | 6.0208
[7 empty] | 2175 | 159 | 8.5313 | 6.2255
[7 empty] | 2176 | 160 | 8.4041 | 6.1296
[7 empty] | 2177 | 161 | 9.1753 | 6.7117
[7 empty] | 2178 | 162 | 8.6753 | 6.3343
[7 empty] | 2179 | 163 | 9.0397 | 6.6094
[7 empty] | 2180 | 164 | 7.6754 | 5.5794
[7 empty] | 2181 | 165 | 10.8362 | 7.9656
[7 empty] | 2182 | 166 | 8.7685 | 6.4046
[7 empty] | 2183 | 167 | 5.1247 | 3.6537
[7 empty] | 2184 | 168 | 4.4722 | 3.1611
[7 empty] | 2185 | 1 | 2.9978 | 2.048
[7 empty] | 2186 | 2 | 2.8876 | 1.9648
[7 empty] | 2187 | 3 | 2.8791 | 1.9584
[7 empty] | 2188 | 4 | 3.0147 | 2.0608
[7 empty] | 2189 | 5 | 3.0317 | 2.0736
[7 empty] | 2190 | 6 | 3.4638 | 2.3999
[7 empty] | 2191 | 7 | 4.1926 | 2.95
[7 empty] | 2192 | 8 | 4.8705 | 3.4618
[7 empty] | 2193 | 9 | 4.8451 | 3.4426
[7 empty] | 2194 | 10 | 6.3789 | 4.6006
[7 empty] | 2195 | 11 | 8.4804 | 6.1871
[7 empty] | 2196 | 12 | 9.4549 | 6.9228
[7 empty] | 2197 | 13 | 9.8362 | 7.2107
[7 empty] | 2198 | 14 | 9.6159 | 7.0444
[7 empty] | 2199 | 15 | 9.5227 | 6.974
[7 empty] | 2200 | 16 | 10.7175 | 7.8761
[7 empty] | 2201 | 17 | 12.0564 | 8.8868
[7 empty] | 2202 | 18 | 11.8107 | 8.7013
[7 empty] | 2203 | 19 | 12.3445 | 9.1044
[7 empty] | 2204 | 20 | 12.2767 | 9.0532
[7 empty] | 2205 | 21 | 12.853 | 9.4882
[7 empty] | 2206 | 22 | 8.8533 | 6.4686
[7 empty] | 2207 | 23 | 5.04 | 3.5898
[7 empty] | 2208 | 24 | 3.3504 | 2.3142
[7 empty] | 2209 | 25 | 3.252 | 2.2399
[7 empty] | 2210 | 26 | 3.1418 | 2.1567
[7 empty] | 2211 | 27 | 3.0401 | 2.08
[7 empty] | 2212 | 28 | 3.1249 | 2.144
[7 empty] | 2213 | 29 | 3.3706 | 2.3295
[7 empty] | 2214 | 30 | 3.6164 | 2.515
[7 empty] | 2215 | 31 | 4.4722 | 3.1611
[7 empty] | 2216 | 32 | 4.8281 | 3.4298
[7 empty] | 2217 | 33 | 5.4976 | 3.9352
[7 empty] | 2218 | 34 | 6.4043 | 4.6198
[7 empty] | 2219 | 35 | 8.5991 | 6.2767
[7 empty] | 2220 | 36 | 9.6413 | 7.0636
[7 empty] | 2221 | 37 | 9.7176 | 7.1212
[7 empty] | 2222 | 38 | 9.7939 | 7.1787
[7 empty] | 2223 | 39 | 9.4634 | 6.9292
[7 empty] | 2224 | 40 | 10.5311 | 7.7353
[7 empty] | 2225 | 41 | 11.0904 | 8.1575
[7 empty] | 2226 | 42 | 11.1073 | 8.1703
[7 empty] | 2227 | 43 | 11.4802 | 8.4518
[7 empty] | 2228 | 44 | 12.6496 | 9.3347
[7 empty] | 2229 | 45 | 12.2428 | 9.0276
[7 empty] | 2230 | 46 | 9.4634 | 6.9292
[7 empty] | 2231 | 47 | 5.8196 | 4.1783
[7 empty] | 2232 | 48 | 4.3028 | 3.0332
[7 empty] | 2233 | 49 | 3.6333 | 2.5278
[7 empty] | 2234 | 50 | 3.3198 | 2.2911
[7 empty] | 2235 | 51 | 3.2096 | 2.2079
[7 empty] | 2236 | 52 | 3.2435 | 2.2335
[7 empty] | 2237 | 53 | 3.2689 | 2.2527
[7 empty] | 2238 | 54 | 3.8536 | 2.6941
[7 empty] | 2239 | 55 | 5.0061 | 3.5642
[7 empty] | 2240 | 56 | 5.2518 | 3.7497
[7 empty] | 2241 | 57 | 6.2094 | 4.4726
[7 empty] | 2242 | 58 | 7.328 | 5.3171
[7 empty] | 2243 | 59 | 8.5482 | 6.2383
[7 empty] | 2244 | 60 | 9.1838 | 6.7181
[7 empty] | 2245 | 61 | 9.8701 | 7.2363
[7 empty] | 2246 | 62 | 9.6668 | 7.0828
[7 empty] | 2247 | 63 | 10.2684 | 7.537
[7 empty] | 2248 | 64 | 11.226 | 8.2599
[7 empty] | 2249 | 65 | 11.853 | 8.7333
[7 empty] | 2250 | 66 | 11.7514 | 8.6565
[7 empty] | 2251 | 67 | 12.4971 | 9.2195
[7 empty] | 2252 | 68 | 12.7428 | 9.405
[7 empty] | 2253 | 69 | 12.2259 | 9.0148
[7 empty] | 2254 | 70 | 9.904 | 7.2619
[7 empty] | 2255 | 71 | 5.3366 | 3.8137
[7 empty] | 2256 | 72 | 4.2398 | 2.9857
[7 empty] | 2257 | 73 | 3.5147 | 2.4382
[7 empty] | 2258 | 74 | 3.2859 | 2.2655
[7 empty] | 2259 | 75 | 3.1842 | 2.1887
[7 empty] | 2260 | 76 | 3.1249 | 2.144
[7 empty] | 2261 | 77 | 3.3028 | 2.2783
[7 empty] | 2262 | 78 | 3.7096 | 2.5854
[7 empty] | 2263 | 79 | 4.8366 | 3.4362
[7 empty] | 2264 | 80 | 5.0146 | 3.5706
[7 empty] | 2265 | 81 | 6.2094 | 4.4726
[7 empty] | 2266 | 82 | 7.311 | 5.3043
[7 empty] | 2267 | 83 | 8.0567 | 5.8673
[7 empty] | 2268 | 84 | 9.3109 | 6.8141
[7 empty] | 2269 | 85 | 9.0058 | 6.5838
[7 empty] | 2270 | 86 | 8.4889 | 6.1935
[7 empty] | 2271 | 87 | 8.938 | 6.5326
[7 empty] | 2272 | 88 | 9.6075 | 7.038
[7 empty] | 2273 | 89 | 10.9718 | 8.068
[7 empty] | 2274 | 90 | 10.3786 | 7.6202
[7 empty] | 2275 | 91 | 11.0734 | 8.1447
[7 empty] | 2276 | 92 | 10.4633 | 7.6841
[7 empty] | 2277 | 93 | 8.0228 | 5.8417
[7 empty] | 2278 | 94 | 7.1076 | 5.1507
[7 empty] | 2279 | 95 | 5.2264 | 3.7305
[7 empty] | 2280 | 96 | 4.2265 | 2.9756
[7 empty] | 2281 | 97 | 4.1757 | 2.9372
[7 empty] | 2282 | 98 | 3.8791 | 2.7133
[7 empty] | 2283 | 99 | 3.8197 | 2.6685
[7 empty] | 2284 | 100 | 3.4638 | 2.3999
[7 empty] | 2285 | 101 | 3.4045 | 2.3551
[7 empty] | 2286 | 102 | 3.6418 | 2.5342
[7 empty] | 2287 | 103 | 4.396 | 3.1036
[7 empty] | 2288 | 104 | 4.6502 | 3.2955
[7 empty] | 2289 | 105 | 5.1417 | 3.6665
[7 empty] | 2290 | 106 | 6.6161 | 4.7797
[7 empty] | 2291 | 107 | 6.9721 | 5.0484
[7 empty] | 2292 | 108 | 8.5652 | 6.2511
[7 empty] | 2293 | 109 | 7.8957 | 5.7457
[7 empty] | 2294 | 110 | 7.4381 | 5.4002
[7 empty] | 2295 | 111 | 7.2771 | 5.2787
[7 empty] | 2296 | 112 | 7.3449 | 5.3299
[7 empty] | 2297 | 113 | 6.9975 | 5.0676
[7 empty] | 2298 | 114 | 7.167 | 5.1955
[7 empty] | 2299 | 115 | 6.7094 | 4.8501
[7 empty] | 2300 | 116 | 7.3958 | 5.3683
[7 empty] | 2301 | 117 | 6.9721 | 5.0484
[7 empty] | 2302 | 118 | 6.1924 | 4.4598
[7 empty] | 2303 | 119 | 4.5824 | 3.2443
[7 empty] | 2304 | 120 | 4.2615 | 3.0021
[7 empty] | 2305 | 121 | 3.5232 | 2.4446
[7 empty] | 2306 | 122 | 3.1079 | 2.1312
[7 empty] | 2307 | 123 | 3.0232 | 2.0672
[7 empty] | 2308 | 124 | 2.9893 | 2.0416
[7 empty] | 2309 | 125 | 2.9469 | 2.0096
[7 empty] | 2310 | 126 | 3.091 | 2.1184
[7 empty] | 2311 | 127 | 4.6163 | 3.2699
[7 empty] | 2312 | 128 | 6.1924 | 4.4598
[7 empty] | 2313 | 129 | 6.8788 | 4.978
[7 empty] | 2314 | 130 | 7.3195 | 5.3107
[7 empty] | 2315 | 131 | 7.4805 | 5.4322
[7 empty] | 2316 | 132 | 7.2263 | 5.2403
[7 empty] | 2317 | 133 | 7.8703 | 5.7265
[7 empty] | 2318 | 134 | 8.1754 | 5.9568
[7 empty] | 2319 | 135 | 8.2431 | 6.008
[7 empty] | 2320 | 136 | 7.4212 | 5.3875
[7 empty] | 2321 | 137 | 7.3195 | 5.3107
[7 empty] | 2322 | 138 | 7.2686 | 5.2723
[7 empty] | 2323 | 139 | 6.9297 | 5.0164
[7 empty] | 2324 | 140 | 6.9382 | 5.0228
[7 empty] | 2325 | 141 | 6.2772 | 4.5238
[7 empty] | 2326 | 142 | 5.6332 | 4.0376
[7 empty] | 2327 | 143 | 4.7434 | 3.3659
[7 empty] | 2328 | 144 | 4.1248 | 2.8989
[7 empty] | 2329 | 145 | 3.6503 | 2.5406
[7 empty] | 2330 | 146 | 3.4384 | 2.3807
[7 empty] | 2331 | 147 | 3.3706 | 2.3295
[7 empty] | 2332 | 148 | 3.3622 | 2.3231
[7 empty] | 2333 | 149 | 3.3622 | 2.3231
[7 empty] | 2334 | 150 | 3.3706 | 2.3295
[7 empty] | 2335 | 151 | 4.4638 | 3.1547
[7 empty] | 2336 | 152 | 6.006 | 4.3191
[7 empty] | 2337 | 153 | 6.6246 | 4.7861
[7 empty] | 2338 | 154 | 7.1924 | 5.2147
[7 empty] | 2339 | 155 | 7.0398 | 5.0996
[7 empty] | 2340 | 156 | 7.2093 | 5.2275
[7 empty] | 2341 | 157 | 7.9296 | 5.7713
[7 empty] | 2342 | 158 | 8.2601 | 6.0208
[7 empty] | 2343 | 159 | 8.5313 | 6.2255
[7 empty] | 2344 | 160 | 8.4041 | 6.1296
[7 empty] | 2345 | 161 | 9.1753 | 6.7117
[7 empty] | 2346 | 162 | 8.6753 | 6.3343
[7 empty] | 2347 | 163 | 9.0397 | 6.6094
[7 empty] | 2348 | 164 | 7.6754 | 5.5794
[7 empty] | 2349 | 165 | 10.8362 | 7.9656
[7 empty] | 2350 | 166 | 8.7685 | 6.4046
[7 empty] | 2351 | 167 | 5.1247 | 3.6537
[7 empty] | 2352 | 168 | 4.4722 | 3.1611
[7 empty] | 2353 | 1 | 2.9978 | 2.048
[7 empty] | 2354 | 2 | 2.8876 | 1.9648
[7 empty] | 2355 | 3 | 2.8791 | 1.9584
[7 empty] | 2356 | 4 | 3.0147 | 2.0608
[7 empty] | 2357 | 5 | 3.0317 | 2.0736
[7 empty] | 2358 | 6 | 3.4638 | 2.3999
[7 empty] | 2359 | 7 | 4.1926 | 2.95
[7 empty] | 2360 | 8 | 4.8705 | 3.4618
[7 empty] | 2361 | 9 | 4.8451 | 3.4426
[7 empty] | 2362 | 10 | 6.3789 | 4.6006
[7 empty] | 2363 | 11 | 8.4804 | 6.1871
[7 empty] | 2364 | 12 | 9.4549 | 6.9228
[7 empty] | 2365 | 13 | 9.8362 | 7.2107
[7 empty] | 2366 | 14 | 9.6159 | 7.0444
[7 empty] | 2367 | 15 | 9.5227 | 6.974
[7 empty] | 2368 | 16 | 10.7175 | 7.8761
[7 empty] | 2369 | 17 | 12.0564 | 8.8868
[7 empty] | 2370 | 18 | 11.8107 | 8.7013
[7 empty] | 2371 | 19 | 12.3445 | 9.1044
[7 empty] | 2372 | 20 | 12.2767 | 9.0532
[7 empty] | 2373 | 21 | 12.853 | 9.4882
[7 empty] | 2374 | 22 | 8.8533 | 6.4686
[7 empty] | 2375 | 23 | 5.04 | 3.5898
[7 empty] | 2376 | 24 | 3.3504 | 2.3142
[7 empty] | 2377 | 25 | 3.252 | 2.2399
[7 empty] | 2378 | 26 | 3.1418 | 2.1567
[7 empty] | 2379 | 27 | 3.0401 | 2.08
[7 empty] | 2380 | 28 | 3.1249 | 2.144
[7 empty] | 2381 | 29 | 3.3706 | 2.3295
[7 empty] | 2382 | 30 | 3.6164 | 2.515
[7 empty] | 2383 | 31 | 4.4722 | 3.1611
[7 empty] | 2384 | 32 | 4.8281 | 3.4298
[7 empty] | 2385 | 33 | 5.4976 | 3.9352
[7 empty] | 2386 | 34 | 6.4043 | 4.6198
[7 empty] | 2387 | 35 | 8.5991 | 6.2767
[7 empty] | 2388 | 36 | 9.6413 | 7.0636
[7 empty] | 2389 | 37 | 9.7176 | 7.1212
[7 empty] | 2390 | 38 | 9.7939 | 7.1787
[7 empty] | 2391 | 39 | 9.4634 | 6.9292
[7 empty] | 2392 | 40 | 10.5311 | 7.7353
[7 empty] | 2393 | 41 | 11.0904 | 8.1575
[7 empty] | 2394 | 42 | 11.1073 | 8.1703
[7 empty] | 2395 | 43 | 11.4802 | 8.4518
[7 empty] | 2396 | 44 | 12.6496 | 9.3347
[7 empty] | 2397 | 45 | 12.2428 | 9.0276
[7 empty] | 2398 | 46 | 9.4634 | 6.9292
[7 empty] | 2399 | 47 | 5.8196 | 4.1783
[7 empty] | 2400 | 48 | 4.3028 | 3.0332
[7 empty] | 2401 | 49 | 3.6333 | 2.5278
[7 empty] | 2402 | 50 | 3.3198 | 2.2911
[7 empty] | 2403 | 51 | 3.2096 | 2.2079
[7 empty] | 2404 | 52 | 3.2435 | 2.2335
[7 empty] | 2405 | 53 | 3.2689 | 2.2527
[7 empty] | 2406 | 54 | 3.8536 | 2.6941
[7 empty] | 2407 | 55 | 5.0061 | 3.5642
[7 empty] | 2408 | 56 | 5.2518 | 3.7497
[7 empty] | 2409 | 57 | 6.2094 | 4.4726
[7 empty] | 2410 | 58 | 7.328 | 5.3171
[7 empty] | 2411 | 59 | 8.5482 | 6.2383
[7 empty] | 2412 | 60 | 9.1838 | 6.7181
[7 empty] | 2413 | 61 | 9.8701 | 7.2363
[7 empty] | 2414 | 62 | 9.6668 | 7.0828
[7 empty] | 2415 | 63 | 10.2684 | 7.537
[7 empty] | 2416 | 64 | 11.226 | 8.2599
[7 empty] | 2417 | 65 | 11.853 | 8.7333
[7 empty] | 2418 | 66 | 11.7514 | 8.6565
[7 empty] | 2419 | 67 | 12.4971 | 9.2195
[7 empty] | 2420 | 68 | 12.7428 | 9.405
[7 empty] | 2421 | 69 | 12.2259 | 9.0148
[7 empty] | 2422 | 70 | 9.904 | 7.2619
[7 empty] | 2423 | 71 | 5.3366 | 3.8137
[7 empty] | 2424 | 72 | 4.2398 | 2.9857
[7 empty] | 2425 | 73 | 3.5147 | 2.4382
[7 empty] | 2426 | 74 | 3.2859 | 2.2655
[7 empty] | 2427 | 75 | 3.1842 | 2.1887
[7 empty] | 2428 | 76 | 3.1249 | 2.144
[7 empty] | 2429 | 77 | 3.3028 | 2.2783
[7 empty] | 2430 | 78 | 3.7096 | 2.5854
[7 empty] | 2431 | 79 | 4.8366 | 3.4362
[7 empty] | 2432 | 80 | 5.0146 | 3.5706
[7 empty] | 2433 | 81 | 6.2094 | 4.4726
[7 empty] | 2434 | 82 | 7.311 | 5.3043
[7 empty] | 2435 | 83 | 8.0567 | 5.8673
[7 empty] | 2436 | 84 | 9.3109 | 6.8141
[7 empty] | 2437 | 85 | 9.0058 | 6.5838
[7 empty] | 2438 | 86 | 8.4889 | 6.1935
[7 empty] | 2439 | 87 | 8.938 | 6.5326
[7 empty] | 2440 | 88 | 9.6075 | 7.038
[7 empty] | 2441 | 89 | 10.9718 | 8.068
[7 empty] | 2442 | 90 | 10.3786 | 7.6202
[7 empty] | 2443 | 91 | 11.0734 | 8.1447
[7 empty] | 2444 | 92 | 10.4633 | 7.6841
[7 empty] | 2445 | 93 | 8.0228 | 5.8417
[7 empty] | 2446 | 94 | 7.1076 | 5.1507
[7 empty] | 2447 | 95 | 5.2264 | 3.7305
[7 empty] | 2448 | 96 | 4.2265 | 2.9756
[7 empty] | 2449 | 97 | 4.1757 | 2.9372
[7 empty] | 2450 | 98 | 3.8791 | 2.7133
[7 empty] | 2451 | 99 | 3.8197 | 2.6685
[7 empty] | 2452 | 100 | 3.4638 | 2.3999
[7 empty] | 2453 | 101 | 3.4045 | 2.3551
[7 empty] | 2454 | 102 | 3.6418 | 2.5342
[7 empty] | 2455 | 103 | 4.396 | 3.1036
[7 empty] | 2456 | 104 | 4.6502 | 3.2955
[7 empty] | 2457 | 105 | 5.1417 | 3.6665
[7 empty] | 2458 | 106 | 6.6161 | 4.7797
[7 empty] | 2459 | 107 | 6.9721 | 5.0484
[7 empty] | 2460 | 108 | 8.5652 | 6.2511
[7 empty] | 2461 | 109 | 7.8957 | 5.7457
[7 empty] | 2462 | 110 | 7.4381 | 5.4002
[7 empty] | 2463 | 111 | 7.2771 | 5.2787
[7 empty] | 2464 | 112 | 7.3449 | 5.3299
[7 empty] | 2465 | 113 | 6.9975 | 5.0676
[7 empty] | 2466 | 114 | 7.167 | 5.1955
[7 empty] | 2467 | 115 | 6.7094 | 4.8501
[7 empty] | 2468 | 116 | 7.3958 | 5.3683
[7 empty] | 2469 | 117 | 6.9721 | 5.0484
[7 empty] | 2470 | 118 | 6.1924 | 4.4598
[7 empty] | 2471 | 119 | 4.5824 | 3.2443
[7 empty] | 2472 | 120 | 4.2615 | 3.0021
[7 empty] | 2473 | 121 | 3.5232 | 2.4446
[7 empty] | 2474 | 122 | 3.1079 | 2.1312
[7 empty] | 2475 | 123 | 3.0232 | 2.0672
[7 empty] | 2476 | 124 | 2.9893 | 2.0416
[7 empty] | 2477 | 125 | 2.9469 | 2.0096
[7 empty] | 2478 | 126 | 3.091 | 2.1184
[7 empty] | 2479 | 127 | 4.6163 | 3.2699
[7 empty] | 2480 | 128 | 6.1924 | 4.4598
[7 empty] | 2481 | 129 | 6.8788 | 4.978
[7 empty] | 2482 | 130 | 7.3195 | 5.3107
[7 empty] | 2483 | 131 | 7.4805 | 5.4322
[7 empty] | 2484 | 132 | 7.2263 | 5.2403
[7 empty] | 2485 | 133 | 7.8703 | 5.7265
[7 empty] | 2486 | 134 | 8.1754 | 5.9568
[7 empty] | 2487 | 135 | 8.2431 | 6.008
[7 empty] | 2488 | 136 | 7.4212 | 5.3875
[7 empty] | 2489 | 137 | 7.3195 | 5.3107
[7 empty] | 2490 | 138 | 7.2686 | 5.2723
[7 empty] | 2491 | 139 | 6.9297 | 5.0164
[7 empty] | 2492 | 140 | 6.9382 | 5.0228
[7 empty] | 2493 | 141 | 6.2772 | 4.5238
[7 empty] | 2494 | 142 | 5.6332 | 4.0376
[7 empty] | 2495 | 143 | 4.7434 | 3.3659
[7 empty] | 2496 | 144 | 4.1248 | 2.8989
[7 empty] | 2497 | 145 | 3.6503 | 2.5406
[7 empty] | 2498 | 146 | 3.4384 | 2.3807
[7 empty] | 2499 | 147 | 3.3706 | 2.3295
[7 empty] | 2500 | 148 | 3.3622 | 2.3231
[7 empty] | 2501 | 149 | 3.3622 | 2.3231
[7 empty] | 2502 | 150 | 3.3706 | 2.3295
[7 empty] | 2503 | 151 | 4.4638 | 3.1547
[7 empty] | 2504 | 152 | 6.006 | 4.3191
[7 empty] | 2505 | 153 | 6.6246 | 4.7861
[7 empty] | 2506 | 154 | 7.1924 | 5.2147
[7 empty] | 2507 | 155 | 7.0398 | 5.0996
[7 empty] | 2508 | 156 | 7.2093 | 5.2275
[7 empty] | 2509 | 157 | 7.9296 | 5.7713
[7 empty] | 2510 | 158 | 8.2601 | 6.0208
[7 empty] | 2511 | 159 | 8.5313 | 6.2255
[7 empty] | 2512 | 160 | 8.4041 | 6.1296
[7 empty] | 2513 | 161 | 9.1753 | 6.7117
[7 empty] | 2514 | 162 | 8.6753 | 6.3343
[7 empty] | 2515 | 163 | 9.0397 | 6.6094
[7 empty] | 2516 | 164 | 7.6754 | 5.5794
[7 empty] | 2517 | 165 | 10.8362 | 7.9656
[7 empty] | 2518 | 166 | 8.7685 | 6.4046
[7 empty] | 2519 | 167 | 5.1247 | 3.6537
[7 empty] | 2520 | 168 | 4.4722 | 3.1611
[7 empty] | 2521 | 1 | 2.9978 | 2.048
[7 empty] | 2522 | 2 | 2.8876 | 1.9648
[7 empty] | 2523 | 3 | 2.8791 | 1.9584
[7 empty] | 2524 | 4 | 3.0147 | 2.0608
[7 empty] | 2525 | 5 | 3.0317 | 2.0736
[7 empty] | 2526 | 6 | 3.4638 | 2.3999
[7 empty] | 2527 | 7 | 4.1926 | 2.95
[7 empty] | 2528 | 8 | 4.8705 | 3.4618
[7 empty] | 2529 | 9 | 4.8451 | 3.4426
[7 empty] | 2530 | 10 | 6.3789 | 4.6006
[7 empty] | 2531 | 11 | 8.4804 | 6.1871
[7 empty] | 2532 | 12 | 9.4549 | 6.9228
[7 empty] | 2533 | 13 | 9.8362 | 7.2107
[7 empty] | 2534 | 14 | 9.6159 | 7.0444
[7 empty] | 2535 | 15 | 9.5227 | 6.974
[7 empty] | 2536 | 16 | 10.7175 | 7.8761
[7 empty] | 2537 | 17 | 12.0564 | 8.8868
[7 empty] | 2538 | 18 | 11.8107 | 8.7013
[7 empty] | 2539 | 19 | 12.3445 | 9.1044
[7 empty] | 2540 | 20 | 12.2767 | 9.0532
[7 empty] | 2541 | 21 | 12.853 | 9.4882
[7 empty] | 2542 | 22 | 8.8533 | 6.4686
[7 empty] | 2543 | 23 | 5.04 | 3.5898
[7 empty] | 2544 | 24 | 3.3504 | 2.3142
[7 empty] | 2545 | 25 | 3.252 | 2.2399
[7 empty] | 2546 | 26 | 3.1418 | 2.1567
[7 empty] | 2547 | 27 | 3.0401 | 2.08
[7 empty] | 2548 | 28 | 3.1249 | 2.144
[7 empty] | 2549 | 29 | 3.3706 | 2.3295
[7 empty] | 2550 | 30 | 3.6164 | 2.515
[7 empty] | 2551 | 31 | 4.4722 | 3.1611
[7 empty] | 2552 | 32 | 4.8281 | 3.4298
[7 empty] | 2553 | 33 | 5.4976 | 3.9352
[7 empty] | 2554 | 34 | 6.4043 | 4.6198
[7 empty] | 2555 | 35 | 8.5991 | 6.2767
[7 empty] | 2556 | 36 | 9.6413 | 7.0636
[7 empty] | 2557 | 37 | 9.7176 | 7.1212
[7 empty] | 2558 | 38 | 9.7939 | 7.1787
[7 empty] | 2559 | 39 | 9.4634 | 6.9292
[7 empty] | 2560 | 40 | 10.5311 | 7.7353
[7 empty] | 2561 | 41 | 11.0904 | 8.1575
[7 empty] | 2562 | 42 | 11.1073 | 8.1703
[7 empty] | 2563 | 43 | 11.4802 | 8.4518
[7 empty] | 2564 | 44 | 12.6496 | 9.3347
[7 empty] | 2565 | 45 | 12.2428 | 9.0276
[7 empty] | 2566 | 46 | 9.4634 | 6.9292
[7 empty] | 2567 | 47 | 5.8196 | 4.1783
[7 empty] | 2568 | 48 | 4.3028 | 3.0332
[7 empty] | 2569 | 49 | 3.6333 | 2.5278
[7 empty] | 2570 | 50 | 3.3198 | 2.2911
[7 empty] | 2571 | 51 | 3.2096 | 2.2079
[7 empty] | 2572 | 52 | 3.2435 | 2.2335
[7 empty] | 2573 | 53 | 3.2689 | 2.2527
[7 empty] | 2574 | 54 | 3.8536 | 2.6941
[7 empty] | 2575 | 55 | 5.0061 | 3.5642
[7 empty] | 2576 | 56 | 5.2518 | 3.7497
[7 empty] | 2577 | 57 | 6.2094 | 4.4726
[7 empty] | 2578 | 58 | 7.328 | 5.3171
[7 empty] | 2579 | 59 | 8.5482 | 6.2383
[7 empty] | 2580 | 60 | 9.1838 | 6.7181
[7 empty] | 2581 | 61 | 9.8701 | 7.2363
[7 empty] | 2582 | 62 | 9.6668 | 7.0828
[7 empty] | 2583 | 63 | 10.2684 | 7.537
[7 empty] | 2584 | 64 | 11.226 | 8.2599
[7 empty] | 2585 | 65 | 11.853 | 8.7333
[7 empty] | 2586 | 66 | 11.7514 | 8.6565
[7 empty] | 2587 | 67 | 12.4971 | 9.2195
[7 empty] | 2588 | 68 | 12.7428 | 9.405
[7 empty] | 2589 | 69 | 12.2259 | 9.0148
[7 empty] | 2590 | 70 | 9.904 | 7.2619
[7 empty] | 2591 | 71 | 5.3366 | 3.8137
[7 empty] | 2592 | 72 | 4.2398 | 2.9857
[7 empty] | 2593 | 73 | 3.5147 | 2.4382
[7 empty] | 2594 | 74 | 3.2859 | 2.2655
[7 empty] | 2595 | 75 | 3.1842 | 2.1887
[7 empty] | 2596 | 76 | 3.1249 | 2.144
[7 empty] | 2597 | 77 | 3.3028 | 2.2783
[7 empty] | 2598 | 78 | 3.7096 | 2.5854
[7 empty] | 2599 | 79 | 4.8366 | 3.4362
[7 empty] | 2600 | 80 | 5.0146 | 3.5706
[7 empty] | 2601 | 81 | 6.2094 | 4.4726
[7 empty] | 2602 | 82 | 7.311 | 5.3043
[7 empty] | 2603 | 83 | 8.0567 | 5.8673
[7 empty] | 2604 | 84 | 9.3109 | 6.8141
[7 empty] | 2605 | 85 | 9.0058 | 6.5838
[7 empty] | 2606 | 86 | 8.4889 | 6.1935
[7 empty] | 2607 | 87 | 8.938 | 6.5326
[7 empty] | 2608 | 88 | 9.6075 | 7.038
[7 empty] | 2609 | 89 | 10.9718 | 8.068
[7 empty] | 2610 | 90 | 10.3786 | 7.6202
[7 empty] | 2611 | 91 | 11.0734 | 8.1447
[7 empty] | 2612 | 92 | 10.4633 | 7.6841
[7 empty] | 2613 | 93 | 8.0228 | 5.8417
[7 empty] | 2614 | 94 | 7.1076 | 5.1507
[7 empty] | 2615 | 95 | 5.2264 | 3.7305
[7 empty] | 2616 | 96 | 4.2265 | 2.9756
[7 empty] | 2617 | 97 | 4.1757 | 2.9372
[7 empty] | 2618 | 98 | 3.8791 | 2.7133
[7 empty] | 2619 | 99 | 3.8197 | 2.6685
[7 empty] | 2620 | 100 | 3.4638 | 2.3999
[7 empty] | 2621 | 101 | 3.4045 | 2.3551
[7 empty] | 2622 | 102 | 3.6418 | 2.5342
[7 empty] | 2623 | 103 | 4.396 | 3.1036
[7 empty] | 2624 | 104 | 4.6502 | 3.2955
[7 empty] | 2625 | 105 | 5.1417 | 3.6665
[7 empty] | 2626 | 106 | 6.6161 | 4.7797
[7 empty] | 2627 | 107 | 6.9721 | 5.0484
[7 empty] | 2628 | 108 | 8.5652 | 6.2511
[7 empty] | 2629 | 109 | 7.8957 | 5.7457
[7 empty] | 2630 | 110 | 7.4381 | 5.4002
[7 empty] | 2631 | 111 | 7.2771 | 5.2787
[7 empty] | 2632 | 112 | 7.3449 | 5.3299
[7 empty] | 2633 | 113 | 6.9975 | 5.0676
[7 empty] | 2634 | 114 | 7.167 | 5.1955
[7 empty] | 2635 | 115 | 6.7094 | 4.8501
[7 empty] | 2636 | 116 | 7.3958 | 5.3683
[7 empty] | 2637 | 117 | 6.9721 | 5.0484
[7 empty] | 2638 | 118 | 6.1924 | 4.4598
[7 empty] | 2639 | 119 | 4.5824 | 3.2443
[7 empty] | 2640 | 120 | 4.2615 | 3.0021
[7 empty] | 2641 | 121 | 3.5232 | 2.4446
[7 empty] | 2642 | 122 | 3.1079 | 2.1312
[7 empty] | 2643 | 123 | 3.0232 | 2.0672
[7 empty] | 2644 | 124 | 2.9893 | 2.0416
[7 empty] | 2645 | 125 | 2.9469 | 2.0096
[7 empty] | 2646 | 126 | 3.091 | 2.1184
[7 empty] | 2647 | 127 | 4.6163 | 3.2699
[7 empty] | 2648 | 128 | 6.1924 | 4.4598
[7 empty] | 2649 | 129 | 6.8788 | 4.978
[7 empty] | 2650 | 130 | 7.3195 | 5.3107
[7 empty] | 2651 | 131 | 7.4805 | 5.4322
[7 empty] | 2652 | 132 | 7.2263 | 5.2403
[7 empty] | 2653 | 133 | 7.8703 | 5.7265
[7 empty] | 2654 | 134 | 8.1754 | 5.9568
[7 empty] | 2655 | 135 | 8.2431 | 6.008
[7 empty] | 2656 | 136 | 7.4212 | 5.3875
[7 empty] | 2657 | 137 | 7.3195 | 5.3107
[7 empty] | 2658 | 138 | 7.2686 | 5.2723
[7 empty] | 2659 | 139 | 6.9297 | 5.0164
[7 empty] | 2660 | 140 | 6.9382 | 5.0228
[7 empty] | 2661 | 141 | 6.2772 | 4.5238
[7 empty] | 2662 | 142 | 5.6332 | 4.0376
[7 empty] | 2663 | 143 | 4.7434 | 3.3659
[7 empty] | 2664 | 144 | 4.1248 | 2.8989
[7 empty] | 2665 | 145 | 3.6503 | 2.5406
[7 empty] | 2666 | 146 | 3.4384 | 2.3807
[7 empty] | 2667 | 147 | 3.3706 | 2.3295
[7 empty] | 2668 | 148 | 3.3622 | 2.3231
[7 empty] | 2669 | 149 | 3.3622 | 2.3231
[7 empty] | 2670 | 150 | 3.3706 | 2.3295
[7 empty] | 2671 | 151 | 4.4638 | 3.1547
[7 empty] | 2672 | 152 | 6.006 | 4.3191
[7 empty] | 2673 | 153 | 6.6246 | 4.7861
[7 empty] | 2674 | 154 | 7.1924 | 5.2147
[7 empty] | 2675 | 155 | 7.0398 | 5.0996
[7 empty] | 2676 | 156 | 7.2093 | 5.2275
[7 empty] | 2677 | 157 | 7.9296 | 5.7713
[7 empty] | 2678 | 158 | 8.2601 | 6.0208
[7 empty] | 2679 | 159 | 8.5313 | 6.2255
[7 empty] | 2680 | 160 | 8.4041 | 6.1296
[7 empty] | 2681 | 161 | 9.1753 | 6.7117
[7 empty] | 2682 | 162 | 8.6753 | 6.3343
[7 empty] | 2683 | 163 | 9.0397 | 6.6094
[7 empty] | 2684 | 164 | 7.6754 | 5.5794
[7 empty] | 2685 | 165 | 10.8362 | 7.9656
[7 empty] | 2686 | 166 | 8.7685 | 6.4046
[7 empty] | 2687 | 167 | 5.1247 | 3.6537
[7 empty] | 2688 | 168 | 4.4722 | 3.1611
[7 empty] | 2689 | 1 | 2.9978 | 2.048
[7 empty] | 2690 | 2 | 2.8876 | 1.9648
[7 empty] | 2691 | 3 | 2.8791 | 1.9584
[7 empty] | 2692 | 4 | 3.0147 | 2.0608
[7 empty] | 2693 | 5 | 3.0317 | 2.0736
[7 empty] | 2694 | 6 | 3.4638 | 2.3999
[7 empty] | 2695 | 7 | 4.1926 | 2.95
[7 empty] | 2696 | 8 | 4.8705 | 3.4618
[7 empty] | 2697 | 9 | 4.8451 | 3.4426
[7 empty] | 2698 | 10 | 6.3789 | 4.6006
[7 empty] | 2699 | 11 | 8.4804 | 6.1871
[7 empty] | 2700 | 12 | 9.4549 | 6.9228
[7 empty] | 2701 | 13 | 9.8362 | 7.2107
[7 empty] | 2702 | 14 | 9.6159 | 7.0444
[7 empty] | 2703 | 15 | 9.5227 | 6.974
[7 empty] | 2704 | 16 | 10.7175 | 7.8761
[7 empty] | 2705 | 17 | 12.0564 | 8.8868
[7 empty] | 2706 | 18 | 11.8107 | 8.7013
[7 empty] | 2707 | 19 | 12.3445 | 9.1044
[7 empty] | 2708 | 20 | 12.2767 | 9.0532
[7 empty] | 2709 | 21 | 12.853 | 9.4882
[7 empty] | 2710 | 22 | 8.8533 | 6.4686
[7 empty] | 2711 | 23 | 5.04 | 3.5898
[7 empty] | 2712 | 24 | 3.3504 | 2.3142
[7 empty] | 2713 | 25 | 3.252 | 2.2399
[7 empty] | 2714 | 26 | 3.1418 | 2.1567
[7 empty] | 2715 | 27 | 3.0401 | 2.08
[7 empty] | 2716 | 28 | 3.1249 | 2.144
[7 empty] | 2717 | 29 | 3.3706 | 2.3295
[7 empty] | 2718 | 30 | 3.6164 | 2.515
[7 empty] | 2719 | 31 | 4.4722 | 3.1611
[7 empty] | 2720 | 32 | 4.8281 | 3.4298
[7 empty] | 2721 | 33 | 5.4976 | 3.9352
[7 empty] | 2722 | 34 | 6.4043 | 4.6198
[7 empty] | 2723 | 35 | 8.5991 | 6.2767
[7 empty] | 2724 | 36 | 9.6413 | 7.0636
[7 empty] | 2725 | 37 | 9.7176 | 7.1212
[7 empty] | 2726 | 38 | 9.7939 | 7.1787
[7 empty] | 2727 | 39 | 9.4634 | 6.9292
[7 empty] | 2728 | 40 | 10.5311 | 7.7353
[7 empty] | 2729 | 41 | 11.0904 | 8.1575
[7 empty] | 2730 | 42 | 11.1073 | 8.1703
[7 empty] | 2731 | 43 | 11.4802 | 8.4518
[7 empty] | 2732 | 44 | 12.6496 | 9.3347
[7 empty] | 2733 | 45 | 12.2428 | 9.0276
[7 empty] | 2734 | 46 | 9.4634 | 6.9292
[7 empty] | 2735 | 47 | 5.8196 | 4.1783
[7 empty] | 2736 | 48 | 4.3028 | 3.0332
[7 empty] | 2737 | 49 | 3.6333 | 2.5278
[7 empty] | 2738 | 50 | 3.3198 | 2.2911
[7 empty] | 2739 | 51 | 3.2096 | 2.2079
[7 empty] | 2740 | 52 | 3.2435 | 2.2335
[7 empty] | 2741 | 53 | 3.2689 | 2.2527
[7 empty] | 2742 | 54 | 3.8536 | 2.6941
[7 empty] | 2743 | 55 | 5.0061 | 3.5642
[7 empty] | 2744 | 56 | 5.2518 | 3.7497
[7 empty] | 2745 | 57 | 6.2094 | 4.4726
[7 empty] | 2746 | 58 | 7.328 | 5.3171
[7 empty] | 2747 | 59 | 8.5482 | 6.2383
[7 empty] | 2748 | 60 | 9.1838 | 6.7181
[7 empty] | 2749 | 61 | 9.8701 | 7.2363
[7 empty] | 2750 | 62 | 9.6668 | 7.0828
[7 empty] | 2751 | 63 | 10.2684 | 7.537
[7 empty] | 2752 | 64 | 11.226 | 8.2599
[7 empty] | 2753 | 65 | 11.853 | 8.7333
[7 empty] | 2754 | 66 | 11.7514 | 8.6565
[7 empty] | 2755 | 67 | 12.4971 | 9.2195
[7 empty] | 2756 | 68 | 12.7428 | 9.405
[7 empty] | 2757 | 69 | 12.2259 | 9.0148
[7 empty] | 2758 | 70 | 9.904 | 7.2619
[7 empty] | 2759 | 71 | 5.3366 | 3.8137
[7 empty] | 2760 | 72 | 4.2398 | 2.9857
[7 empty] | 2761 | 73 | 3.5147 | 2.4382
[7 empty] | 2762 | 74 | 3.2859 | 2.2655
[7 empty] | 2763 | 75 | 3.1842 | 2.1887
[7 empty] | 2764 | 76 | 3.1249 | 2.144
[7 empty] | 2765 | 77 | 3.3028 | 2.2783
[7 empty] | 2766 | 78 | 3.7096 | 2.5854
[7 empty] | 2767 | 79 | 4.8366 | 3.4362
[7 empty] | 2768 | 80 | 5.0146 | 3.5706
[7 empty] | 2769 | 81 | 6.2094 | 4.4726
[7 empty] | 2770 | 82 | 7.311 | 5.3043
[7 empty] | 2771 | 83 | 8.0567 | 5.8673
[7 empty] | 2772 | 84 | 9.3109 | 6.8141
[7 empty] | 2773 | 85 | 9.0058 | 6.5838
[7 empty] | 2774 | 86 | 8.4889 | 6.1935
[7 empty] | 2775 | 87 | 8.938 | 6.5326
[7 empty] | 2776 | 88 | 9.6075 | 7.038
[7 empty] | 2777 | 89 | 10.9718 | 8.068
[7 empty] | 2778 | 90 | 10.3786 | 7.6202
[7 empty] | 2779 | 91 | 11.0734 | 8.1447
[7 empty] | 2780 | 92 | 10.4633 | 7.6841
[7 empty] | 2781 | 93 | 8.0228 | 5.8417
[7 empty] | 2782 | 94 | 7.1076 | 5.1507
[7 empty] | 2783 | 95 | 5.2264 | 3.7305
[7 empty] | 2784 | 96 | 4.2265 | 2.9756
[7 empty] | 2785 | 97 | 4.1757 | 2.9372
[7 empty] | 2786 | 98 | 3.8791 | 2.7133
[7 empty] | 2787 | 99 | 3.8197 | 2.6685
[7 empty] | 2788 | 100 | 3.4638 | 2.3999
[7 empty] | 2789 | 101 | 3.4045 | 2.3551
[7 empty] | 2790 | 102 | 3.6418 | 2.5342
[7 empty] | 2791 | 103 | 4.396 | 3.1036
[7 empty] | 2792 | 104 | 4.6502 | 3.2955
[7 empty] | 2793 | 105 | 5.1417 | 3.6665
[7 empty] | 2794 | 106 | 6.6161 | 4.7797
[7 empty] | 2795 | 107 | 6.9721 | 5.0484
[7 empty] | 2796 | 108 | 8.5652 | 6.2511
[7 empty] | 2797 | 109 | 7.8957 | 5.7457
[7 empty] | 2798 | 110 | 7.4381 | 5.4002
[7 empty] | 2799 | 111 | 7.2771 | 5.2787
[7 empty] | 2800 | 112 | 7.3449 | 5.3299
[7 empty] | 2801 | 113 | 6.9975 | 5.0676
[7 empty] | 2802 | 114 | 7.167 | 5.1955
[7 empty] | 2803 | 115 | 6.7094 | 4.8501
[7 empty] | 2804 | 116 | 7.3958 | 5.3683
[7 empty] | 2805 | 117 | 6.9721 | 5.0484
[7 empty] | 2806 | 118 | 6.1924 | 4.4598
[7 empty] | 2807 | 119 | 4.5824 | 3.2443
[7 empty] | 2808 | 120 | 4.2615 | 3.0021
[7 empty] | 2809 | 121 | 3.5232 | 2.4446
[7 empty] | 2810 | 122 | 3.1079 | 2.1312
[7 empty] | 2811 | 123 | 3.0232 | 2.0672
[7 empty] | 2812 | 124 | 2.9893 | 2.0416
[7 empty] | 2813 | 125 | 2.9469 | 2.0096
[7 empty] | 2814 | 126 | 3.091 | 2.1184
[7 empty] | 2815 | 127 | 4.6163 | 3.2699
[7 empty] | 2816 | 128 | 6.1924 | 4.4598
[7 empty] | 2817 | 129 | 6.8788 | 4.978
[7 empty] | 2818 | 130 | 7.3195 | 5.3107
[7 empty] | 2819 | 131 | 7.4805 | 5.4322
[7 empty] | 2820 | 132 | 7.2263 | 5.2403
[7 empty] | 2821 | 133 | 7.8703 | 5.7265
[7 empty] | 2822 | 134 | 8.1754 | 5.9568
[7 empty] | 2823 | 135 | 8.2431 | 6.008
[7 empty] | 2824 | 136 | 7.4212 | 5.3875
[7 empty] | 2825 | 137 | 7.3195 | 5.3107
[7 empty] | 2826 | 138 | 7.2686 | 5.2723
[7 empty] | 2827 | 139 | 6.9297 | 5.0164
[7 empty] | 2828 | 140 | 6.9382 | 5.0228
[7 empty] | 2829 | 141 | 6.2772 | 4.5238
[7 empty] | 2830 | 142 | 5.6332 | 4.0376
[7 empty] | 2831 | 143 | 4.7434 | 3.3659
[7 empty] | 2832 | 144 | 4.1248 | 2.8989
[7 empty] | 2833 | 145 | 3.6503 | 2.5406
[7 empty] | 2834 | 146 | 3.4384 | 2.3807
[7 empty] | 2835 | 147 | 3.3706 | 2.3295
[7 empty] | 2836 | 148 | 3.3622 | 2.3231
[7 empty] | 2837 | 149 | 3.3622 | 2.3231
[7 empty] | 2838 | 150 | 3.3706 | 2.3295
[7 empty] | 2839 | 151 | 4.4638 | 3.1547
[7 empty] | 2840 | 152 | 6.006 | 4.3191
[7 empty] | 2841 | 153 | 6.6246 | 4.7861
[7 empty] | 2842 | 154 | 7.1924 | 5.2147
[7 empty] | 2843 | 155 | 7.0398 | 5.0996
[7 empty] | 2844 | 156 | 7.2093 | 5.2275
[7 empty] | 2845 | 157 | 7.9296 | 5.7713
[7 empty] | 2846 | 158 | 8.2601 | 6.0208
[7 empty] | 2847 | 159 | 8.5313 | 6.2255
[7 empty] | 2848 | 160 | 8.4041 | 6.1296
[7 empty] | 2849 | 161 | 9.1753 | 6.7117
[7 empty] | 2850 | 162 | 8.6753 | 6.3343
[7 empty] | 2851 | 163 | 9.0397 | 6.6094
[7 empty] | 2852 | 164 | 7.6754 | 5.5794
[7 empty] | 2853 | 165 | 10.8362 | 7.9656
[7 empty] | 2854 | 166 | 8.7685 | 6.4046
[7 empty] | 2855 | 167 | 5.1247 | 3.6537
[7 empty] | 2856 | 168 | 4.4722 | 3.1611
[7 empty] | 2857 | 1 | 2.9978 | 2.048
[7 empty] | 2858 | 2 | 2.8876 | 1.9648
[7 empty] | 2859 | 3 | 2.8791 | 1.9584
[7 empty] | 2860 | 4 | 3.0147 | 2.0608
[7 empty] | 2861 | 5 | 3.0317 | 2.0736
[7 empty] | 2862 | 6 | 3.4638 | 2.3999
[7 empty] | 2863 | 7 | 4.1926 | 2.95
[7 empty] | 2864 | 8 | 4.8705 | 3.4618
[7 empty] | 2865 | 9 | 4.8451 | 3.4426
[7 empty] | 2866 | 10 | 6.3789 | 4.6006
[7 empty] | 2867 | 11 | 8.4804 | 6.1871
[7 empty] | 2868 | 12 | 9.4549 | 6.9228
[7 empty] | 2869 | 13 | 9.8362 | 7.2107
[7 empty] | 2870 | 14 | 9.6159 | 7.0444
[7 empty] | 2871 | 15 | 9.5227 | 6.974
[7 empty] | 2872 | 16 | 10.7175 | 7.8761
[7 empty] | 2873 | 17 | 12.0564 | 8.8868
[7 empty] | 2874 | 18 | 11.8107 | 8.7013
[7 empty] | 2875 | 19 | 12.3445 | 9.1044
[7 empty] | 2876 | 20 | 12.2767 | 9.0532
[7 empty] | 2877 | 21 | 12.853 | 9.4882
[7 empty] | 2878 | 22 | 8.8533 | 6.4686
[7 empty] | 2879 | 23 | 5.04 | 3.5898
[7 empty] | 2880 | 24 | 3.3504 | 2.3142
[7 empty] | 2881 | 25 | 3.252 | 2.2399
[7 empty] | 2882 | 26 | 3.1418 | 2.1567
[7 empty] | 2883 | 27 | 3.0401 | 2.08
[7 empty] | 2884 | 28 | 3.1249 | 2.144
[7 empty] | 2885 | 29 | 3.3706 | 2.3295
[7 empty] | 2886 | 30 | 3.6164 | 2.515
[7 empty] | 2887 | 31 | 4.4722 | 3.1611
[7 empty] | 2888 | 32 | 4.8281 | 3.4298
[7 empty] | 2889 | 33 | 5.4976 | 3.9352
[7 empty] | 2890 | 34 | 6.4043 | 4.6198
[7 empty] | 2891 | 35 | 8.5991 | 6.2767
[7 empty] | 2892 | 36 | 9.6413 | 7.0636
[7 empty] | 2893 | 37 | 9.7176 | 7.1212
[7 empty] | 2894 | 38 | 9.7939 | 7.1787
[7 empty] | 2895 | 39 | 9.4634 | 6.9292
[7 empty] | 2896 | 40 | 10.5311 | 7.7353
[7 empty] | 2897 | 41 | 11.0904 | 8.1575
[7 empty] | 2898 | 42 | 11.1073 | 8.1703
[7 empty] | 2899 | 43 | 11.4802 | 8.4518
[7 empty] | 2900 | 44 | 12.6496 | 9.3347
[7 empty] | 2901 | 45 | 12.2428 | 9.0276
[7 empty] | 2902 | 46 | 9.4634 | 6.9292
[7 empty] | 2903 | 47 | 5.8196 | 4.1783
[7 empty] | 2904 | 48 | 4.3028 | 3.0332
[7 empty] | 2905 | 49 | 3.6333 | 2.5278
[7 empty] | 2906 | 50 | 3.3198 | 2.2911
[7 empty] | 2907 | 51 | 3.2096 | 2.2079
[7 empty] | 2908 | 52 | 3.2435 | 2.2335
[7 empty] | 2909 | 53 | 3.2689 | 2.2527
[7 empty] | 2910 | 54 | 3.8536 | 2.6941
[7 empty] | 2911 | 55 | 5.0061 | 3.5642
[7 empty] | 2912 | 56 | 5.2518 | 3.7497
[7 empty] | 2913 | 57 | 6.2094 | 4.4726
[7 empty] | 2914 | 58 | 7.328 | 5.3171
[7 empty] | 2915 | 59 | 8.5482 | 6.2383
[7 empty] | 2916 | 60 | 9.1838 | 6.7181
[7 empty] | 2917 | 61 | 9.8701 | 7.2363
[7 empty] | 2918 | 62 | 9.6668 | 7.0828
[7 empty] | 2919 | 63 | 10.2684 | 7.537
[7 empty] | 2920 | 64 | 11.226 | 8.2599
[7 empty] | 2921 | 65 | 11.853 | 8.7333
[7 empty] | 2922 | 66 | 11.7514 | 8.6565
[7 empty] | 2923 | 67 | 12.4971 | 9.2195
[7 empty] | 2924 | 68 | 12.7428 | 9.405
[7 empty] | 2925 | 69 | 12.2259 | 9.0148
[7 empty] | 2926 | 70 | 9.904 | 7.2619
[7 empty] | 2927 | 71 | 5.3366 | 3.8137
[7 empty] | 2928 | 72 | 4.2398 | 2.9857
[7 empty] | 2929 | 73 | 3.5147 | 2.4382
[7 empty] | 2930 | 74 | 3.2859 | 2.2655
[7 empty] | 2931 | 75 | 3.1842 | 2.1887
[7 empty] | 2932 | 76 | 3.1249 | 2.144
[7 empty] | 2933 | 77 | 3.3028 | 2.2783
[7 empty] | 2934 | 78 | 3.7096 | 2.5854
[7 empty] | 2935 | 79 | 4.8366 | 3.4362
[7 empty] | 2936 | 80 | 5.0146 | 3.5706
[7 empty] | 2937 | 81 | 6.2094 | 4.4726
[7 empty] | 2938 | 82 | 7.311 | 5.3043
[7 empty] | 2939 | 83 | 8.0567 | 5.8673
[7 empty] | 2940 | 84 | 9.3109 | 6.8141
[7 empty] | 2941 | 85 | 9.0058 | 6.5838
[7 empty] | 2942 | 86 | 8.4889 | 6.1935
[7 empty] | 2943 | 87 | 8.938 | 6.5326
[7 empty] | 2944 | 88 | 9.6075 | 7.038
[7 empty] | 2945 | 89 | 10.9718 | 8.068
[7 empty] | 2946 | 90 | 10.3786 | 7.6202
[7 empty] | 2947 | 91 | 11.0734 | 8.1447
[7 empty] | 2948 | 92 | 10.4633 | 7.6841
[7 empty] | 2949 | 93 | 8.0228 | 5.8417
[7 empty] | 2950 | 94 | 7.1076 | 5.1507
[7 empty] | 2951 | 95 | 5.2264 | 3.7305
[7 empty] | 2952 | 96 | 4.2265 | 2.9756
[7 empty] | 2953 | 97 | 4.1757 | 2.9372
[7 empty] | 2954 | 98 | 3.8791 | 2.7133
[7 empty] | 2955 | 99 | 3.8197 | 2.6685
[7 empty] | 2956 | 100 | 3.4638 | 2.3999
[7 empty] | 2957 | 101 | 3.4045 | 2.3551
[7 empty] | 2958 | 102 | 3.6418 | 2.5342
[7 empty] | 2959 | 103 | 4.396 | 3.1036
[7 empty] | 2960 | 104 | 4.6502 | 3.2955
[7 empty] | 2961 | 105 | 5.1417 | 3.6665
[7 empty] | 2962 | 106 | 6.6161 | 4.7797
[7 empty] | 2963 | 107 | 6.9721 | 5.0484
[7 empty] | 2964 | 108 | 8.5652 | 6.2511
[7 empty] | 2965 | 109 | 7.8957 | 5.7457
[7 empty] | 2966 | 110 | 7.4381 | 5.4002
[7 empty] | 2967 | 111 | 7.2771 | 5.2787
[7 empty] | 2968 | 112 | 7.3449 | 5.3299
[7 empty] | 2969 | 113 | 6.9975 | 5.0676
[7 empty] | 2970 | 114 | 7.167 | 5.1955
[7 empty] | 2971 | 115 | 6.7094 | 4.8501
[7 empty] | 2972 | 116 | 7.3958 | 5.3683
[7 empty] | 2973 | 117 | 6.9721 | 5.0484
[7 empty] | 2974 | 118 | 6.1924 | 4.4598
[7 empty] | 2975 | 119 | 4.5824 | 3.2443
[7 empty] | 2976 | 120 | 4.2615 | 3.0021
[7 empty] | 2977 | 121 | 3.5232 | 2.4446
[7 empty] | 2978 | 122 | 3.1079 | 2.1312
[7 empty] | 2979 | 123 | 3.0232 | 2.0672
[7 empty] | 2980 | 124 | 2.9893 | 2.0416
[7 empty] | 2981 | 125 | 2.9469 | 2.0096
[7 empty] | 2982 | 126 | 3.091 | 2.1184
[7 empty] | 2983 | 127 | 4.6163 | 3.2699
[7 empty] | 2984 | 128 | 6.1924 | 4.4598
[7 empty] | 2985 | 129 | 6.8788 | 4.978
[7 empty] | 2986 | 130 | 7.3195 | 5.3107
[7 empty] | 2987 | 131 | 7.4805 | 5.4322
[7 empty] | 2988 | 132 | 7.2263 | 5.2403
[7 empty] | 2989 | 133 | 7.8703 | 5.7265
[7 empty] | 2990 | 134 | 8.1754 | 5.9568
[7 empty] | 2991 | 135 | 8.2431 | 6.008
[7 empty] | 2992 | 136 | 7.4212 | 5.3875
[7 empty] | 2993 | 137 | 7.3195 | 5.3107
[7 empty] | 2994 | 138 | 7.2686 | 5.2723
[7 empty] | 2995 | 139 | 6.9297 | 5.0164
[7 empty] | 2996 | 140 | 6.9382 | 5.0228
[7 empty] | 2997 | 141 | 6.2772 | 4.5238
[7 empty] | 2998 | 142 | 5.6332 | 4.0376
[7 empty] | 2999 | 143 | 4.7434 | 3.3659
[7 empty] | 3000 | 144 | 4.1248 | 2.8989
[7 empty] | 3001 | 145 | 3.6503 | 2.5406
[7 empty] | 3002 | 146 | 3.4384 | 2.3807
[7 empty] | 3003 | 147 | 3.3706 | 2.3295
[7 empty] | 3004 | 148 | 3.3622 | 2.3231
[7 empty] | 3005 | 149 | 3.3622 | 2.3231
[7 empty] | 3006 | 150 | 3.3706 | 2.3295
[7 empty] | 3007 | 151 | 4.4638 | 3.1547
[7 empty] | 3008 | 152 | 6.006 | 4.3191
[7 empty] | 3009 | 153 | 6.6246 | 4.7861
[7 empty] | 3010 | 154 | 7.1924 | 5.2147
[7 empty] | 3011 | 155 | 7.0398 | 5.0996
[7 empty] | 3012 | 156 | 7.2093 | 5.2275
[7 empty] | 3013 | 157 | 7.9296 | 5.7713
[7 empty] | 3014 | 158 | 8.2601 | 6.0208
[7 empty] | 3015 | 159 | 8.5313 | 6.2255
[7 empty] | 3016 | 160 | 8.4041 | 6.1296
[7 empty] | 3017 | 161 | 9.1753 | 6.7117
[7 empty] | 3018 | 162 | 8.6753 | 6.3343
[7 empty] | 3019 | 163 | 9.0397 | 6.6094
[7 empty] | 3020 | 164 | 7.6754 | 5.5794
[7 empty] | 3021 | 165 | 10.8362 | 7.9656
[7 empty] | 3022 | 166 | 8.7685 | 6.4046
[7 empty] | 3023 | 167 | 5.1247 | 3.6537
[7 empty] | 3024 | 168 | 4.4722 | 3.1611
[7 empty] | 3025 | 1 | 2.9978 | 2.048
[7 empty] | 3026 | 2 | 2.8876 | 1.9648
[7 empty] | 3027 | 3 | 2.8791 | 1.9584
[7 empty] | 3028 | 4 | 3.0147 | 2.0608
[7 empty] | 3029 | 5 | 3.0317 | 2.0736
[7 empty] | 3030 | 6 | 3.4638 | 2.3999
[7 empty] | 3031 | 7 | 4.1926 | 2.95
[7 empty] | 3032 | 8 | 4.8705 | 3.4618
[7 empty] | 3033 | 9 | 4.8451 | 3.4426
[7 empty] | 3034 | 10 | 6.3789 | 4.6006
[7 empty] | 3035 | 11 | 8.4804 | 6.1871
[7 empty] | 3036 | 12 | 9.4549 | 6.9228
[7 empty] | 3037 | 13 | 9.8362 | 7.2107
[7 empty] | 3038 | 14 | 9.6159 | 7.0444
[7 empty] | 3039 | 15 | 9.5227 | 6.974
[7 empty] | 3040 | 16 | 10.7175 | 7.8761
[7 empty] | 3041 | 17 | 12.0564 | 8.8868
[7 empty] | 3042 | 18 | 11.8107 | 8.7013
[7 empty] | 3043 | 19 | 12.3445 | 9.1044
[7 empty] | 3044 | 20 | 12.2767 | 9.0532
[7 empty] | 3045 | 21 | 12.853 | 9.4882
[7 empty] | 3046 | 22 | 8.8533 | 6.4686
[7 empty] | 3047 | 23 | 5.04 | 3.5898
[7 empty] | 3048 | 24 | 3.3504 | 2.3142
[7 empty] | 3049 | 25 | 3.252 | 2.2399
[7 empty] | 3050 | 26 | 3.1418 | 2.1567
[7 empty] | 3051 | 27 | 3.0401 | 2.08
[7 empty] | 3052 | 28 | 3.1249 | 2.144
[7 empty] | 3053 | 29 | 3.3706 | 2.3295
[7 empty] | 3054 | 30 | 3.6164 | 2.515
[7 empty] | 3055 | 31 | 4.4722 | 3.1611
[7 empty] | 3056 | 32 | 4.8281 | 3.4298
[7 empty] | 3057 | 33 | 5.4976 | 3.9352
[7 empty] | 3058 | 34 | 6.4043 | 4.6198
[7 empty] | 3059 | 35 | 8.5991 | 6.2767
[7 empty] | 3060 | 36 | 9.6413 | 7.0636
[7 empty] | 3061 | 37 | 9.7176 | 7.1212
[7 empty] | 3062 | 38 | 9.7939 | 7.1787
[7 empty] | 3063 | 39 | 9.4634 | 6.9292
[7 empty] | 3064 | 40 | 10.5311 | 7.7353
[7 empty] | 3065 | 41 | 11.0904 | 8.1575
[7 empty] | 3066 | 42 | 11.1073 | 8.1703
[7 empty] | 3067 | 43 | 11.4802 | 8.4518
[7 empty] | 3068 | 44 | 12.6496 | 9.3347
[7 empty] | 3069 | 45 | 12.2428 | 9.0276
[7 empty] | 3070 | 46 | 9.4634 | 6.9292
[7 empty] | 3071 | 47 | 5.8196 | 4.1783
[7 empty] | 3072 | 48 | 4.3028 | 3.0332
[7 empty] | 3073 | 49 | 3.6333 | 2.5278
[7 empty] | 3074 | 50 | 3.3198 | 2.2911
[7 empty] | 3075 | 51 | 3.2096 | 2.2079
[7 empty] | 3076 | 52 | 3.2435 | 2.2335
[7 empty] | 3077 | 53 | 3.2689 | 2.2527
[7 empty] | 3078 | 54 | 3.8536 | 2.6941
[7 empty] | 3079 | 55 | 5.0061 | 3.5642
[7 empty] | 3080 | 56 | 5.2518 | 3.7497
[7 empty] | 3081 | 57 | 6.2094 | 4.4726
[7 empty] | 3082 | 58 | 7.328 | 5.3171
[7 empty] | 3083 | 59 | 8.5482 | 6.2383
[7 empty] | 3084 | 60 | 9.1838 | 6.7181
[7 empty] | 3085 | 61 | 9.8701 | 7.2363
[7 empty] | 3086 | 62 | 9.6668 | 7.0828
[7 empty] | 3087 | 63 | 10.2684 | 7.537
[7 empty] | 3088 | 64 | 11.226 | 8.2599
[7 empty] | 3089 | 65 | 11.853 | 8.7333
[7 empty] | 3090 | 66 | 11.7514 | 8.6565
[7 empty] | 3091 | 67 | 12.4971 | 9.2195
[7 empty] | 3092 | 68 | 12.7428 | 9.405
[7 empty] | 3093 | 69 | 12.2259 | 9.0148
[7 empty] | 3094 | 70 | 9.904 | 7.2619
[7 empty] | 3095 | 71 | 5.3366 | 3.8137
[7 empty] | 3096 | 72 | 4.2398 | 2.9857
[7 empty] | 3097 | 73 | 3.5147 | 2.4382
[7 empty] | 3098 | 74 | 3.2859 | 2.2655
[7 empty] | 3099 | 75 | 3.1842 | 2.1887
[7 empty] | 3100 | 76 | 3.1249 | 2.144
[7 empty] | 3101 | 77 | 3.3028 | 2.2783
[7 empty] | 3102 | 78 | 3.7096 | 2.5854
[7 empty] | 3103 | 79 | 4.8366 | 3.4362
[7 empty] | 3104 | 80 | 5.0146 | 3.5706
[7 empty] | 3105 | 81 | 6.2094 | 4.4726
[7 empty] | 3106 | 82 | 7.311 | 5.3043
[7 empty] | 3107 | 83 | 8.0567 | 5.8673
[7 empty] | 3108 | 84 | 9.3109 | 6.8141
[7 empty] | 3109 | 85 | 9.0058 | 6.5838
[7 empty] | 3110 | 86 | 8.4889 | 6.1935
[7 empty] | 3111 | 87 | 8.938 | 6.5326
[7 empty] | 3112 | 88 | 9.6075 | 7.038
[7 empty] | 3113 | 89 | 10.9718 | 8.068
[7 empty] | 3114 | 90 | 10.3786 | 7.6202
[7 empty] | 3115 | 91 | 11.0734 | 8.1447
[7 empty] | 3116 | 92 | 10.4633 | 7.6841
[7 empty] | 3117 | 93 | 8.0228 | 5.8417
[7 empty] | 3118 | 94 | 7.1076 | 5.1507
[7 empty] | 3119 | 95 | 5.2264 | 3.7305
[7 empty] | 3120 | 96 | 4.2265 | 2.9756
[7 empty] | 3121 | 97 | 4.1757 | 2.9372
[7 empty] | 3122 | 98 | 3.8791 | 2.7133
[7 empty] | 3123 | 99 | 3.8197 | 2.6685
[7 empty] | 3124 | 100 | 3.4638 | 2.3999
[7 empty] | 3125 | 101 | 3.4045 | 2.3551
[7 empty] | 3126 | 102 | 3.6418 | 2.5342
[7 empty] | 3127 | 103 | 4.396 | 3.1036
[7 empty] | 3128 | 104 | 4.6502 | 3.2955
[7 empty] | 3129 | 105 | 5.1417 | 3.6665
[7 empty] | 3130 | 106 | 6.6161 | 4.7797
[7 empty] | 3131 | 107 | 6.9721 | 5.0484
[7 empty] | 3132 | 108 | 8.5652 | 6.2511
[7 empty] | 3133 | 109 | 7.8957 | 5.7457
[7 empty] | 3134 | 110 | 7.4381 | 5.4002
[7 empty] | 3135 | 111 | 7.2771 | 5.2787
[7 empty] | 3136 | 112 | 7.3449 | 5.3299
[7 empty] | 3137 | 113 | 6.9975 | 5.0676
[7 empty] | 3138 | 114 | 7.167 | 5.1955
[7 empty] | 3139 | 115 | 6.7094 | 4.8501
[7 empty] | 3140 | 116 | 7.3958 | 5.3683
[7 empty] | 3141 | 117 | 6.9721 | 5.0484
[7 empty] | 3142 | 118 | 6.1924 | 4.4598
[7 empty] | 3143 | 119 | 4.5824 | 3.2443
[7 empty] | 3144 | 120 | 4.2615 | 3.0021
[7 empty] | 3145 | 121 | 3.5232 | 2.4446
[7 empty] | 3146 | 122 | 3.1079 | 2.1312
[7 empty] | 3147 | 123 | 3.0232 | 2.0672
[7 empty] | 3148 | 124 | 2.9893 | 2.0416
[7 empty] | 3149 | 125 | 2.9469 | 2.0096
[7 empty] | 3150 | 126 | 3.091 | 2.1184
[7 empty] | 3151 | 127 | 4.6163 | 3.2699
[7 empty] | 3152 | 128 | 6.1924 | 4.4598
[7 empty] | 3153 | 129 | 6.8788 | 4.978
[7 empty] | 3154 | 130 | 7.3195 | 5.3107
[7 empty] | 3155 | 131 | 7.4805 | 5.4322
[7 empty] | 3156 | 132 | 7.2263 | 5.2403
[7 empty] | 3157 | 133 | 7.8703 | 5.7265
[7 empty] | 3158 | 134 | 8.1754 | 5.9568
[7 empty] | 3159 | 135 | 8.2431 | 6.008
[7 empty] | 3160 | 136 | 7.4212 | 5.3875
[7 empty] | 3161 | 137 | 7.3195 | 5.3107
[7 empty] | 3162 | 138 | 7.2686 | 5.2723
[7 empty] | 3163 | 139 | 6.9297 | 5.0164
[7 empty] | 3164 | 140 | 6.9382 | 5.0228
[7 empty] | 3165 | 141 | 6.2772 | 4.5238
[7 empty] | 3166 | 142 | 5.6332 | 4.0376
[7 empty] | 3167 | 143 | 4.7434 | 3.3659
[7 empty] | 3168 | 144 | 4.1248 | 2.8989
[7 empty] | 3169 | 145 | 3.6503 | 2.5406
[7 empty] | 3170 | 146 | 3.4384 | 2.3807
[7 empty] | 3171 | 147 | 3.3706 | 2.3295
[7 empty] | 3172 | 148 | 3.3622 | 2.3231
[7 empty] | 3173 | 149 | 3.3622 | 2.3231
[7 empty] | 3174 | 150 | 3.3706 | 2.3295
[7 empty] | 3175 | 151 | 4.4638 | 3.1547
[7 empty] | 3176 | 152 | 6.006 | 4.3191
[7 empty] | 3177 | 153 | 6.6246 | 4.7861
[7 empty] | 3178 | 154 | 7.1924 | 5.2147
[7 empty] | 3179 | 155 | 7.0398 | 5.0996
[7 empty] | 3180 | 156 | 7.2093 | 5.2275
[7 empty] | 3181 | 157 | 7.9296 | 5.7713
[7 empty] | 3182 | 158 | 8.2601 | 6.0208
[7 empty] | 3183 | 159 | 8.5313 | 6.2255
[7 empty] | 3184 | 160 | 8.4041 | 6.1296
[7 empty] | 3185 | 161 | 9.1753 | 6.7117
[7 empty] | 3186 | 162 | 8.6753 | 6.3343
[7 empty] | 3187 | 163 | 9.0397 | 6.6094
[7 empty] | 3188 | 164 | 7.6754 | 5.5794
[7 empty] | 3189 | 165 | 10.8362 | 7.9656
[7 empty] | 3190 | 166 | 8.7685 | 6.4046
[7 empty] | 3191 | 167 | 5.1247 | 3.6537
[7 empty] | 3192 | 168 | 4.4722 | 3.1611
[7 empty] | 3193 | 1 | 2.9978 | 2.048
[7 empty] | 3194 | 2 | 2.8876 | 1.9648
[7 empty] | 3195 | 3 | 2.8791 | 1.9584
[7 empty] | 3196 | 4 | 3.0147 | 2.0608
[7 empty] | 3197 | 5 | 3.0317 | 2.0736
[7 empty] | 3198 | 6 | 3.4638 | 2.3999
[7 empty] | 3199 | 7 | 4.1926 | 2.95
[7 empty] | 3200 | 8 | 4.8705 | 3.4618
[7 empty] | 3201 | 9 | 4.8451 | 3.4426
[7 empty] | 3202 | 10 | 6.3789 | 4.6006
[7 empty] | 3203 | 11 | 8.4804 | 6.1871
[7 empty] | 3204 | 12 | 9.4549 | 6.9228
[7 empty] | 3205 | 13 | 9.8362 | 7.2107
[7 empty] | 3206 | 14 | 9.6159 | 7.0444
[7 empty] | 3207 | 15 | 9.5227 | 6.974
[7 empty] | 3208 | 16 | 10.7175 | 7.8761
[7 empty] | 3209 | 17 | 12.0564 | 8.8868
[7 empty] | 3210 | 18 | 11.8107 | 8.7013
[7 empty] | 3211 | 19 | 12.3445 | 9.1044
[7 empty] | 3212 | 20 | 12.2767 | 9.0532
[7 empty] | 3213 | 21 | 12.853 | 9.4882
[7 empty] | 3214 | 22 | 8.8533 | 6.4686
[7 empty] | 3215 | 23 | 5.04 | 3.5898
[7 empty] | 3216 | 24 | 3.3504 | 2.3142
[7 empty] | 3217 | 25 | 3.252 | 2.2399
[7 empty] | 3218 | 26 | 3.1418 | 2.1567
[7 empty] | 3219 | 27 | 3.0401 | 2.08
[7 empty] | 3220 | 28 | 3.1249 | 2.144
[7 empty] | 3221 | 29 | 3.3706 | 2.3295
[7 empty] | 3222 | 30 | 3.6164 | 2.515
[7 empty] | 3223 | 31 | 4.4722 | 3.1611
[7 empty] | 3224 | 32 | 4.8281 | 3.4298
[7 empty] | 3225 | 33 | 5.4976 | 3.9352
[7 empty] | 3226 | 34 | 6.4043 | 4.6198
[7 empty] | 3227 | 35 | 8.5991 | 6.2767
[7 empty] | 3228 | 36 | 9.6413 | 7.0636
[7 empty] | 3229 | 37 | 9.7176 | 7.1212
[7 empty] | 3230 | 38 | 9.7939 | 7.1787
[7 empty] | 3231 | 39 | 9.4634 | 6.9292
[7 empty] | 3232 | 40 | 10.5311 | 7.7353
[7 empty] | 3233 | 41 | 11.0904 | 8.1575
[7 empty] | 3234 | 42 | 11.1073 | 8.1703
[7 empty] | 3235 | 43 | 11.4802 | 8.4518
[7 empty] | 3236 | 44 | 12.6496 | 9.3347
[7 empty] | 3237 | 45 | 12.2428 | 9.0276
[7 empty] | 3238 | 46 | 9.4634 | 6.9292
[7 empty] | 3239 | 47 | 5.8196 | 4.1783
[7 empty] | 3240 | 48 | 4.3028 | 3.0332
[7 empty] | 3241 | 49 | 3.6333 | 2.5278
[7 empty] | 3242 | 50 | 3.3198 | 2.2911
[7 empty] | 3243 | 51 | 3.2096 | 2.2079
[7 empty] | 3244 | 52 | 3.2435 | 2.2335
[7 empty] | 3245 | 53 | 3.2689 | 2.2527
[7 empty] | 3246 | 54 | 3.8536 | 2.6941
[7 empty] | 3247 | 55 | 5.0061 | 3.5642
[7 empty] | 3248 | 56 | 5.2518 | 3.7497
[7 empty] | 3249 | 57 | 6.2094 | 4.4726
[7 empty] | 3250 | 58 | 7.328 | 5.3171
[7 empty] | 3251 | 59 | 8.5482 | 6.2383
[7 empty] | 3252 | 60 | 9.1838 | 6.7181
[7 empty] | 3253 | 61 | 9.8701 | 7.2363
[7 empty] | 3254 | 62 | 9.6668 | 7.0828
[7 empty] | 3255 | 63 | 10.2684 | 7.537
[7 empty] | 3256 | 64 | 11.226 | 8.2599
[7 empty] | 3257 | 65 | 11.853 | 8.7333
[7 empty] | 3258 | 66 | 11.7514 | 8.6565
[7 empty] | 3259 | 67 | 12.4971 | 9.2195
[7 empty] | 3260 | 68 | 12.7428 | 9.405
[7 empty] | 3261 | 69 | 12.2259 | 9.0148
[7 empty] | 3262 | 70 | 9.904 | 7.2619
[7 empty] | 3263 | 71 | 5.3366 | 3.8137
[7 empty] | 3264 | 72 | 4.2398 | 2.9857
[7 empty] | 3265 | 73 | 3.5147 | 2.4382
[7 empty] | 3266 | 74 | 3.2859 | 2.2655
[7 empty] | 3267 | 75 | 3.1842 | 2.1887
[7 empty] | 3268 | 76 | 3.1249 | 2.144
[7 empty] | 3269 | 77 | 3.3028 | 2.2783
[7 empty] | 3270 | 78 | 3.7096 | 2.5854
[7 empty] | 3271 | 79 | 4.8366 | 3.4362
[7 empty] | 3272 | 80 | 5.0146 | 3.5706
[7 empty] | 3273 | 81 | 6.2094 | 4.4726
[7 empty] | 3274 | 82 | 7.311 | 5.3043
[7 empty] | 3275 | 83 | 8.0567 | 5.8673
[7 empty] | 3276 | 84 | 9.3109 | 6.8141
[7 empty] | 3277 | 85 | 9.0058 | 6.5838
[7 empty] | 3278 | 86 | 8.4889 | 6.1935
[7 empty] | 3279 | 87 | 8.938 | 6.5326
[7 empty] | 3280 | 88 | 9.6075 | 7.038
[7 empty] | 3281 | 89 | 10.9718 | 8.068
[7 empty] | 3282 | 90 | 10.3786 | 7.6202
[7 empty] | 3283 | 91 | 11.0734 | 8.1447
[7 empty] | 3284 | 92 | 10.4633 | 7.6841
[7 empty] | 3285 | 93 | 8.0228 | 5.8417
[7 empty] | 3286 | 94 | 7.1076 | 5.1507
[7 empty] | 3287 | 95 | 5.2264 | 3.7305
[7 empty] | 3288 | 96 | 4.2265 | 2.9756
[7 empty] | 3289 | 97 | 4.1757 | 2.9372
[7 empty] | 3290 | 98 | 3.8791 | 2.7133
[7 empty] | 3291 | 99 | 3.8197 | 2.6685
[7 empty] | 3292 | 100 | 3.4638 | 2.3999
[7 empty] | 3293 | 101 | 3.4045 | 2.3551
[7 empty] | 3294 | 102 | 3.6418 | 2.5342
[7 empty] | 3295 | 103 | 4.396 | 3.1036
[7 empty] | 3296 | 104 | 4.6502 | 3.2955
[7 empty] | 3297 | 105 | 5.1417 | 3.6665
[7 empty] | 3298 | 106 | 6.6161 | 4.7797
[7 empty] | 3299 | 107 | 6.9721 | 5.0484
[7 empty] | 3300 | 108 | 8.5652 | 6.2511
[7 empty] | 3301 | 109 | 7.8957 | 5.7457
[7 empty] | 3302 | 110 | 7.4381 | 5.4002
[7 empty] | 3303 | 111 | 7.2771 | 5.2787
[7 empty] | 3304 | 112 | 7.3449 | 5.3299
[7 empty] | 3305 | 113 | 6.9975 | 5.0676
[7 empty] | 3306 | 114 | 7.167 | 5.1955
[7 empty] | 3307 | 115 | 6.7094 | 4.8501
[7 empty] | 3308 | 116 | 7.3958 | 5.3683
[7 empty] | 3309 | 117 | 6.9721 | 5.0484
[7 empty] | 3310 | 118 | 6.1924 | 4.4598
[7 empty] | 3311 | 119 | 4.5824 | 3.2443
[7 empty] | 3312 | 120 | 4.2615 | 3.0021
[7 empty] | 3313 | 121 | 3.5232 | 2.4446
[7 empty] | 3314 | 122 | 3.1079 | 2.1312
[7 empty] | 3315 | 123 | 3.0232 | 2.0672
[7 empty] | 3316 | 124 | 2.9893 | 2.0416
[7 empty] | 3317 | 125 | 2.9469 | 2.0096
[7 empty] | 3318 | 126 | 3.091 | 2.1184
[7 empty] | 3319 | 127 | 4.6163 | 3.2699
[7 empty] | 3320 | 128 | 6.1924 | 4.4598
[7 empty] | 3321 | 129 | 6.8788 | 4.978
[7 empty] | 3322 | 130 | 7.3195 | 5.3107
[7 empty] | 3323 | 131 | 7.4805 | 5.4322
[7 empty] | 3324 | 132 | 7.2263 | 5.2403
[7 empty] | 3325 | 133 | 7.8703 | 5.7265
[7 empty] | 3326 | 134 | 8.1754 | 5.9568
[7 empty] | 3327 | 135 | 8.2431 | 6.008
[7 empty] | 3328 | 136 | 7.4212 | 5.3875
[7 empty] | 3329 | 137 | 7.3195 | 5.3107
[7 empty] | 3330 | 138 | 7.2686 | 5.2723
[7 empty] | 3331 | 139 | 6.9297 | 5.0164
[7 empty] | 3332 | 140 | 6.9382 | 5.0228
[7 empty] | 3333 | 141 | 6.2772 | 4.5238
[7 empty] | 3334 | 142 | 5.6332 | 4.0376
[7 empty] | 3335 | 143 | 4.7434 | 3.3659
[7 empty] | 3336 | 144 | 4.1248 | 2.8989
[7 empty] | 3337 | 145 | 3.6503 | 2.5406
[7 empty] | 3338 | 146 | 3.4384 | 2.3807
[7 empty] | 3339 | 147 | 3.3706 | 2.3295
[7 empty] | 3340 | 148 | 3.3622 | 2.3231
[7 empty] | 3341 | 149 | 3.3622 | 2.3231
[7 empty] | 3342 | 150 | 3.3706 | 2.3295
[7 empty] | 3343 | 151 | 4.4638 | 3.1547
[7 empty] | 3344 | 152 | 6.006 | 4.3191
[7 empty] | 3345 | 153 | 6.6246 | 4.7861
[7 empty] | 3346 | 154 | 7.1924 | 5.2147
[7 empty] | 3347 | 155 | 7.0398 | 5.0996
[7 empty] | 3348 | 156 | 7.2093 | 5.2275
[7 empty] | 3349 | 157 | 7.9296 | 5.7713
[7 empty] | 3350 | 158 | 8.2601 | 6.0208
[7 empty] | 3351 | 159 | 8.5313 | 6.2255
[7 empty] | 3352 | 160 | 8.4041 | 6.1296
[7 empty] | 3353 | 161 | 9.1753 | 6.7117
[7 empty] | 3354 | 162 | 8.6753 | 6.3343
[7 empty] | 3355 | 163 | 9.0397 | 6.6094
[7 empty] | 3356 | 164 | 7.6754 | 5.5794
[7 empty] | 3357 | 165 | 10.8362 | 7.9656
[7 empty] | 3358 | 166 | 8.7685 | 6.4046
[7 empty] | 3359 | 167 | 5.1247 | 3.6537
[7 empty] | 3360 | 168 | 4.4722 | 3.1611
[7 empty] | 3361 | 1 | 2.9978 | 2.048
[7 empty] | 3362 | 2 | 2.8876 | 1.9648
[7 empty] | 3363 | 3 | 2.8791 | 1.9584
[7 empty] | 3364 | 4 | 3.0147 | 2.0608
[7 empty] | 3365 | 5 | 3.0317 | 2.0736
[7 empty] | 3366 | 6 | 3.4638 | 2.3999
[7 empty] | 3367 | 7 | 4.1926 | 2.95
[7 empty] | 3368 | 8 | 4.8705 | 3.4618
[7 empty] | 3369 | 9 | 4.8451 | 3.4426
[7 empty] | 3370 | 10 | 6.3789 | 4.6006
[7 empty] | 3371 | 11 | 8.4804 | 6.1871
[7 empty] | 3372 | 12 | 9.4549 | 6.9228
[7 empty] | 3373 | 13 | 9.8362 | 7.2107
[7 empty] | 3374 | 14 | 9.6159 | 7.0444
[7 empty] | 3375 | 15 | 9.5227 | 6.974
[7 empty] | 3376 | 16 | 10.7175 | 7.8761
[7 empty] | 3377 | 17 | 12.0564 | 8.8868
[7 empty] | 3378 | 18 | 11.8107 | 8.7013
[7 empty] | 3379 | 19 | 12.3445 | 9.1044
[7 empty] | 3380 | 20 | 12.2767 | 9.0532
[7 empty] | 3381 | 21 | 12.853 | 9.4882
[7 empty] | 3382 | 22 | 8.8533 | 6.4686
[7 empty] | 3383 | 23 | 5.04 | 3.5898
[7 empty] | 3384 | 24 | 3.3504 | 2.3142
[7 empty] | 3385 | 25 | 3.252 | 2.2399
[7 empty] | 3386 | 26 | 3.1418 | 2.1567
[7 empty] | 3387 | 27 | 3.0401 | 2.08
[7 empty] | 3388 | 28 | 3.1249 | 2.144
[7 empty] | 3389 | 29 | 3.3706 | 2.3295
[7 empty] | 3390 | 30 | 3.6164 | 2.515
[7 empty] | 3391 | 31 | 4.4722 | 3.1611
[7 empty] | 3392 | 32 | 4.8281 | 3.4298
[7 empty] | 3393 | 33 | 5.4976 | 3.9352
[7 empty] | 3394 | 34 | 6.4043 | 4.6198
[7 empty] | 3395 | 35 | 8.5991 | 6.2767
[7 empty] | 3396 | 36 | 9.6413 | 7.0636
[7 empty] | 3397 | 37 | 9.7176 | 7.1212
[7 empty] | 3398 | 38 | 9.7939 | 7.1787
[7 empty] | 3399 | 39 | 9.4634 | 6.9292
[7 empty] | 3400 | 40 | 10.5311 | 7.7353
[7 empty] | 3401 | 41 | 11.0904 | 8.1575
[7 empty] | 3402 | 42 | 11.1073 | 8.1703
[7 empty] | 3403 | 43 | 11.4802 | 8.4518
[7 empty] | 3404 | 44 | 12.6496 | 9.3347
[7 empty] | 3405 | 45 | 12.2428 | 9.0276
[7 empty] | 3406 | 46 | 9.4634 | 6.9292
[7 empty] | 3407 | 47 | 5.8196 | 4.1783
[7 empty] | 3408 | 48 | 4.3028 | 3.0332
[7 empty] | 3409 | 49 | 3.6333 | 2.5278
[7 empty] | 3410 | 50 | 3.3198 | 2.2911
[7 empty] | 3411 | 51 | 3.2096 | 2.2079
[7 empty] | 3412 | 52 | 3.2435 | 2.2335
[7 empty] | 3413 | 53 | 3.2689 | 2.2527
[7 empty] | 3414 | 54 | 3.8536 | 2.6941
[7 empty] | 3415 | 55 | 5.0061 | 3.5642
[7 empty] | 3416 | 56 | 5.2518 | 3.7497
[7 empty] | 3417 | 57 | 6.2094 | 4.4726
[7 empty] | 3418 | 58 | 7.328 | 5.3171
[7 empty] | 3419 | 59 | 8.5482 | 6.2383
[7 empty] | 3420 | 60 | 9.1838 | 6.7181
[7 empty] | 3421 | 61 | 9.8701 | 7.2363
[7 empty] | 3422 | 62 | 9.6668 | 7.0828
[7 empty] | 3423 | 63 | 10.2684 | 7.537
[7 empty] | 3424 | 64 | 11.226 | 8.2599
[7 empty] | 3425 | 65 | 11.853 | 8.7333
[7 empty] | 3426 | 66 | 11.7514 | 8.6565
[7 empty] | 3427 | 67 | 12.4971 | 9.2195
[7 empty] | 3428 | 68 | 12.7428 | 9.405
[7 empty] | 3429 | 69 | 12.2259 | 9.0148
[7 empty] | 3430 | 70 | 9.904 | 7.2619
[7 empty] | 3431 | 71 | 5.3366 | 3.8137
[7 empty] | 3432 | 72 | 4.2398 | 2.9857
[7 empty] | 3433 | 73 | 3.5147 | 2.4382
[7 empty] | 3434 | 74 | 3.2859 | 2.2655
[7 empty] | 3435 | 75 | 3.1842 | 2.1887
[7 empty] | 3436 | 76 | 3.1249 | 2.144
[7 empty] | 3437 | 77 | 3.3028 | 2.2783
[7 empty] | 3438 | 78 | 3.7096 | 2.5854
[7 empty] | 3439 | 79 | 4.8366 | 3.4362
[7 empty] | 3440 | 80 | 5.0146 | 3.5706
[7 empty] | 3441 | 81 | 6.2094 | 4.4726
[7 empty] | 3442 | 82 | 7.311 | 5.3043
[7 empty] | 3443 | 83 | 8.0567 | 5.8673
[7 empty] | 3444 | 84 | 9.3109 | 6.8141
[7 empty] | 3445 | 85 | 9.0058 | 6.5838
[7 empty] | 3446 | 86 | 8.4889 | 6.1935
[7 empty] | 3447 | 87 | 8.938 | 6.5326
[7 empty] | 3448 | 88 | 9.6075 | 7.038
[7 empty] | 3449 | 89 | 10.9718 | 8.068
[7 empty] | 3450 | 90 | 10.3786 | 7.6202
[7 empty] | 3451 | 91 | 11.0734 | 8.1447
[7 empty] | 3452 | 92 | 10.4633 | 7.6841
[7 empty] | 3453 | 93 | 8.0228 | 5.8417
[7 empty] | 3454 | 94 | 7.1076 | 5.1507
[7 empty] | 3455 | 95 | 5.2264 | 3.7305
[7 empty] | 3456 | 96 | 4.2265 | 2.9756
[7 empty] | 3457 | 97 | 4.1757 | 2.9372
[7 empty] | 3458 | 98 | 3.8791 | 2.7133
[7 empty] | 3459 | 99 | 3.8197 | 2.6685
[7 empty] | 3460 | 100 | 3.4638 | 2.3999
[7 empty] | 3461 | 101 | 3.4045 | 2.3551
[7 empty] | 3462 | 102 | 3.6418 | 2.5342
[7 empty] | 3463 | 103 | 4.396 | 3.1036
[7 empty] | 3464 | 104 | 4.6502 | 3.2955
[7 empty] | 3465 | 105 | 5.1417 | 3.6665
[7 empty] | 3466 | 106 | 6.6161 | 4.7797
[7 empty] | 3467 | 107 | 6.9721 | 5.0484
[7 empty] | 3468 | 108 | 8.5652 | 6.2511
[7 empty] | 3469 | 109 | 7.8957 | 5.7457
[7 empty] | 3470 | 110 | 7.4381 | 5.4002
[7 empty] | 3471 | 111 | 7.2771 | 5.2787
[7 empty] | 3472 | 112 | 7.3449 | 5.3299
[7 empty] | 3473 | 113 | 6.9975 | 5.0676
[7 empty] | 3474 | 114 | 7.167 | 5.1955
[7 empty] | 3475 | 115 | 6.7094 | 4.8501
[7 empty] | 3476 | 116 | 7.3958 | 5.3683
[7 empty] | 3477 | 117 | 6.9721 | 5.0484
[7 empty] | 3478 | 118 | 6.1924 | 4.4598
[7 empty] | 3479 | 119 | 4.5824 | 3.2443
[7 empty] | 3480 | 120 | 4.2615 | 3.0021
[7 empty] | 3481 | 121 | 3.5232 | 2.4446
[7 empty] | 3482 | 122 | 3.1079 | 2.1312
[7 empty] | 3483 | 123 | 3.0232 | 2.0672
[7 empty] | 3484 | 124 | 2.9893 | 2.0416
[7 empty] | 3485 | 125 | 2.9469 | 2.0096
[7 empty] | 3486 | 126 | 3.091 | 2.1184
[7 empty] | 3487 | 127 | 4.6163 | 3.2699
[7 empty] | 3488 | 128 | 6.1924 | 4.4598
[7 empty] | 3489 | 129 | 6.8788 | 4.978
[7 empty] | 3490 | 130 | 7.3195 | 5.3107
[7 empty] | 3491 | 131 | 7.4805 | 5.4322
[7 empty] | 3492 | 132 | 7.2263 | 5.2403
[7 empty] | 3493 | 133 | 7.8703 | 5.7265
[7 empty] | 3494 | 134 | 8.1754 | 5.9568
[7 empty] | 3495 | 135 | 8.2431 | 6.008
[7 empty] | 3496 | 136 | 7.4212 | 5.3875
[7 empty] | 3497 | 137 | 7.3195 | 5.3107
[7 empty] | 3498 | 138 | 7.2686 | 5.2723
[7 empty] | 3499 | 139 | 6.9297 | 5.0164
[7 empty] | 3500 | 140 | 6.9382 | 5.0228
[7 empty] | 3501 | 141 | 6.2772 | 4.5238
[7 empty] | 3502 | 142 | 5.6332 | 4.0376
[7 empty] | 3503 | 143 | 4.7434 | 3.3659
[7 empty] | 3504 | 144 | 4.1248 | 2.8989
[7 empty] | 3505 | 145 | 3.6503 | 2.5406
[7 empty] | 3506 | 146 | 3.4384 | 2.3807
[7 empty] | 3507 | 147 | 3.3706 | 2.3295
[7 empty] | 3508 | 148 | 3.3622 | 2.3231
[7 empty] | 3509 | 149 | 3.3622 | 2.3231
[7 empty] | 3510 | 150 | 3.3706 | 2.3295
[7 empty] | 3511 | 151 | 4.4638 | 3.1547
[7 empty] | 3512 | 152 | 6.006 | 4.3191
[7 empty] | 3513 | 153 | 6.6246 | 4.7861
[7 empty] | 3514 | 154 | 7.1924 | 5.2147
[7 empty] | 3515 | 155 | 7.0398 | 5.0996
[7 empty] | 3516 | 156 | 7.2093 | 5.2275
[7 empty] | 3517 | 157 | 7.9296 | 5.7713
[7 empty] | 3518 | 158 | 8.2601 | 6.0208
[7 empty] | 3519 | 159 | 8.5313 | 6.2255
[7 empty] | 3520 | 160 | 8.4041 | 6.1296
[7 empty] | 3521 | 161 | 9.1753 | 6.7117
[7 empty] | 3522 | 162 | 8.6753 | 6.3343
[7 empty] | 3523 | 163 | 9.0397 | 6.6094
[7 empty] | 3524 | 164 | 7.6754 | 5.5794
[7 empty] | 3525 | 165 | 10.8362 | 7.9656
[7 empty] | 3526 | 166 | 8.7685 | 6.4046
[7 empty] | 3527 | 167 | 5.1247 | 3.6537
[7 empty] | 3528 | 168 | 4.4722 | 3.1611
[7 empty] | 3529 | 1 | 2.9978 | 2.048
[7 empty] | 3530 | 2 | 2.8876 | 1.9648
[7 empty] | 3531 | 3 | 2.8791 | 1.9584
[7 empty] | 3532 | 4 | 3.0147 | 2.0608
[7 empty] | 3533 | 5 | 3.0317 | 2.0736
[7 empty] | 3534 | 6 | 3.4638 | 2.3999
[7 empty] | 3535 | 7 | 4.1926 | 2.95
[7 empty] | 3536 | 8 | 4.8705 | 3.4618
[7 empty] | 3537 | 9 | 4.8451 | 3.4426
[7 empty] | 3538 | 10 | 6.3789 | 4.6006
[7 empty] | 3539 | 11 | 8.4804 | 6.1871
[7 empty] | 3540 | 12 | 9.4549 | 6.9228
[7 empty] | 3541 | 13 | 9.8362 | 7.2107
[7 empty] | 3542 | 14 | 9.6159 | 7.0444
[7 empty] | 3543 | 15 | 9.5227 | 6.974
[7 empty] | 3544 | 16 | 10.7175 | 7.8761
[7 empty] | 3545 | 17 | 12.0564 | 8.8868
[7 empty] | 3546 | 18 | 11.8107 | 8.7013
[7 empty] | 3547 | 19 | 12.3445 | 9.1044
[7 empty] | 3548 | 20 | 12.2767 | 9.0532
[7 empty] | 3549 | 21 | 12.853 | 9.4882
[7 empty] | 3550 | 22 | 8.8533 | 6.4686
[7 empty] | 3551 | 23 | 5.04 | 3.5898
[7 empty] | 3552 | 24 | 3.3504 | 2.3142
[7 empty] | 3553 | 25 | 3.252 | 2.2399
[7 empty] | 3554 | 26 | 3.1418 | 2.1567
[7 empty] | 3555 | 27 | 3.0401 | 2.08
[7 empty] | 3556 | 28 | 3.1249 | 2.144
[7 empty] | 3557 | 29 | 3.3706 | 2.3295
[7 empty] | 3558 | 30 | 3.6164 | 2.515
[7 empty] | 3559 | 31 | 4.4722 | 3.1611
[7 empty] | 3560 | 32 | 4.8281 | 3.4298
[7 empty] | 3561 | 33 | 5.4976 | 3.9352
[7 empty] | 3562 | 34 | 6.4043 | 4.6198
[7 empty] | 3563 | 35 | 8.5991 | 6.2767
[7 empty] | 3564 | 36 | 9.6413 | 7.0636
[7 empty] | 3565 | 37 | 9.7176 | 7.1212
[7 empty] | 3566 | 38 | 9.7939 | 7.1787
[7 empty] | 3567 | 39 | 9.4634 | 6.9292
[7 empty] | 3568 | 40 | 10.5311 | 7.7353
[7 empty] | 3569 | 41 | 11.0904 | 8.1575
[7 empty] | 3570 | 42 | 11.1073 | 8.1703
[7 empty] | 3571 | 43 | 11.4802 | 8.4518
[7 empty] | 3572 | 44 | 12.6496 | 9.3347
[7 empty] | 3573 | 45 | 12.2428 | 9.0276
[7 empty] | 3574 | 46 | 9.4634 | 6.9292
[7 empty] | 3575 | 47 | 5.8196 | 4.1783
[7 empty] | 3576 | 48 | 4.3028 | 3.0332
[7 empty] | 3577 | 49 | 3.6333 | 2.5278
[7 empty] | 3578 | 50 | 3.3198 | 2.2911
[7 empty] | 3579 | 51 | 3.2096 | 2.2079
[7 empty] | 3580 | 52 | 3.2435 | 2.2335
[7 empty] | 3581 | 53 | 3.2689 | 2.2527
[7 empty] | 3582 | 54 | 3.8536 | 2.6941
[7 empty] | 3583 | 55 | 5.0061 | 3.5642
[7 empty] | 3584 | 56 | 5.2518 | 3.7497
[7 empty] | 3585 | 57 | 6.2094 | 4.4726
[7 empty] | 3586 | 58 | 7.328 | 5.3171
[7 empty] | 3587 | 59 | 8.5482 | 6.2383
[7 empty] | 3588 | 60 | 9.1838 | 6.7181
[7 empty] | 3589 | 61 | 9.8701 | 7.2363
[7 empty] | 3590 | 62 | 9.6668 | 7.0828
[7 empty] | 3591 | 63 | 10.2684 | 7.537
[7 empty] | 3592 | 64 | 11.226 | 8.2599
[7 empty] | 3593 | 65 | 11.853 | 8.7333
[7 empty] | 3594 | 66 | 11.7514 | 8.6565
[7 empty] | 3595 | 67 | 12.4971 | 9.2195
[7 empty] | 3596 | 68 | 12.7428 | 9.405
[7 empty] | 3597 | 69 | 12.2259 | 9.0148
[7 empty] | 3598 | 70 | 9.904 | 7.2619
[7 empty] | 3599 | 71 | 5.3366 | 3.8137
[7 empty] | 3600 | 72 | 4.2398 | 2.9857
[7 empty] | 3601 | 73 | 3.5147 | 2.4382
[7 empty] | 3602 | 74 | 3.2859 | 2.2655
[7 empty] | 3603 | 75 | 3.1842 | 2.1887
[7 empty] | 3604 | 76 | 3.1249 | 2.144
[7 empty] | 3605 | 77 | 3.3028 | 2.2783
[7 empty] | 3606 | 78 | 3.7096 | 2.5854
[7 empty] | 3607 | 79 | 4.8366 | 3.4362
[7 empty] | 3608 | 80 | 5.0146 | 3.5706
[7 empty] | 3609 | 81 | 6.2094 | 4.4726
[7 empty] | 3610 | 82 | 7.311 | 5.3043
[7 empty] | 3611 | 83 | 8.0567 | 5.8673
[7 empty] | 3612 | 84 | 9.3109 | 6.8141
[7 empty] | 3613 | 85 | 9.0058 | 6.5838
[7 empty] | 3614 | 86 | 8.4889 | 6.1935
[7 empty] | 3615 | 87 | 8.938 | 6.5326
[7 empty] | 3616 | 88 | 9.6075 | 7.038
[7 empty] | 3617 | 89 | 10.9718 | 8.068
[7 empty] | 3618 | 90 | 10.3786 | 7.6202
[7 empty] | 3619 | 91 | 11.0734 | 8.1447
[7 empty] | 3620 | 92 | 10.4633 | 7.6841
[7 empty] | 3621 | 93 | 8.0228 | 5.8417
[7 empty] | 3622 | 94 | 7.1076 | 5.1507
[7 empty] | 3623 | 95 | 5.2264 | 3.7305
[7 empty] | 3624 | 96 | 4.2265 | 2.9756
[7 empty] | 3625 | 97 | 4.1757 | 2.9372
[7 empty] | 3626 | 98 | 3.8791 | 2.7133
[7 empty] | 3627 | 99 | 3.8197 | 2.6685
[7 empty] | 3628 | 100 | 3.4638 | 2.3999
[7 empty] | 3629 | 101 | 3.4045 | 2.3551
[7 empty] | 3630 | 102 | 3.6418 | 2.5342
[7 empty] | 3631 | 103 | 4.396 | 3.1036
[7 empty] | 3632 | 104 | 4.6502 | 3.2955
[7 empty] | 3633 | 105 | 5.1417 | 3.6665
[7 empty] | 3634 | 106 | 6.6161 | 4.7797
[7 empty] | 3635 | 107 | 6.9721 | 5.0484
[7 empty] | 3636 | 108 | 8.5652 | 6.2511
[7 empty] | 3637 | 109 | 7.8957 | 5.7457
[7 empty] | 3638 | 110 | 7.4381 | 5.4002
[7 empty] | 3639 | 111 | 7.2771 | 5.2787
[7 empty] | 3640 | 112 | 7.3449 | 5.3299
[7 empty] | 3641 | 113 | 6.9975 | 5.0676
[7 empty] | 3642 | 114 | 7.167 | 5.1955
[7 empty] | 3643 | 115 | 6.7094 | 4.8501
[7 empty] | 3644 | 116 | 7.3958 | 5.3683
[7 empty] | 3645 | 117 | 6.9721 | 5.0484
[7 empty] | 3646 | 118 | 6.1924 | 4.4598
[7 empty] | 3647 | 119 | 4.5824 | 3.2443
[7 empty] | 3648 | 120 | 4.2615 | 3.0021
[7 empty] | 3649 | 121 | 3.5232 | 2.4446
[7 empty] | 3650 | 122 | 3.1079 | 2.1312
[7 empty] | 3651 | 123 | 3.0232 | 2.0672
[7 empty] | 3652 | 124 | 2.9893 | 2.0416
[7 empty] | 3653 | 125 | 2.9469 | 2.0096
[7 empty] | 3654 | 126 | 3.091 | 2.1184
[7 empty] | 3655 | 127 | 4.6163 | 3.2699
[7 empty] | 3656 | 128 | 6.1924 | 4.4598
[7 empty] | 3657 | 129 | 6.8788 | 4.978
[7 empty] | 3658 | 130 | 7.3195 | 5.3107
[7 empty] | 3659 | 131 | 7.4805 | 5.4322
[7 empty] | 3660 | 132 | 7.2263 | 5.2403
[7 empty] | 3661 | 133 | 7.8703 | 5.7265
[7 empty] | 3662 | 134 | 8.1754 | 5.9568
[7 empty] | 3663 | 135 | 8.2431 | 6.008
[7 empty] | 3664 | 136 | 7.4212 | 5.3875
[7 empty] | 3665 | 137 | 7.3195 | 5.3107
[7 empty] | 3666 | 138 | 7.2686 | 5.2723
[7 empty] | 3667 | 139 | 6.9297 | 5.0164
[7 empty] | 3668 | 140 | 6.9382 | 5.0228
[7 empty] | 3669 | 141 | 6.2772 | 4.5238
[7 empty] | 3670 | 142 | 5.6332 | 4.0376
[7 empty] | 3671 | 143 | 4.7434 | 3.3659
[7 empty] | 3672 | 144 | 4.1248 | 2.8989
[7 empty] | 3673 | 145 | 3.6503 | 2.5406
[7 empty] | 3674 | 146 | 3.4384 | 2.3807
[7 empty] | 3675 | 147 | 3.3706 | 2.3295
[7 empty] | 3676 | 148 | 3.3622 | 2.3231
[7 empty] | 3677 | 149 | 3.3622 | 2.3231
[7 empty] | 3678 | 150 | 3.3706 | 2.3295
[7 empty] | 3679 | 151 | 4.4638 | 3.1547
[7 empty] | 3680 | 152 | 6.006 | 4.3191
[7 empty] | 3681 | 153 | 6.6246 | 4.7861
[7 empty] | 3682 | 154 | 7.1924 | 5.2147
[7 empty] | 3683 | 155 | 7.0398 | 5.0996
[7 empty] | 3684 | 156 | 7.2093 | 5.2275
[7 empty] | 3685 | 157 | 7.9296 | 5.7713
[7 empty] | 3686 | 158 | 8.2601 | 6.0208
[7 empty] | 3687 | 159 | 8.5313 | 6.2255
[7 empty] | 3688 | 160 | 8.4041 | 6.1296
[7 empty] | 3689 | 161 | 9.1753 | 6.7117
[7 empty] | 3690 | 162 | 8.6753 | 6.3343
[7 empty] | 3691 | 163 | 9.0397 | 6.6094
[7 empty] | 3692 | 164 | 7.6754 | 5.5794
[7 empty] | 3693 | 165 | 10.8362 | 7.9656
[7 empty] | 3694 | 166 | 8.7685 | 6.4046
[7 empty] | 3695 | 167 | 5.1247 | 3.6537
[7 empty] | 3696 | 168 | 4.4722 | 3.1611
[7 empty] | 3697 | 1 | 2.9978 | 2.048
[7 empty] | 3698 | 2 | 2.8876 | 1.9648
[7 empty] | 3699 | 3 | 2.8791 | 1.9584
[7 empty] | 3700 | 4 | 3.0147 | 2.0608
[7 empty] | 3701 | 5 | 3.0317 | 2.0736
[7 empty] | 3702 | 6 | 3.4638 | 2.3999
[7 empty] | 3703 | 7 | 4.1926 | 2.95
[7 empty] | 3704 | 8 | 4.8705 | 3.4618
[7 empty] | 3705 | 9 | 4.8451 | 3.4426
[7 empty] | 3706 | 10 | 6.3789 | 4.6006
[7 empty] | 3707 | 11 | 8.4804 | 6.1871
[7 empty] | 3708 | 12 | 9.4549 | 6.9228
[7 empty] | 3709 | 13 | 9.8362 | 7.2107
[7 empty] | 3710 | 14 | 9.6159 | 7.0444
[7 empty] | 3711 | 15 | 9.5227 | 6.974
[7 empty] | 3712 | 16 | 10.7175 | 7.8761
[7 empty] | 3713 | 17 | 12.0564 | 8.8868
[7 empty] | 3714 | 18 | 11.8107 | 8.7013
[7 empty] | 3715 | 19 | 12.3445 | 9.1044
[7 empty] | 3716 | 20 | 12.2767 | 9.0532
[7 empty] | 3717 | 21 | 12.853 | 9.4882
[7 empty] | 3718 | 22 | 8.8533 | 6.4686
[7 empty] | 3719 | 23 | 5.04 | 3.5898
[7 empty] | 3720 | 24 | 3.3504 | 2.3142
[7 empty] | 3721 | 25 | 3.252 | 2.2399
[7 empty] | 3722 | 26 | 3.1418 | 2.1567
[7 empty] | 3723 | 27 | 3.0401 | 2.08
[7 empty] | 3724 | 28 | 3.1249 | 2.144
[7 empty] | 3725 | 29 | 3.3706 | 2.3295
[7 empty] | 3726 | 30 | 3.6164 | 2.515
[7 empty] | 3727 | 31 | 4.4722 | 3.1611
[7 empty] | 3728 | 32 | 4.8281 | 3.4298
[7 empty] | 3729 | 33 | 5.4976 | 3.9352
[7 empty] | 3730 | 34 | 6.4043 | 4.6198
[7 empty] | 3731 | 35 | 8.5991 | 6.2767
[7 empty] | 3732 | 36 | 9.6413 | 7.0636
[7 empty] | 3733 | 37 | 9.7176 | 7.1212
[7 empty] | 3734 | 38 | 9.7939 | 7.1787
[7 empty] | 3735 | 39 | 9.4634 | 6.9292
[7 empty] | 3736 | 40 | 10.5311 | 7.7353
[7 empty] | 3737 | 41 | 11.0904 | 8.1575
[7 empty] | 3738 | 42 | 11.1073 | 8.1703
[7 empty] | 3739 | 43 | 11.4802 | 8.4518
[7 empty] | 3740 | 44 | 12.6496 | 9.3347
[7 empty] | 3741 | 45 | 12.2428 | 9.0276
[7 empty] | 3742 | 46 | 9.4634 | 6.9292
[7 empty] | 3743 | 47 | 5.8196 | 4.1783
[7 empty] | 3744 | 48 | 4.3028 | 3.0332
[7 empty] | 3745 | 49 | 3.6333 | 2.5278
[7 empty] | 3746 | 50 | 3.3198 | 2.2911
[7 empty] | 3747 | 51 | 3.2096 | 2.2079
[7 empty] | 3748 | 52 | 3.2435 | 2.2335
[7 empty] | 3749 | 53 | 3.2689 | 2.2527
[7 empty] | 3750 | 54 | 3.8536 | 2.6941
[7 empty] | 3751 | 55 | 5.0061 | 3.5642
[7 empty] | 3752 | 56 | 5.2518 | 3.7497
[7 empty] | 3753 | 57 | 6.2094 | 4.4726
[7 empty] | 3754 | 58 | 7.328 | 5.3171
[7 empty] | 3755 | 59 | 8.5482 | 6.2383
[7 empty] | 3756 | 60 | 9.1838 | 6.7181
[7 empty] | 3757 | 61 | 9.8701 | 7.2363
[7 empty] | 3758 | 62 | 9.6668 | 7.0828
[7 empty] | 3759 | 63 | 10.2684 | 7.537
[7 empty] | 3760 | 64 | 11.226 | 8.2599
[7 empty] | 3761 | 65 | 11.853 | 8.7333
[7 empty] | 3762 | 66 | 11.7514 | 8.6565
[7 empty] | 3763 | 67 | 12.4971 | 9.2195
[7 empty] | 3764 | 68 | 12.7428 | 9.405
[7 empty] | 3765 | 69 | 12.2259 | 9.0148
[7 empty] | 3766 | 70 | 9.904 | 7.2619
[7 empty] | 3767 | 71 | 5.3366 | 3.8137
[7 empty] | 3768 | 72 | 4.2398 | 2.9857
[7 empty] | 3769 | 73 | 3.5147 | 2.4382
[7 empty] | 3770 | 74 | 3.2859 | 2.2655
[7 empty] | 3771 | 75 | 3.1842 | 2.1887
[7 empty] | 3772 | 76 | 3.1249 | 2.144
[7 empty] | 3773 | 77 | 3.3028 | 2.2783
[7 empty] | 3774 | 78 | 3.7096 | 2.5854
[7 empty] | 3775 | 79 | 4.8366 | 3.4362
[7 empty] | 3776 | 80 | 5.0146 | 3.5706
[7 empty] | 3777 | 81 | 6.2094 | 4.4726
[7 empty] | 3778 | 82 | 7.311 | 5.3043
[7 empty] | 3779 | 83 | 8.0567 | 5.8673
[7 empty] | 3780 | 84 | 9.3109 | 6.8141
[7 empty] | 3781 | 85 | 9.0058 | 6.5838
[7 empty] | 3782 | 86 | 8.4889 | 6.1935
[7 empty] | 3783 | 87 | 8.938 | 6.5326
[7 empty] | 3784 | 88 | 9.6075 | 7.038
[7 empty] | 3785 | 89 | 10.9718 | 8.068
[7 empty] | 3786 | 90 | 10.3786 | 7.6202
[7 empty] | 3787 | 91 | 11.0734 | 8.1447
[7 empty] | 3788 | 92 | 10.4633 | 7.6841
[7 empty] | 3789 | 93 | 8.0228 | 5.8417
[7 empty] | 3790 | 94 | 7.1076 | 5.1507
[7 empty] | 3791 | 95 | 5.2264 | 3.7305
[7 empty] | 3792 | 96 | 4.2265 | 2.9756
[7 empty] | 3793 | 97 | 4.1757 | 2.9372
[7 empty] | 3794 | 98 | 3.8791 | 2.7133
[7 empty] | 3795 | 99 | 3.8197 | 2.6685
[7 empty] | 3796 | 100 | 3.4638 | 2.3999
[7 empty] | 3797 | 101 | 3.4045 | 2.3551
[7 empty] | 3798 | 102 | 3.6418 | 2.5342
[7 empty] | 3799 | 103 | 4.396 | 3.1036
[7 empty] | 3800 | 104 | 4.6502 | 3.2955
[7 empty] | 3801 | 105 | 5.1417 | 3.6665
[7 empty] | 3802 | 106 | 6.6161 | 4.7797
[7 empty] | 3803 | 107 | 6.9721 | 5.0484
[7 empty] | 3804 | 108 | 8.5652 | 6.2511
[7 empty] | 3805 | 109 | 7.8957 | 5.7457
[7 empty] | 3806 | 110 | 7.4381 | 5.4002
[7 empty] | 3807 | 111 | 7.2771 | 5.2787
[7 empty] | 3808 | 112 | 7.3449 | 5.3299
[7 empty] | 3809 | 113 | 6.9975 | 5.0676
[7 empty] | 3810 | 114 | 7.167 | 5.1955
[7 empty] | 3811 | 115 | 6.7094 | 4.8501
[7 empty] | 3812 | 116 | 7.3958 | 5.3683
[7 empty] | 3813 | 117 | 6.9721 | 5.0484
[7 empty] | 3814 | 118 | 6.1924 | 4.4598
[7 empty] | 3815 | 119 | 4.5824 | 3.2443
[7 empty] | 3816 | 120 | 4.2615 | 3.0021
[7 empty] | 3817 | 121 | 3.5232 | 2.4446
[7 empty] | 3818 | 122 | 3.1079 | 2.1312
[7 empty] | 3819 | 123 | 3.0232 | 2.0672
[7 empty] | 3820 | 124 | 2.9893 | 2.0416
[7 empty] | 3821 | 125 | 2.9469 | 2.0096
[7 empty] | 3822 | 126 | 3.091 | 2.1184
[7 empty] | 3823 | 127 | 4.6163 | 3.2699
[7 empty] | 3824 | 128 | 6.1924 | 4.4598
[7 empty] | 3825 | 129 | 6.8788 | 4.978
[7 empty] | 3826 | 130 | 7.3195 | 5.3107
[7 empty] | 3827 | 131 | 7.4805 | 5.4322
[7 empty] | 3828 | 132 | 7.2263 | 5.2403
[7 empty] | 3829 | 133 | 7.8703 | 5.7265
[7 empty] | 3830 | 134 | 8.1754 | 5.9568
[7 empty] | 3831 | 135 | 8.2431 | 6.008
[7 empty] | 3832 | 136 | 7.4212 | 5.3875
[7 empty] | 3833 | 137 | 7.3195 | 5.3107
[7 empty] | 3834 | 138 | 7.2686 | 5.2723
[7 empty] | 3835 | 139 | 6.9297 | 5.0164
[7 empty] | 3836 | 140 | 6.9382 | 5.0228
[7 empty] | 3837 | 141 | 6.2772 | 4.5238
[7 empty] | 3838 | 142 | 5.6332 | 4.0376
[7 empty] | 3839 | 143 | 4.7434 | 3.3659
[7 empty] | 3840 | 144 | 4.1248 | 2.8989
[7 empty] | 3841 | 145 | 3.6503 | 2.5406
[7 empty] | 3842 | 146 | 3.4384 | 2.3807
[7 empty] | 3843 | 147 | 3.3706 | 2.3295
[7 empty] | 3844 | 148 | 3.3622 | 2.3231
[7 empty] | 3845 | 149 | 3.3622 | 2.3231
[7 empty] | 3846 | 150 | 3.3706 | 2.3295
[7 empty] | 3847 | 151 | 4.4638 | 3.1547
[7 empty] | 3848 | 152 | 6.006 | 4.3191
[7 empty] | 3849 | 153 | 6.6246 | 4.7861
[7 empty] | 3850 | 154 | 7.1924 | 5.2147
[7 empty] | 3851 | 155 | 7.0398 | 5.0996
[7 empty] | 3852 | 156 | 7.2093 | 5.2275
[7 empty] | 3853 | 157 | 7.9296 | 5.7713
[7 empty] | 3854 | 158 | 8.2601 | 6.0208
[7 empty] | 3855 | 159 | 8.5313 | 6.2255
[7 empty] | 3856 | 160 | 8.4041 | 6.1296
[7 empty] | 3857 | 161 | 9.1753 | 6.7117
[7 empty] | 3858 | 162 | 8.6753 | 6.3343
[7 empty] | 3859 | 163 | 9.0397 | 6.6094
[7 empty] | 3860 | 164 | 7.6754 | 5.5794
[7 empty] | 3861 | 165 | 10.8362 | 7.9656
[7 empty] | 3862 | 166 | 8.7685 | 6.4046
[7 empty] | 3863 | 167 | 5.1247 | 3.6537
[7 empty] | 3864 | 168 | 4.4722 | 3.1611
[7 empty] | 3865 | 1 | 2.9978 | 2.048
[7 empty] | 3866 | 2 | 2.8876 | 1.9648
[7 empty] | 3867 | 3 | 2.8791 | 1.9584
[7 empty] | 3868 | 4 | 3.0147 | 2.0608
[7 empty] | 3869 | 5 | 3.0317 | 2.0736
[7 empty] | 3870 | 6 | 3.4638 | 2.3999
[7 empty] | 3871 | 7 | 4.1926 | 2.95
[7 empty] | 3872 | 8 | 4.8705 | 3.4618
[7 empty] | 3873 | 9 | 4.8451 | 3.4426
[7 empty] | 3874 | 10 | 6.3789 | 4.6006
[7 empty] | 3875 | 11 | 8.4804 | 6.1871
[7 empty] | 3876 | 12 | 9.4549 | 6.9228
[7 empty] | 3877 | 13 | 9.8362 | 7.2107
[7 empty] | 3878 | 14 | 9.6159 | 7.0444
[7 empty] | 3879 | 15 | 9.5227 | 6.974
[7 empty] | 3880 | 16 | 10.7175 | 7.8761
[7 empty] | 3881 | 17 | 12.0564 | 8.8868
[7 empty] | 3882 | 18 | 11.8107 | 8.7013
[7 empty] | 3883 | 19 | 12.3445 | 9.1044
[7 empty] | 3884 | 20 | 12.2767 | 9.0532
[7 empty] | 3885 | 21 | 12.853 | 9.4882
[7 empty] | 3886 | 22 | 8.8533 | 6.4686
[7 empty] | 3887 | 23 | 5.04 | 3.5898
[7 empty] | 3888 | 24 | 3.3504 | 2.3142
[7 empty] | 3889 | 25 | 3.252 | 2.2399
[7 empty] | 3890 | 26 | 3.1418 | 2.1567
[7 empty] | 3891 | 27 | 3.0401 | 2.08
[7 empty] | 3892 | 28 | 3.1249 | 2.144
[7 empty] | 3893 | 29 | 3.3706 | 2.3295
[7 empty] | 3894 | 30 | 3.6164 | 2.515
[7 empty] | 3895 | 31 | 4.4722 | 3.1611
[7 empty] | 3896 | 32 | 4.8281 | 3.4298
[7 empty] | 3897 | 33 | 5.4976 | 3.9352
[7 empty] | 3898 | 34 | 6.4043 | 4.6198
[7 empty] | 3899 | 35 | 8.5991 | 6.2767
[7 empty] | 3900 | 36 | 9.6413 | 7.0636
[7 empty] | 3901 | 37 | 9.7176 | 7.1212
[7 empty] | 3902 | 38 | 9.7939 | 7.1787
[7 empty] | 3903 | 39 | 9.4634 | 6.9292
[7 empty] | 3904 | 40 | 10.5311 | 7.7353
[7 empty] | 3905 | 41 | 11.0904 | 8.1575
[7 empty] | 3906 | 42 | 11.1073 | 8.1703
[7 empty] | 3907 | 43 | 11.4802 | 8.4518
[7 empty] | 3908 | 44 | 12.6496 | 9.3347
[7 empty] | 3909 | 45 | 12.2428 | 9.0276
[7 empty] | 3910 | 46 | 9.4634 | 6.9292
[7 empty] | 3911 | 47 | 5.8196 | 4.1783
[7 empty] | 3912 | 48 | 4.3028 | 3.0332
[7 empty] | 3913 | 49 | 3.6333 | 2.5278
[7 empty] | 3914 | 50 | 3.3198 | 2.2911
[7 empty] | 3915 | 51 | 3.2096 | 2.2079
[7 empty] | 3916 | 52 | 3.2435 | 2.2335
[7 empty] | 3917 | 53 | 3.2689 | 2.2527
[7 empty] | 3918 | 54 | 3.8536 | 2.6941
[7 empty] | 3919 | 55 | 5.0061 | 3.5642
[7 empty] | 3920 | 56 | 5.2518 | 3.7497
[7 empty] | 3921 | 57 | 6.2094 | 4.4726
[7 empty] | 3922 | 58 | 7.328 | 5.3171
[7 empty] | 3923 | 59 | 8.5482 | 6.2383
[7 empty] | 3924 | 60 | 9.1838 | 6.7181
[7 empty] | 3925 | 61 | 9.8701 | 7.2363
[7 empty] | 3926 | 62 | 9.6668 | 7.0828
[7 empty] | 3927 | 63 | 10.2684 | 7.537
[7 empty] | 3928 | 64 | 11.226 | 8.2599
[7 empty] | 3929 | 65 | 11.853 | 8.7333
[7 empty] | 3930 | 66 | 11.7514 | 8.6565
[7 empty] | 3931 | 67 | 12.4971 | 9.2195
[7 empty] | 3932 | 68 | 12.7428 | 9.405
[7 empty] | 3933 | 69 | 12.2259 | 9.0148
[7 empty] | 3934 | 70 | 9.904 | 7.2619
[7 empty] | 3935 | 71 | 5.3366 | 3.8137
[7 empty] | 3936 | 72 | 4.2398 | 2.9857
[7 empty] | 3937 | 73 | 3.5147 | 2.4382
[7 empty] | 3938 | 74 | 3.2859 | 2.2655
[7 empty] | 3939 | 75 | 3.1842 | 2.1887
[7 empty] | 3940 | 76 | 3.1249 | 2.144
[7 empty] | 3941 | 77 | 3.3028 | 2.2783
[7 empty] | 3942 | 78 | 3.7096 | 2.5854
[7 empty] | 3943 | 79 | 4.8366 | 3.4362
[7 empty] | 3944 | 80 | 5.0146 | 3.5706
[7 empty] | 3945 | 81 | 6.2094 | 4.4726
[7 empty] | 3946 | 82 | 7.311 | 5.3043
[7 empty] | 3947 | 83 | 8.0567 | 5.8673
[7 empty] | 3948 | 84 | 9.3109 | 6.8141
[7 empty] | 3949 | 85 | 9.0058 | 6.5838
[7 empty] | 3950 | 86 | 8.4889 | 6.1935
[7 empty] | 3951 | 87 | 8.938 | 6.5326
[7 empty] | 3952 | 88 | 9.6075 | 7.038
[7 empty] | 3953 | 89 | 10.9718 | 8.068
[7 empty] | 3954 | 90 | 10.3786 | 7.6202
[7 empty] | 3955 | 91 | 11.0734 | 8.1447
[7 empty] | 3956 | 92 | 10.4633 | 7.6841
[7 empty] | 3957 | 93 | 8.0228 | 5.8417
[7 empty] | 3958 | 94 | 7.1076 | 5.1507
[7 empty] | 3959 | 95 | 5.2264 | 3.7305
[7 empty] | 3960 | 96 | 4.2265 | 2.9756
[7 empty] | 3961 | 97 | 4.1757 | 2.9372
[7 empty] | 3962 | 98 | 3.8791 | 2.7133
[7 empty] | 3963 | 99 | 3.8197 | 2.6685
[7 empty] | 3964 | 100 | 3.4638 | 2.3999
[7 empty] | 3965 | 101 | 3.4045 | 2.3551
[7 empty] | 3966 | 102 | 3.6418 | 2.5342
[7 empty] | 3967 | 103 | 4.396 | 3.1036
[7 empty] | 3968 | 104 | 4.6502 | 3.2955
[7 empty] | 3969 | 105 | 5.1417 | 3.6665
[7 empty] | 3970 | 106 | 6.6161 | 4.7797
[7 empty] | 3971 | 107 | 6.9721 | 5.0484
[7 empty] | 3972 | 108 | 8.5652 | 6.2511
[7 empty] | 3973 | 109 | 7.8957 | 5.7457
[7 empty] | 3974 | 110 | 7.4381 | 5.4002
[7 empty] | 3975 | 111 | 7.2771 | 5.2787
[7 empty] | 3976 | 112 | 7.3449 | 5.3299
[7 empty] | 3977 | 113 | 6.9975 | 5.0676
[7 empty] | 3978 | 114 | 7.167 | 5.1955
[7 empty] | 3979 | 115 | 6.7094 | 4.8501
[7 empty] | 3980 | 116 | 7.3958 | 5.3683
[7 empty] | 3981 | 117 | 6.9721 | 5.0484
[7 empty] | 3982 | 118 | 6.1924 | 4.4598
[7 empty] | 3983 | 119 | 4.5824 | 3.2443
[7 empty] | 3984 | 120 | 4.2615 | 3.0021
[7 empty] | 3985 | 121 | 3.5232 | 2.4446
[7 empty] | 3986 | 122 | 3.1079 | 2.1312
[7 empty] | 3987 | 123 | 3.0232 | 2.0672
[7 empty] | 3988 | 124 | 2.9893 | 2.0416
[7 empty] | 3989 | 125 | 2.9469 | 2.0096
[7 empty] | 3990 | 126 | 3.091 | 2.1184
[7 empty] | 3991 | 127 | 4.6163 | 3.2699
[7 empty] | 3992 | 128 | 6.1924 | 4.4598
[7 empty] | 3993 | 129 | 6.8788 | 4.978
[7 empty] | 3994 | 130 | 7.3195 | 5.3107
[7 empty] | 3995 | 131 | 7.4805 | 5.4322
[7 empty] | 3996 | 132 | 7.2263 | 5.2403
[7 empty] | 3997 | 133 | 7.8703 | 5.7265
[7 empty] | 3998 | 134 | 8.1754 | 5.9568
[7 empty] | 3999 | 135 | 8.2431 | 6.008
[7 empty] | 4000 | 136 | 7.4212 | 5.3875
[7 empty] | 4001 | 137 | 7.3195 | 5.3107
[7 empty] | 4002 | 138 | 7.2686 | 5.2723
[7 empty] | 4003 | 139 | 6.9297 | 5.0164
[7 empty] | 4004 | 140 | 6.9382 | 5.0228
[7 empty] | 4005 | 141 | 6.2772 | 4.5238
[7 empty] | 4006 | 142 | 5.6332 | 4.0376
[7 empty] | 4007 | 143 | 4.7434 | 3.3659
[7 empty] | 4008 | 144 | 4.1248 | 2.8989
[7 empty] | 4009 | 145 | 3.6503 | 2.5406
[7 empty] | 4010 | 146 | 3.4384 | 2.3807
[7 empty] | 4011 | 147 | 3.3706 | 2.3295
[7 empty] | 4012 | 148 | 3.3622 | 2.3231
[7 empty] | 4013 | 149 | 3.3622 | 2.3231
[7 empty] | 4014 | 150 | 3.3706 | 2.3295
[7 empty] | 4015 | 151 | 4.4638 | 3.1547
[7 empty] | 4016 | 152 | 6.006 | 4.3191
[7 empty] | 4017 | 153 | 6.6246 | 4.7861
[7 empty] | 4018 | 154 | 7.1924 | 5.2147
[7 empty] | 4019 | 155 | 7.0398 | 5.0996
[7 empty] | 4020 | 156 | 7.2093 | 5.2275
[7 empty] | 4021 | 157 | 7.9296 | 5.7713
[7 empty] | 4022 | 158 | 8.2601 | 6.0208
[7 empty] | 4023 | 159 | 8.5313 | 6.2255
[7 empty] | 4024 | 160 | 8.4041 | 6.1296
[7 empty] | 4025 | 161 | 9.1753 | 6.7117
[7 empty] | 4026 | 162 | 8.6753 | 6.3343
[7 empty] | 4027 | 163 | 9.0397 | 6.6094
[7 empty] | 4028 | 164 | 7.6754 | 5.5794
[7 empty] | 4029 | 165 | 10.8362 | 7.9656
[7 empty] | 4030 | 166 | 8.7685 | 6.4046
[7 empty] | 4031 | 167 | 5.1247 | 3.6537
[7 empty] | 4032 | 168 | 4.4722 | 3.1611
[7 empty] | 4033 | 1 | 2.9978 | 2.048
[7 empty] | 4034 | 2 | 2.8876 | 1.9648
[7 empty] | 4035 | 3 | 2.8791 | 1.9584
[7 empty] | 4036 | 4 | 3.0147 | 2.0608
[7 empty] | 4037 | 5 | 3.0317 | 2.0736
[7 empty] | 4038 | 6 | 3.4638 | 2.3999
[7 empty] | 4039 | 7 | 4.1926 | 2.95
[7 empty] | 4040 | 8 | 4.8705 | 3.4618
[7 empty] | 4041 | 9 | 4.8451 | 3.4426
[7 empty] | 4042 | 10 | 6.3789 | 4.6006
[7 empty] | 4043 | 11 | 8.4804 | 6.1871
[7 empty] | 4044 | 12 | 9.4549 | 6.9228
[7 empty] | 4045 | 13 | 9.8362 | 7.2107
[7 empty] | 4046 | 14 | 9.6159 | 7.0444
[7 empty] | 4047 | 15 | 9.5227 | 6.974
[7 empty] | 4048 | 16 | 10.7175 | 7.8761
[7 empty] | 4049 | 17 | 12.0564 | 8.8868
[7 empty] | 4050 | 18 | 11.8107 | 8.7013
[7 empty] | 4051 | 19 | 12.3445 | 9.1044
[7 empty] | 4052 | 20 | 12.2767 | 9.0532
[7 empty] | 4053 | 21 | 12.853 | 9.4882
[7 empty] | 4054 | 22 | 8.8533 | 6.4686
[7 empty] | 4055 | 23 | 5.04 | 3.5898
[7 empty] | 4056 | 24 | 3.3504 | 2.3142
[7 empty] | 4057 | 25 | 3.252 | 2.2399
[7 empty] | 4058 | 26 | 3.1418 | 2.1567
[7 empty] | 4059 | 27 | 3.0401 | 2.08
[7 empty] | 4060 | 28 | 3.1249 | 2.144
[7 empty] | 4061 | 29 | 3.3706 | 2.3295
[7 empty] | 4062 | 30 | 3.6164 | 2.515
[7 empty] | 4063 | 31 | 4.4722 | 3.1611
[7 empty] | 4064 | 32 | 4.8281 | 3.4298
[7 empty] | 4065 | 33 | 5.4976 | 3.9352
[7 empty] | 4066 | 34 | 6.4043 | 4.6198
[7 empty] | 4067 | 35 | 8.5991 | 6.2767
[7 empty] | 4068 | 36 | 9.6413 | 7.0636
[7 empty] | 4069 | 37 | 9.7176 | 7.1212
[7 empty] | 4070 | 38 | 9.7939 | 7.1787
[7 empty] | 4071 | 39 | 9.4634 | 6.9292
[7 empty] | 4072 | 40 | 10.5311 | 7.7353
[7 empty] | 4073 | 41 | 11.0904 | 8.1575
[7 empty] | 4074 | 42 | 11.1073 | 8.1703
[7 empty] | 4075 | 43 | 11.4802 | 8.4518
[7 empty] | 4076 | 44 | 12.6496 | 9.3347
[7 empty] | 4077 | 45 | 12.2428 | 9.0276
[7 empty] | 4078 | 46 | 9.4634 | 6.9292
[7 empty] | 4079 | 47 | 5.8196 | 4.1783
[7 empty] | 4080 | 48 | 4.3028 | 3.0332
[7 empty] | 4081 | 49 | 3.6333 | 2.5278
[7 empty] | 4082 | 50 | 3.3198 | 2.2911
[7 empty] | 4083 | 51 | 3.2096 | 2.2079
[7 empty] | 4084 | 52 | 3.2435 | 2.2335
[7 empty] | 4085 | 53 | 3.2689 | 2.2527
[7 empty] | 4086 | 54 | 3.8536 | 2.6941
[7 empty] | 4087 | 55 | 5.0061 | 3.5642
[7 empty] | 4088 | 56 | 5.2518 | 3.7497
[7 empty] | 4089 | 57 | 6.2094 | 4.4726
[7 empty] | 4090 | 58 | 7.328 | 5.3171
[7 empty] | 4091 | 59 | 8.5482 | 6.2383
[7 empty] | 4092 | 60 | 9.1838 | 6.7181
[7 empty] | 4093 | 61 | 9.8701 | 7.2363
[7 empty] | 4094 | 62 | 9.6668 | 7.0828
[7 empty] | 4095 | 63 | 10.2684 | 7.537
[7 empty] | 4096 | 64 | 11.226 | 8.2599
[7 empty] | 4097 | 65 | 11.853 | 8.7333
[7 empty] | 4098 | 66 | 11.7514 | 8.6565
[7 empty] | 4099 | 67 | 12.4971 | 9.2195
[7 empty] | 4100 | 68 | 12.7428 | 9.405
[7 empty] | 4101 | 69 | 12.2259 | 9.0148
[7 empty] | 4102 | 70 | 9.904 | 7.2619
[7 empty] | 4103 | 71 | 5.3366 | 3.8137
[7 empty] | 4104 | 72 | 4.2398 | 2.9857
[7 empty] | 4105 | 73 | 3.5147 | 2.4382
[7 empty] | 4106 | 74 | 3.2859 | 2.2655
[7 empty] | 4107 | 75 | 3.1842 | 2.1887
[7 empty] | 4108 | 76 | 3.1249 | 2.144
[7 empty] | 4109 | 77 | 3.3028 | 2.2783
[7 empty] | 4110 | 78 | 3.7096 | 2.5854
[7 empty] | 4111 | 79 | 4.8366 | 3.4362
[7 empty] | 4112 | 80 | 5.0146 | 3.5706
[7 empty] | 4113 | 81 | 6.2094 | 4.4726
[7 empty] | 4114 | 82 | 7.311 | 5.3043
[7 empty] | 4115 | 83 | 8.0567 | 5.8673
[7 empty] | 4116 | 84 | 9.3109 | 6.8141
[7 empty] | 4117 | 85 | 9.0058 | 6.5838
[7 empty] | 4118 | 86 | 8.4889 | 6.1935
[7 empty] | 4119 | 87 | 8.938 | 6.5326
[7 empty] | 4120 | 88 | 9.6075 | 7.038
[7 empty] | 4121 | 89 | 10.9718 | 8.068
[7 empty] | 4122 | 90 | 10.3786 | 7.6202
[7 empty] | 4123 | 91 | 11.0734 | 8.1447
[7 empty] | 4124 | 92 | 10.4633 | 7.6841
[7 empty] | 4125 | 93 | 8.0228 | 5.8417
[7 empty] | 4126 | 94 | 7.1076 | 5.1507
[7 empty] | 4127 | 95 | 5.2264 | 3.7305
[7 empty] | 4128 | 96 | 4.2265 | 2.9756
[7 empty] | 4129 | 97 | 4.1757 | 2.9372
[7 empty] | 4130 | 98 | 3.8791 | 2.7133
[7 empty] | 4131 | 99 | 3.8197 | 2.6685
[7 empty] | 4132 | 100 | 3.4638 | 2.3999
[7 empty] | 4133 | 101 | 3.4045 | 2.3551
[7 empty] | 4134 | 102 | 3.6418 | 2.5342
[7 empty] | 4135 | 103 | 4.396 | 3.1036
[7 empty] | 4136 | 104 | 4.6502 | 3.2955
[7 empty] | 4137 | 105 | 5.1417 | 3.6665
[7 empty] | 4138 | 106 | 6.6161 | 4.7797
[7 empty] | 4139 | 107 | 6.9721 | 5.0484
[7 empty] | 4140 | 108 | 8.5652 | 6.2511
[7 empty] | 4141 | 109 | 7.8957 | 5.7457
[7 empty] | 4142 | 110 | 7.4381 | 5.4002
[7 empty] | 4143 | 111 | 7.2771 | 5.2787
[7 empty] | 4144 | 112 | 7.3449 | 5.3299
[7 empty] | 4145 | 113 | 6.9975 | 5.0676
[7 empty] | 4146 | 114 | 7.167 | 5.1955
[7 empty] | 4147 | 115 | 6.7094 | 4.8501
[7 empty] | 4148 | 116 | 7.3958 | 5.3683
[7 empty] | 4149 | 117 | 6.9721 | 5.0484
[7 empty] | 4150 | 118 | 6.1924 | 4.4598
[7 empty] | 4151 | 119 | 4.5824 | 3.2443
[7 empty] | 4152 | 120 | 4.2615 | 3.0021
[7 empty] | 4153 | 121 | 3.5232 | 2.4446
[7 empty] | 4154 | 122 | 3.1079 | 2.1312
[7 empty] | 4155 | 123 | 3.0232 | 2.0672
[7 empty] | 4156 | 124 | 2.9893 | 2.0416
[7 empty] | 4157 | 125 | 2.9469 | 2.0096
[7 empty] | 4158 | 126 | 3.091 | 2.1184
[7 empty] | 4159 | 127 | 4.6163 | 3.2699
[7 empty] | 4160 | 128 | 6.1924 | 4.4598
[7 empty] | 4161 | 129 | 6.8788 | 4.978
[7 empty] | 4162 | 130 | 7.3195 | 5.3107
[7 empty] | 4163 | 131 | 7.4805 | 5.4322
[7 empty] | 4164 | 132 | 7.2263 | 5.2403
[7 empty] | 4165 | 133 | 7.8703 | 5.7265
[7 empty] | 4166 | 134 | 8.1754 | 5.9568
[7 empty] | 4167 | 135 | 8.2431 | 6.008
[7 empty] | 4168 | 136 | 7.4212 | 5.3875
[7 empty] | 4169 | 137 | 7.3195 | 5.3107
[7 empty] | 4170 | 138 | 7.2686 | 5.2723
[7 empty] | 4171 | 139 | 6.9297 | 5.0164
[7 empty] | 4172 | 140 | 6.9382 | 5.0228
[7 empty] | 4173 | 141 | 6.2772 | 4.5238
[7 empty] | 4174 | 142 | 5.6332 | 4.0376
[7 empty] | 4175 | 143 | 4.7434 | 3.3659
[7 empty] | 4176 | 144 | 4.1248 | 2.8989
[7 empty] | 4177 | 145 | 3.6503 | 2.5406
[7 empty] | 4178 | 146 | 3.4384 | 2.3807
[7 empty] | 4179 | 147 | 3.3706 | 2.3295
[7 empty] | 4180 | 148 | 3.3622 | 2.3231
[7 empty] | 4181 | 149 | 3.3622 | 2.3231
[7 empty] | 4182 | 150 | 3.3706 | 2.3295
[7 empty] | 4183 | 151 | 4.4638 | 3.1547
[7 empty] | 4184 | 152 | 6.006 | 4.3191
[7 empty] | 4185 | 153 | 6.6246 | 4.7861
[7 empty] | 4186 | 154 | 7.1924 | 5.2147
[7 empty] | 4187 | 155 | 7.0398 | 5.0996
[7 empty] | 4188 | 156 | 7.2093 | 5.2275
[7 empty] | 4189 | 157 | 7.9296 | 5.7713
[7 empty] | 4190 | 158 | 8.2601 | 6.0208
[7 empty] | 4191 | 159 | 8.5313 | 6.2255
[7 empty] | 4192 | 160 | 8.4041 | 6.1296
[7 empty] | 4193 | 161 | 9.1753 | 6.7117
[7 empty] | 4194 | 162 | 8.6753 | 6.3343
[7 empty] | 4195 | 163 | 9.0397 | 6.6094
[7 empty] | 4196 | 164 | 7.6754 | 5.5794
[7 empty] | 4197 | 165 | 10.8362 | 7.9656
[7 empty] | 4198 | 166 | 8.7685 | 6.4046
[7 empty] | 4199 | 167 | 5.1247 | 3.6537
[7 empty] | 4200 | 168 | 4.4722 | 3.1611
[7 empty] | 4201 | 1 | 2.9978 | 2.048
[7 empty] | 4202 | 2 | 2.8876 | 1.9648
[7 empty] | 4203 | 3 | 2.8791 | 1.9584
[7 empty] | 4204 | 4 | 3.0147 | 2.0608
[7 empty] | 4205 | 5 | 3.0317 | 2.0736
[7 empty] | 4206 | 6 | 3.4638 | 2.3999
[7 empty] | 4207 | 7 | 4.1926 | 2.95
[7 empty] | 4208 | 8 | 4.8705 | 3.4618
[7 empty] | 4209 | 9 | 4.8451 | 3.4426
[7 empty] | 4210 | 10 | 6.3789 | 4.6006
[7 empty] | 4211 | 11 | 8.4804 | 6.1871
[7 empty] | 4212 | 12 | 9.4549 | 6.9228
[7 empty] | 4213 | 13 | 9.8362 | 7.2107
[7 empty] | 4214 | 14 | 9.6159 | 7.0444
[7 empty] | 4215 | 15 | 9.5227 | 6.974
[7 empty] | 4216 | 16 | 10.7175 | 7.8761
[7 empty] | 4217 | 17 | 12.0564 | 8.8868
[7 empty] | 4218 | 18 | 11.8107 | 8.7013
[7 empty] | 4219 | 19 | 12.3445 | 9.1044
[7 empty] | 4220 | 20 | 12.2767 | 9.0532
[7 empty] | 4221 | 21 | 12.853 | 9.4882
[7 empty] | 4222 | 22 | 8.8533 | 6.4686
[7 empty] | 4223 | 23 | 5.04 | 3.5898
[7 empty] | 4224 | 24 | 3.3504 | 2.3142
[7 empty] | 4225 | 25 | 3.252 | 2.2399
[7 empty] | 4226 | 26 | 3.1418 | 2.1567
[7 empty] | 4227 | 27 | 3.0401 | 2.08
[7 empty] | 4228 | 28 | 3.1249 | 2.144
[7 empty] | 4229 | 29 | 3.3706 | 2.3295
[7 empty] | 4230 | 30 | 3.6164 | 2.515
[7 empty] | 4231 | 31 | 4.4722 | 3.1611
[7 empty] | 4232 | 32 | 4.8281 | 3.4298
[7 empty] | 4233 | 33 | 5.4976 | 3.9352
[7 empty] | 4234 | 34 | 6.4043 | 4.6198
[7 empty] | 4235 | 35 | 8.5991 | 6.2767
[7 empty] | 4236 | 36 | 9.6413 | 7.0636
[7 empty] | 4237 | 37 | 9.7176 | 7.1212
[7 empty] | 4238 | 38 | 9.7939 | 7.1787
[7 empty] | 4239 | 39 | 9.4634 | 6.9292
[7 empty] | 4240 | 40 | 10.5311 | 7.7353
[7 empty] | 4241 | 41 | 11.0904 | 8.1575
[7 empty] | 4242 | 42 | 11.1073 | 8.1703
[7 empty] | 4243 | 43 | 11.4802 | 8.4518
[7 empty] | 4244 | 44 | 12.6496 | 9.3347
[7 empty] | 4245 | 45 | 12.2428 | 9.0276
[7 empty] | 4246 | 46 | 9.4634 | 6.9292
[7 empty] | 4247 | 47 | 5.8196 | 4.1783
[7 empty] | 4248 | 48 | 4.3028 | 3.0332
[7 empty] | 4249 | 49 | 3.6333 | 2.5278
[7 empty] | 4250 | 50 | 3.3198 | 2.2911
[7 empty] | 4251 | 51 | 3.2096 | 2.2079
[7 empty] | 4252 | 52 | 3.2435 | 2.2335
[7 empty] | 4253 | 53 | 3.2689 | 2.2527
[7 empty] | 4254 | 54 | 3.8536 | 2.6941
[7 empty] | 4255 | 55 | 5.0061 | 3.5642
[7 empty] | 4256 | 56 | 5.2518 | 3.7497
[7 empty] | 4257 | 57 | 6.2094 | 4.4726
[7 empty] | 4258 | 58 | 7.328 | 5.3171
[7 empty] | 4259 | 59 | 8.5482 | 6.2383
[7 empty] | 4260 | 60 | 9.1838 | 6.7181
[7 empty] | 4261 | 61 | 9.8701 | 7.2363
[7 empty] | 4262 | 62 | 9.6668 | 7.0828
[7 empty] | 4263 | 63 | 10.2684 | 7.537
[7 empty] | 4264 | 64 | 11.226 | 8.2599
[7 empty] | 4265 | 65 | 11.853 | 8.7333
[7 empty] | 4266 | 66 | 11.7514 | 8.6565
[7 empty] | 4267 | 67 | 12.4971 | 9.2195
[7 empty] | 4268 | 68 | 12.7428 | 9.405
[7 empty] | 4269 | 69 | 12.2259 | 9.0148
[7 empty] | 4270 | 70 | 9.904 | 7.2619
[7 empty] | 4271 | 71 | 5.3366 | 3.8137
[7 empty] | 4272 | 72 | 4.2398 | 2.9857
[7 empty] | 4273 | 73 | 3.5147 | 2.4382
[7 empty] | 4274 | 74 | 3.2859 | 2.2655
[7 empty] | 4275 | 75 | 3.1842 | 2.1887
[7 empty] | 4276 | 76 | 3.1249 | 2.144
[7 empty] | 4277 | 77 | 3.3028 | 2.2783
[7 empty] | 4278 | 78 | 3.7096 | 2.5854
[7 empty] | 4279 | 79 | 4.8366 | 3.4362
[7 empty] | 4280 | 80 | 5.0146 | 3.5706
[7 empty] | 4281 | 81 | 6.2094 | 4.4726
[7 empty] | 4282 | 82 | 7.311 | 5.3043
[7 empty] | 4283 | 83 | 8.0567 | 5.8673
[7 empty] | 4284 | 84 | 9.3109 | 6.8141
[7 empty] | 4285 | 85 | 9.0058 | 6.5838
[7 empty] | 4286 | 86 | 8.4889 | 6.1935
[7 empty] | 4287 | 87 | 8.938 | 6.5326
[7 empty] | 4288 | 88 | 9.6075 | 7.038
[7 empty] | 4289 | 89 | 10.9718 | 8.068
[7 empty] | 4290 | 90 | 10.3786 | 7.6202
[7 empty] | 4291 | 91 | 11.0734 | 8.1447
[7 empty] | 4292 | 92 | 10.4633 | 7.6841
[7 empty] | 4293 | 93 | 8.0228 | 5.8417
[7 empty] | 4294 | 94 | 7.1076 | 5.1507
[7 empty] | 4295 | 95 | 5.2264 | 3.7305
[7 empty] | 4296 | 96 | 4.2265 | 2.9756
[7 empty] | 4297 | 97 | 4.1757 | 2.9372
[7 empty] | 4298 | 98 | 3.8791 | 2.7133
[7 empty] | 4299 | 99 | 3.8197 | 2.6685
[7 empty] | 4300 | 100 | 3.4638 | 2.3999
[7 empty] | 4301 | 101 | 3.4045 | 2.3551
[7 empty] | 4302 | 102 | 3.6418 | 2.5342
[7 empty] | 4303 | 103 | 4.396 | 3.1036
[7 empty] | 4304 | 104 | 4.6502 | 3.2955
[7 empty] | 4305 | 105 | 5.1417 | 3.6665
[7 empty] | 4306 | 106 | 6.6161 | 4.7797
[7 empty] | 4307 | 107 | 6.9721 | 5.0484
[7 empty] | 4308 | 108 | 8.5652 | 6.2511
[7 empty] | 4309 | 109 | 7.8957 | 5.7457
[7 empty] | 4310 | 110 | 7.4381 | 5.4002
[7 empty] | 4311 | 111 | 7.2771 | 5.2787
[7 empty] | 4312 | 112 | 7.3449 | 5.3299
[7 empty] | 4313 | 113 | 6.9975 | 5.0676
[7 empty] | 4314 | 114 | 7.167 | 5.1955
[7 empty] | 4315 | 115 | 6.7094 | 4.8501
[7 empty] | 4316 | 116 | 7.3958 | 5.3683
[7 empty] | 4317 | 117 | 6.9721 | 5.0484
[7 empty] | 4318 | 118 | 6.1924 | 4.4598
[7 empty] | 4319 | 119 | 4.5824 | 3.2443
[7 empty] | 4320 | 120 | 4.2615 | 3.0021
[7 empty] | 4321 | 121 | 3.5232 | 2.4446
[7 empty] | 4322 | 122 | 3.1079 | 2.1312
[7 empty] | 4323 | 123 | 3.0232 | 2.0672
[7 empty] | 4324 | 124 | 2.9893 | 2.0416
[7 empty] | 4325 | 125 | 2.9469 | 2.0096
[7 empty] | 4326 | 126 | 3.091 | 2.1184
[7 empty] | 4327 | 127 | 4.6163 | 3.2699
[7 empty] | 4328 | 128 | 6.1924 | 4.4598
[7 empty] | 4329 | 129 | 6.8788 | 4.978
[7 empty] | 4330 | 130 | 7.3195 | 5.3107
[7 empty] | 4331 | 131 | 7.4805 | 5.4322
[7 empty] | 4332 | 132 | 7.2263 | 5.2403
[7 empty] | 4333 | 133 | 7.8703 | 5.7265
[7 empty] | 4334 | 134 | 8.1754 | 5.9568
[7 empty] | 4335 | 135 | 8.2431 | 6.008
[7 empty] | 4336 | 136 | 7.4212 | 5.3875
[7 empty] | 4337 | 137 | 7.3195 | 5.3107
[7 empty] | 4338 | 138 | 7.2686 | 5.2723
[7 empty] | 4339 | 139 | 6.9297 | 5.0164
[7 empty] | 4340 | 140 | 6.9382 | 5.0228
[7 empty] | 4341 | 141 | 6.2772 | 4.5238
[7 empty] | 4342 | 142 | 5.6332 | 4.0376
[7 empty] | 4343 | 143 | 4.7434 | 3.3659
[7 empty] | 4344 | 144 | 4.1248 | 2.8989
[7 empty] | 4345 | 145 | 3.6503 | 2.5406
[7 empty] | 4346 | 146 | 3.4384 | 2.3807
[7 empty] | 4347 | 147 | 3.3706 | 2.3295
[7 empty] | 4348 | 148 | 3.3622 | 2.3231
[7 empty] | 4349 | 149 | 3.3622 | 2.3231
[7 empty] | 4350 | 150 | 3.3706 | 2.3295
[7 empty] | 4351 | 151 | 4.4638 | 3.1547
[7 empty] | 4352 | 152 | 6.006 | 4.3191
[7 empty] | 4353 | 153 | 6.6246 | 4.7861
[7 empty] | 4354 | 154 | 7.1924 | 5.2147
[7 empty] | 4355 | 155 | 7.0398 | 5.0996
[7 empty] | 4356 | 156 | 7.2093 | 5.2275
[7 empty] | 4357 | 157 | 7.9296 | 5.7713
[7 empty] | 4358 | 158 | 8.2601 | 6.0208
[7 empty] | 4359 | 159 | 8.5313 | 6.2255
[7 empty] | 4360 | 160 | 8.4041 | 6.1296
[7 empty] | 4361 | 161 | 9.1753 | 6.7117
[7 empty] | 4362 | 162 | 8.6753 | 6.3343
[7 empty] | 4363 | 163 | 9.0397 | 6.6094
[7 empty] | 4364 | 164 | 7.6754 | 5.5794
[7 empty] | 4365 | 165 | 10.8362 | 7.9656
[7 empty] | 4366 | 166 | 8.7685 | 6.4046
[7 empty] | 4367 | 167 | 5.1247 | 3.6537
[7 empty] | 4368 | 168 | 4.4722 | 3.1611
[7 empty] | 4369 | 1 | 2.9978 | 2.048
[7 empty] | 4370 | 2 | 2.8876 | 1.9648
[7 empty] | 4371 | 3 | 2.8791 | 1.9584
[7 empty] | 4372 | 4 | 3.0147 | 2.0608
[7 empty] | 4373 | 5 | 3.0317 | 2.0736
[7 empty] | 4374 | 6 | 3.4638 | 2.3999
[7 empty] | 4375 | 7 | 4.1926 | 2.95
[7 empty] | 4376 | 8 | 4.8705 | 3.4618
[7 empty] | 4377 | 9 | 4.8451 | 3.4426
[7 empty] | 4378 | 10 | 6.3789 | 4.6006
[7 empty] | 4379 | 11 | 8.4804 | 6.1871
[7 empty] | 4380 | 12 | 9.4549 | 6.9228
[7 empty] | 4381 | 13 | 9.8362 | 7.2107
[7 empty] | 4382 | 14 | 9.6159 | 7.0444
[7 empty] | 4383 | 15 | 9.5227 | 6.974
[7 empty] | 4384 | 16 | 10.7175 | 7.8761
[7 empty] | 4385 | 17 | 12.0564 | 8.8868
[7 empty] | 4386 | 18 | 11.8107 | 8.7013
[7 empty] | 4387 | 19 | 12.3445 | 9.1044
[7 empty] | 4388 | 20 | 12.2767 | 9.0532
[7 empty] | 4389 | 21 | 12.853 | 9.4882
[7 empty] | 4390 | 22 | 8.8533 | 6.4686
[7 empty] | 4391 | 23 | 5.04 | 3.5898
[7 empty] | 4392 | 24 | 3.3504 | 2.3142
[7 empty] | 4393 | 25 | 3.252 | 2.2399
[7 empty] | 4394 | 26 | 3.1418 | 2.1567
[7 empty] | 4395 | 27 | 3.0401 | 2.08
[7 empty] | 4396 | 28 | 3.1249 | 2.144
[7 empty] | 4397 | 29 | 3.3706 | 2.3295
[7 empty] | 4398 | 30 | 3.6164 | 2.515
[7 empty] | 4399 | 31 | 4.4722 | 3.1611
[7 empty] | 4400 | 32 | 4.8281 | 3.4298
[7 empty] | 4401 | 33 | 5.4976 | 3.9352
[7 empty] | 4402 | 34 | 6.4043 | 4.6198
[7 empty] | 4403 | 35 | 8.5991 | 6.2767
[7 empty] | 4404 | 36 | 9.6413 | 7.0636
[7 empty] | 4405 | 37 | 9.7176 | 7.1212
[7 empty] | 4406 | 38 | 9.7939 | 7.1787
[7 empty] | 4407 | 39 | 9.4634 | 6.9292
[7 empty] | 4408 | 40 | 10.5311 | 7.7353
[7 empty] | 4409 | 41 | 11.0904 | 8.1575
[7 empty] | 4410 | 42 | 11.1073 | 8.1703
[7 empty] | 4411 | 43 | 11.4802 | 8.4518
[7 empty] | 4412 | 44 | 12.6496 | 9.3347
[7 empty] | 4413 | 45 | 12.2428 | 9.0276
[7 empty] | 4414 | 46 | 9.4634 | 6.9292
[7 empty] | 4415 | 47 | 5.8196 | 4.1783
[7 empty] | 4416 | 48 | 4.3028 | 3.0332
[7 empty] | 4417 | 49 | 3.6333 | 2.5278
[7 empty] | 4418 | 50 | 3.3198 | 2.2911
[7 empty] | 4419 | 51 | 3.2096 | 2.2079
[7 empty] | 4420 | 52 | 3.2435 | 2.2335
[7 empty] | 4421 | 53 | 3.2689 | 2.2527
[7 empty] | 4422 | 54 | 3.8536 | 2.6941
[7 empty] | 4423 | 55 | 5.0061 | 3.5642
[7 empty] | 4424 | 56 | 5.2518 | 3.7497
[7 empty] | 4425 | 57 | 6.2094 | 4.4726
[7 empty] | 4426 | 58 | 7.328 | 5.3171
[7 empty] | 4427 | 59 | 8.5482 | 6.2383
[7 empty] | 4428 | 60 | 9.1838 | 6.7181
[7 empty] | 4429 | 61 | 9.8701 | 7.2363
[7 empty] | 4430 | 62 | 9.6668 | 7.0828
[7 empty] | 4431 | 63 | 10.2684 | 7.537
[7 empty] | 4432 | 64 | 11.226 | 8.2599
[7 empty] | 4433 | 65 | 11.853 | 8.7333
[7 empty] | 4434 | 66 | 11.7514 | 8.6565
[7 empty] | 4435 | 67 | 12.4971 | 9.2195
[7 empty] | 4436 | 68 | 12.7428 | 9.405
[7 empty] | 4437 | 69 | 12.2259 | 9.0148
[7 empty] | 4438 | 70 | 9.904 | 7.2619
[7 empty] | 4439 | 71 | 5.3366 | 3.8137
[7 empty] | 4440 | 72 | 4.2398 | 2.9857
[7 empty] | 4441 | 73 | 3.5147 | 2.4382
[7 empty] | 4442 | 74 | 3.2859 | 2.2655
[7 empty] | 4443 | 75 | 3.1842 | 2.1887
[7 empty] | 4444 | 76 | 3.1249 | 2.144
[7 empty] | 4445 | 77 | 3.3028 | 2.2783
[7 empty] | 4446 | 78 | 3.7096 | 2.5854
[7 empty] | 4447 | 79 | 4.8366 | 3.4362
[7 empty] | 4448 | 80 | 5.0146 | 3.5706
[7 empty] | 4449 | 81 | 6.2094 | 4.4726
[7 empty] | 4450 | 82 | 7.311 | 5.3043
[7 empty] | 4451 | 83 | 8.0567 | 5.8673
[7 empty] | 4452 | 84 | 9.3109 | 6.8141
[7 empty] | 4453 | 85 | 9.0058 | 6.5838
[7 empty] | 4454 | 86 | 8.4889 | 6.1935
[7 empty] | 4455 | 87 | 8.938 | 6.5326
[7 empty] | 4456 | 88 | 9.6075 | 7.038
[7 empty] | 4457 | 89 | 10.9718 | 8.068
[7 empty] | 4458 | 90 | 10.3786 | 7.6202
[7 empty] | 4459 | 91 | 11.0734 | 8.1447
[7 empty] | 4460 | 92 | 10.4633 | 7.6841
[7 empty] | 4461 | 93 | 8.0228 | 5.8417
[7 empty] | 4462 | 94 | 7.1076 | 5.1507
[7 empty] | 4463 | 95 | 5.2264 | 3.7305
[7 empty] | 4464 | 96 | 4.2265 | 2.9756
[7 empty] | 4465 | 97 | 4.1757 | 2.9372
[7 empty] | 4466 | 98 | 3.8791 | 2.7133
[7 empty] | 4467 | 99 | 3.8197 | 2.6685
[7 empty] | 4468 | 100 | 3.4638 | 2.3999
[7 empty] | 4469 | 101 | 3.4045 | 2.3551
[7 empty] | 4470 | 102 | 3.6418 | 2.5342
[7 empty] | 4471 | 103 | 4.396 | 3.1036
[7 empty] | 4472 | 104 | 4.6502 | 3.2955
[7 empty] | 4473 | 105 | 5.1417 | 3.6665
[7 empty] | 4474 | 106 | 6.6161 | 4.7797
[7 empty] | 4475 | 107 | 6.9721 | 5.0484
[7 empty] | 4476 | 108 | 8.5652 | 6.2511
[7 empty] | 4477 | 109 | 7.8957 | 5.7457
[7 empty] | 4478 | 110 | 7.4381 | 5.4002
[7 empty] | 4479 | 111 | 7.2771 | 5.2787
[7 empty] | 4480 | 112 | 7.3449 | 5.3299
[7 empty] | 4481 | 113 | 6.9975 | 5.0676
[7 empty] | 4482 | 114 | 7.167 | 5.1955
[7 empty] | 4483 | 115 | 6.7094 | 4.8501
[7 empty] | 4484 | 116 | 7.3958 | 5.3683
[7 empty] | 4485 | 117 | 6.9721 | 5.0484
[7 empty] | 4486 | 118 | 6.1924 | 4.4598
[7 empty] | 4487 | 119 | 4.5824 | 3.2443
[7 empty] | 4488 | 120 | 4.2615 | 3.0021
[7 empty] | 4489 | 121 | 3.5232 | 2.4446
[7 empty] | 4490 | 122 | 3.1079 | 2.1312
[7 empty] | 4491 | 123 | 3.0232 | 2.0672
[7 empty] | 4492 | 124 | 2.9893 | 2.0416
[7 empty] | 4493 | 125 | 2.9469 | 2.0096
[7 empty] | 4494 | 126 | 3.091 | 2.1184
[7 empty] | 4495 | 127 | 4.6163 | 3.2699
[7 empty] | 4496 | 128 | 6.1924 | 4.4598
[7 empty] | 4497 | 129 | 6.8788 | 4.978
[7 empty] | 4498 | 130 | 7.3195 | 5.3107
[7 empty] | 4499 | 131 | 7.4805 | 5.4322
[7 empty] | 4500 | 132 | 7.2263 | 5.2403
[7 empty] | 4501 | 133 | 7.8703 | 5.7265
[7 empty] | 4502 | 134 | 8.1754 | 5.9568
[7 empty] | 4503 | 135 | 8.2431 | 6.008
[7 empty] | 4504 | 136 | 7.4212 | 5.3875
[7 empty] | 4505 | 137 | 7.3195 | 5.3107
[7 empty] | 4506 | 138 | 7.2686 | 5.2723
[7 empty] | 4507 | 139 | 6.9297 | 5.0164
[7 empty] | 4508 | 140 | 6.9382 | 5.0228
[7 empty] | 4509 | 141 | 6.2772 | 4.5238
[7 empty] | 4510 | 142 | 5.6332 | 4.0376
[7 empty] | 4511 | 143 | 4.7434 | 3.3659
[7 empty] | 4512 | 144 | 4.1248 | 2.8989
[7 empty] | 4513 | 145 | 3.6503 | 2.5406
[7 empty] | 4514 | 146 | 3.4384 | 2.3807
[7 empty] | 4515 | 147 | 3.3706 | 2.3295
[7 empty] | 4516 | 148 | 3.3622 | 2.3231
[7 empty] | 4517 | 149 | 3.3622 | 2.3231
[7 empty] | 4518 | 150 | 3.3706 | 2.3295
[7 empty] | 4519 | 151 | 4.4638 | 3.1547
[7 empty] | 4520 | 152 | 6.006 | 4.3191
[7 empty] | 4521 | 153 | 6.6246 | 4.7861
[7 empty] | 4522 | 154 | 7.1924 | 5.2147
[7 empty] | 4523 | 155 | 7.0398 | 5.0996
[7 empty] | 4524 | 156 | 7.2093 | 5.2275
[7 empty] | 4525 | 157 | 7.9296 | 5.7713
[7 empty] | 4526 | 158 | 8.2601 | 6.0208
[7 empty] | 4527 | 159 | 8.5313 | 6.2255
[7 empty] | 4528 | 160 | 8.4041 | 6.1296
[7 empty] | 4529 | 161 | 9.1753 | 6.7117
[7 empty] | 4530 | 162 | 8.6753 | 6.3343
[7 empty] | 4531 | 163 | 9.0397 | 6.6094
[7 empty] | 4532 | 164 | 7.6754 | 5.5794
[7 empty] | 4533 | 165 | 10.8362 | 7.9656
[7 empty] | 4534 | 166 | 8.7685 | 6.4046
[7 empty] | 4535 | 167 | 5.1247 | 3.6537
[7 empty] | 4536 | 168 | 4.4722 | 3.1611
[7 empty] | 4537 | 1 | 2.9978 | 2.048
[7 empty] | 4538 | 2 | 2.8876 | 1.9648
[7 empty] | 4539 | 3 | 2.8791 | 1.9584
[7 empty] | 4540 | 4 | 3.0147 | 2.0608
[7 empty] | 4541 | 5 | 3.0317 | 2.0736
[7 empty] | 4542 | 6 | 3.4638 | 2.3999
[7 empty] | 4543 | 7 | 4.1926 | 2.95
[7 empty] | 4544 | 8 | 4.8705 | 3.4618
[7 empty] | 4545 | 9 | 4.8451 | 3.4426
[7 empty] | 4546 | 10 | 6.3789 | 4.6006
[7 empty] | 4547 | 11 | 8.4804 | 6.1871
[7 empty] | 4548 | 12 | 9.4549 | 6.9228
[7 empty] | 4549 | 13 | 9.8362 | 7.2107
[7 empty] | 4550 | 14 | 9.6159 | 7.0444
[7 empty] | 4551 | 15 | 9.5227 | 6.974
[7 empty] | 4552 | 16 | 10.7175 | 7.8761
[7 empty] | 4553 | 17 | 12.0564 | 8.8868
[7 empty] | 4554 | 18 | 11.8107 | 8.7013
[7 empty] | 4555 | 19 | 12.3445 | 9.1044
[7 empty] | 4556 | 20 | 12.2767 | 9.0532
[7 empty] | 4557 | 21 | 12.853 | 9.4882
[7 empty] | 4558 | 22 | 8.8533 | 6.4686
[7 empty] | 4559 | 23 | 5.04 | 3.5898
[7 empty] | 4560 | 24 | 3.3504 | 2.3142
[7 empty] | 4561 | 25 | 3.252 | 2.2399
[7 empty] | 4562 | 26 | 3.1418 | 2.1567
[7 empty] | 4563 | 27 | 3.0401 | 2.08
[7 empty] | 4564 | 28 | 3.1249 | 2.144
[7 empty] | 4565 | 29 | 3.3706 | 2.3295
[7 empty] | 4566 | 30 | 3.6164 | 2.515
[7 empty] | 4567 | 31 | 4.4722 | 3.1611
[7 empty] | 4568 | 32 | 4.8281 | 3.4298
[7 empty] | 4569 | 33 | 5.4976 | 3.9352
[7 empty] | 4570 | 34 | 6.4043 | 4.6198
[7 empty] | 4571 | 35 | 8.5991 | 6.2767
[7 empty] | 4572 | 36 | 9.6413 | 7.0636
[7 empty] | 4573 | 37 | 9.7176 | 7.1212
[7 empty] | 4574 | 38 | 9.7939 | 7.1787
[7 empty] | 4575 | 39 | 9.4634 | 6.9292
[7 empty] | 4576 | 40 | 10.5311 | 7.7353
[7 empty] | 4577 | 41 | 11.0904 | 8.1575
[7 empty] | 4578 | 42 | 11.1073 | 8.1703
[7 empty] | 4579 | 43 | 11.4802 | 8.4518
[7 empty] | 4580 | 44 | 12.6496 | 9.3347
[7 empty] | 4581 | 45 | 12.2428 | 9.0276
[7 empty] | 4582 | 46 | 9.4634 | 6.9292
[7 empty] | 4583 | 47 | 5.8196 | 4.1783
[7 empty] | 4584 | 48 | 4.3028 | 3.0332
[7 empty] | 4585 | 49 | 3.6333 | 2.5278
[7 empty] | 4586 | 50 | 3.3198 | 2.2911
[7 empty] | 4587 | 51 | 3.2096 | 2.2079
[7 empty] | 4588 | 52 | 3.2435 | 2.2335
[7 empty] | 4589 | 53 | 3.2689 | 2.2527
[7 empty] | 4590 | 54 | 3.8536 | 2.6941
[7 empty] | 4591 | 55 | 5.0061 | 3.5642
[7 empty] | 4592 | 56 | 5.2518 | 3.7497
[7 empty] | 4593 | 57 | 6.2094 | 4.4726
[7 empty] | 4594 | 58 | 7.328 | 5.3171
[7 empty] | 4595 | 59 | 8.5482 | 6.2383
[7 empty] | 4596 | 60 | 9.1838 | 6.7181
[7 empty] | 4597 | 61 | 9.8701 | 7.2363
[7 empty] | 4598 | 62 | 9.6668 | 7.0828
[7 empty] | 4599 | 63 | 10.2684 | 7.537
[7 empty] | 4600 | 64 | 11.226 | 8.2599
[7 empty] | 4601 | 65 | 11.853 | 8.7333
[7 empty] | 4602 | 66 | 11.7514 | 8.6565
[7 empty] | 4603 | 67 | 12.4971 | 9.2195
[7 empty] | 4604 | 68 | 12.7428 | 9.405
[7 empty] | 4605 | 69 | 12.2259 | 9.0148
[7 empty] | 4606 | 70 | 9.904 | 7.2619
[7 empty] | 4607 | 71 | 5.3366 | 3.8137
[7 empty] | 4608 | 72 | 4.2398 | 2.9857
[7 empty] | 4609 | 73 | 3.5147 | 2.4382
[7 empty] | 4610 | 74 | 3.2859 | 2.2655
[7 empty] | 4611 | 75 | 3.1842 | 2.1887
[7 empty] | 4612 | 76 | 3.1249 | 2.144
[7 empty] | 4613 | 77 | 3.3028 | 2.2783
[7 empty] | 4614 | 78 | 3.7096 | 2.5854
[7 empty] | 4615 | 79 | 4.8366 | 3.4362
[7 empty] | 4616 | 80 | 5.0146 | 3.5706
[7 empty] | 4617 | 81 | 6.2094 | 4.4726
[7 empty] | 4618 | 82 | 7.311 | 5.3043
[7 empty] | 4619 | 83 | 8.0567 | 5.8673
[7 empty] | 4620 | 84 | 9.3109 | 6.8141
[7 empty] | 4621 | 85 | 9.0058 | 6.5838
[7 empty] | 4622 | 86 | 8.4889 | 6.1935
[7 empty] | 4623 | 87 | 8.938 | 6.5326
[7 empty] | 4624 | 88 | 9.6075 | 7.038
[7 empty] | 4625 | 89 | 10.9718 | 8.068
[7 empty] | 4626 | 90 | 10.3786 | 7.6202
[7 empty] | 4627 | 91 | 11.0734 | 8.1447
[7 empty] | 4628 | 92 | 10.4633 | 7.6841
[7 empty] | 4629 | 93 | 8.0228 | 5.8417
[7 empty] | 4630 | 94 | 7.1076 | 5.1507
[7 empty] | 4631 | 95 | 5.2264 | 3.7305
[7 empty] | 4632 | 96 | 4.2265 | 2.9756
[7 empty] | 4633 | 97 | 4.1757 | 2.9372
[7 empty] | 4634 | 98 | 3.8791 | 2.7133
[7 empty] | 4635 | 99 | 3.8197 | 2.6685
[7 empty] | 4636 | 100 | 3.4638 | 2.3999
[7 empty] | 4637 | 101 | 3.4045 | 2.3551
[7 empty] | 4638 | 102 | 3.6418 | 2.5342
[7 empty] | 4639 | 103 | 4.396 | 3.1036
[7 empty] | 4640 | 104 | 4.6502 | 3.2955
[7 empty] | 4641 | 105 | 5.1417 | 3.6665
[7 empty] | 4642 | 106 | 6.6161 | 4.7797
[7 empty] | 4643 | 107 | 6.9721 | 5.0484
[7 empty] | 4644 | 108 | 8.5652 | 6.2511
[7 empty] | 4645 | 109 | 7.8957 | 5.7457
[7 empty] | 4646 | 110 | 7.4381 | 5.4002
[7 empty] | 4647 | 111 | 7.2771 | 5.2787
[7 empty] | 4648 | 112 | 7.3449 | 5.3299
[7 empty] | 4649 | 113 | 6.9975 | 5.0676
[7 empty] | 4650 | 114 | 7.167 | 5.1955
[7 empty] | 4651 | 115 | 6.7094 | 4.8501
[7 empty] | 4652 | 116 | 7.3958 | 5.3683
[7 empty] | 4653 | 117 | 6.9721 | 5.0484
[7 empty] | 4654 | 118 | 6.1924 | 4.4598
[7 empty] | 4655 | 119 | 4.5824 | 3.2443
[7 empty] | 4656 | 120 | 4.2615 | 3.0021
[7 empty] | 4657 | 121 | 3.5232 | 2.4446
[7 empty] | 4658 | 122 | 3.1079 | 2.1312
[7 empty] | 4659 | 123 | 3.0232 | 2.0672
[7 empty] | 4660 | 124 | 2.9893 | 2.0416
[7 empty] | 4661 | 125 | 2.9469 | 2.0096
[7 empty] | 4662 | 126 | 3.091 | 2.1184
[7 empty] | 4663 | 127 | 4.6163 | 3.2699
[7 empty] | 4664 | 128 | 6.1924 | 4.4598
[7 empty] | 4665 | 129 | 6.8788 | 4.978
[7 empty] | 4666 | 130 | 7.3195 | 5.3107
[7 empty] | 4667 | 131 | 7.4805 | 5.4322
[7 empty] | 4668 | 132 | 7.2263 | 5.2403
[7 empty] | 4669 | 133 | 7.8703 | 5.7265
[7 empty] | 4670 | 134 | 8.1754 | 5.9568
[7 empty] | 4671 | 135 | 8.2431 | 6.008
[7 empty] | 4672 | 136 | 7.4212 | 5.3875
[7 empty] | 4673 | 137 | 7.3195 | 5.3107
[7 empty] | 4674 | 138 | 7.2686 | 5.2723
[7 empty] | 4675 | 139 | 6.9297 | 5.0164
[7 empty] | 4676 | 140 | 6.9382 | 5.0228
[7 empty] | 4677 | 141 | 6.2772 | 4.5238
[7 empty] | 4678 | 142 | 5.6332 | 4.0376
[7 empty] | 4679 | 143 | 4.7434 | 3.3659
[7 empty] | 4680 | 144 | 4.1248 | 2.8989
[7 empty] | 4681 | 145 | 3.6503 | 2.5406
[7 empty] | 4682 | 146 | 3.4384 | 2.3807
[7 empty] | 4683 | 147 | 3.3706 | 2.3295
[7 empty] | 4684 | 148 | 3.3622 | 2.3231
[7 empty] | 4685 | 149 | 3.3622 | 2.3231
[7 empty] | 4686 | 150 | 3.3706 | 2.3295
[7 empty] | 4687 | 151 | 4.4638 | 3.1547
[7 empty] | 4688 | 152 | 6.006 | 4.3191
[7 empty] | 4689 | 153 | 6.6246 | 4.7861
[7 empty] | 4690 | 154 | 7.1924 | 5.2147
[7 empty] | 4691 | 155 | 7.0398 | 5.0996
[7 empty] | 4692 | 156 | 7.2093 | 5.2275
[7 empty] | 4693 | 157 | 7.9296 | 5.7713
[7 empty] | 4694 | 158 | 8.2601 | 6.0208
[7 empty] | 4695 | 159 | 8.5313 | 6.2255
[7 empty] | 4696 | 160 | 8.4041 | 6.1296
[7 empty] | 4697 | 161 | 9.1753 | 6.7117
[7 empty] | 4698 | 162 | 8.6753 | 6.3343
[7 empty] | 4699 | 163 | 9.0397 | 6.6094
[7 empty] | 4700 | 164 | 7.6754 | 5.5794
[7 empty] | 4701 | 165 | 10.8362 | 7.9656
[7 empty] | 4702 | 166 | 8.7685 | 6.4046
[7 empty] | 4703 | 167 | 5.1247 | 3.6537
[7 empty] | 4704 | 168 | 4.4722 | 3.1611
[7 empty] | 4705 | 1 | 2.9978 | 2.048
[7 empty] | 4706 | 2 | 2.8876 | 1.9648
[7 empty] | 4707 | 3 | 2.8791 | 1.9584
[7 empty] | 4708 | 4 | 3.0147 | 2.0608
[7 empty] | 4709 | 5 | 3.0317 | 2.0736
[7 empty] | 4710 | 6 | 3.4638 | 2.3999
[7 empty] | 4711 | 7 | 4.1926 | 2.95
[7 empty] | 4712 | 8 | 4.8705 | 3.4618
[7 empty] | 4713 | 9 | 4.8451 | 3.4426
[7 empty] | 4714 | 10 | 6.3789 | 4.6006
[7 empty] | 4715 | 11 | 8.4804 | 6.1871
[7 empty] | 4716 | 12 | 9.4549 | 6.9228
[7 empty] | 4717 | 13 | 9.8362 | 7.2107
[7 empty] | 4718 | 14 | 9.6159 | 7.0444
[7 empty] | 4719 | 15 | 9.5227 | 6.974
[7 empty] | 4720 | 16 | 10.7175 | 7.8761
[7 empty] | 4721 | 17 | 12.0564 | 8.8868
[7 empty] | 4722 | 18 | 11.8107 | 8.7013
[7 empty] | 4723 | 19 | 12.3445 | 9.1044
[7 empty] | 4724 | 20 | 12.2767 | 9.0532
[7 empty] | 4725 | 21 | 12.853 | 9.4882
[7 empty] | 4726 | 22 | 8.8533 | 6.4686
[7 empty] | 4727 | 23 | 5.04 | 3.5898
[7 empty] | 4728 | 24 | 3.3504 | 2.3142
[7 empty] | 4729 | 25 | 3.252 | 2.2399
[7 empty] | 4730 | 26 | 3.1418 | 2.1567
[7 empty] | 4731 | 27 | 3.0401 | 2.08
[7 empty] | 4732 | 28 | 3.1249 | 2.144
[7 empty] | 4733 | 29 | 3.3706 | 2.3295
[7 empty] | 4734 | 30 | 3.6164 | 2.515
[7 empty] | 4735 | 31 | 4.4722 | 3.1611
[7 empty] | 4736 | 32 | 4.8281 | 3.4298
[7 empty] | 4737 | 33 | 5.4976 | 3.9352
[7 empty] | 4738 | 34 | 6.4043 | 4.6198
[7 empty] | 4739 | 35 | 8.5991 | 6.2767
[7 empty] | 4740 | 36 | 9.6413 | 7.0636
[7 empty] | 4741 | 37 | 9.7176 | 7.1212
[7 empty] | 4742 | 38 | 9.7939 | 7.1787
[7 empty] | 4743 | 39 | 9.4634 | 6.9292
[7 empty] | 4744 | 40 | 10.5311 | 7.7353
[7 empty] | 4745 | 41 | 11.0904 | 8.1575
[7 empty] | 4746 | 42 | 11.1073 | 8.1703
[7 empty] | 4747 | 43 | 11.4802 | 8.4518
[7 empty] | 4748 | 44 | 12.6496 | 9.3347
[7 empty] | 4749 | 45 | 12.2428 | 9.0276
[7 empty] | 4750 | 46 | 9.4634 | 6.9292
[7 empty] | 4751 | 47 | 5.8196 | 4.1783
[7 empty] | 4752 | 48 | 4.3028 | 3.0332
[7 empty] | 4753 | 49 | 3.6333 | 2.5278
[7 empty] | 4754 | 50 | 3.3198 | 2.2911
[7 empty] | 4755 | 51 | 3.2096 | 2.2079
[7 empty] | 4756 | 52 | 3.2435 | 2.2335
[7 empty] | 4757 | 53 | 3.2689 | 2.2527
[7 empty] | 4758 | 54 | 3.8536 | 2.6941
[7 empty] | 4759 | 55 | 5.0061 | 3.5642
[7 empty] | 4760 | 56 | 5.2518 | 3.7497
[7 empty] | 4761 | 57 | 6.2094 | 4.4726
[7 empty] | 4762 | 58 | 7.328 | 5.3171
[7 empty] | 4763 | 59 | 8.5482 | 6.2383
[7 empty] | 4764 | 60 | 9.1838 | 6.7181
[7 empty] | 4765 | 61 | 9.8701 | 7.2363
[7 empty] | 4766 | 62 | 9.6668 | 7.0828
[7 empty] | 4767 | 63 | 10.2684 | 7.537
[7 empty] | 4768 | 64 | 11.226 | 8.2599
[7 empty] | 4769 | 65 | 11.853 | 8.7333
[7 empty] | 4770 | 66 | 11.7514 | 8.6565
[7 empty] | 4771 | 67 | 12.4971 | 9.2195
[7 empty] | 4772 | 68 | 12.7428 | 9.405
[7 empty] | 4773 | 69 | 12.2259 | 9.0148
[7 empty] | 4774 | 70 | 9.904 | 7.2619
[7 empty] | 4775 | 71 | 5.3366 | 3.8137
[7 empty] | 4776 | 72 | 4.2398 | 2.9857
[7 empty] | 4777 | 73 | 3.5147 | 2.4382
[7 empty] | 4778 | 74 | 3.2859 | 2.2655
[7 empty] | 4779 | 75 | 3.1842 | 2.1887
[7 empty] | 4780 | 76 | 3.1249 | 2.144
[7 empty] | 4781 | 77 | 3.3028 | 2.2783
[7 empty] | 4782 | 78 | 3.7096 | 2.5854
[7 empty] | 4783 | 79 | 4.8366 | 3.4362
[7 empty] | 4784 | 80 | 5.0146 | 3.5706
[7 empty] | 4785 | 81 | 6.2094 | 4.4726
[7 empty] | 4786 | 82 | 7.311 | 5.3043
[7 empty] | 4787 | 83 | 8.0567 | 5.8673
[7 empty] | 4788 | 84 | 9.3109 | 6.8141
[7 empty] | 4789 | 85 | 9.0058 | 6.5838
[7 empty] | 4790 | 86 | 8.4889 | 6.1935
[7 empty] | 4791 | 87 | 8.938 | 6.5326
[7 empty] | 4792 | 88 | 9.6075 | 7.038
[7 empty] | 4793 | 89 | 10.9718 | 8.068
[7 empty] | 4794 | 90 | 10.3786 | 7.6202
[7 empty] | 4795 | 91 | 11.0734 | 8.1447
[7 empty] | 4796 | 92 | 10.4633 | 7.6841
[7 empty] | 4797 | 93 | 8.0228 | 5.8417
[7 empty] | 4798 | 94 | 7.1076 | 5.1507
[7 empty] | 4799 | 95 | 5.2264 | 3.7305
[7 empty] | 4800 | 96 | 4.2265 | 2.9756
[7 empty] | 4801 | 97 | 4.1757 | 2.9372
[7 empty] | 4802 | 98 | 3.8791 | 2.7133
[7 empty] | 4803 | 99 | 3.8197 | 2.6685
[7 empty] | 4804 | 100 | 3.4638 | 2.3999
[7 empty] | 4805 | 101 | 3.4045 | 2.3551
[7 empty] | 4806 | 102 | 3.6418 | 2.5342
[7 empty] | 4807 | 103 | 4.396 | 3.1036
[7 empty] | 4808 | 104 | 4.6502 | 3.2955
[7 empty] | 4809 | 105 | 5.1417 | 3.6665
[7 empty] | 4810 | 106 | 6.6161 | 4.7797
[7 empty] | 4811 | 107 | 6.9721 | 5.0484
[7 empty] | 4812 | 108 | 8.5652 | 6.2511
[7 empty] | 4813 | 109 | 7.8957 | 5.7457
[7 empty] | 4814 | 110 | 7.4381 | 5.4002
[7 empty] | 4815 | 111 | 7.2771 | 5.2787
[7 empty] | 4816 | 112 | 7.3449 | 5.3299
[7 empty] | 4817 | 113 | 6.9975 | 5.0676
[7 empty] | 4818 | 114 | 7.167 | 5.1955
[7 empty] | 4819 | 115 | 6.7094 | 4.8501
[7 empty] | 4820 | 116 | 7.3958 | 5.3683
[7 empty] | 4821 | 117 | 6.9721 | 5.0484
[7 empty] | 4822 | 118 | 6.1924 | 4.4598
[7 empty] | 4823 | 119 | 4.5824 | 3.2443
[7 empty] | 4824 | 120 | 4.2615 | 3.0021
[7 empty] | 4825 | 121 | 3.5232 | 2.4446
[7 empty] | 4826 | 122 | 3.1079 | 2.1312
[7 empty] | 4827 | 123 | 3.0232 | 2.0672
[7 empty] | 4828 | 124 | 2.9893 | 2.0416
[7 empty] | 4829 | 125 | 2.9469 | 2.0096
[7 empty] | 4830 | 126 | 3.091 | 2.1184
[7 empty] | 4831 | 127 | 4.6163 | 3.2699
[7 empty] | 4832 | 128 | 6.1924 | 4.4598
[7 empty] | 4833 | 129 | 6.8788 | 4.978
[7 empty] | 4834 | 130 | 7.3195 | 5.3107
[7 empty] | 4835 | 131 | 7.4805 | 5.4322
[7 empty] | 4836 | 132 | 7.2263 | 5.2403
[7 empty] | 4837 | 133 | 7.8703 | 5.7265
[7 empty] | 4838 | 134 | 8.1754 | 5.9568
[7 empty] | 4839 | 135 | 8.2431 | 6.008
[7 empty] | 4840 | 136 | 7.4212 | 5.3875
[7 empty] | 4841 | 137 | 7.3195 | 5.3107
[7 empty] | 4842 | 138 | 7.2686 | 5.2723
[7 empty] | 4843 | 139 | 6.9297 | 5.0164
[7 empty] | 4844 | 140 | 6.9382 | 5.0228
[7 empty] | 4845 | 141 | 6.2772 | 4.5238
[7 empty] | 4846 | 142 | 5.6332 | 4.0376
[7 empty] | 4847 | 143 | 4.7434 | 3.3659
[7 empty] | 4848 | 144 | 4.1248 | 2.8989
[7 empty] | 4849 | 145 | 3.6503 | 2.5406
[7 empty] | 4850 | 146 | 3.4384 | 2.3807
[7 empty] | 4851 | 147 | 3.3706 | 2.3295
[7 empty] | 4852 | 148 | 3.3622 | 2.3231
[7 empty] | 4853 | 149 | 3.3622 | 2.3231
[7 empty] | 4854 | 150 | 3.3706 | 2.3295
[7 empty] | 4855 | 151 | 4.4638 | 3.1547
[7 empty] | 4856 | 152 | 6.006 | 4.3191
[7 empty] | 4857 | 153 | 6.6246 | 4.7861
[7 empty] | 4858 | 154 | 7.1924 | 5.2147
[7 empty] | 4859 | 155 | 7.0398 | 5.0996
[7 empty] | 4860 | 156 | 7.2093 | 5.2275
[7 empty] | 4861 | 157 | 7.9296 | 5.7713
[7 empty] | 4862 | 158 | 8.2601 | 6.0208
[7 empty] | 4863 | 159 | 8.5313 | 6.2255
[7 empty] | 4864 | 160 | 8.4041 | 6.1296
[7 empty] | 4865 | 161 | 9.1753 | 6.7117
[7 empty] | 4866 | 162 | 8.6753 | 6.3343
[7 empty] | 4867 | 163 | 9.0397 | 6.6094
[7 empty] | 4868 | 164 | 7.6754 | 5.5794
[7 empty] | 4869 | 165 | 10.8362 | 7.9656
[7 empty] | 4870 | 166 | 8.7685 | 6.4046
[7 empty] | 4871 | 167 | 5.1247 | 3.6537
[7 empty] | 4872 | 168 | 4.4722 | 3.1611
[7 empty] | 4873 | 1 | 2.9978 | 2.048
[7 empty] | 4874 | 2 | 2.8876 | 1.9648
[7 empty] | 4875 | 3 | 2.8791 | 1.9584
[7 empty] | 4876 | 4 | 3.0147 | 2.0608
[7 empty] | 4877 | 5 | 3.0317 | 2.0736
[7 empty] | 4878 | 6 | 3.4638 | 2.3999
[7 empty] | 4879 | 7 | 4.1926 | 2.95
[7 empty] | 4880 | 8 | 4.8705 | 3.4618
[7 empty] | 4881 | 9 | 4.8451 | 3.4426
[7 empty] | 4882 | 10 | 6.3789 | 4.6006
[7 empty] | 4883 | 11 | 8.4804 | 6.1871
[7 empty] | 4884 | 12 | 9.4549 | 6.9228
[7 empty] | 4885 | 13 | 9.8362 | 7.2107
[7 empty] | 4886 | 14 | 9.6159 | 7.0444
[7 empty] | 4887 | 15 | 9.5227 | 6.974
[7 empty] | 4888 | 16 | 10.7175 | 7.8761
[7 empty] | 4889 | 17 | 12.0564 | 8.8868
[7 empty] | 4890 | 18 | 11.8107 | 8.7013
[7 empty] | 4891 | 19 | 12.3445 | 9.1044
[7 empty] | 4892 | 20 | 12.2767 | 9.0532
[7 empty] | 4893 | 21 | 12.853 | 9.4882
[7 empty] | 4894 | 22 | 8.8533 | 6.4686
[7 empty] | 4895 | 23 | 5.04 | 3.5898
[7 empty] | 4896 | 24 | 3.3504 | 2.3142
[7 empty] | 4897 | 25 | 3.252 | 2.2399
[7 empty] | 4898 | 26 | 3.1418 | 2.1567
[7 empty] | 4899 | 27 | 3.0401 | 2.08
[7 empty] | 4900 | 28 | 3.1249 | 2.144
[7 empty] | 4901 | 29 | 3.3706 | 2.3295
[7 empty] | 4902 | 30 | 3.6164 | 2.515
[7 empty] | 4903 | 31 | 4.4722 | 3.1611
[7 empty] | 4904 | 32 | 4.8281 | 3.4298
[7 empty] | 4905 | 33 | 5.4976 | 3.9352
[7 empty] | 4906 | 34 | 6.4043 | 4.6198
[7 empty] | 4907 | 35 | 8.5991 | 6.2767
[7 empty] | 4908 | 36 | 9.6413 | 7.0636
[7 empty] | 4909 | 37 | 9.7176 | 7.1212
[7 empty] | 4910 | 38 | 9.7939 | 7.1787
[7 empty] | 4911 | 39 | 9.4634 | 6.9292
[7 empty] | 4912 | 40 | 10.5311 | 7.7353
[7 empty] | 4913 | 41 | 11.0904 | 8.1575
[7 empty] | 4914 | 42 | 11.1073 | 8.1703
[7 empty] | 4915 | 43 | 11.4802 | 8.4518
[7 empty] | 4916 | 44 | 12.6496 | 9.3347
[7 empty] | 4917 | 45 | 12.2428 | 9.0276
[7 empty] | 4918 | 46 | 9.4634 | 6.9292
[7 empty] | 4919 | 47 | 5.8196 | 4.1783
[7 empty] | 4920 | 48 | 4.3028 | 3.0332
[7 empty] | 4921 | 49 | 3.6333 | 2.5278
[7 empty] | 4922 | 50 | 3.3198 | 2.2911
[7 empty] | 4923 | 51 | 3.2096 | 2.2079
[7 empty] | 4924 | 52 | 3.2435 | 2.2335
[7 empty] | 4925 | 53 | 3.2689 | 2.2527
[7 empty] | 4926 | 54 | 3.8536 | 2.6941
[7 empty] | 4927 | 55 | 5.0061 | 3.5642
[7 empty] | 4928 | 56 | 5.2518 | 3.7497
[7 empty] | 4929 | 57 | 6.2094 | 4.4726
[7 empty] | 4930 | 58 | 7.328 | 5.3171
[7 empty] | 4931 | 59 | 8.5482 | 6.2383
[7 empty] | 4932 | 60 | 9.1838 | 6.7181
[7 empty] | 4933 | 61 | 9.8701 | 7.2363
[7 empty] | 4934 | 62 | 9.6668 | 7.0828
[7 empty] | 4935 | 63 | 10.2684 | 7.537
[7 empty] | 4936 | 64 | 11.226 | 8.2599
[7 empty] | 4937 | 65 | 11.853 | 8.7333
[7 empty] | 4938 | 66 | 11.7514 | 8.6565
[7 empty] | 4939 | 67 | 12.4971 | 9.2195
[7 empty] | 4940 | 68 | 12.7428 | 9.405
[7 empty] | 4941 | 69 | 12.2259 | 9.0148
[7 empty] | 4942 | 70 | 9.904 | 7.2619
[7 empty] | 4943 | 71 | 5.3366 | 3.8137
[7 empty] | 4944 | 72 | 4.2398 | 2.9857
[7 empty] | 4945 | 73 | 3.5147 | 2.4382
[7 empty] | 4946 | 74 | 3.2859 | 2.2655
[7 empty] | 4947 | 75 | 3.1842 | 2.1887
[7 empty] | 4948 | 76 | 3.1249 | 2.144
[7 empty] | 4949 | 77 | 3.3028 | 2.2783
[7 empty] | 4950 | 78 | 3.7096 | 2.5854
[7 empty] | 4951 | 79 | 4.8366 | 3.4362
[7 empty] | 4952 | 80 | 5.0146 | 3.5706
[7 empty] | 4953 | 81 | 6.2094 | 4.4726
[7 empty] | 4954 | 82 | 7.311 | 5.3043
[7 empty] | 4955 | 83 | 8.0567 | 5.8673
[7 empty] | 4956 | 84 | 9.3109 | 6.8141
[7 empty] | 4957 | 85 | 9.0058 | 6.5838
[7 empty] | 4958 | 86 | 8.4889 | 6.1935
[7 empty] | 4959 | 87 | 8.938 | 6.5326
[7 empty] | 4960 | 88 | 9.6075 | 7.038
[7 empty] | 4961 | 89 | 10.9718 | 8.068
[7 empty] | 4962 | 90 | 10.3786 | 7.6202
[7 empty] | 4963 | 91 | 11.0734 | 8.1447
[7 empty] | 4964 | 92 | 10.4633 | 7.6841
[7 empty] | 4965 | 93 | 8.0228 | 5.8417
[7 empty] | 4966 | 94 | 7.1076 | 5.1507
[7 empty] | 4967 | 95 | 5.2264 | 3.7305
[7 empty] | 4968 | 96 | 4.2265 | 2.9756
[7 empty] | 4969 | 97 | 4.1757 | 2.9372
[7 empty] | 4970 | 98 | 3.8791 | 2.7133
[7 empty] | 4971 | 99 | 3.8197 | 2.6685
[7 empty] | 4972 | 100 | 3.4638 | 2.3999
[7 empty] | 4973 | 101 | 3.4045 | 2.3551
[7 empty] | 4974 | 102 | 3.6418 | 2.5342
[7 empty] | 4975 | 103 | 4.396 | 3.1036
[7 empty] | 4976 | 104 | 4.6502 | 3.2955
[7 empty] | 4977 | 105 | 5.1417 | 3.6665
[7 empty] | 4978 | 106 | 6.6161 | 4.7797
[7 empty] | 4979 | 107 | 6.9721 | 5.0484
[7 empty] | 4980 | 108 | 8.5652 | 6.2511
[7 empty] | 4981 | 109 | 7.8957 | 5.7457
[7 empty] | 4982 | 110 | 7.4381 | 5.4002
[7 empty] | 4983 | 111 | 7.2771 | 5.2787
[7 empty] | 4984 | 112 | 7.3449 | 5.3299
[7 empty] | 4985 | 113 | 6.9975 | 5.0676
[7 empty] | 4986 | 114 | 7.167 | 5.1955
[7 empty] | 4987 | 115 | 6.7094 | 4.8501
[7 empty] | 4988 | 116 | 7.3958 | 5.3683
[7 empty] | 4989 | 117 | 6.9721 | 5.0484
[7 empty] | 4990 | 118 | 6.1924 | 4.4598
[7 empty] | 4991 | 119 | 4.5824 | 3.2443
[7 empty] | 4992 | 120 | 4.2615 | 3.0021
[7 empty] | 4993 | 121 | 3.5232 | 2.4446
[7 empty] | 4994 | 122 | 3.1079 | 2.1312
[7 empty] | 4995 | 123 | 3.0232 | 2.0672
[7 empty] | 4996 | 124 | 2.9893 | 2.0416
[7 empty] | 4997 | 125 | 2.9469 | 2.0096
[7 empty] | 4998 | 126 | 3.091 | 2.1184
[7 empty] | 4999 | 127 | 4.6163 | 3.2699
[7 empty] | 5000 | 128 | 6.1924 | 4.4598
[7 empty] | 5001 | 129 | 6.8788 | 4.978
[7 empty] | 5002 | 130 | 7.3195 | 5.3107
[7 empty] | 5003 | 131 | 7.4805 | 5.4322
[7 empty] | 5004 | 132 | 7.2263 | 5.2403
[7 empty] | 5005 | 133 | 7.8703 | 5.7265
[7 empty] | 5006 | 134 | 8.1754 | 5.9568
[7 empty] | 5007 | 135 | 8.2431 | 6.008
[7 empty] | 5008 | 136 | 7.4212 | 5.3875
[7 empty] | 5009 | 137 | 7.3195 | 5.3107
[7 empty] | 5010 | 138 | 7.2686 | 5.2723
[7 empty] | 5011 | 139 | 6.9297 | 5.0164
[7 empty] | 5012 | 140 | 6.9382 | 5.0228
[7 empty] | 5013 | 141 | 6.2772 | 4.5238
[7 empty] | 5014 | 142 | 5.6332 | 4.0376
[7 empty] | 5015 | 143 | 4.7434 | 3.3659
[7 empty] | 5016 | 144 | 4.1248 | 2.8989
[7 empty] | 5017 | 145 | 3.6503 | 2.5406
[7 empty] | 5018 | 146 | 3.4384 | 2.3807
[7 empty] | 5019 | 147 | 3.3706 | 2.3295
[7 empty] | 5020 | 148 | 3.3622 | 2.3231
[7 empty] | 5021 | 149 | 3.3622 | 2.3231
[7 empty] | 5022 | 150 | 3.3706 | 2.3295
[7 empty] | 5023 | 151 | 4.4638 | 3.1547
[7 empty] | 5024 | 152 | 6.006 | 4.3191
[7 empty] | 5025 | 153 | 6.6246 | 4.7861
[7 empty] | 5026 | 154 | 7.1924 | 5.2147
[7 empty] | 5027 | 155 | 7.0398 | 5.0996
[7 empty] | 5028 | 156 | 7.2093 | 5.2275
[7 empty] | 5029 | 157 | 7.9296 | 5.7713
[7 empty] | 5030 | 158 | 8.2601 | 6.0208
[7 empty] | 5031 | 159 | 8.5313 | 6.2255
[7 empty] | 5032 | 160 | 8.4041 | 6.1296
[7 empty] | 5033 | 161 | 9.1753 | 6.7117
[7 empty] | 5034 | 162 | 8.6753 | 6.3343
[7 empty] | 5035 | 163 | 9.0397 | 6.6094
[7 empty] | 5036 | 164 | 7.6754 | 5.5794
[7 empty] | 5037 | 165 | 10.8362 | 7.9656
[7 empty] | 5038 | 166 | 8.7685 | 6.4046
[7 empty] | 5039 | 167 | 5.1247 | 3.6537
[7 empty] | 5040 | 168 | 4.4722 | 3.1611
[7 empty] | 5041 | 1 | 2.9978 | 2.048
[7 empty] | 5042 | 2 | 2.8876 | 1.9648
[7 empty] | 5043 | 3 | 2.8791 | 1.9584
[7 empty] | 5044 | 4 | 3.0147 | 2.0608
[7 empty] | 5045 | 5 | 3.0317 | 2.0736
[7 empty] | 5046 | 6 | 3.4638 | 2.3999
[7 empty] | 5047 | 7 | 4.1926 | 2.95
[7 empty] | 5048 | 8 | 4.8705 | 3.4618
[7 empty] | 5049 | 9 | 4.8451 | 3.4426
[7 empty] | 5050 | 10 | 6.3789 | 4.6006
[7 empty] | 5051 | 11 | 8.4804 | 6.1871
[7 empty] | 5052 | 12 | 9.4549 | 6.9228
[7 empty] | 5053 | 13 | 9.8362 | 7.2107
[7 empty] | 5054 | 14 | 9.6159 | 7.0444
[7 empty] | 5055 | 15 | 9.5227 | 6.974
[7 empty] | 5056 | 16 | 10.7175 | 7.8761
[7 empty] | 5057 | 17 | 12.0564 | 8.8868
[7 empty] | 5058 | 18 | 11.8107 | 8.7013
[7 empty] | 5059 | 19 | 12.3445 | 9.1044
[7 empty] | 5060 | 20 | 12.2767 | 9.0532
[7 empty] | 5061 | 21 | 12.853 | 9.4882
[7 empty] | 5062 | 22 | 8.8533 | 6.4686
[7 empty] | 5063 | 23 | 5.04 | 3.5898
[7 empty] | 5064 | 24 | 3.3504 | 2.3142
[7 empty] | 5065 | 25 | 3.252 | 2.2399
[7 empty] | 5066 | 26 | 3.1418 | 2.1567
[7 empty] | 5067 | 27 | 3.0401 | 2.08
[7 empty] | 5068 | 28 | 3.1249 | 2.144
[7 empty] | 5069 | 29 | 3.3706 | 2.3295
[7 empty] | 5070 | 30 | 3.6164 | 2.515
[7 empty] | 5071 | 31 | 4.4722 | 3.1611
[7 empty] | 5072 | 32 | 4.8281 | 3.4298
[7 empty] | 5073 | 33 | 5.4976 | 3.9352
[7 empty] | 5074 | 34 | 6.4043 | 4.6198
[7 empty] | 5075 | 35 | 8.5991 | 6.2767
[7 empty] | 5076 | 36 | 9.6413 | 7.0636
[7 empty] | 5077 | 37 | 9.7176 | 7.1212
[7 empty] | 5078 | 38 | 9.7939 | 7.1787
[7 empty] | 5079 | 39 | 9.4634 | 6.9292
[7 empty] | 5080 | 40 | 10.5311 | 7.7353
[7 empty] | 5081 | 41 | 11.0904 | 8.1575
[7 empty] | 5082 | 42 | 11.1073 | 8.1703
[7 empty] | 5083 | 43 | 11.4802 | 8.4518
[7 empty] | 5084 | 44 | 12.6496 | 9.3347
[7 empty] | 5085 | 45 | 12.2428 | 9.0276
[7 empty] | 5086 | 46 | 9.4634 | 6.9292
[7 empty] | 5087 | 47 | 5.8196 | 4.1783
[7 empty] | 5088 | 48 | 4.3028 | 3.0332
[7 empty] | 5089 | 49 | 3.6333 | 2.5278
[7 empty] | 5090 | 50 | 3.3198 | 2.2911
[7 empty] | 5091 | 51 | 3.2096 | 2.2079
[7 empty] | 5092 | 52 | 3.2435 | 2.2335
[7 empty] | 5093 | 53 | 3.2689 | 2.2527
[7 empty] | 5094 | 54 | 3.8536 | 2.6941
[7 empty] | 5095 | 55 | 5.0061 | 3.5642
[7 empty] | 5096 | 56 | 5.2518 | 3.7497
[7 empty] | 5097 | 57 | 6.2094 | 4.4726
[7 empty] | 5098 | 58 | 7.328 | 5.3171
[7 empty] | 5099 | 59 | 8.5482 | 6.2383
[7 empty] | 5100 | 60 | 9.1838 | 6.7181
[7 empty] | 5101 | 61 | 9.8701 | 7.2363
[7 empty] | 5102 | 62 | 9.6668 | 7.0828
[7 empty] | 5103 | 63 | 10.2684 | 7.537
[7 empty] | 5104 | 64 | 11.226 | 8.2599
[7 empty] | 5105 | 65 | 11.853 | 8.7333
[7 empty] | 5106 | 66 | 11.7514 | 8.6565
[7 empty] | 5107 | 67 | 12.4971 | 9.2195
[7 empty] | 5108 | 68 | 12.7428 | 9.405
[7 empty] | 5109 | 69 | 12.2259 | 9.0148
[7 empty] | 5110 | 70 | 9.904 | 7.2619
[7 empty] | 5111 | 71 | 5.3366 | 3.8137
[7 empty] | 5112 | 72 | 4.2398 | 2.9857
[7 empty] | 5113 | 73 | 3.5147 | 2.4382
[7 empty] | 5114 | 74 | 3.2859 | 2.2655
[7 empty] | 5115 | 75 | 3.1842 | 2.1887
[7 empty] | 5116 | 76 | 3.1249 | 2.144
[7 empty] | 5117 | 77 | 3.3028 | 2.2783
[7 empty] | 5118 | 78 | 3.7096 | 2.5854
[7 empty] | 5119 | 79 | 4.8366 | 3.4362
[7 empty] | 5120 | 80 | 5.0146 | 3.5706
[7 empty] | 5121 | 81 | 6.2094 | 4.4726
[7 empty] | 5122 | 82 | 7.311 | 5.3043
[7 empty] | 5123 | 83 | 8.0567 | 5.8673
[7 empty] | 5124 | 84 | 9.3109 | 6.8141
[7 empty] | 5125 | 85 | 9.0058 | 6.5838
[7 empty] | 5126 | 86 | 8.4889 | 6.1935
[7 empty] | 5127 | 87 | 8.938 | 6.5326
[7 empty] | 5128 | 88 | 9.6075 | 7.038
[7 empty] | 5129 | 89 | 10.9718 | 8.068
[7 empty] | 5130 | 90 | 10.3786 | 7.6202
[7 empty] | 5131 | 91 | 11.0734 | 8.1447
[7 empty] | 5132 | 92 | 10.4633 | 7.6841
[7 empty] | 5133 | 93 | 8.0228 | 5.8417
[7 empty] | 5134 | 94 | 7.1076 | 5.1507
[7 empty] | 5135 | 95 | 5.2264 | 3.7305
[7 empty] | 5136 | 96 | 4.2265 | 2.9756
[7 empty] | 5137 | 97 | 4.1757 | 2.9372
[7 empty] | 5138 | 98 | 3.8791 | 2.7133
[7 empty] | 5139 | 99 | 3.8197 | 2.6685
[7 empty] | 5140 | 100 | 3.4638 | 2.3999
[7 empty] | 5141 | 101 | 3.4045 | 2.3551
[7 empty] | 5142 | 102 | 3.6418 | 2.5342
[7 empty] | 5143 | 103 | 4.396 | 3.1036
[7 empty] | 5144 | 104 | 4.6502 | 3.2955
[7 empty] | 5145 | 105 | 5.1417 | 3.6665
[7 empty] | 5146 | 106 | 6.6161 | 4.7797
[7 empty] | 5147 | 107 | 6.9721 | 5.0484
[7 empty] | 5148 | 108 | 8.5652 | 6.2511
[7 empty] | 5149 | 109 | 7.8957 | 5.7457
[7 empty] | 5150 | 110 | 7.4381 | 5.4002
[7 empty] | 5151 | 111 | 7.2771 | 5.2787
[7 empty] | 5152 | 112 | 7.3449 | 5.3299
[7 empty] | 5153 | 113 | 6.9975 | 5.0676
[7 empty] | 5154 | 114 | 7.167 | 5.1955
[7 empty] | 5155 | 115 | 6.7094 | 4.8501
[7 empty] | 5156 | 116 | 7.3958 | 5.3683
[7 empty] | 5157 | 117 | 6.9721 | 5.0484
[7 empty] | 5158 | 118 | 6.1924 | 4.4598
[7 empty] | 5159 | 119 | 4.5824 | 3.2443
[7 empty] | 5160 | 120 | 4.2615 | 3.0021
[7 empty] | 5161 | 121 | 3.5232 | 2.4446
[7 empty] | 5162 | 122 | 3.1079 | 2.1312
[7 empty] | 5163 | 123 | 3.0232 | 2.0672
[7 empty] | 5164 | 124 | 2.9893 | 2.0416
[7 empty] | 5165 | 125 | 2.9469 | 2.0096
[7 empty] | 5166 | 126 | 3.091 | 2.1184
[7 empty] | 5167 | 127 | 4.6163 | 3.2699
[7 empty] | 5168 | 128 | 6.1924 | 4.4598
[7 empty] | 5169 | 129 | 6.8788 | 4.978
[7 empty] | 5170 | 130 | 7.3195 | 5.3107
[7 empty] | 5171 | 131 | 7.4805 | 5.4322
[7 empty] | 5172 | 132 | 7.2263 | 5.2403
[7 empty] | 5173 | 133 | 7.8703 | 5.7265
[7 empty] | 5174 | 134 | 8.1754 | 5.9568
[7 empty] | 5175 | 135 | 8.2431 | 6.008
[7 empty] | 5176 | 136 | 7.4212 | 5.3875
[7 empty] | 5177 | 137 | 7.3195 | 5.3107
[7 empty] | 5178 | 138 | 7.2686 | 5.2723
[7 empty] | 5179 | 139 | 6.9297 | 5.0164
[7 empty] | 5180 | 140 | 6.9382 | 5.0228
[7 empty] | 5181 | 141 | 6.2772 | 4.5238
[7 empty] | 5182 | 142 | 5.6332 | 4.0376
[7 empty] | 5183 | 143 | 4.7434 | 3.3659
[7 empty] | 5184 | 144 | 4.1248 | 2.8989
[7 empty] | 5185 | 145 | 3.6503 | 2.5406
[7 empty] | 5186 | 146 | 3.4384 | 2.3807
[7 empty] | 5187 | 147 | 3.3706 | 2.3295
[7 empty] | 5188 | 148 | 3.3622 | 2.3231
[7 empty] | 5189 | 149 | 3.3622 | 2.3231
[7 empty] | 5190 | 150 | 3.3706 | 2.3295
[7 empty] | 5191 | 151 | 4.4638 | 3.1547
[7 empty] | 5192 | 152 | 6.006 | 4.3191
[7 empty] | 5193 | 153 | 6.6246 | 4.7861
[7 empty] | 5194 | 154 | 7.1924 | 5.2147
[7 empty] | 5195 | 155 | 7.0398 | 5.0996
[7 empty] | 5196 | 156 | 7.2093 | 5.2275
[7 empty] | 5197 | 157 | 7.9296 | 5.7713
[7 empty] | 5198 | 158 | 8.2601 | 6.0208
[7 empty] | 5199 | 159 | 8.5313 | 6.2255
[7 empty] | 5200 | 160 | 8.4041 | 6.1296
[7 empty] | 5201 | 161 | 9.1753 | 6.7117
[7 empty] | 5202 | 162 | 8.6753 | 6.3343
[7 empty] | 5203 | 163 | 9.0397 | 6.6094
[7 empty] | 5204 | 164 | 7.6754 | 5.5794
[7 empty] | 5205 | 165 | 10.8362 | 7.9656
[7 empty] | 5206 | 166 | 8.7685 | 6.4046
[7 empty] | 5207 | 167 | 5.1247 | 3.6537
[7 empty] | 5208 | 168 | 4.4722 | 3.1611
[7 empty] | 5209 | 1 | 2.9978 | 2.048
[7 empty] | 5210 | 2 | 2.8876 | 1.9648
[7 empty] | 5211 | 3 | 2.8791 | 1.9584
[7 empty] | 5212 | 4 | 3.0147 | 2.0608
[7 empty] | 5213 | 5 | 3.0317 | 2.0736
[7 empty] | 5214 | 6 | 3.4638 | 2.3999
[7 empty] | 5215 | 7 | 4.1926 | 2.95
[7 empty] | 5216 | 8 | 4.8705 | 3.4618
[7 empty] | 5217 | 9 | 4.8451 | 3.4426
[7 empty] | 5218 | 10 | 6.3789 | 4.6006
[7 empty] | 5219 | 11 | 8.4804 | 6.1871
[7 empty] | 5220 | 12 | 9.4549 | 6.9228
[7 empty] | 5221 | 13 | 9.8362 | 7.2107
[7 empty] | 5222 | 14 | 9.6159 | 7.0444
[7 empty] | 5223 | 15 | 9.5227 | 6.974
[7 empty] | 5224 | 16 | 10.7175 | 7.8761
[7 empty] | 5225 | 17 | 12.0564 | 8.8868
[7 empty] | 5226 | 18 | 11.8107 | 8.7013
[7 empty] | 5227 | 19 | 12.3445 | 9.1044
[7 empty] | 5228 | 20 | 12.2767 | 9.0532
[7 empty] | 5229 | 21 | 12.853 | 9.4882
[7 empty] | 5230 | 22 | 8.8533 | 6.4686
[7 empty] | 5231 | 23 | 5.04 | 3.5898
[7 empty] | 5232 | 24 | 3.3504 | 2.3142
[7 empty] | 5233 | 25 | 3.252 | 2.2399
[7 empty] | 5234 | 26 | 3.1418 | 2.1567
[7 empty] | 5235 | 27 | 3.0401 | 2.08
[7 empty] | 5236 | 28 | 3.1249 | 2.144
[7 empty] | 5237 | 29 | 3.3706 | 2.3295
[7 empty] | 5238 | 30 | 3.6164 | 2.515
[7 empty] | 5239 | 31 | 4.4722 | 3.1611
[7 empty] | 5240 | 32 | 4.8281 | 3.4298
[7 empty] | 5241 | 33 | 5.4976 | 3.9352
[7 empty] | 5242 | 34 | 6.4043 | 4.6198
[7 empty] | 5243 | 35 | 8.5991 | 6.2767
[7 empty] | 5244 | 36 | 9.6413 | 7.0636
[7 empty] | 5245 | 37 | 9.7176 | 7.1212
[7 empty] | 5246 | 38 | 9.7939 | 7.1787
[7 empty] | 5247 | 39 | 9.4634 | 6.9292
[7 empty] | 5248 | 40 | 10.5311 | 7.7353
[7 empty] | 5249 | 41 | 11.0904 | 8.1575
[7 empty] | 5250 | 42 | 11.1073 | 8.1703
[7 empty] | 5251 | 43 | 11.4802 | 8.4518
[7 empty] | 5252 | 44 | 12.6496 | 9.3347
[7 empty] | 5253 | 45 | 12.2428 | 9.0276
[7 empty] | 5254 | 46 | 9.4634 | 6.9292
[7 empty] | 5255 | 47 | 5.8196 | 4.1783
[7 empty] | 5256 | 48 | 4.3028 | 3.0332
[7 empty] | 5257 | 49 | 3.6333 | 2.5278
[7 empty] | 5258 | 50 | 3.3198 | 2.2911
[7 empty] | 5259 | 51 | 3.2096 | 2.2079
[7 empty] | 5260 | 52 | 3.2435 | 2.2335
[7 empty] | 5261 | 53 | 3.2689 | 2.2527
[7 empty] | 5262 | 54 | 3.8536 | 2.6941
[7 empty] | 5263 | 55 | 5.0061 | 3.5642
[7 empty] | 5264 | 56 | 5.2518 | 3.7497
[7 empty] | 5265 | 57 | 6.2094 | 4.4726
[7 empty] | 5266 | 58 | 7.328 | 5.3171
[7 empty] | 5267 | 59 | 8.5482 | 6.2383
[7 empty] | 5268 | 60 | 9.1838 | 6.7181
[7 empty] | 5269 | 61 | 9.8701 | 7.2363
[7 empty] | 5270 | 62 | 9.6668 | 7.0828
[7 empty] | 5271 | 63 | 10.2684 | 7.537
[7 empty] | 5272 | 64 | 11.226 | 8.2599
[7 empty] | 5273 | 65 | 11.853 | 8.7333
[7 empty] | 5274 | 66 | 11.7514 | 8.6565
[7 empty] | 5275 | 67 | 12.4971 | 9.2195
[7 empty] | 5276 | 68 | 12.7428 | 9.405
[7 empty] | 5277 | 69 | 12.2259 | 9.0148
[7 empty] | 5278 | 70 | 9.904 | 7.2619
[7 empty] | 5279 | 71 | 5.3366 | 3.8137
[7 empty] | 5280 | 72 | 4.2398 | 2.9857
[7 empty] | 5281 | 73 | 3.5147 | 2.4382
[7 empty] | 5282 | 74 | 3.2859 | 2.2655
[7 empty] | 5283 | 75 | 3.1842 | 2.1887
[7 empty] | 5284 | 76 | 3.1249 | 2.144
[7 empty] | 5285 | 77 | 3.3028 | 2.2783
[7 empty] | 5286 | 78 | 3.7096 | 2.5854
[7 empty] | 5287 | 79 | 4.8366 | 3.4362
[7 empty] | 5288 | 80 | 5.0146 | 3.5706
[7 empty] | 5289 | 81 | 6.2094 | 4.4726
[7 empty] | 5290 | 82 | 7.311 | 5.3043
[7 empty] | 5291 | 83 | 8.0567 | 5.8673
[7 empty] | 5292 | 84 | 9.3109 | 6.8141
[7 empty] | 5293 | 85 | 9.0058 | 6.5838
[7 empty] | 5294 | 86 | 8.4889 | 6.1935
[7 empty] | 5295 | 87 | 8.938 | 6.5326
[7 empty] | 5296 | 88 | 9.6075 | 7.038
[7 empty] | 5297 | 89 | 10.9718 | 8.068
[7 empty] | 5298 | 90 | 10.3786 | 7.6202
[7 empty] | 5299 | 91 | 11.0734 | 8.1447
[7 empty] | 5300 | 92 | 10.4633 | 7.6841
[7 empty] | 5301 | 93 | 8.0228 | 5.8417
[7 empty] | 5302 | 94 | 7.1076 | 5.1507
[7 empty] | 5303 | 95 | 5.2264 | 3.7305
[7 empty] | 5304 | 96 | 4.2265 | 2.9756
[7 empty] | 5305 | 97 | 4.1757 | 2.9372
[7 empty] | 5306 | 98 | 3.8791 | 2.7133
[7 empty] | 5307 | 99 | 3.8197 | 2.6685
[7 empty] | 5308 | 100 | 3.4638 | 2.3999
[7 empty] | 5309 | 101 | 3.4045 | 2.3551
[7 empty] | 5310 | 102 | 3.6418 | 2.5342
[7 empty] | 5311 | 103 | 4.396 | 3.1036
[7 empty] | 5312 | 104 | 4.6502 | 3.2955
[7 empty] | 5313 | 105 | 5.1417 | 3.6665
[7 empty] | 5314 | 106 | 6.6161 | 4.7797
[7 empty] | 5315 | 107 | 6.9721 | 5.0484
[7 empty] | 5316 | 108 | 8.5652 | 6.2511
[7 empty] | 5317 | 109 | 7.8957 | 5.7457
[7 empty] | 5318 | 110 | 7.4381 | 5.4002
[7 empty] | 5319 | 111 | 7.2771 | 5.2787
[7 empty] | 5320 | 112 | 7.3449 | 5.3299
[7 empty] | 5321 | 113 | 6.9975 | 5.0676
[7 empty] | 5322 | 114 | 7.167 | 5.1955
[7 empty] | 5323 | 115 | 6.7094 | 4.8501
[7 empty] | 5324 | 116 | 7.3958 | 5.3683
[7 empty] | 5325 | 117 | 6.9721 | 5.0484
[7 empty] | 5326 | 118 | 6.1924 | 4.4598
[7 empty] | 5327 | 119 | 4.5824 | 3.2443
[7 empty] | 5328 | 120 | 4.2615 | 3.0021
[7 empty] | 5329 | 121 | 3.5232 | 2.4446
[7 empty] | 5330 | 122 | 3.1079 | 2.1312
[7 empty] | 5331 | 123 | 3.0232 | 2.0672
[7 empty] | 5332 | 124 | 2.9893 | 2.0416
[7 empty] | 5333 | 125 | 2.9469 | 2.0096
[7 empty] | 5334 | 126 | 3.091 | 2.1184
[7 empty] | 5335 | 127 | 4.6163 | 3.2699
[7 empty] | 5336 | 128 | 6.1924 | 4.4598
[7 empty] | 5337 | 129 | 6.8788 | 4.978
[7 empty] | 5338 | 130 | 7.3195 | 5.3107
[7 empty] | 5339 | 131 | 7.4805 | 5.4322
[7 empty] | 5340 | 132 | 7.2263 | 5.2403
[7 empty] | 5341 | 133 | 7.8703 | 5.7265
[7 empty] | 5342 | 134 | 8.1754 | 5.9568
[7 empty] | 5343 | 135 | 8.2431 | 6.008
[7 empty] | 5344 | 136 | 7.4212 | 5.3875
[7 empty] | 5345 | 137 | 7.3195 | 5.3107
[7 empty] | 5346 | 138 | 7.2686 | 5.2723
[7 empty] | 5347 | 139 | 6.9297 | 5.0164
[7 empty] | 5348 | 140 | 6.9382 | 5.0228
[7 empty] | 5349 | 141 | 6.2772 | 4.5238
[7 empty] | 5350 | 142 | 5.6332 | 4.0376
[7 empty] | 5351 | 143 | 4.7434 | 3.3659
[7 empty] | 5352 | 144 | 4.1248 | 2.8989
[7 empty] | 5353 | 145 | 3.6503 | 2.5406
[7 empty] | 5354 | 146 | 3.4384 | 2.3807
[7 empty] | 5355 | 147 | 3.3706 | 2.3295
[7 empty] | 5356 | 148 | 3.3622 | 2.3231
[7 empty] | 5357 | 149 | 3.3622 | 2.3231
[7 empty] | 5358 | 150 | 3.3706 | 2.3295
[7 empty] | 5359 | 151 | 4.4638 | 3.1547
[7 empty] | 5360 | 152 | 6.006 | 4.3191
[7 empty] | 5361 | 153 | 6.6246 | 4.7861
[7 empty] | 5362 | 154 | 7.1924 | 5.2147
[7 empty] | 5363 | 155 | 7.0398 | 5.0996
[7 empty] | 5364 | 156 | 7.2093 | 5.2275
[7 empty] | 5365 | 157 | 7.9296 | 5.7713
[7 empty] | 5366 | 158 | 8.2601 | 6.0208
[7 empty] | 5367 | 159 | 8.5313 | 6.2255
[7 empty] | 5368 | 160 | 8.4041 | 6.1296
[7 empty] | 5369 | 161 | 9.1753 | 6.7117
[7 empty] | 5370 | 162 | 8.6753 | 6.3343
[7 empty] | 5371 | 163 | 9.0397 | 6.6094
[7 empty] | 5372 | 164 | 7.6754 | 5.5794
[7 empty] | 5373 | 165 | 10.8362 | 7.9656
[7 empty] | 5374 | 166 | 8.7685 | 6.4046
[7 empty] | 5375 | 167 | 5.1247 | 3.6537
[7 empty] | 5376 | 168 | 4.4722 | 3.1611
[7 empty] | 5377 | 1 | 2.9978 | 2.048
[7 empty] | 5378 | 2 | 2.8876 | 1.9648
[7 empty] | 5379 | 3 | 2.8791 | 1.9584
[7 empty] | 5380 | 4 | 3.0147 | 2.0608
[7 empty] | 5381 | 5 | 3.0317 | 2.0736
[7 empty] | 5382 | 6 | 3.4638 | 2.3999
[7 empty] | 5383 | 7 | 4.1926 | 2.95
[7 empty] | 5384 | 8 | 4.8705 | 3.4618
[7 empty] | 5385 | 9 | 4.8451 | 3.4426
[7 empty] | 5386 | 10 | 6.3789 | 4.6006
[7 empty] | 5387 | 11 | 8.4804 | 6.1871
[7 empty] | 5388 | 12 | 9.4549 | 6.9228
[7 empty] | 5389 | 13 | 9.8362 | 7.2107
[7 empty] | 5390 | 14 | 9.6159 | 7.0444
[7 empty] | 5391 | 15 | 9.5227 | 6.974
[7 empty] | 5392 | 16 | 10.7175 | 7.8761
[7 empty] | 5393 | 17 | 12.0564 | 8.8868
[7 empty] | 5394 | 18 | 11.8107 | 8.7013
[7 empty] | 5395 | 19 | 12.3445 | 9.1044
[7 empty] | 5396 | 20 | 12.2767 | 9.0532
[7 empty] | 5397 | 21 | 12.853 | 9.4882
[7 empty] | 5398 | 22 | 8.8533 | 6.4686
[7 empty] | 5399 | 23 | 5.04 | 3.5898
[7 empty] | 5400 | 24 | 3.3504 | 2.3142
[7 empty] | 5401 | 25 | 3.252 | 2.2399
[7 empty] | 5402 | 26 | 3.1418 | 2.1567
[7 empty] | 5403 | 27 | 3.0401 | 2.08
[7 empty] | 5404 | 28 | 3.1249 | 2.144
[7 empty] | 5405 | 29 | 3.3706 | 2.3295
[7 empty] | 5406 | 30 | 3.6164 | 2.515
[7 empty] | 5407 | 31 | 4.4722 | 3.1611
[7 empty] | 5408 | 32 | 4.8281 | 3.4298
[7 empty] | 5409 | 33 | 5.4976 | 3.9352
[7 empty] | 5410 | 34 | 6.4043 | 4.6198
[7 empty] | 5411 | 35 | 8.5991 | 6.2767
[7 empty] | 5412 | 36 | 9.6413 | 7.0636
[7 empty] | 5413 | 37 | 9.7176 | 7.1212
[7 empty] | 5414 | 38 | 9.7939 | 7.1787
[7 empty] | 5415 | 39 | 9.4634 | 6.9292
[7 empty] | 5416 | 40 | 10.5311 | 7.7353
[7 empty] | 5417 | 41 | 11.0904 | 8.1575
[7 empty] | 5418 | 42 | 11.1073 | 8.1703
[7 empty] | 5419 | 43 | 11.4802 | 8.4518
[7 empty] | 5420 | 44 | 12.6496 | 9.3347
[7 empty] | 5421 | 45 | 12.2428 | 9.0276
[7 empty] | 5422 | 46 | 9.4634 | 6.9292
[7 empty] | 5423 | 47 | 5.8196 | 4.1783
[7 empty] | 5424 | 48 | 4.3028 | 3.0332
[7 empty] | 5425 | 49 | 3.6333 | 2.5278
[7 empty] | 5426 | 50 | 3.3198 | 2.2911
[7 empty] | 5427 | 51 | 3.2096 | 2.2079
[7 empty] | 5428 | 52 | 3.2435 | 2.2335
[7 empty] | 5429 | 53 | 3.2689 | 2.2527
[7 empty] | 5430 | 54 | 3.8536 | 2.6941
[7 empty] | 5431 | 55 | 5.0061 | 3.5642
[7 empty] | 5432 | 56 | 5.2518 | 3.7497
[7 empty] | 5433 | 57 | 6.2094 | 4.4726
[7 empty] | 5434 | 58 | 7.328 | 5.3171
[7 empty] | 5435 | 59 | 8.5482 | 6.2383
[7 empty] | 5436 | 60 | 9.1838 | 6.7181
[7 empty] | 5437 | 61 | 9.8701 | 7.2363
[7 empty] | 5438 | 62 | 9.6668 | 7.0828
[7 empty] | 5439 | 63 | 10.2684 | 7.537
[7 empty] | 5440 | 64 | 11.226 | 8.2599
[7 empty] | 5441 | 65 | 11.853 | 8.7333
[7 empty] | 5442 | 66 | 11.7514 | 8.6565
[7 empty] | 5443 | 67 | 12.4971 | 9.2195
[7 empty] | 5444 | 68 | 12.7428 | 9.405
[7 empty] | 5445 | 69 | 12.2259 | 9.0148
[7 empty] | 5446 | 70 | 9.904 | 7.2619
[7 empty] | 5447 | 71 | 5.3366 | 3.8137
[7 empty] | 5448 | 72 | 4.2398 | 2.9857
[7 empty] | 5449 | 73 | 3.5147 | 2.4382
[7 empty] | 5450 | 74 | 3.2859 | 2.2655
[7 empty] | 5451 | 75 | 3.1842 | 2.1887
[7 empty] | 5452 | 76 | 3.1249 | 2.144
[7 empty] | 5453 | 77 | 3.3028 | 2.2783
[7 empty] | 5454 | 78 | 3.7096 | 2.5854
[7 empty] | 5455 | 79 | 4.8366 | 3.4362
[7 empty] | 5456 | 80 | 5.0146 | 3.5706
[7 empty] | 5457 | 81 | 6.2094 | 4.4726
[7 empty] | 5458 | 82 | 7.311 | 5.3043
[7 empty] | 5459 | 83 | 8.0567 | 5.8673
[7 empty] | 5460 | 84 | 9.3109 | 6.8141
[7 empty] | 5461 | 85 | 9.0058 | 6.5838
[7 empty] | 5462 | 86 | 8.4889 | 6.1935
[7 empty] | 5463 | 87 | 8.938 | 6.5326
[7 empty] | 5464 | 88 | 9.6075 | 7.038
[7 empty] | 5465 | 89 | 10.9718 | 8.068
[7 empty] | 5466 | 90 | 10.3786 | 7.6202
[7 empty] | 5467 | 91 | 11.0734 | 8.1447
[7 empty] | 5468 | 92 | 10.4633 | 7.6841
[7 empty] | 5469 | 93 | 8.0228 | 5.8417
[7 empty] | 5470 | 94 | 7.1076 | 5.1507
[7 empty] | 5471 | 95 | 5.2264 | 3.7305
[7 empty] | 5472 | 96 | 4.2265 | 2.9756
[7 empty] | 5473 | 97 | 4.1757 | 2.9372
[7 empty] | 5474 | 98 | 3.8791 | 2.7133
[7 empty] | 5475 | 99 | 3.8197 | 2.6685
[7 empty] | 5476 | 100 | 3.4638 | 2.3999
[7 empty] | 5477 | 101 | 3.4045 | 2.3551
[7 empty] | 5478 | 102 | 3.6418 | 2.5342
[7 empty] | 5479 | 103 | 4.396 | 3.1036
[7 empty] | 5480 | 104 | 4.6502 | 3.2955
[7 empty] | 5481 | 105 | 5.1417 | 3.6665
[7 empty] | 5482 | 106 | 6.6161 | 4.7797
[7 empty] | 5483 | 107 | 6.9721 | 5.0484
[7 empty] | 5484 | 108 | 8.5652 | 6.2511
[7 empty] | 5485 | 109 | 7.8957 | 5.7457
[7 empty] | 5486 | 110 | 7.4381 | 5.4002
[7 empty] | 5487 | 111 | 7.2771 | 5.2787
[7 empty] | 5488 | 112 | 7.3449 | 5.3299
[7 empty] | 5489 | 113 | 6.9975 | 5.0676
[7 empty] | 5490 | 114 | 7.167 | 5.1955
[7 empty] | 5491 | 115 | 6.7094 | 4.8501
[7 empty] | 5492 | 116 | 7.3958 | 5.3683
[7 empty] | 5493 | 117 | 6.9721 | 5.0484
[7 empty] | 5494 | 118 | 6.1924 | 4.4598
[7 empty] | 5495 | 119 | 4.5824 | 3.2443
[7 empty] | 5496 | 120 | 4.2615 | 3.0021
[7 empty] | 5497 | 121 | 3.5232 | 2.4446
[7 empty] | 5498 | 122 | 3.1079 | 2.1312
[7 empty] | 5499 | 123 | 3.0232 | 2.0672
[7 empty] | 5500 | 124 | 2.9893 | 2.0416
[7 empty] | 5501 | 125 | 2.9469 | 2.0096
[7 empty] | 5502 | 126 | 3.091 | 2.1184
[7 empty] | 5503 | 127 | 4.6163 | 3.2699
[7 empty] | 5504 | 128 | 6.1924 | 4.4598
[7 empty] | 5505 | 129 | 6.8788 | 4.978
[7 empty] | 5506 | 130 | 7.3195 | 5.3107
[7 empty] | 5507 | 131 | 7.4805 | 5.4322
[7 empty] | 5508 | 132 | 7.2263 | 5.2403
[7 empty] | 5509 | 133 | 7.8703 | 5.7265
[7 empty] | 5510 | 134 | 8.1754 | 5.9568
[7 empty] | 5511 | 135 | 8.2431 | 6.008
[7 empty] | 5512 | 136 | 7.4212 | 5.3875
[7 empty] | 5513 | 137 | 7.3195 | 5.3107
[7 empty] | 5514 | 138 | 7.2686 | 5.2723
[7 empty] | 5515 | 139 | 6.9297 | 5.0164
[7 empty] | 5516 | 140 | 6.9382 | 5.0228
[7 empty] | 5517 | 141 | 6.2772 | 4.5238
[7 empty] | 5518 | 142 | 5.6332 | 4.0376
[7 empty] | 5519 | 143 | 4.7434 | 3.3659
[7 empty] | 5520 | 144 | 4.1248 | 2.8989
[7 empty] | 5521 | 145 | 3.6503 | 2.5406
[7 empty] | 5522 | 146 | 3.4384 | 2.3807
[7 empty] | 5523 | 147 | 3.3706 | 2.3295
[7 empty] | 5524 | 148 | 3.3622 | 2.3231
[7 empty] | 5525 | 149 | 3.3622 | 2.3231
[7 empty] | 5526 | 150 | 3.3706 | 2.3295
[7 empty] | 5527 | 151 | 4.4638 | 3.1547
[7 empty] | 5528 | 152 | 6.006 | 4.3191
[7 empty] | 5529 | 153 | 6.6246 | 4.7861
[7 empty] | 5530 | 154 | 7.1924 | 5.2147
[7 empty] | 5531 | 155 | 7.0398 | 5.0996
[7 empty] | 5532 | 156 | 7.2093 | 5.2275
[7 empty] | 5533 | 157 | 7.9296 | 5.7713
[7 empty] | 5534 | 158 | 8.2601 | 6.0208
[7 empty] | 5535 | 159 | 8.5313 | 6.2255
[7 empty] | 5536 | 160 | 8.4041 | 6.1296
[7 empty] | 5537 | 161 | 9.1753 | 6.7117
[7 empty] | 5538 | 162 | 8.6753 | 6.3343
[7 empty] | 5539 | 163 | 9.0397 | 6.6094
[7 empty] | 5540 | 164 | 7.6754 | 5.5794
[7 empty] | 5541 | 165 | 10.8362 | 7.9656
[7 empty] | 5542 | 166 | 8.7685 | 6.4046
[7 empty] | 5543 | 167 | 5.1247 | 3.6537
[7 empty] | 5544 | 168 | 4.4722 | 3.1611
[7 empty] | 5545 | 1 | 2.9978 | 2.048
[7 empty] | 5546 | 2 | 2.8876 | 1.9648
[7 empty] | 5547 | 3 | 2.8791 | 1.9584
[7 empty] | 5548 | 4 | 3.0147 | 2.0608
[7 empty] | 5549 | 5 | 3.0317 | 2.0736
[7 empty] | 5550 | 6 | 3.4638 | 2.3999
[7 empty] | 5551 | 7 | 4.1926 | 2.95
[7 empty] | 5552 | 8 | 4.8705 | 3.4618
[7 empty] | 5553 | 9 | 4.8451 | 3.4426
[7 empty] | 5554 | 10 | 6.3789 | 4.6006
[7 empty] | 5555 | 11 | 8.4804 | 6.1871
[7 empty] | 5556 | 12 | 9.4549 | 6.9228
[7 empty] | 5557 | 13 | 9.8362 | 7.2107
[7 empty] | 5558 | 14 | 9.6159 | 7.0444
[7 empty] | 5559 | 15 | 9.5227 | 6.974
[7 empty] | 5560 | 16 | 10.7175 | 7.8761
[7 empty] | 5561 | 17 | 12.0564 | 8.8868
[7 empty] | 5562 | 18 | 11.8107 | 8.7013
[7 empty] | 5563 | 19 | 12.3445 | 9.1044
[7 empty] | 5564 | 20 | 12.2767 | 9.0532
[7 empty] | 5565 | 21 | 12.853 | 9.4882
[7 empty] | 5566 | 22 | 8.8533 | 6.4686
[7 empty] | 5567 | 23 | 5.04 | 3.5898
[7 empty] | 5568 | 24 | 3.3504 | 2.3142
[7 empty] | 5569 | 25 | 3.252 | 2.2399
[7 empty] | 5570 | 26 | 3.1418 | 2.1567
[7 empty] | 5571 | 27 | 3.0401 | 2.08
[7 empty] | 5572 | 28 | 3.1249 | 2.144
[7 empty] | 5573 | 29 | 3.3706 | 2.3295
[7 empty] | 5574 | 30 | 3.6164 | 2.515
[7 empty] | 5575 | 31 | 4.4722 | 3.1611
[7 empty] | 5576 | 32 | 4.8281 | 3.4298
[7 empty] | 5577 | 33 | 5.4976 | 3.9352
[7 empty] | 5578 | 34 | 6.4043 | 4.6198
[7 empty] | 5579 | 35 | 8.5991 | 6.2767
[7 empty] | 5580 | 36 | 9.6413 | 7.0636
[7 empty] | 5581 | 37 | 9.7176 | 7.1212
[7 empty] | 5582 | 38 | 9.7939 | 7.1787
[7 empty] | 5583 | 39 | 9.4634 | 6.9292
[7 empty] | 5584 | 40 | 10.5311 | 7.7353
[7 empty] | 5585 | 41 | 11.0904 | 8.1575
[7 empty] | 5586 | 42 | 11.1073 | 8.1703
[7 empty] | 5587 | 43 | 11.4802 | 8.4518
[7 empty] | 5588 | 44 | 12.6496 | 9.3347
[7 empty] | 5589 | 45 | 12.2428 | 9.0276
[7 empty] | 5590 | 46 | 9.4634 | 6.9292
[7 empty] | 5591 | 47 | 5.8196 | 4.1783
[7 empty] | 5592 | 48 | 4.3028 | 3.0332
[7 empty] | 5593 | 49 | 3.6333 | 2.5278
[7 empty] | 5594 | 50 | 3.3198 | 2.2911
[7 empty] | 5595 | 51 | 3.2096 | 2.2079
[7 empty] | 5596 | 52 | 3.2435 | 2.2335
[7 empty] | 5597 | 53 | 3.2689 | 2.2527
[7 empty] | 5598 | 54 | 3.8536 | 2.6941
[7 empty] | 5599 | 55 | 5.0061 | 3.5642
[7 empty] | 5600 | 56 | 5.2518 | 3.7497
[7 empty] | 5601 | 57 | 6.2094 | 4.4726
[7 empty] | 5602 | 58 | 7.328 | 5.3171
[7 empty] | 5603 | 59 | 8.5482 | 6.2383
[7 empty] | 5604 | 60 | 9.1838 | 6.7181
[7 empty] | 5605 | 61 | 9.8701 | 7.2363
[7 empty] | 5606 | 62 | 9.6668 | 7.0828
[7 empty] | 5607 | 63 | 10.2684 | 7.537
[7 empty] | 5608 | 64 | 11.226 | 8.2599
[7 empty] | 5609 | 65 | 11.853 | 8.7333
[7 empty] | 5610 | 66 | 11.7514 | 8.6565
[7 empty] | 5611 | 67 | 12.4971 | 9.2195
[7 empty] | 5612 | 68 | 12.7428 | 9.405
[7 empty] | 5613 | 69 | 12.2259 | 9.0148
[7 empty] | 5614 | 70 | 9.904 | 7.2619
[7 empty] | 5615 | 71 | 5.3366 | 3.8137
[7 empty] | 5616 | 72 | 4.2398 | 2.9857
[7 empty] | 5617 | 73 | 3.5147 | 2.4382
[7 empty] | 5618 | 74 | 3.2859 | 2.2655
[7 empty] | 5619 | 75 | 3.1842 | 2.1887
[7 empty] | 5620 | 76 | 3.1249 | 2.144
[7 empty] | 5621 | 77 | 3.3028 | 2.2783
[7 empty] | 5622 | 78 | 3.7096 | 2.5854
[7 empty] | 5623 | 79 | 4.8366 | 3.4362
[7 empty] | 5624 | 80 | 5.0146 | 3.5706
[7 empty] | 5625 | 81 | 6.2094 | 4.4726
[7 empty] | 5626 | 82 | 7.311 | 5.3043
[7 empty] | 5627 | 83 | 8.0567 | 5.8673
[7 empty] | 5628 | 84 | 9.3109 | 6.8141
[7 empty] | 5629 | 85 | 9.0058 | 6.5838
[7 empty] | 5630 | 86 | 8.4889 | 6.1935
[7 empty] | 5631 | 87 | 8.938 | 6.5326
[7 empty] | 5632 | 88 | 9.6075 | 7.038
[7 empty] | 5633 | 89 | 10.9718 | 8.068
[7 empty] | 5634 | 90 | 10.3786 | 7.6202
[7 empty] | 5635 | 91 | 11.0734 | 8.1447
[7 empty] | 5636 | 92 | 10.4633 | 7.6841
[7 empty] | 5637 | 93 | 8.0228 | 5.8417
[7 empty] | 5638 | 94 | 7.1076 | 5.1507
[7 empty] | 5639 | 95 | 5.2264 | 3.7305
[7 empty] | 5640 | 96 | 4.2265 | 2.9756
[7 empty] | 5641 | 97 | 4.1757 | 2.9372
[7 empty] | 5642 | 98 | 3.8791 | 2.7133
[7 empty] | 5643 | 99 | 3.8197 | 2.6685
[7 empty] | 5644 | 100 | 3.4638 | 2.3999
[7 empty] | 5645 | 101 | 3.4045 | 2.3551
[7 empty] | 5646 | 102 | 3.6418 | 2.5342
[7 empty] | 5647 | 103 | 4.396 | 3.1036
[7 empty] | 5648 | 104 | 4.6502 | 3.2955
[7 empty] | 5649 | 105 | 5.1417 | 3.6665
[7 empty] | 5650 | 106 | 6.6161 | 4.7797
[7 empty] | 5651 | 107 | 6.9721 | 5.0484
[7 empty] | 5652 | 108 | 8.5652 | 6.2511
[7 empty] | 5653 | 109 | 7.8957 | 5.7457
[7 empty] | 5654 | 110 | 7.4381 | 5.4002
[7 empty] | 5655 | 111 | 7.2771 | 5.2787
[7 empty] | 5656 | 112 | 7.3449 | 5.3299
[7 empty] | 5657 | 113 | 6.9975 | 5.0676
[7 empty] | 5658 | 114 | 7.167 | 5.1955
[7 empty] | 5659 | 115 | 6.7094 | 4.8501
[7 empty] | 5660 | 116 | 7.3958 | 5.3683
[7 empty] | 5661 | 117 | 6.9721 | 5.0484
[7 empty] | 5662 | 118 | 6.1924 | 4.4598
[7 empty] | 5663 | 119 | 4.5824 | 3.2443
[7 empty] | 5664 | 120 | 4.2615 | 3.0021
[7 empty] | 5665 | 121 | 3.5232 | 2.4446
[7 empty] | 5666 | 122 | 3.1079 | 2.1312
[7 empty] | 5667 | 123 | 3.0232 | 2.0672
[7 empty] | 5668 | 124 | 2.9893 | 2.0416
[7 empty] | 5669 | 125 | 2.9469 | 2.0096
[7 empty] | 5670 | 126 | 3.091 | 2.1184
[7 empty] | 5671 | 127 | 4.6163 | 3.2699
[7 empty] | 5672 | 128 | 6.1924 | 4.4598
[7 empty] | 5673 | 129 | 6.8788 | 4.978
[7 empty] | 5674 | 130 | 7.3195 | 5.3107
[7 empty] | 5675 | 131 | 7.4805 | 5.4322
[7 empty] | 5676 | 132 | 7.2263 | 5.2403
[7 empty] | 5677 | 133 | 7.8703 | 5.7265
[7 empty] | 5678 | 134 | 8.1754 | 5.9568
[7 empty] | 5679 | 135 | 8.2431 | 6.008
[7 empty] | 5680 | 136 | 7.4212 | 5.3875
[7 empty] | 5681 | 137 | 7.3195 | 5.3107
[7 empty] | 5682 | 138 | 7.2686 | 5.2723
[7 empty] | 5683 | 139 | 6.9297 | 5.0164
[7 empty] | 5684 | 140 | 6.9382 | 5.0228
[7 empty] | 5685 | 141 | 6.2772 | 4.5238
[7 empty] | 5686 | 142 | 5.6332 | 4.0376
[7 empty] | 5687 | 143 | 4.7434 | 3.3659
[7 empty] | 5688 | 144 | 4.1248 | 2.8989
[7 empty] | 5689 | 145 | 3.6503 | 2.5406
[7 empty] | 5690 | 146 | 3.4384 | 2.3807
[7 empty] | 5691 | 147 | 3.3706 | 2.3295
[7 empty] | 5692 | 148 | 3.3622 | 2.3231
[7 empty] | 5693 | 149 | 3.3622 | 2.3231
[7 empty] | 5694 | 150 | 3.3706 | 2.3295
[7 empty] | 5695 | 151 | 4.4638 | 3.1547
[7 empty] | 5696 | 152 | 6.006 | 4.3191
[7 empty] | 5697 | 153 | 6.6246 | 4.7861
[7 empty] | 5698 | 154 | 7.1924 | 5.2147
[7 empty] | 5699 | 155 | 7.0398 | 5.0996
[7 empty] | 5700 | 156 | 7.2093 | 5.2275
[7 empty] | 5701 | 157 | 7.9296 | 5.7713
[7 empty] | 5702 | 158 | 8.2601 | 6.0208
[7 empty] | 5703 | 159 | 8.5313 | 6.2255
[7 empty] | 5704 | 160 | 8.4041 | 6.1296
[7 empty] | 5705 | 161 | 9.1753 | 6.7117
[7 empty] | 5706 | 162 | 8.6753 | 6.3343
[7 empty] | 5707 | 163 | 9.0397 | 6.6094
[7 empty] | 5708 | 164 | 7.6754 | 5.5794
[7 empty] | 5709 | 165 | 10.8362 | 7.9656
[7 empty] | 5710 | 166 | 8.7685 | 6.4046
[7 empty] | 5711 | 167 | 5.1247 | 3.6537
[7 empty] | 5712 | 168 | 4.4722 | 3.1611
[7 empty] | 5713 | 1 | 2.9978 | 2.048
[7 empty] | 5714 | 2 | 2.8876 | 1.9648
[7 empty] | 5715 | 3 | 2.8791 | 1.9584
[7 empty] | 5716 | 4 | 3.0147 | 2.0608
[7 empty] | 5717 | 5 | 3.0317 | 2.0736
[7 empty] | 5718 | 6 | 3.4638 | 2.3999
[7 empty] | 5719 | 7 | 4.1926 | 2.95
[7 empty] | 5720 | 8 | 4.8705 | 3.4618
[7 empty] | 5721 | 9 | 4.8451 | 3.4426
[7 empty] | 5722 | 10 | 6.3789 | 4.6006
[7 empty] | 5723 | 11 | 8.4804 | 6.1871
[7 empty] | 5724 | 12 | 9.4549 | 6.9228
[7 empty] | 5725 | 13 | 9.8362 | 7.2107
[7 empty] | 5726 | 14 | 9.6159 | 7.0444
[7 empty] | 5727 | 15 | 9.5227 | 6.974
[7 empty] | 5728 | 16 | 10.7175 | 7.8761
[7 empty] | 5729 | 17 | 12.0564 | 8.8868
[7 empty] | 5730 | 18 | 11.8107 | 8.7013
[7 empty] | 5731 | 19 | 12.3445 | 9.1044
[7 empty] | 5732 | 20 | 12.2767 | 9.0532
[7 empty] | 5733 | 21 | 12.853 | 9.4882
[7 empty] | 5734 | 22 | 8.8533 | 6.4686
[7 empty] | 5735 | 23 | 5.04 | 3.5898
[7 empty] | 5736 | 24 | 3.3504 | 2.3142
[7 empty] | 5737 | 25 | 3.252 | 2.2399
[7 empty] | 5738 | 26 | 3.1418 | 2.1567
[7 empty] | 5739 | 27 | 3.0401 | 2.08
[7 empty] | 5740 | 28 | 3.1249 | 2.144
[7 empty] | 5741 | 29 | 3.3706 | 2.3295
[7 empty] | 5742 | 30 | 3.6164 | 2.515
[7 empty] | 5743 | 31 | 4.4722 | 3.1611
[7 empty] | 5744 | 32 | 4.8281 | 3.4298
[7 empty] | 5745 | 33 | 5.4976 | 3.9352
[7 empty] | 5746 | 34 | 6.4043 | 4.6198
[7 empty] | 5747 | 35 | 8.5991 | 6.2767
[7 empty] | 5748 | 36 | 9.6413 | 7.0636
[7 empty] | 5749 | 37 | 9.7176 | 7.1212
[7 empty] | 5750 | 38 | 9.7939 | 7.1787
[7 empty] | 5751 | 39 | 9.4634 | 6.9292
[7 empty] | 5752 | 40 | 10.5311 | 7.7353
[7 empty] | 5753 | 41 | 11.0904 | 8.1575
[7 empty] | 5754 | 42 | 11.1073 | 8.1703
[7 empty] | 5755 | 43 | 11.4802 | 8.4518
[7 empty] | 5756 | 44 | 12.6496 | 9.3347
[7 empty] | 5757 | 45 | 12.2428 | 9.0276
[7 empty] | 5758 | 46 | 9.4634 | 6.9292
[7 empty] | 5759 | 47 | 5.8196 | 4.1783
[7 empty] | 5760 | 48 | 4.3028 | 3.0332
[7 empty] | 5761 | 49 | 3.6333 | 2.5278
[7 empty] | 5762 | 50 | 3.3198 | 2.2911
[7 empty] | 5763 | 51 | 3.2096 | 2.2079
[7 empty] | 5764 | 52 | 3.2435 | 2.2335
[7 empty] | 5765 | 53 | 3.2689 | 2.2527
[7 empty] | 5766 | 54 | 3.8536 | 2.6941
[7 empty] | 5767 | 55 | 5.0061 | 3.5642
[7 empty] | 5768 | 56 | 5.2518 | 3.7497
[7 empty] | 5769 | 57 | 6.2094 | 4.4726
[7 empty] | 5770 | 58 | 7.328 | 5.3171
[7 empty] | 5771 | 59 | 8.5482 | 6.2383
[7 empty] | 5772 | 60 | 9.1838 | 6.7181
[7 empty] | 5773 | 61 | 9.8701 | 7.2363
[7 empty] | 5774 | 62 | 9.6668 | 7.0828
[7 empty] | 5775 | 63 | 10.2684 | 7.537
[7 empty] | 5776 | 64 | 11.226 | 8.2599
[7 empty] | 5777 | 65 | 11.853 | 8.7333
[7 empty] | 5778 | 66 | 11.7514 | 8.6565
[7 empty] | 5779 | 67 | 12.4971 | 9.2195
[7 empty] | 5780 | 68 | 12.7428 | 9.405
[7 empty] | 5781 | 69 | 12.2259 | 9.0148
[7 empty] | 5782 | 70 | 9.904 | 7.2619
[7 empty] | 5783 | 71 | 5.3366 | 3.8137
[7 empty] | 5784 | 72 | 4.2398 | 2.9857
[7 empty] | 5785 | 73 | 3.5147 | 2.4382
[7 empty] | 5786 | 74 | 3.2859 | 2.2655
[7 empty] | 5787 | 75 | 3.1842 | 2.1887
[7 empty] | 5788 | 76 | 3.1249 | 2.144
[7 empty] | 5789 | 77 | 3.3028 | 2.2783
[7 empty] | 5790 | 78 | 3.7096 | 2.5854
[7 empty] | 5791 | 79 | 4.8366 | 3.4362
[7 empty] | 5792 | 80 | 5.0146 | 3.5706
[7 empty] | 5793 | 81 | 6.2094 | 4.4726
[7 empty] | 5794 | 82 | 7.311 | 5.3043
[7 empty] | 5795 | 83 | 8.0567 | 5.8673
[7 empty] | 5796 | 84 | 9.3109 | 6.8141
[7 empty] | 5797 | 85 | 9.0058 | 6.5838
[7 empty] | 5798 | 86 | 8.4889 | 6.1935
[7 empty] | 5799 | 87 | 8.938 | 6.5326
[7 empty] | 5800 | 88 | 9.6075 | 7.038
[7 empty] | 5801 | 89 | 10.9718 | 8.068
[7 empty] | 5802 | 90 | 10.3786 | 7.6202
[7 empty] | 5803 | 91 | 11.0734 | 8.1447
[7 empty] | 5804 | 92 | 10.4633 | 7.6841
[7 empty] | 5805 | 93 | 8.0228 | 5.8417
[7 empty] | 5806 | 94 | 7.1076 | 5.1507
[7 empty] | 5807 | 95 | 5.2264 | 3.7305
[7 empty] | 5808 | 96 | 4.2265 | 2.9756
[7 empty] | 5809 | 97 | 4.1757 | 2.9372
[7 empty] | 5810 | 98 | 3.8791 | 2.7133
[7 empty] | 5811 | 99 | 3.8197 | 2.6685
[7 empty] | 5812 | 100 | 3.4638 | 2.3999
[7 empty] | 5813 | 101 | 3.4045 | 2.3551
[7 empty] | 5814 | 102 | 3.6418 | 2.5342
[7 empty] | 5815 | 103 | 4.396 | 3.1036
[7 empty] | 5816 | 104 | 4.6502 | 3.2955
[7 empty] | 5817 | 105 | 5.1417 | 3.6665
[7 empty] | 5818 | 106 | 6.6161 | 4.7797
[7 empty] | 5819 | 107 | 6.9721 | 5.0484
[7 empty] | 5820 | 108 | 8.5652 | 6.2511
[7 empty] | 5821 | 109 | 7.8957 | 5.7457
[7 empty] | 5822 | 110 | 7.4381 | 5.4002
[7 empty] | 5823 | 111 | 7.2771 | 5.2787
[7 empty] | 5824 | 112 | 7.3449 | 5.3299
[7 empty] | 5825 | 113 | 6.9975 | 5.0676
[7 empty] | 5826 | 114 | 7.167 | 5.1955
[7 empty] | 5827 | 115 | 6.7094 | 4.8501
[7 empty] | 5828 | 116 | 7.3958 | 5.3683
[7 empty] | 5829 | 117 | 6.9721 | 5.0484
[7 empty] | 5830 | 118 | 6.1924 | 4.4598
[7 empty] | 5831 | 119 | 4.5824 | 3.2443
[7 empty] | 5832 | 120 | 4.2615 | 3.0021
[7 empty] | 5833 | 121 | 3.5232 | 2.4446
[7 empty] | 5834 | 122 | 3.1079 | 2.1312
[7 empty] | 5835 | 123 | 3.0232 | 2.0672
[7 empty] | 5836 | 124 | 2.9893 | 2.0416
[7 empty] | 5837 | 125 | 2.9469 | 2.0096
[7 empty] | 5838 | 126 | 3.091 | 2.1184
[7 empty] | 5839 | 127 | 4.6163 | 3.2699
[7 empty] | 5840 | 128 | 6.1924 | 4.4598
[7 empty] | 5841 | 129 | 6.8788 | 4.978
[7 empty] | 5842 | 130 | 7.3195 | 5.3107
[7 empty] | 5843 | 131 | 7.4805 | 5.4322
[7 empty] | 5844 | 132 | 7.2263 | 5.2403
[7 empty] | 5845 | 133 | 7.8703 | 5.7265
[7 empty] | 5846 | 134 | 8.1754 | 5.9568
[7 empty] | 5847 | 135 | 8.2431 | 6.008
[7 empty] | 5848 | 136 | 7.4212 | 5.3875
[7 empty] | 5849 | 137 | 7.3195 | 5.3107
[7 empty] | 5850 | 138 | 7.2686 | 5.2723
[7 empty] | 5851 | 139 | 6.9297 | 5.0164
[7 empty] | 5852 | 140 | 6.9382 | 5.0228
[7 empty] | 5853 | 141 | 6.2772 | 4.5238
[7 empty] | 5854 | 142 | 5.6332 | 4.0376
[7 empty] | 5855 | 143 | 4.7434 | 3.3659
[7 empty] | 5856 | 144 | 4.1248 | 2.8989
[7 empty] | 5857 | 145 | 3.6503 | 2.5406
[7 empty] | 5858 | 146 | 3.4384 | 2.3807
[7 empty] | 5859 | 147 | 3.3706 | 2.3295
[7 empty] | 5860 | 148 | 3.3622 | 2.3231
[7 empty] | 5861 | 149 | 3.3622 | 2.3231
[7 empty] | 5862 | 150 | 3.3706 | 2.3295
[7 empty] | 5863 | 151 | 4.4638 | 3.1547
[7 empty] | 5864 | 152 | 6.006 | 4.3191
[7 empty] | 5865 | 153 | 6.6246 | 4.7861
[7 empty] | 5866 | 154 | 7.1924 | 5.2147
[7 empty] | 5867 | 155 | 7.0398 | 5.0996
[7 empty] | 5868 | 156 | 7.2093 | 5.2275
[7 empty] | 5869 | 157 | 7.9296 | 5.7713
[7 empty] | 5870 | 158 | 8.2601 | 6.0208
[7 empty] | 5871 | 159 | 8.5313 | 6.2255
[7 empty] | 5872 | 160 | 8.4041 | 6.1296
[7 empty] | 5873 | 161 | 9.1753 | 6.7117
[7 empty] | 5874 | 162 | 8.6753 | 6.3343
[7 empty] | 5875 | 163 | 9.0397 | 6.6094
[7 empty] | 5876 | 164 | 7.6754 | 5.5794
[7 empty] | 5877 | 165 | 10.8362 | 7.9656
[7 empty] | 5878 | 166 | 8.7685 | 6.4046
[7 empty] | 5879 | 167 | 5.1247 | 3.6537
[7 empty] | 5880 | 168 | 4.4722 | 3.1611
[7 empty] | 5881 | 1 | 2.9978 | 2.048
[7 empty] | 5882 | 2 | 2.8876 | 1.9648
[7 empty] | 5883 | 3 | 2.8791 | 1.9584
[7 empty] | 5884 | 4 | 3.0147 | 2.0608
[7 empty] | 5885 | 5 | 3.0317 | 2.0736
[7 empty] | 5886 | 6 | 3.4638 | 2.3999
[7 empty] | 5887 | 7 | 4.1926 | 2.95
[7 empty] | 5888 | 8 | 4.8705 | 3.4618
[7 empty] | 5889 | 9 | 4.8451 | 3.4426
[7 empty] | 5890 | 10 | 6.3789 | 4.6006
[7 empty] | 5891 | 11 | 8.4804 | 6.1871
[7 empty] | 5892 | 12 | 9.4549 | 6.9228
[7 empty] | 5893 | 13 | 9.8362 | 7.2107
[7 empty] | 5894 | 14 | 9.6159 | 7.0444
[7 empty] | 5895 | 15 | 9.5227 | 6.974
[7 empty] | 5896 | 16 | 10.7175 | 7.8761
[7 empty] | 5897 | 17 | 12.0564 | 8.8868
[7 empty] | 5898 | 18 | 11.8107 | 8.7013
[7 empty] | 5899 | 19 | 12.3445 | 9.1044
[7 empty] | 5900 | 20 | 12.2767 | 9.0532
[7 empty] | 5901 | 21 | 12.853 | 9.4882
[7 empty] | 5902 | 22 | 8.8533 | 6.4686
[7 empty] | 5903 | 23 | 5.04 | 3.5898
[7 empty] | 5904 | 24 | 3.3504 | 2.3142
[7 empty] | 5905 | 25 | 3.252 | 2.2399
[7 empty] | 5906 | 26 | 3.1418 | 2.1567
[7 empty] | 5907 | 27 | 3.0401 | 2.08
[7 empty] | 5908 | 28 | 3.1249 | 2.144
[7 empty] | 5909 | 29 | 3.3706 | 2.3295
[7 empty] | 5910 | 30 | 3.6164 | 2.515
[7 empty] | 5911 | 31 | 4.4722 | 3.1611
[7 empty] | 5912 | 32 | 4.8281 | 3.4298
[7 empty] | 5913 | 33 | 5.4976 | 3.9352
[7 empty] | 5914 | 34 | 6.4043 | 4.6198
[7 empty] | 5915 | 35 | 8.5991 | 6.2767
[7 empty] | 5916 | 36 | 9.6413 | 7.0636
[7 empty] | 5917 | 37 | 9.7176 | 7.1212
[7 empty] | 5918 | 38 | 9.7939 | 7.1787
[7 empty] | 5919 | 39 | 9.4634 | 6.9292
[7 empty] | 5920 | 40 | 10.5311 | 7.7353
[7 empty] | 5921 | 41 | 11.0904 | 8.1575
[7 empty] | 5922 | 42 | 11.1073 | 8.1703
[7 empty] | 5923 | 43 | 11.4802 | 8.4518
[7 empty] | 5924 | 44 | 12.6496 | 9.3347
[7 empty] | 5925 | 45 | 12.2428 | 9.0276
[7 empty] | 5926 | 46 | 9.4634 | 6.9292
[7 empty] | 5927 | 47 | 5.8196 | 4.1783
[7 empty] | 5928 | 48 | 4.3028 | 3.0332
[7 empty] | 5929 | 49 | 3.6333 | 2.5278
[7 empty] | 5930 | 50 | 3.3198 | 2.2911
[7 empty] | 5931 | 51 | 3.2096 | 2.2079
[7 empty] | 5932 | 52 | 3.2435 | 2.2335
[7 empty] | 5933 | 53 | 3.2689 | 2.2527
[7 empty] | 5934 | 54 | 3.8536 | 2.6941
[7 empty] | 5935 | 55 | 5.0061 | 3.5642
[7 empty] | 5936 | 56 | 5.2518 | 3.7497
[7 empty] | 5937 | 57 | 6.2094 | 4.4726
[7 empty] | 5938 | 58 | 7.328 | 5.3171
[7 empty] | 5939 | 59 | 8.5482 | 6.2383
[7 empty] | 5940 | 60 | 9.1838 | 6.7181
[7 empty] | 5941 | 61 | 9.8701 | 7.2363
[7 empty] | 5942 | 62 | 9.6668 | 7.0828
[7 empty] | 5943 | 63 | 10.2684 | 7.537
[7 empty] | 5944 | 64 | 11.226 | 8.2599
[7 empty] | 5945 | 65 | 11.853 | 8.7333
[7 empty] | 5946 | 66 | 11.7514 | 8.6565
[7 empty] | 5947 | 67 | 12.4971 | 9.2195
[7 empty] | 5948 | 68 | 12.7428 | 9.405
[7 empty] | 5949 | 69 | 12.2259 | 9.0148
[7 empty] | 5950 | 70 | 9.904 | 7.2619
[7 empty] | 5951 | 71 | 5.3366 | 3.8137
[7 empty] | 5952 | 72 | 4.2398 | 2.9857
[7 empty] | 5953 | 73 | 3.5147 | 2.4382
[7 empty] | 5954 | 74 | 3.2859 | 2.2655
[7 empty] | 5955 | 75 | 3.1842 | 2.1887
[7 empty] | 5956 | 76 | 3.1249 | 2.144
[7 empty] | 5957 | 77 | 3.3028 | 2.2783
[7 empty] | 5958 | 78 | 3.7096 | 2.5854
[7 empty] | 5959 | 79 | 4.8366 | 3.4362
[7 empty] | 5960 | 80 | 5.0146 | 3.5706
[7 empty] | 5961 | 81 | 6.2094 | 4.4726
[7 empty] | 5962 | 82 | 7.311 | 5.3043
[7 empty] | 5963 | 83 | 8.0567 | 5.8673
[7 empty] | 5964 | 84 | 9.3109 | 6.8141
[7 empty] | 5965 | 85 | 9.0058 | 6.5838
[7 empty] | 5966 | 86 | 8.4889 | 6.1935
[7 empty] | 5967 | 87 | 8.938 | 6.5326
[7 empty] | 5968 | 88 | 9.6075 | 7.038
[7 empty] | 5969 | 89 | 10.9718 | 8.068
[7 empty] | 5970 | 90 | 10.3786 | 7.6202
[7 empty] | 5971 | 91 | 11.0734 | 8.1447
[7 empty] | 5972 | 92 | 10.4633 | 7.6841
[7 empty] | 5973 | 93 | 8.0228 | 5.8417
[7 empty] | 5974 | 94 | 7.1076 | 5.1507
[7 empty] | 5975 | 95 | 5.2264 | 3.7305
[7 empty] | 5976 | 96 | 4.2265 | 2.9756
[7 empty] | 5977 | 97 | 4.1757 | 2.9372
[7 empty] | 5978 | 98 | 3.8791 | 2.7133
[7 empty] | 5979 | 99 | 3.8197 | 2.6685
[7 empty] | 5980 | 100 | 3.4638 | 2.3999
[7 empty] | 5981 | 101 | 3.4045 | 2.3551
[7 empty] | 5982 | 102 | 3.6418 | 2.5342
[7 empty] | 5983 | 103 | 4.396 | 3.1036
[7 empty] | 5984 | 104 | 4.6502 | 3.2955
[7 empty] | 5985 | 105 | 5.1417 | 3.6665
[7 empty] | 5986 | 106 | 6.6161 | 4.7797
[7 empty] | 5987 | 107 | 6.9721 | 5.0484
[7 empty] | 5988 | 108 | 8.5652 | 6.2511
[7 empty] | 5989 | 109 | 7.8957 | 5.7457
[7 empty] | 5990 | 110 | 7.4381 | 5.4002
[7 empty] | 5991 | 111 | 7.2771 | 5.2787
[7 empty] | 5992 | 112 | 7.3449 | 5.3299
[7 empty] | 5993 | 113 | 6.9975 | 5.0676
[7 empty] | 5994 | 114 | 7.167 | 5.1955
[7 empty] | 5995 | 115 | 6.7094 | 4.8501
[7 empty] | 5996 | 116 | 7.3958 | 5.3683
[7 empty] | 5997 | 117 | 6.9721 | 5.0484
[7 empty] | 5998 | 118 | 6.1924 | 4.4598
[7 empty] | 5999 | 119 | 4.5824 | 3.2443
[7 empty] | 6000 | 120 | 4.2615 | 3.0021
[7 empty] | 6001 | 121 | 3.5232 | 2.4446
[7 empty] | 6002 | 122 | 3.1079 | 2.1312
[7 empty] | 6003 | 123 | 3.0232 | 2.0672
[7 empty] | 6004 | 124 | 2.9893 | 2.0416
[7 empty] | 6005 | 125 | 2.9469 | 2.0096
[7 empty] | 6006 | 126 | 3.091 | 2.1184
[7 empty] | 6007 | 127 | 4.6163 | 3.2699
[7 empty] | 6008 | 128 | 6.1924 | 4.4598
[7 empty] | 6009 | 129 | 6.8788 | 4.978
[7 empty] | 6010 | 130 | 7.3195 | 5.3107
[7 empty] | 6011 | 131 | 7.4805 | 5.4322
[7 empty] | 6012 | 132 | 7.2263 | 5.2403
[7 empty] | 6013 | 133 | 7.8703 | 5.7265
[7 empty] | 6014 | 134 | 8.1754 | 5.9568
[7 empty] | 6015 | 135 | 8.2431 | 6.008
[7 empty] | 6016 | 136 | 7.4212 | 5.3875
[7 empty] | 6017 | 137 | 7.3195 | 5.3107
[7 empty] | 6018 | 138 | 7.2686 | 5.2723
[7 empty] | 6019 | 139 | 6.9297 | 5.0164
[7 empty] | 6020 | 140 | 6.9382 | 5.0228
[7 empty] | 6021 | 141 | 6.2772 | 4.5238
[7 empty] | 6022 | 142 | 5.6332 | 4.0376
[7 empty] | 6023 | 143 | 4.7434 | 3.3659
[7 empty] | 6024 | 144 | 4.1248 | 2.8989
[7 empty] | 6025 | 145 | 3.6503 | 2.5406
[7 empty] | 6026 | 146 | 3.4384 | 2.3807
[7 empty] | 6027 | 147 | 3.3706 | 2.3295
[7 empty] | 6028 | 148 | 3.3622 | 2.3231
[7 empty] | 6029 | 149 | 3.3622 | 2.3231
[7 empty] | 6030 | 150 | 3.3706 | 2.3295
[7 empty] | 6031 | 151 | 4.4638 | 3.1547
[7 empty] | 6032 | 152 | 6.006 | 4.3191
[7 empty] | 6033 | 153 | 6.6246 | 4.7861
[7 empty] | 6034 | 154 | 7.1924 | 5.2147
[7 empty] | 6035 | 155 | 7.0398 | 5.0996
[7 empty] | 6036 | 156 | 7.2093 | 5.2275
[7 empty] | 6037 | 157 | 7.9296 | 5.7713
[7 empty] | 6038 | 158 | 8.2601 | 6.0208
[7 empty] | 6039 | 159 | 8.5313 | 6.2255
[7 empty] | 6040 | 160 | 8.4041 | 6.1296
[7 empty] | 6041 | 161 | 9.1753 | 6.7117
[7 empty] | 6042 | 162 | 8.6753 | 6.3343
[7 empty] | 6043 | 163 | 9.0397 | 6.6094
[7 empty] | 6044 | 164 | 7.6754 | 5.5794
[7 empty] | 6045 | 165 | 10.8362 | 7.9656
[7 empty] | 6046 | 166 | 8.7685 | 6.4046
[7 empty] | 6047 | 167 | 5.1247 | 3.6537
[7 empty] | 6048 | 168 | 4.4722 | 3.1611
[7 empty] | 6049 | 1 | 2.9978 | 2.048
[7 empty] | 6050 | 2 | 2.8876 | 1.9648
[7 empty] | 6051 | 3 | 2.8791 | 1.9584
[7 empty] | 6052 | 4 | 3.0147 | 2.0608
[7 empty] | 6053 | 5 | 3.0317 | 2.0736
[7 empty] | 6054 | 6 | 3.4638 | 2.3999
[7 empty] | 6055 | 7 | 4.1926 | 2.95
[7 empty] | 6056 | 8 | 4.8705 | 3.4618
[7 empty] | 6057 | 9 | 4.8451 | 3.4426
[7 empty] | 6058 | 10 | 6.3789 | 4.6006
[7 empty] | 6059 | 11 | 8.4804 | 6.1871
[7 empty] | 6060 | 12 | 9.4549 | 6.9228
[7 empty] | 6061 | 13 | 9.8362 | 7.2107
[7 empty] | 6062 | 14 | 9.6159 | 7.0444
[7 empty] | 6063 | 15 | 9.5227 | 6.974
[7 empty] | 6064 | 16 | 10.7175 | 7.8761
[7 empty] | 6065 | 17 | 12.0564 | 8.8868
[7 empty] | 6066 | 18 | 11.8107 | 8.7013
[7 empty] | 6067 | 19 | 12.3445 | 9.1044
[7 empty] | 6068 | 20 | 12.2767 | 9.0532
[7 empty] | 6069 | 21 | 12.853 | 9.4882
[7 empty] | 6070 | 22 | 8.8533 | 6.4686
[7 empty] | 6071 | 23 | 5.04 | 3.5898
[7 empty] | 6072 | 24 | 3.3504 | 2.3142
[7 empty] | 6073 | 25 | 3.252 | 2.2399
[7 empty] | 6074 | 26 | 3.1418 | 2.1567
[7 empty] | 6075 | 27 | 3.0401 | 2.08
[7 empty] | 6076 | 28 | 3.1249 | 2.144
[7 empty] | 6077 | 29 | 3.3706 | 2.3295
[7 empty] | 6078 | 30 | 3.6164 | 2.515
[7 empty] | 6079 | 31 | 4.4722 | 3.1611
[7 empty] | 6080 | 32 | 4.8281 | 3.4298
[7 empty] | 6081 | 33 | 5.4976 | 3.9352
[7 empty] | 6082 | 34 | 6.4043 | 4.6198
[7 empty] | 6083 | 35 | 8.5991 | 6.2767
[7 empty] | 6084 | 36 | 9.6413 | 7.0636
[7 empty] | 6085 | 37 | 9.7176 | 7.1212
[7 empty] | 6086 | 38 | 9.7939 | 7.1787
[7 empty] | 6087 | 39 | 9.4634 | 6.9292
[7 empty] | 6088 | 40 | 10.5311 | 7.7353
[7 empty] | 6089 | 41 | 11.0904 | 8.1575
[7 empty] | 6090 | 42 | 11.1073 | 8.1703
[7 empty] | 6091 | 43 | 11.4802 | 8.4518
[7 empty] | 6092 | 44 | 12.6496 | 9.3347
[7 empty] | 6093 | 45 | 12.2428 | 9.0276
[7 empty] | 6094 | 46 | 9.4634 | 6.9292
[7 empty] | 6095 | 47 | 5.8196 | 4.1783
[7 empty] | 6096 | 48 | 4.3028 | 3.0332
[7 empty] | 6097 | 49 | 3.6333 | 2.5278
[7 empty] | 6098 | 50 | 3.3198 | 2.2911
[7 empty] | 6099 | 51 | 3.2096 | 2.2079
[7 empty] | 6100 | 52 | 3.2435 | 2.2335
[7 empty] | 6101 | 53 | 3.2689 | 2.2527
[7 empty] | 6102 | 54 | 3.8536 | 2.6941
[7 empty] | 6103 | 55 | 5.0061 | 3.5642
[7 empty] | 6104 | 56 | 5.2518 | 3.7497
[7 empty] | 6105 | 57 | 6.2094 | 4.4726
[7 empty] | 6106 | 58 | 7.328 | 5.3171
[7 empty] | 6107 | 59 | 8.5482 | 6.2383
[7 empty] | 6108 | 60 | 9.1838 | 6.7181
[7 empty] | 6109 | 61 | 9.8701 | 7.2363
[7 empty] | 6110 | 62 | 9.6668 | 7.0828
[7 empty] | 6111 | 63 | 10.2684 | 7.537
[7 empty] | 6112 | 64 | 11.226 | 8.2599
[7 empty] | 6113 | 65 | 11.853 | 8.7333
[7 empty] | 6114 | 66 | 11.7514 | 8.6565
[7 empty] | 6115 | 67 | 12.4971 | 9.2195
[7 empty] | 6116 | 68 | 12.7428 | 9.405
[7 empty] | 6117 | 69 | 12.2259 | 9.0148
[7 empty] | 6118 | 70 | 9.904 | 7.2619
[7 empty] | 6119 | 71 | 5.3366 | 3.8137
[7 empty] | 6120 | 72 | 4.2398 | 2.9857
[7 empty] | 6121 | 73 | 3.5147 | 2.4382
[7 empty] | 6122 | 74 | 3.2859 | 2.2655
[7 empty] | 6123 | 75 | 3.1842 | 2.1887
[7 empty] | 6124 | 76 | 3.1249 | 2.144
[7 empty] | 6125 | 77 | 3.3028 | 2.2783
[7 empty] | 6126 | 78 | 3.7096 | 2.5854
[7 empty] | 6127 | 79 | 4.8366 | 3.4362
[7 empty] | 6128 | 80 | 5.0146 | 3.5706
[7 empty] | 6129 | 81 | 6.2094 | 4.4726
[7 empty] | 6130 | 82 | 7.311 | 5.3043
[7 empty] | 6131 | 83 | 8.0567 | 5.8673
[7 empty] | 6132 | 84 | 9.3109 | 6.8141
[7 empty] | 6133 | 85 | 9.0058 | 6.5838
[7 empty] | 6134 | 86 | 8.4889 | 6.1935
[7 empty] | 6135 | 87 | 8.938 | 6.5326
[7 empty] | 6136 | 88 | 9.6075 | 7.038
[7 empty] | 6137 | 89 | 10.9718 | 8.068
[7 empty] | 6138 | 90 | 10.3786 | 7.6202
[7 empty] | 6139 | 91 | 11.0734 | 8.1447
[7 empty] | 6140 | 92 | 10.4633 | 7.6841
[7 empty] | 6141 | 93 | 8.0228 | 5.8417
[7 empty] | 6142 | 94 | 7.1076 | 5.1507
[7 empty] | 6143 | 95 | 5.2264 | 3.7305
[7 empty] | 6144 | 96 | 4.2265 | 2.9756
[7 empty] | 6145 | 97 | 4.1757 | 2.9372
[7 empty] | 6146 | 98 | 3.8791 | 2.7133
[7 empty] | 6147 | 99 | 3.8197 | 2.6685
[7 empty] | 6148 | 100 | 3.4638 | 2.3999
[7 empty] | 6149 | 101 | 3.4045 | 2.3551
[7 empty] | 6150 | 102 | 3.6418 | 2.5342
[7 empty] | 6151 | 103 | 4.396 | 3.1036
[7 empty] | 6152 | 104 | 4.6502 | 3.2955
[7 empty] | 6153 | 105 | 5.1417 | 3.6665
[7 empty] | 6154 | 106 | 6.6161 | 4.7797
[7 empty] | 6155 | 107 | 6.9721 | 5.0484
[7 empty] | 6156 | 108 | 8.5652 | 6.2511
[7 empty] | 6157 | 109 | 7.8957 | 5.7457
[7 empty] | 6158 | 110 | 7.4381 | 5.4002
[7 empty] | 6159 | 111 | 7.2771 | 5.2787
[7 empty] | 6160 | 112 | 7.3449 | 5.3299
[7 empty] | 6161 | 113 | 6.9975 | 5.0676
[7 empty] | 6162 | 114 | 7.167 | 5.1955
[7 empty] | 6163 | 115 | 6.7094 | 4.8501
[7 empty] | 6164 | 116 | 7.3958 | 5.3683
[7 empty] | 6165 | 117 | 6.9721 | 5.0484
[7 empty] | 6166 | 118 | 6.1924 | 4.4598
[7 empty] | 6167 | 119 | 4.5824 | 3.2443
[7 empty] | 6168 | 120 | 4.2615 | 3.0021
[7 empty] | 6169 | 121 | 3.5232 | 2.4446
[7 empty] | 6170 | 122 | 3.1079 | 2.1312
[7 empty] | 6171 | 123 | 3.0232 | 2.0672
[7 empty] | 6172 | 124 | 2.9893 | 2.0416
[7 empty] | 6173 | 125 | 2.9469 | 2.0096
[7 empty] | 6174 | 126 | 3.091 | 2.1184
[7 empty] | 6175 | 127 | 4.6163 | 3.2699
[7 empty] | 6176 | 128 | 6.1924 | 4.4598
[7 empty] | 6177 | 129 | 6.8788 | 4.978
[7 empty] | 6178 | 130 | 7.3195 | 5.3107
[7 empty] | 6179 | 131 | 7.4805 | 5.4322
[7 empty] | 6180 | 132 | 7.2263 | 5.2403
[7 empty] | 6181 | 133 | 7.8703 | 5.7265
[7 empty] | 6182 | 134 | 8.1754 | 5.9568
[7 empty] | 6183 | 135 | 8.2431 | 6.008
[7 empty] | 6184 | 136 | 7.4212 | 5.3875
[7 empty] | 6185 | 137 | 7.3195 | 5.3107
[7 empty] | 6186 | 138 | 7.2686 | 5.2723
[7 empty] | 6187 | 139 | 6.9297 | 5.0164
[7 empty] | 6188 | 140 | 6.9382 | 5.0228
[7 empty] | 6189 | 141 | 6.2772 | 4.5238
[7 empty] | 6190 | 142 | 5.6332 | 4.0376
[7 empty] | 6191 | 143 | 4.7434 | 3.3659
[7 empty] | 6192 | 144 | 4.1248 | 2.8989
[7 empty] | 6193 | 145 | 3.6503 | 2.5406
[7 empty] | 6194 | 146 | 3.4384 | 2.3807
[7 empty] | 6195 | 147 | 3.3706 | 2.3295
[7 empty] | 6196 | 148 | 3.3622 | 2.3231
[7 empty] | 6197 | 149 | 3.3622 | 2.3231
[7 empty] | 6198 | 150 | 3.3706 | 2.3295
[7 empty] | 6199 | 151 | 4.4638 | 3.1547
[7 empty] | 6200 | 152 | 6.006 | 4.3191
[7 empty] | 6201 | 153 | 6.6246 | 4.7861
[7 empty] | 6202 | 154 | 7.1924 | 5.2147
[7 empty] | 6203 | 155 | 7.0398 | 5.0996
[7 empty] | 6204 | 156 | 7.2093 | 5.2275
[7 empty] | 6205 | 157 | 7.9296 | 5.7713
[7 empty] | 6206 | 158 | 8.2601 | 6.0208
[7 empty] | 6207 | 159 | 8.5313 | 6.2255
[7 empty] | 6208 | 160 | 8.4041 | 6.1296
[7 empty] | 6209 | 161 | 9.1753 | 6.7117
[7 empty] | 6210 | 162 | 8.6753 | 6.3343
[7 empty] | 6211 | 163 | 9.0397 | 6.6094
[7 empty] | 6212 | 164 | 7.6754 | 5.5794
[7 empty] | 6213 | 165 | 10.8362 | 7.9656
[7 empty] | 6214 | 166 | 8.7685 | 6.4046
[7 empty] | 6215 | 167 | 5.1247 | 3.6537
[7 empty] | 6216 | 168 | 4.4722 | 3.1611
[7 empty] | 6217 | 1 | 2.9978 | 2.048
[7 empty] | 6218 | 2 | 2.8876 | 1.9648
[7 empty] | 6219 | 3 | 2.8791 | 1.9584
[7 empty] | 6220 | 4 | 3.0147 | 2.0608
[7 empty] | 6221 | 5 | 3.0317 | 2.0736
[7 empty] | 6222 | 6 | 3.4638 | 2.3999
[7 empty] | 6223 | 7 | 4.1926 | 2.95
[7 empty] | 6224 | 8 | 4.8705 | 3.4618
[7 empty] | 6225 | 9 | 4.8451 | 3.4426
[7 empty] | 6226 | 10 | 6.3789 | 4.6006
[7 empty] | 6227 | 11 | 8.4804 | 6.1871
[7 empty] | 6228 | 12 | 9.4549 | 6.9228
[7 empty] | 6229 | 13 | 9.8362 | 7.2107
[7 empty] | 6230 | 14 | 9.6159 | 7.0444
[7 empty] | 6231 | 15 | 9.5227 | 6.974
[7 empty] | 6232 | 16 | 10.7175 | 7.8761
[7 empty] | 6233 | 17 | 12.0564 | 8.8868
[7 empty] | 6234 | 18 | 11.8107 | 8.7013
[7 empty] | 6235 | 19 | 12.3445 | 9.1044
[7 empty] | 6236 | 20 | 12.2767 | 9.0532
[7 empty] | 6237 | 21 | 12.853 | 9.4882
[7 empty] | 6238 | 22 | 8.8533 | 6.4686
[7 empty] | 6239 | 23 | 5.04 | 3.5898
[7 empty] | 6240 | 24 | 3.3504 | 2.3142
[7 empty] | 6241 | 25 | 3.252 | 2.2399
[7 empty] | 6242 | 26 | 3.1418 | 2.1567
[7 empty] | 6243 | 27 | 3.0401 | 2.08
[7 empty] | 6244 | 28 | 3.1249 | 2.144
[7 empty] | 6245 | 29 | 3.3706 | 2.3295
[7 empty] | 6246 | 30 | 3.6164 | 2.515
[7 empty] | 6247 | 31 | 4.4722 | 3.1611
[7 empty] | 6248 | 32 | 4.8281 | 3.4298
[7 empty] | 6249 | 33 | 5.4976 | 3.9352
[7 empty] | 6250 | 34 | 6.4043 | 4.6198
[7 empty] | 6251 | 35 | 8.5991 | 6.2767
[7 empty] | 6252 | 36 | 9.6413 | 7.0636
[7 empty] | 6253 | 37 | 9.7176 | 7.1212
[7 empty] | 6254 | 38 | 9.7939 | 7.1787
[7 empty] | 6255 | 39 | 9.4634 | 6.9292
[7 empty] | 6256 | 40 | 10.5311 | 7.7353
[7 empty] | 6257 | 41 | 11.0904 | 8.1575
[7 empty] | 6258 | 42 | 11.1073 | 8.1703
[7 empty] | 6259 | 43 | 11.4802 | 8.4518
[7 empty] | 6260 | 44 | 12.6496 | 9.3347
[7 empty] | 6261 | 45 | 12.2428 | 9.0276
[7 empty] | 6262 | 46 | 9.4634 | 6.9292
[7 empty] | 6263 | 47 | 5.8196 | 4.1783
[7 empty] | 6264 | 48 | 4.3028 | 3.0332
[7 empty] | 6265 | 49 | 3.6333 | 2.5278
[7 empty] | 6266 | 50 | 3.3198 | 2.2911
[7 empty] | 6267 | 51 | 3.2096 | 2.2079
[7 empty] | 6268 | 52 | 3.2435 | 2.2335
[7 empty] | 6269 | 53 | 3.2689 | 2.2527
[7 empty] | 6270 | 54 | 3.8536 | 2.6941
[7 empty] | 6271 | 55 | 5.0061 | 3.5642
[7 empty] | 6272 | 56 | 5.2518 | 3.7497
[7 empty] | 6273 | 57 | 6.2094 | 4.4726
[7 empty] | 6274 | 58 | 7.328 | 5.3171
[7 empty] | 6275 | 59 | 8.5482 | 6.2383
[7 empty] | 6276 | 60 | 9.1838 | 6.7181
[7 empty] | 6277 | 61 | 9.8701 | 7.2363
[7 empty] | 6278 | 62 | 9.6668 | 7.0828
[7 empty] | 6279 | 63 | 10.2684 | 7.537
[7 empty] | 6280 | 64 | 11.226 | 8.2599
[7 empty] | 6281 | 65 | 11.853 | 8.7333
[7 empty] | 6282 | 66 | 11.7514 | 8.6565
[7 empty] | 6283 | 67 | 12.4971 | 9.2195
[7 empty] | 6284 | 68 | 12.7428 | 9.405
[7 empty] | 6285 | 69 | 12.2259 | 9.0148
[7 empty] | 6286 | 70 | 9.904 | 7.2619
[7 empty] | 6287 | 71 | 5.3366 | 3.8137
[7 empty] | 6288 | 72 | 4.2398 | 2.9857
[7 empty] | 6289 | 73 | 3.5147 | 2.4382
[7 empty] | 6290 | 74 | 3.2859 | 2.2655
[7 empty] | 6291 | 75 | 3.1842 | 2.1887
[7 empty] | 6292 | 76 | 3.1249 | 2.144
[7 empty] | 6293 | 77 | 3.3028 | 2.2783
[7 empty] | 6294 | 78 | 3.7096 | 2.5854
[7 empty] | 6295 | 79 | 4.8366 | 3.4362
[7 empty] | 6296 | 80 | 5.0146 | 3.5706
[7 empty] | 6297 | 81 | 6.2094 | 4.4726
[7 empty] | 6298 | 82 | 7.311 | 5.3043
[7 empty] | 6299 | 83 | 8.0567 | 5.8673
[7 empty] | 6300 | 84 | 9.3109 | 6.8141
[7 empty] | 6301 | 85 | 9.0058 | 6.5838
[7 empty] | 6302 | 86 | 8.4889 | 6.1935
[7 empty] | 6303 | 87 | 8.938 | 6.5326
[7 empty] | 6304 | 88 | 9.6075 | 7.038
[7 empty] | 6305 | 89 | 10.9718 | 8.068
[7 empty] | 6306 | 90 | 10.3786 | 7.6202
[7 empty] | 6307 | 91 | 11.0734 | 8.1447
[7 empty] | 6308 | 92 | 10.4633 | 7.6841
[7 empty] | 6309 | 93 | 8.0228 | 5.8417
[7 empty] | 6310 | 94 | 7.1076 | 5.1507
[7 empty] | 6311 | 95 | 5.2264 | 3.7305
[7 empty] | 6312 | 96 | 4.2265 | 2.9756
[7 empty] | 6313 | 97 | 4.1757 | 2.9372
[7 empty] | 6314 | 98 | 3.8791 | 2.7133
[7 empty] | 6315 | 99 | 3.8197 | 2.6685
[7 empty] | 6316 | 100 | 3.4638 | 2.3999
[7 empty] | 6317 | 101 | 3.4045 | 2.3551
[7 empty] | 6318 | 102 | 3.6418 | 2.5342
[7 empty] | 6319 | 103 | 4.396 | 3.1036
[7 empty] | 6320 | 104 | 4.6502 | 3.2955
[7 empty] | 6321 | 105 | 5.1417 | 3.6665
[7 empty] | 6322 | 106 | 6.6161 | 4.7797
[7 empty] | 6323 | 107 | 6.9721 | 5.0484
[7 empty] | 6324 | 108 | 8.5652 | 6.2511
[7 empty] | 6325 | 109 | 7.8957 | 5.7457
[7 empty] | 6326 | 110 | 7.4381 | 5.4002
[7 empty] | 6327 | 111 | 7.2771 | 5.2787
[7 empty] | 6328 | 112 | 7.3449 | 5.3299
[7 empty] | 6329 | 113 | 6.9975 | 5.0676
[7 empty] | 6330 | 114 | 7.167 | 5.1955
[7 empty] | 6331 | 115 | 6.7094 | 4.8501
[7 empty] | 6332 | 116 | 7.3958 | 5.3683
[7 empty] | 6333 | 117 | 6.9721 | 5.0484
[7 empty] | 6334 | 118 | 6.1924 | 4.4598
[7 empty] | 6335 | 119 | 4.5824 | 3.2443
[7 empty] | 6336 | 120 | 4.2615 | 3.0021
[7 empty] | 6337 | 121 | 3.5232 | 2.4446
[7 empty] | 6338 | 122 | 3.1079 | 2.1312
[7 empty] | 6339 | 123 | 3.0232 | 2.0672
[7 empty] | 6340 | 124 | 2.9893 | 2.0416
[7 empty] | 6341 | 125 | 2.9469 | 2.0096
[7 empty] | 6342 | 126 | 3.091 | 2.1184
[7 empty] | 6343 | 127 | 4.6163 | 3.2699
[7 empty] | 6344 | 128 | 6.1924 | 4.4598
[7 empty] | 6345 | 129 | 6.8788 | 4.978
[7 empty] | 6346 | 130 | 7.3195 | 5.3107
[7 empty] | 6347 | 131 | 7.4805 | 5.4322
[7 empty] | 6348 | 132 | 7.2263 | 5.2403
[7 empty] | 6349 | 133 | 7.8703 | 5.7265
[7 empty] | 6350 | 134 | 8.1754 | 5.9568
[7 empty] | 6351 | 135 | 8.2431 | 6.008
[7 empty] | 6352 | 136 | 7.4212 | 5.3875
[7 empty] | 6353 | 137 | 7.3195 | 5.3107
[7 empty] | 6354 | 138 | 7.2686 | 5.2723
[7 empty] | 6355 | 139 | 6.9297 | 5.0164
[7 empty] | 6356 | 140 | 6.9382 | 5.0228
[7 empty] | 6357 | 141 | 6.2772 | 4.5238
[7 empty] | 6358 | 142 | 5.6332 | 4.0376
[7 empty] | 6359 | 143 | 4.7434 | 3.3659
[7 empty] | 6360 | 144 | 4.1248 | 2.8989
[7 empty] | 6361 | 145 | 3.6503 | 2.5406
[7 empty] | 6362 | 146 | 3.4384 | 2.3807
[7 empty] | 6363 | 147 | 3.3706 | 2.3295
[7 empty] | 6364 | 148 | 3.3622 | 2.3231
[7 empty] | 6365 | 149 | 3.3622 | 2.3231
[7 empty] | 6366 | 150 | 3.3706 | 2.3295
[7 empty] | 6367 | 151 | 4.4638 | 3.1547
[7 empty] | 6368 | 152 | 6.006 | 4.3191
[7 empty] | 6369 | 153 | 6.6246 | 4.7861
[7 empty] | 6370 | 154 | 7.1924 | 5.2147
[7 empty] | 6371 | 155 | 7.0398 | 5.0996
[7 empty] | 6372 | 156 | 7.2093 | 5.2275
[7 empty] | 6373 | 157 | 7.9296 | 5.7713
[7 empty] | 6374 | 158 | 8.2601 | 6.0208
[7 empty] | 6375 | 159 | 8.5313 | 6.2255
[7 empty] | 6376 | 160 | 8.4041 | 6.1296
[7 empty] | 6377 | 161 | 9.1753 | 6.7117
[7 empty] | 6378 | 162 | 8.6753 | 6.3343
[7 empty] | 6379 | 163 | 9.0397 | 6.6094
[7 empty] | 6380 | 164 | 7.6754 | 5.5794
[7 empty] | 6381 | 165 | 10.8362 | 7.9656
[7 empty] | 6382 | 166 | 8.7685 | 6.4046
[7 empty] | 6383 | 167 | 5.1247 | 3.6537
[7 empty] | 6384 | 168 | 4.4722 | 3.1611
[7 empty] | 6385 | 1 | 2.9978 | 2.048
[7 empty] | 6386 | 2 | 2.8876 | 1.9648
[7 empty] | 6387 | 3 | 2.8791 | 1.9584
[7 empty] | 6388 | 4 | 3.0147 | 2.0608
[7 empty] | 6389 | 5 | 3.0317 | 2.0736
[7 empty] | 6390 | 6 | 3.4638 | 2.3999
[7 empty] | 6391 | 7 | 4.1926 | 2.95
[7 empty] | 6392 | 8 | 4.8705 | 3.4618
[7 empty] | 6393 | 9 | 4.8451 | 3.4426
[7 empty] | 6394 | 10 | 6.3789 | 4.6006
[7 empty] | 6395 | 11 | 8.4804 | 6.1871
[7 empty] | 6396 | 12 | 9.4549 | 6.9228
[7 empty] | 6397 | 13 | 9.8362 | 7.2107
[7 empty] | 6398 | 14 | 9.6159 | 7.0444
[7 empty] | 6399 | 15 | 9.5227 | 6.974
[7 empty] | 6400 | 16 | 10.7175 | 7.8761
[7 empty] | 6401 | 17 | 12.0564 | 8.8868
[7 empty] | 6402 | 18 | 11.8107 | 8.7013
[7 empty] | 6403 | 19 | 12.3445 | 9.1044
[7 empty] | 6404 | 20 | 12.2767 | 9.0532
[7 empty] | 6405 | 21 | 12.853 | 9.4882
[7 empty] | 6406 | 22 | 8.8533 | 6.4686
[7 empty] | 6407 | 23 | 5.04 | 3.5898
[7 empty] | 6408 | 24 | 3.3504 | 2.3142
[7 empty] | 6409 | 25 | 3.252 | 2.2399
[7 empty] | 6410 | 26 | 3.1418 | 2.1567
[7 empty] | 6411 | 27 | 3.0401 | 2.08
[7 empty] | 6412 | 28 | 3.1249 | 2.144
[7 empty] | 6413 | 29 | 3.3706 | 2.3295
[7 empty] | 6414 | 30 | 3.6164 | 2.515
[7 empty] | 6415 | 31 | 4.4722 | 3.1611
[7 empty] | 6416 | 32 | 4.8281 | 3.4298
[7 empty] | 6417 | 33 | 5.4976 | 3.9352
[7 empty] | 6418 | 34 | 6.4043 | 4.6198
[7 empty] | 6419 | 35 | 8.5991 | 6.2767
[7 empty] | 6420 | 36 | 9.6413 | 7.0636
[7 empty] | 6421 | 37 | 9.7176 | 7.1212
[7 empty] | 6422 | 38 | 9.7939 | 7.1787
[7 empty] | 6423 | 39 | 9.4634 | 6.9292
[7 empty] | 6424 | 40 | 10.5311 | 7.7353
[7 empty] | 6425 | 41 | 11.0904 | 8.1575
[7 empty] | 6426 | 42 | 11.1073 | 8.1703
[7 empty] | 6427 | 43 | 11.4802 | 8.4518
[7 empty] | 6428 | 44 | 12.6496 | 9.3347
[7 empty] | 6429 | 45 | 12.2428 | 9.0276
[7 empty] | 6430 | 46 | 9.4634 | 6.9292
[7 empty] | 6431 | 47 | 5.8196 | 4.1783
[7 empty] | 6432 | 48 | 4.3028 | 3.0332
[7 empty] | 6433 | 49 | 3.6333 | 2.5278
[7 empty] | 6434 | 50 | 3.3198 | 2.2911
[7 empty] | 6435 | 51 | 3.2096 | 2.2079
[7 empty] | 6436 | 52 | 3.2435 | 2.2335
[7 empty] | 6437 | 53 | 3.2689 | 2.2527
[7 empty] | 6438 | 54 | 3.8536 | 2.6941
[7 empty] | 6439 | 55 | 5.0061 | 3.5642
[7 empty] | 6440 | 56 | 5.2518 | 3.7497
[7 empty] | 6441 | 57 | 6.2094 | 4.4726
[7 empty] | 6442 | 58 | 7.328 | 5.3171
[7 empty] | 6443 | 59 | 8.5482 | 6.2383
[7 empty] | 6444 | 60 | 9.1838 | 6.7181
[7 empty] | 6445 | 61 | 9.8701 | 7.2363
[7 empty] | 6446 | 62 | 9.6668 | 7.0828
[7 empty] | 6447 | 63 | 10.2684 | 7.537
[7 empty] | 6448 | 64 | 11.226 | 8.2599
[7 empty] | 6449 | 65 | 11.853 | 8.7333
[7 empty] | 6450 | 66 | 11.7514 | 8.6565
[7 empty] | 6451 | 67 | 12.4971 | 9.2195
[7 empty] | 6452 | 68 | 12.7428 | 9.405
[7 empty] | 6453 | 69 | 12.2259 | 9.0148
[7 empty] | 6454 | 70 | 9.904 | 7.2619
[7 empty] | 6455 | 71 | 5.3366 | 3.8137
[7 empty] | 6456 | 72 | 4.2398 | 2.9857
[7 empty] | 6457 | 73 | 3.5147 | 2.4382
[7 empty] | 6458 | 74 | 3.2859 | 2.2655
[7 empty] | 6459 | 75 | 3.1842 | 2.1887
[7 empty] | 6460 | 76 | 3.1249 | 2.144
[7 empty] | 6461 | 77 | 3.3028 | 2.2783
[7 empty] | 6462 | 78 | 3.7096 | 2.5854
[7 empty] | 6463 | 79 | 4.8366 | 3.4362
[7 empty] | 6464 | 80 | 5.0146 | 3.5706
[7 empty] | 6465 | 81 | 6.2094 | 4.4726
[7 empty] | 6466 | 82 | 7.311 | 5.3043
[7 empty] | 6467 | 83 | 8.0567 | 5.8673
[7 empty] | 6468 | 84 | 9.3109 | 6.8141
[7 empty] | 6469 | 85 | 9.0058 | 6.5838
[7 empty] | 6470 | 86 | 8.4889 | 6.1935
[7 empty] | 6471 | 87 | 8.938 | 6.5326
[7 empty] | 6472 | 88 | 9.6075 | 7.038
[7 empty] | 6473 | 89 | 10.9718 | 8.068
[7 empty] | 6474 | 90 | 10.3786 | 7.6202
[7 empty] | 6475 | 91 | 11.0734 | 8.1447
[7 empty] | 6476 | 92 | 10.4633 | 7.6841
[7 empty] | 6477 | 93 | 8.0228 | 5.8417
[7 empty] | 6478 | 94 | 7.1076 | 5.1507
[7 empty] | 6479 | 95 | 5.2264 | 3.7305
[7 empty] | 6480 | 96 | 4.2265 | 2.9756
[7 empty] | 6481 | 97 | 4.1757 | 2.9372
[7 empty] | 6482 | 98 | 3.8791 | 2.7133
[7 empty] | 6483 | 99 | 3.8197 | 2.6685
[7 empty] | 6484 | 100 | 3.4638 | 2.3999
[7 empty] | 6485 | 101 | 3.4045 | 2.3551
[7 empty] | 6486 | 102 | 3.6418 | 2.5342
[7 empty] | 6487 | 103 | 4.396 | 3.1036
[7 empty] | 6488 | 104 | 4.6502 | 3.2955
[7 empty] | 6489 | 105 | 5.1417 | 3.6665
[7 empty] | 6490 | 106 | 6.6161 | 4.7797
[7 empty] | 6491 | 107 | 6.9721 | 5.0484
[7 empty] | 6492 | 108 | 8.5652 | 6.2511
[7 empty] | 6493 | 109 | 7.8957 | 5.7457
[7 empty] | 6494 | 110 | 7.4381 | 5.4002
[7 empty] | 6495 | 111 | 7.2771 | 5.2787
[7 empty] | 6496 | 112 | 7.3449 | 5.3299
[7 empty] | 6497 | 113 | 6.9975 | 5.0676
[7 empty] | 6498 | 114 | 7.167 | 5.1955
[7 empty] | 6499 | 115 | 6.7094 | 4.8501
[7 empty] | 6500 | 116 | 7.3958 | 5.3683
[7 empty] | 6501 | 117 | 6.9721 | 5.0484
[7 empty] | 6502 | 118 | 6.1924 | 4.4598
[7 empty] | 6503 | 119 | 4.5824 | 3.2443
[7 empty] | 6504 | 120 | 4.2615 | 3.0021
[7 empty] | 6505 | 121 | 3.5232 | 2.4446
[7 empty] | 6506 | 122 | 3.1079 | 2.1312
[7 empty] | 6507 | 123 | 3.0232 | 2.0672
[7 empty] | 6508 | 124 | 2.9893 | 2.0416
[7 empty] | 6509 | 125 | 2.9469 | 2.0096
[7 empty] | 6510 | 126 | 3.091 | 2.1184
[7 empty] | 6511 | 127 | 4.6163 | 3.2699
[7 empty] | 6512 | 128 | 6.1924 | 4.4598
[7 empty] | 6513 | 129 | 6.8788 | 4.978
[7 empty] | 6514 | 130 | 7.3195 | 5.3107
[7 empty] | 6515 | 131 | 7.4805 | 5.4322
[7 empty] | 6516 | 132 | 7.2263 | 5.2403
[7 empty] | 6517 | 133 | 7.8703 | 5.7265
[7 empty] | 6518 | 134 | 8.1754 | 5.9568
[7 empty] | 6519 | 135 | 8.2431 | 6.008
[7 empty] | 6520 | 136 | 7.4212 | 5.3875
[7 empty] | 6521 | 137 | 7.3195 | 5.3107
[7 empty] | 6522 | 138 | 7.2686 | 5.2723
[7 empty] | 6523 | 139 | 6.9297 | 5.0164
[7 empty] | 6524 | 140 | 6.9382 | 5.0228
[7 empty] | 6525 | 141 | 6.2772 | 4.5238
[7 empty] | 6526 | 142 | 5.6332 | 4.0376
[7 empty] | 6527 | 143 | 4.7434 | 3.3659
[7 empty] | 6528 | 144 | 4.1248 | 2.8989
[7 empty] | 6529 | 145 | 3.6503 | 2.5406
[7 empty] | 6530 | 146 | 3.4384 | 2.3807
[7 empty] | 6531 | 147 | 3.3706 | 2.3295
[7 empty] | 6532 | 148 | 3.3622 | 2.3231
[7 empty] | 6533 | 149 | 3.3622 | 2.3231
[7 empty] | 6534 | 150 | 3.3706 | 2.3295
[7 empty] | 6535 | 151 | 4.4638 | 3.1547
[7 empty] | 6536 | 152 | 6.006 | 4.3191
[7 empty] | 6537 | 153 | 6.6246 | 4.7861
[7 empty] | 6538 | 154 | 7.1924 | 5.2147
[7 empty] | 6539 | 155 | 7.0398 | 5.0996
[7 empty] | 6540 | 156 | 7.2093 | 5.2275
[7 empty] | 6541 | 157 | 7.9296 | 5.7713
[7 empty] | 6542 | 158 | 8.2601 | 6.0208
[7 empty] | 6543 | 159 | 8.5313 | 6.2255
[7 empty] | 6544 | 160 | 8.4041 | 6.1296
[7 empty] | 6545 | 161 | 9.1753 | 6.7117
[7 empty] | 6546 | 162 | 8.6753 | 6.3343
[7 empty] | 6547 | 163 | 9.0397 | 6.6094
[7 empty] | 6548 | 164 | 7.6754 | 5.5794
[7 empty] | 6549 | 165 | 10.8362 | 7.9656
[7 empty] | 6550 | 166 | 8.7685 | 6.4046
[7 empty] | 6551 | 167 | 5.1247 | 3.6537
[7 empty] | 6552 | 168 | 4.4722 | 3.1611
[7 empty] | 6553 | 1 | 2.9978 | 2.048
[7 empty] | 6554 | 2 | 2.8876 | 1.9648
[7 empty] | 6555 | 3 | 2.8791 | 1.9584
[7 empty] | 6556 | 4 | 3.0147 | 2.0608
[7 empty] | 6557 | 5 | 3.0317 | 2.0736
[7 empty] | 6558 | 6 | 3.4638 | 2.3999
[7 empty] | 6559 | 7 | 4.1926 | 2.95
[7 empty] | 6560 | 8 | 4.8705 | 3.4618
[7 empty] | 6561 | 9 | 4.8451 | 3.4426
[7 empty] | 6562 | 10 | 6.3789 | 4.6006
[7 empty] | 6563 | 11 | 8.4804 | 6.1871
[7 empty] | 6564 | 12 | 9.4549 | 6.9228
[7 empty] | 6565 | 13 | 9.8362 | 7.2107
[7 empty] | 6566 | 14 | 9.6159 | 7.0444
[7 empty] | 6567 | 15 | 9.5227 | 6.974
[7 empty] | 6568 | 16 | 10.7175 | 7.8761
[7 empty] | 6569 | 17 | 12.0564 | 8.8868
[7 empty] | 6570 | 18 | 11.8107 | 8.7013
[7 empty] | 6571 | 19 | 12.3445 | 9.1044
[7 empty] | 6572 | 20 | 12.2767 | 9.0532
[7 empty] | 6573 | 21 | 12.853 | 9.4882
[7 empty] | 6574 | 22 | 8.8533 | 6.4686
[7 empty] | 6575 | 23 | 5.04 | 3.5898
[7 empty] | 6576 | 24 | 3.3504 | 2.3142
[7 empty] | 6577 | 25 | 3.252 | 2.2399
[7 empty] | 6578 | 26 | 3.1418 | 2.1567
[7 empty] | 6579 | 27 | 3.0401 | 2.08
[7 empty] | 6580 | 28 | 3.1249 | 2.144
[7 empty] | 6581 | 29 | 3.3706 | 2.3295
[7 empty] | 6582 | 30 | 3.6164 | 2.515
[7 empty] | 6583 | 31 | 4.4722 | 3.1611
[7 empty] | 6584 | 32 | 4.8281 | 3.4298
[7 empty] | 6585 | 33 | 5.4976 | 3.9352
[7 empty] | 6586 | 34 | 6.4043 | 4.6198
[7 empty] | 6587 | 35 | 8.5991 | 6.2767
[7 empty] | 6588 | 36 | 9.6413 | 7.0636
[7 empty] | 6589 | 37 | 9.7176 | 7.1212
[7 empty] | 6590 | 38 | 9.7939 | 7.1787
[7 empty] | 6591 | 39 | 9.4634 | 6.9292
[7 empty] | 6592 | 40 | 10.5311 | 7.7353
[7 empty] | 6593 | 41 | 11.0904 | 8.1575
[7 empty] | 6594 | 42 | 11.1073 | 8.1703
[7 empty] | 6595 | 43 | 11.4802 | 8.4518
[7 empty] | 6596 | 44 | 12.6496 | 9.3347
[7 empty] | 6597 | 45 | 12.2428 | 9.0276
[7 empty] | 6598 | 46 | 9.4634 | 6.9292
[7 empty] | 6599 | 47 | 5.8196 | 4.1783
[7 empty] | 6600 | 48 | 4.3028 | 3.0332
[7 empty] | 6601 | 49 | 3.6333 | 2.5278
[7 empty] | 6602 | 50 | 3.3198 | 2.2911
[7 empty] | 6603 | 51 | 3.2096 | 2.2079
[7 empty] | 6604 | 52 | 3.2435 | 2.2335
[7 empty] | 6605 | 53 | 3.2689 | 2.2527
[7 empty] | 6606 | 54 | 3.8536 | 2.6941
[7 empty] | 6607 | 55 | 5.0061 | 3.5642
[7 empty] | 6608 | 56 | 5.2518 | 3.7497
[7 empty] | 6609 | 57 | 6.2094 | 4.4726
[7 empty] | 6610 | 58 | 7.328 | 5.3171
[7 empty] | 6611 | 59 | 8.5482 | 6.2383
[7 empty] | 6612 | 60 | 9.1838 | 6.7181
[7 empty] | 6613 | 61 | 9.8701 | 7.2363
[7 empty] | 6614 | 62 | 9.6668 | 7.0828
[7 empty] | 6615 | 63 | 10.2684 | 7.537
[7 empty] | 6616 | 64 | 11.226 | 8.2599
[7 empty] | 6617 | 65 | 11.853 | 8.7333
[7 empty] | 6618 | 66 | 11.7514 | 8.6565
[7 empty] | 6619 | 67 | 12.4971 | 9.2195
[7 empty] | 6620 | 68 | 12.7428 | 9.405
[7 empty] | 6621 | 69 | 12.2259 | 9.0148
[7 empty] | 6622 | 70 | 9.904 | 7.2619
[7 empty] | 6623 | 71 | 5.3366 | 3.8137
[7 empty] | 6624 | 72 | 4.2398 | 2.9857
[7 empty] | 6625 | 73 | 3.5147 | 2.4382
[7 empty] | 6626 | 74 | 3.2859 | 2.2655
[7 empty] | 6627 | 75 | 3.1842 | 2.1887
[7 empty] | 6628 | 76 | 3.1249 | 2.144
[7 empty] | 6629 | 77 | 3.3028 | 2.2783
[7 empty] | 6630 | 78 | 3.7096 | 2.5854
[7 empty] | 6631 | 79 | 4.8366 | 3.4362
[7 empty] | 6632 | 80 | 5.0146 | 3.5706
[7 empty] | 6633 | 81 | 6.2094 | 4.4726
[7 empty] | 6634 | 82 | 7.311 | 5.3043
[7 empty] | 6635 | 83 | 8.0567 | 5.8673
[7 empty] | 6636 | 84 | 9.3109 | 6.8141
[7 empty] | 6637 | 85 | 9.0058 | 6.5838
[7 empty] | 6638 | 86 | 8.4889 | 6.1935
[7 empty] | 6639 | 87 | 8.938 | 6.5326
[7 empty] | 6640 | 88 | 9.6075 | 7.038
[7 empty] | 6641 | 89 | 10.9718 | 8.068
[7 empty] | 6642 | 90 | 10.3786 | 7.6202
[7 empty] | 6643 | 91 | 11.0734 | 8.1447
[7 empty] | 6644 | 92 | 10.4633 | 7.6841
[7 empty] | 6645 | 93 | 8.0228 | 5.8417
[7 empty] | 6646 | 94 | 7.1076 | 5.1507
[7 empty] | 6647 | 95 | 5.2264 | 3.7305
[7 empty] | 6648 | 96 | 4.2265 | 2.9756
[7 empty] | 6649 | 97 | 4.1757 | 2.9372
[7 empty] | 6650 | 98 | 3.8791 | 2.7133
[7 empty] | 6651 | 99 | 3.8197 | 2.6685
[7 empty] | 6652 | 100 | 3.4638 | 2.3999
[7 empty] | 6653 | 101 | 3.4045 | 2.3551
[7 empty] | 6654 | 102 | 3.6418 | 2.5342
[7 empty] | 6655 | 103 | 4.396 | 3.1036
[7 empty] | 6656 | 104 | 4.6502 | 3.2955
[7 empty] | 6657 | 105 | 5.1417 | 3.6665
[7 empty] | 6658 | 106 | 6.6161 | 4.7797
[7 empty] | 6659 | 107 | 6.9721 | 5.0484
[7 empty] | 6660 | 108 | 8.5652 | 6.2511
[7 empty] | 6661 | 109 | 7.8957 | 5.7457
[7 empty] | 6662 | 110 | 7.4381 | 5.4002
[7 empty] | 6663 | 111 | 7.2771 | 5.2787
[7 empty] | 6664 | 112 | 7.3449 | 5.3299
[7 empty] | 6665 | 113 | 6.9975 | 5.0676
[7 empty] | 6666 | 114 | 7.167 | 5.1955
[7 empty] | 6667 | 115 | 6.7094 | 4.8501
[7 empty] | 6668 | 116 | 7.3958 | 5.3683
[7 empty] | 6669 | 117 | 6.9721 | 5.0484
[7 empty] | 6670 | 118 | 6.1924 | 4.4598
[7 empty] | 6671 | 119 | 4.5824 | 3.2443
[7 empty] | 6672 | 120 | 4.2615 | 3.0021
[7 empty] | 6673 | 121 | 3.5232 | 2.4446
[7 empty] | 6674 | 122 | 3.1079 | 2.1312
[7 empty] | 6675 | 123 | 3.0232 | 2.0672
[7 empty] | 6676 | 124 | 2.9893 | 2.0416
[7 empty] | 6677 | 125 | 2.9469 | 2.0096
[7 empty] | 6678 | 126 | 3.091 | 2.1184
[7 empty] | 6679 | 127 | 4.6163 | 3.2699
[7 empty] | 6680 | 128 | 6.1924 | 4.4598
[7 empty] | 6681 | 129 | 6.8788 | 4.978
[7 empty] | 6682 | 130 | 7.3195 | 5.3107
[7 empty] | 6683 | 131 | 7.4805 | 5.4322
[7 empty] | 6684 | 132 | 7.2263 | 5.2403
[7 empty] | 6685 | 133 | 7.8703 | 5.7265
[7 empty] | 6686 | 134 | 8.1754 | 5.9568
[7 empty] | 6687 | 135 | 8.2431 | 6.008
[7 empty] | 6688 | 136 | 7.4212 | 5.3875
[7 empty] | 6689 | 137 | 7.3195 | 5.3107
[7 empty] | 6690 | 138 | 7.2686 | 5.2723
[7 empty] | 6691 | 139 | 6.9297 | 5.0164
[7 empty] | 6692 | 140 | 6.9382 | 5.0228
[7 empty] | 6693 | 141 | 6.2772 | 4.5238
[7 empty] | 6694 | 142 | 5.6332 | 4.0376
[7 empty] | 6695 | 143 | 4.7434 | 3.3659
[7 empty] | 6696 | 144 | 4.1248 | 2.8989
[7 empty] | 6697 | 145 | 3.6503 | 2.5406
[7 empty] | 6698 | 146 | 3.4384 | 2.3807
[7 empty] | 6699 | 147 | 3.3706 | 2.3295
[7 empty] | 6700 | 148 | 3.3622 | 2.3231
[7 empty] | 6701 | 149 | 3.3622 | 2.3231
[7 empty] | 6702 | 150 | 3.3706 | 2.3295
[7 empty] | 6703 | 151 | 4.4638 | 3.1547
[7 empty] | 6704 | 152 | 6.006 | 4.3191
[7 empty] | 6705 | 153 | 6.6246 | 4.7861
[7 empty] | 6706 | 154 | 7.1924 | 5.2147
[7 empty] | 6707 | 155 | 7.0398 | 5.0996
[7 empty] | 6708 | 156 | 7.2093 | 5.2275
[7 empty] | 6709 | 157 | 7.9296 | 5.7713
[7 empty] | 6710 | 158 | 8.2601 | 6.0208
[7 empty] | 6711 | 159 | 8.5313 | 6.2255
[7 empty] | 6712 | 160 | 8.4041 | 6.1296
[7 empty] | 6713 | 161 | 9.1753 | 6.7117
[7 empty] | 6714 | 162 | 8.6753 | 6.3343
[7 empty] | 6715 | 163 | 9.0397 | 6.6094
[7 empty] | 6716 | 164 | 7.6754 | 5.5794
[7 empty] | 6717 | 165 | 10.8362 | 7.9656
[7 empty] | 6718 | 166 | 8.7685 | 6.4046
[7 empty] | 6719 | 167 | 5.1247 | 3.6537
[7 empty] | 6720 | 168 | 4.4722 | 3.1611
[7 empty] | 6721 | 1 | 2.9978 | 2.048
[7 empty] | 6722 | 2 | 2.8876 | 1.9648
[7 empty] | 6723 | 3 | 2.8791 | 1.9584
[7 empty] | 6724 | 4 | 3.0147 | 2.0608
[7 empty] | 6725 | 5 | 3.0317 | 2.0736
[7 empty] | 6726 | 6 | 3.4638 | 2.3999
[7 empty] | 6727 | 7 | 4.1926 | 2.95
[7 empty] | 6728 | 8 | 4.8705 | 3.4618
[7 empty] | 6729 | 9 | 4.8451 | 3.4426
[7 empty] | 6730 | 10 | 6.3789 | 4.6006
[7 empty] | 6731 | 11 | 8.4804 | 6.1871
[7 empty] | 6732 | 12 | 9.4549 | 6.9228
[7 empty] | 6733 | 13 | 9.8362 | 7.2107
[7 empty] | 6734 | 14 | 9.6159 | 7.0444
[7 empty] | 6735 | 15 | 9.5227 | 6.974
[7 empty] | 6736 | 16 | 10.7175 | 7.8761
[7 empty] | 6737 | 17 | 12.0564 | 8.8868
[7 empty] | 6738 | 18 | 11.8107 | 8.7013
[7 empty] | 6739 | 19 | 12.3445 | 9.1044
[7 empty] | 6740 | 20 | 12.2767 | 9.0532
[7 empty] | 6741 | 21 | 12.853 | 9.4882
[7 empty] | 6742 | 22 | 8.8533 | 6.4686
[7 empty] | 6743 | 23 | 5.04 | 3.5898
[7 empty] | 6744 | 24 | 3.3504 | 2.3142
[7 empty] | 6745 | 25 | 3.252 | 2.2399
[7 empty] | 6746 | 26 | 3.1418 | 2.1567
[7 empty] | 6747 | 27 | 3.0401 | 2.08
[7 empty] | 6748 | 28 | 3.1249 | 2.144
[7 empty] | 6749 | 29 | 3.3706 | 2.3295
[7 empty] | 6750 | 30 | 3.6164 | 2.515
[7 empty] | 6751 | 31 | 4.4722 | 3.1611
[7 empty] | 6752 | 32 | 4.8281 | 3.4298
[7 empty] | 6753 | 33 | 5.4976 | 3.9352
[7 empty] | 6754 | 34 | 6.4043 | 4.6198
[7 empty] | 6755 | 35 | 8.5991 | 6.2767
[7 empty] | 6756 | 36 | 9.6413 | 7.0636
[7 empty] | 6757 | 37 | 9.7176 | 7.1212
[7 empty] | 6758 | 38 | 9.7939 | 7.1787
[7 empty] | 6759 | 39 | 9.4634 | 6.9292
[7 empty] | 6760 | 40 | 10.5311 | 7.7353
[7 empty] | 6761 | 41 | 11.0904 | 8.1575
[7 empty] | 6762 | 42 | 11.1073 | 8.1703
[7 empty] | 6763 | 43 | 11.4802 | 8.4518
[7 empty] | 6764 | 44 | 12.6496 | 9.3347
[7 empty] | 6765 | 45 | 12.2428 | 9.0276
[7 empty] | 6766 | 46 | 9.4634 | 6.9292
[7 empty] | 6767 | 47 | 5.8196 | 4.1783
[7 empty] | 6768 | 48 | 4.3028 | 3.0332
[7 empty] | 6769 | 49 | 3.6333 | 2.5278
[7 empty] | 6770 | 50 | 3.3198 | 2.2911
[7 empty] | 6771 | 51 | 3.2096 | 2.2079
[7 empty] | 6772 | 52 | 3.2435 | 2.2335
[7 empty] | 6773 | 53 | 3.2689 | 2.2527
[7 empty] | 6774 | 54 | 3.8536 | 2.6941
[7 empty] | 6775 | 55 | 5.0061 | 3.5642
[7 empty] | 6776 | 56 | 5.2518 | 3.7497
[7 empty] | 6777 | 57 | 6.2094 | 4.4726
[7 empty] | 6778 | 58 | 7.328 | 5.3171
[7 empty] | 6779 | 59 | 8.5482 | 6.2383
[7 empty] | 6780 | 60 | 9.1838 | 6.7181
[7 empty] | 6781 | 61 | 9.8701 | 7.2363
[7 empty] | 6782 | 62 | 9.6668 | 7.0828
[7 empty] | 6783 | 63 | 10.2684 | 7.537
[7 empty] | 6784 | 64 | 11.226 | 8.2599
[7 empty] | 6785 | 65 | 11.853 | 8.7333
[7 empty] | 6786 | 66 | 11.7514 | 8.6565
[7 empty] | 6787 | 67 | 12.4971 | 9.2195
[7 empty] | 6788 | 68 | 12.7428 | 9.405
[7 empty] | 6789 | 69 | 12.2259 | 9.0148
[7 empty] | 6790 | 70 | 9.904 | 7.2619
[7 empty] | 6791 | 71 | 5.3366 | 3.8137
[7 empty] | 6792 | 72 | 4.2398 | 2.9857
[7 empty] | 6793 | 73 | 3.5147 | 2.4382
[7 empty] | 6794 | 74 | 3.2859 | 2.2655
[7 empty] | 6795 | 75 | 3.1842 | 2.1887
[7 empty] | 6796 | 76 | 3.1249 | 2.144
[7 empty] | 6797 | 77 | 3.3028 | 2.2783
[7 empty] | 6798 | 78 | 3.7096 | 2.5854
[7 empty] | 6799 | 79 | 4.8366 | 3.4362
[7 empty] | 6800 | 80 | 5.0146 | 3.5706
[7 empty] | 6801 | 81 | 6.2094 | 4.4726
[7 empty] | 6802 | 82 | 7.311 | 5.3043
[7 empty] | 6803 | 83 | 8.0567 | 5.8673
[7 empty] | 6804 | 84 | 9.3109 | 6.8141
[7 empty] | 6805 | 85 | 9.0058 | 6.5838
[7 empty] | 6806 | 86 | 8.4889 | 6.1935
[7 empty] | 6807 | 87 | 8.938 | 6.5326
[7 empty] | 6808 | 88 | 9.6075 | 7.038
[7 empty] | 6809 | 89 | 10.9718 | 8.068
[7 empty] | 6810 | 90 | 10.3786 | 7.6202
[7 empty] | 6811 | 91 | 11.0734 | 8.1447
[7 empty] | 6812 | 92 | 10.4633 | 7.6841
[7 empty] | 6813 | 93 | 8.0228 | 5.8417
[7 empty] | 6814 | 94 | 7.1076 | 5.1507
[7 empty] | 6815 | 95 | 5.2264 | 3.7305
[7 empty] | 6816 | 96 | 4.2265 | 2.9756
[7 empty] | 6817 | 97 | 4.1757 | 2.9372
[7 empty] | 6818 | 98 | 3.8791 | 2.7133
[7 empty] | 6819 | 99 | 3.8197 | 2.6685
[7 empty] | 6820 | 100 | 3.4638 | 2.3999
[7 empty] | 6821 | 101 | 3.4045 | 2.3551
[7 empty] | 6822 | 102 | 3.6418 | 2.5342
[7 empty] | 6823 | 103 | 4.396 | 3.1036
[7 empty] | 6824 | 104 | 4.6502 | 3.2955
[7 empty] | 6825 | 105 | 5.1417 | 3.6665
[7 empty] | 6826 | 106 | 6.6161 | 4.7797
[7 empty] | 6827 | 107 | 6.9721 | 5.0484
[7 empty] | 6828 | 108 | 8.5652 | 6.2511
[7 empty] | 6829 | 109 | 7.8957 | 5.7457
[7 empty] | 6830 | 110 | 7.4381 | 5.4002
[7 empty] | 6831 | 111 | 7.2771 | 5.2787
[7 empty] | 6832 | 112 | 7.3449 | 5.3299
[7 empty] | 6833 | 113 | 6.9975 | 5.0676
[7 empty] | 6834 | 114 | 7.167 | 5.1955
[7 empty] | 6835 | 115 | 6.7094 | 4.8501
[7 empty] | 6836 | 116 | 7.3958 | 5.3683
[7 empty] | 6837 | 117 | 6.9721 | 5.0484
[7 empty] | 6838 | 118 | 6.1924 | 4.4598
[7 empty] | 6839 | 119 | 4.5824 | 3.2443
[7 empty] | 6840 | 120 | 4.2615 | 3.0021
[7 empty] | 6841 | 121 | 3.5232 | 2.4446
[7 empty] | 6842 | 122 | 3.1079 | 2.1312
[7 empty] | 6843 | 123 | 3.0232 | 2.0672
[7 empty] | 6844 | 124 | 2.9893 | 2.0416
[7 empty] | 6845 | 125 | 2.9469 | 2.0096
[7 empty] | 6846 | 126 | 3.091 | 2.1184
[7 empty] | 6847 | 127 | 4.6163 | 3.2699
[7 empty] | 6848 | 128 | 6.1924 | 4.4598
[7 empty] | 6849 | 129 | 6.8788 | 4.978
[7 empty] | 6850 | 130 | 7.3195 | 5.3107
[7 empty] | 6851 | 131 | 7.4805 | 5.4322
[7 empty] | 6852 | 132 | 7.2263 | 5.2403
[7 empty] | 6853 | 133 | 7.8703 | 5.7265
[7 empty] | 6854 | 134 | 8.1754 | 5.9568
[7 empty] | 6855 | 135 | 8.2431 | 6.008
[7 empty] | 6856 | 136 | 7.4212 | 5.3875
[7 empty] | 6857 | 137 | 7.3195 | 5.3107
[7 empty] | 6858 | 138 | 7.2686 | 5.2723
[7 empty] | 6859 | 139 | 6.9297 | 5.0164
[7 empty] | 6860 | 140 | 6.9382 | 5.0228
[7 empty] | 6861 | 141 | 6.2772 | 4.5238
[7 empty] | 6862 | 142 | 5.6332 | 4.0376
[7 empty] | 6863 | 143 | 4.7434 | 3.3659
[7 empty] | 6864 | 144 | 4.1248 | 2.8989
[7 empty] | 6865 | 145 | 3.6503 | 2.5406
[7 empty] | 6866 | 146 | 3.4384 | 2.3807
[7 empty] | 6867 | 147 | 3.3706 | 2.3295
[7 empty] | 6868 | 148 | 3.3622 | 2.3231
[7 empty] | 6869 | 149 | 3.3622 | 2.3231
[7 empty] | 6870 | 150 | 3.3706 | 2.3295
[7 empty] | 6871 | 151 | 4.4638 | 3.1547
[7 empty] | 6872 | 152 | 6.006 | 4.3191
[7 empty] | 6873 | 153 | 6.6246 | 4.7861
[7 empty] | 6874 | 154 | 7.1924 | 5.2147
[7 empty] | 6875 | 155 | 7.0398 | 5.0996
[7 empty] | 6876 | 156 | 7.2093 | 5.2275
[7 empty] | 6877 | 157 | 7.9296 | 5.7713
[7 empty] | 6878 | 158 | 8.2601 | 6.0208
[7 empty] | 6879 | 159 | 8.5313 | 6.2255
[7 empty] | 6880 | 160 | 8.4041 | 6.1296
[7 empty] | 6881 | 161 | 9.1753 | 6.7117
[7 empty] | 6882 | 162 | 8.6753 | 6.3343
[7 empty] | 6883 | 163 | 9.0397 | 6.6094
[7 empty] | 6884 | 164 | 7.6754 | 5.5794
[7 empty] | 6885 | 165 | 10.8362 | 7.9656
[7 empty] | 6886 | 166 | 8.7685 | 6.4046
[7 empty] | 6887 | 167 | 5.1247 | 3.6537
[7 empty] | 6888 | 168 | 4.4722 | 3.1611
[7 empty] | 6889 | 1 | 2.9978 | 2.048
[7 empty] | 6890 | 2 | 2.8876 | 1.9648
[7 empty] | 6891 | 3 | 2.8791 | 1.9584
[7 empty] | 6892 | 4 | 3.0147 | 2.0608
[7 empty] | 6893 | 5 | 3.0317 | 2.0736
[7 empty] | 6894 | 6 | 3.4638 | 2.3999
[7 empty] | 6895 | 7 | 4.1926 | 2.95
[7 empty] | 6896 | 8 | 4.8705 | 3.4618
[7 empty] | 6897 | 9 | 4.8451 | 3.4426
[7 empty] | 6898 | 10 | 6.3789 | 4.6006
[7 empty] | 6899 | 11 | 8.4804 | 6.1871
[7 empty] | 6900 | 12 | 9.4549 | 6.9228
[7 empty] | 6901 | 13 | 9.8362 | 7.2107
[7 empty] | 6902 | 14 | 9.6159 | 7.0444
[7 empty] | 6903 | 15 | 9.5227 | 6.974
[7 empty] | 6904 | 16 | 10.7175 | 7.8761
[7 empty] | 6905 | 17 | 12.0564 | 8.8868
[7 empty] | 6906 | 18 | 11.8107 | 8.7013
[7 empty] | 6907 | 19 | 12.3445 | 9.1044
[7 empty] | 6908 | 20 | 12.2767 | 9.0532
[7 empty] | 6909 | 21 | 12.853 | 9.4882
[7 empty] | 6910 | 22 | 8.8533 | 6.4686
[7 empty] | 6911 | 23 | 5.04 | 3.5898
[7 empty] | 6912 | 24 | 3.3504 | 2.3142
[7 empty] | 6913 | 25 | 3.252 | 2.2399
[7 empty] | 6914 | 26 | 3.1418 | 2.1567
[7 empty] | 6915 | 27 | 3.0401 | 2.08
[7 empty] | 6916 | 28 | 3.1249 | 2.144
[7 empty] | 6917 | 29 | 3.3706 | 2.3295
[7 empty] | 6918 | 30 | 3.6164 | 2.515
[7 empty] | 6919 | 31 | 4.4722 | 3.1611
[7 empty] | 6920 | 32 | 4.8281 | 3.4298
[7 empty] | 6921 | 33 | 5.4976 | 3.9352
[7 empty] | 6922 | 34 | 6.4043 | 4.6198
[7 empty] | 6923 | 35 | 8.5991 | 6.2767
[7 empty] | 6924 | 36 | 9.6413 | 7.0636
[7 empty] | 6925 | 37 | 9.7176 | 7.1212
[7 empty] | 6926 | 38 | 9.7939 | 7.1787
[7 empty] | 6927 | 39 | 9.4634 | 6.9292
[7 empty] | 6928 | 40 | 10.5311 | 7.7353
[7 empty] | 6929 | 41 | 11.0904 | 8.1575
[7 empty] | 6930 | 42 | 11.1073 | 8.1703
[7 empty] | 6931 | 43 | 11.4802 | 8.4518
[7 empty] | 6932 | 44 | 12.6496 | 9.3347
[7 empty] | 6933 | 45 | 12.2428 | 9.0276
[7 empty] | 6934 | 46 | 9.4634 | 6.9292
[7 empty] | 6935 | 47 | 5.8196 | 4.1783
[7 empty] | 6936 | 48 | 4.3028 | 3.0332
[7 empty] | 6937 | 49 | 3.6333 | 2.5278
[7 empty] | 6938 | 50 | 3.3198 | 2.2911
[7 empty] | 6939 | 51 | 3.2096 | 2.2079
[7 empty] | 6940 | 52 | 3.2435 | 2.2335
[7 empty] | 6941 | 53 | 3.2689 | 2.2527
[7 empty] | 6942 | 54 | 3.8536 | 2.6941
[7 empty] | 6943 | 55 | 5.0061 | 3.5642
[7 empty] | 6944 | 56 | 5.2518 | 3.7497
[7 empty] | 6945 | 57 | 6.2094 | 4.4726
[7 empty] | 6946 | 58 | 7.328 | 5.3171
[7 empty] | 6947 | 59 | 8.5482 | 6.2383
[7 empty] | 6948 | 60 | 9.1838 | 6.7181
[7 empty] | 6949 | 61 | 9.8701 | 7.2363
[7 empty] | 6950 | 62 | 9.6668 | 7.0828
[7 empty] | 6951 | 63 | 10.2684 | 7.537
[7 empty] | 6952 | 64 | 11.226 | 8.2599
[7 empty] | 6953 | 65 | 11.853 | 8.7333
[7 empty] | 6954 | 66 | 11.7514 | 8.6565
[7 empty] | 6955 | 67 | 12.4971 | 9.2195
[7 empty] | 6956 | 68 | 12.7428 | 9.405
[7 empty] | 6957 | 69 | 12.2259 | 9.0148
[7 empty] | 6958 | 70 | 9.904 | 7.2619
[7 empty] | 6959 | 71 | 5.3366 | 3.8137
[7 empty] | 6960 | 72 | 4.2398 | 2.9857
[7 empty] | 6961 | 73 | 3.5147 | 2.4382
[7 empty] | 6962 | 74 | 3.2859 | 2.2655
[7 empty] | 6963 | 75 | 3.1842 | 2.1887
[7 empty] | 6964 | 76 | 3.1249 | 2.144
[7 empty] | 6965 | 77 | 3.3028 | 2.2783
[7 empty] | 6966 | 78 | 3.7096 | 2.5854
[7 empty] | 6967 | 79 | 4.8366 | 3.4362
[7 empty] | 6968 | 80 | 5.0146 | 3.5706
[7 empty] | 6969 | 81 | 6.2094 | 4.4726
[7 empty] | 6970 | 82 | 7.311 | 5.3043
[7 empty] | 6971 | 83 | 8.0567 | 5.8673
[7 empty] | 6972 | 84 | 9.3109 | 6.8141
[7 empty] | 6973 | 85 | 9.0058 | 6.5838
[7 empty] | 6974 | 86 | 8.4889 | 6.1935
[7 empty] | 6975 | 87 | 8.938 | 6.5326
[7 empty] | 6976 | 88 | 9.6075 | 7.038
[7 empty] | 6977 | 89 | 10.9718 | 8.068
[7 empty] | 6978 | 90 | 10.3786 | 7.6202
[7 empty] | 6979 | 91 | 11.0734 | 8.1447
[7 empty] | 6980 | 92 | 10.4633 | 7.6841
[7 empty] | 6981 | 93 | 8.0228 | 5.8417
[7 empty] | 6982 | 94 | 7.1076 | 5.1507
[7 empty] | 6983 | 95 | 5.2264 | 3.7305
[7 empty] | 6984 | 96 | 4.2265 | 2.9756
[7 empty] | 6985 | 97 | 4.1757 | 2.9372
[7 empty] | 6986 | 98 | 3.8791 | 2.7133
[7 empty] | 6987 | 99 | 3.8197 | 2.6685
[7 empty] | 6988 | 100 | 3.4638 | 2.3999
[7 empty] | 6989 | 101 | 3.4045 | 2.3551
[7 empty] | 6990 | 102 | 3.6418 | 2.5342
[7 empty] | 6991 | 103 | 4.396 | 3.1036
[7 empty] | 6992 | 104 | 4.6502 | 3.2955
[7 empty] | 6993 | 105 | 5.1417 | 3.6665
[7 empty] | 6994 | 106 | 6.6161 | 4.7797
[7 empty] | 6995 | 107 | 6.9721 | 5.0484
[7 empty] | 6996 | 108 | 8.5652 | 6.2511
[7 empty] | 6997 | 109 | 7.8957 | 5.7457
[7 empty] | 6998 | 110 | 7.4381 | 5.4002
[7 empty] | 6999 | 111 | 7.2771 | 5.2787
[7 empty] | 7000 | 112 | 7.3449 | 5.3299
[7 empty] | 7001 | 113 | 6.9975 | 5.0676
[7 empty] | 7002 | 114 | 7.167 | 5.1955
[7 empty] | 7003 | 115 | 6.7094 | 4.8501
[7 empty] | 7004 | 116 | 7.3958 | 5.3683
[7 empty] | 7005 | 117 | 6.9721 | 5.0484
[7 empty] | 7006 | 118 | 6.1924 | 4.4598
[7 empty] | 7007 | 119 | 4.5824 | 3.2443
[7 empty] | 7008 | 120 | 4.2615 | 3.0021
[7 empty] | 7009 | 121 | 3.5232 | 2.4446
[7 empty] | 7010 | 122 | 3.1079 | 2.1312
[7 empty] | 7011 | 123 | 3.0232 | 2.0672
[7 empty] | 7012 | 124 | 2.9893 | 2.0416
[7 empty] | 7013 | 125 | 2.9469 | 2.0096
[7 empty] | 7014 | 126 | 3.091 | 2.1184
[7 empty] | 7015 | 127 | 4.6163 | 3.2699
[7 empty] | 7016 | 128 | 6.1924 | 4.4598
[7 empty] | 7017 | 129 | 6.8788 | 4.978
[7 empty] | 7018 | 130 | 7.3195 | 5.3107
[7 empty] | 7019 | 131 | 7.4805 | 5.4322
[7 empty] | 7020 | 132 | 7.2263 | 5.2403
[7 empty] | 7021 | 133 | 7.8703 | 5.7265
[7 empty] | 7022 | 134 | 8.1754 | 5.9568
[7 empty] | 7023 | 135 | 8.2431 | 6.008
[7 empty] | 7024 | 136 | 7.4212 | 5.3875
[7 empty] | 7025 | 137 | 7.3195 | 5.3107
[7 empty] | 7026 | 138 | 7.2686 | 5.2723
[7 empty] | 7027 | 139 | 6.9297 | 5.0164
[7 empty] | 7028 | 140 | 6.9382 | 5.0228
[7 empty] | 7029 | 141 | 6.2772 | 4.5238
[7 empty] | 7030 | 142 | 5.6332 | 4.0376
[7 empty] | 7031 | 143 | 4.7434 | 3.3659
[7 empty] | 7032 | 144 | 4.1248 | 2.8989
[7 empty] | 7033 | 145 | 3.6503 | 2.5406
[7 empty] | 7034 | 146 | 3.4384 | 2.3807
[7 empty] | 7035 | 147 | 3.3706 | 2.3295
[7 empty] | 7036 | 148 | 3.3622 | 2.3231
[7 empty] | 7037 | 149 | 3.3622 | 2.3231
[7 empty] | 7038 | 150 | 3.3706 | 2.3295
[7 empty] | 7039 | 151 | 4.4638 | 3.1547
[7 empty] | 7040 | 152 | 6.006 | 4.3191
[7 empty] | 7041 | 153 | 6.6246 | 4.7861
[7 empty] | 7042 | 154 | 7.1924 | 5.2147
[7 empty] | 7043 | 155 | 7.0398 | 5.0996
[7 empty] | 7044 | 156 | 7.2093 | 5.2275
[7 empty] | 7045 | 157 | 7.9296 | 5.7713
[7 empty] | 7046 | 158 | 8.2601 | 6.0208
[7 empty] | 7047 | 159 | 8.5313 | 6.2255
[7 empty] | 7048 | 160 | 8.4041 | 6.1296
[7 empty] | 7049 | 161 | 9.1753 | 6.7117
[7 empty] | 7050 | 162 | 8.6753 | 6.3343
[7 empty] | 7051 | 163 | 9.0397 | 6.6094
[7 empty] | 7052 | 164 | 7.6754 | 5.5794
[7 empty] | 7053 | 165 | 10.8362 | 7.9656
[7 empty] | 7054 | 166 | 8.7685 | 6.4046
[7 empty] | 7055 | 167 | 5.1247 | 3.6537
[7 empty] | 7056 | 168 | 4.4722 | 3.1611
[7 empty] | 7057 | 1 | 2.9978 | 2.048
[7 empty] | 7058 | 2 | 2.8876 | 1.9648
[7 empty] | 7059 | 3 | 2.8791 | 1.9584
[7 empty] | 7060 | 4 | 3.0147 | 2.0608
[7 empty] | 7061 | 5 | 3.0317 | 2.0736
[7 empty] | 7062 | 6 | 3.4638 | 2.3999
[7 empty] | 7063 | 7 | 4.1926 | 2.95
[7 empty] | 7064 | 8 | 4.8705 | 3.4618
[7 empty] | 7065 | 9 | 4.8451 | 3.4426
[7 empty] | 7066 | 10 | 6.3789 | 4.6006
[7 empty] | 7067 | 11 | 8.4804 | 6.1871
[7 empty] | 7068 | 12 | 9.4549 | 6.9228
[7 empty] | 7069 | 13 | 9.8362 | 7.2107
[7 empty] | 7070 | 14 | 9.6159 | 7.0444
[7 empty] | 7071 | 15 | 9.5227 | 6.974
[7 empty] | 7072 | 16 | 10.7175 | 7.8761
[7 empty] | 7073 | 17 | 12.0564 | 8.8868
[7 empty] | 7074 | 18 | 11.8107 | 8.7013
[7 empty] | 7075 | 19 | 12.3445 | 9.1044
[7 empty] | 7076 | 20 | 12.2767 | 9.0532
[7 empty] | 7077 | 21 | 12.853 | 9.4882
[7 empty] | 7078 | 22 | 8.8533 | 6.4686
[7 empty] | 7079 | 23 | 5.04 | 3.5898
[7 empty] | 7080 | 24 | 3.3504 | 2.3142
[7 empty] | 7081 | 25 | 3.252 | 2.2399
[7 empty] | 7082 | 26 | 3.1418 | 2.1567
[7 empty] | 7083 | 27 | 3.0401 | 2.08
[7 empty] | 7084 | 28 | 3.1249 | 2.144
[7 empty] | 7085 | 29 | 3.3706 | 2.3295
[7 empty] | 7086 | 30 | 3.6164 | 2.515
[7 empty] | 7087 | 31 | 4.4722 | 3.1611
[7 empty] | 7088 | 32 | 4.8281 | 3.4298
[7 empty] | 7089 | 33 | 5.4976 | 3.9352
[7 empty] | 7090 | 34 | 6.4043 | 4.6198
[7 empty] | 7091 | 35 | 8.5991 | 6.2767
[7 empty] | 7092 | 36 | 9.6413 | 7.0636
[7 empty] | 7093 | 37 | 9.7176 | 7.1212
[7 empty] | 7094 | 38 | 9.7939 | 7.1787
[7 empty] | 7095 | 39 | 9.4634 | 6.9292
[7 empty] | 7096 | 40 | 10.5311 | 7.7353
[7 empty] | 7097 | 41 | 11.0904 | 8.1575
[7 empty] | 7098 | 42 | 11.1073 | 8.1703
[7 empty] | 7099 | 43 | 11.4802 | 8.4518
[7 empty] | 7100 | 44 | 12.6496 | 9.3347
[7 empty] | 7101 | 45 | 12.2428 | 9.0276
[7 empty] | 7102 | 46 | 9.4634 | 6.9292
[7 empty] | 7103 | 47 | 5.8196 | 4.1783
[7 empty] | 7104 | 48 | 4.3028 | 3.0332
[7 empty] | 7105 | 49 | 3.6333 | 2.5278
[7 empty] | 7106 | 50 | 3.3198 | 2.2911
[7 empty] | 7107 | 51 | 3.2096 | 2.2079
[7 empty] | 7108 | 52 | 3.2435 | 2.2335
[7 empty] | 7109 | 53 | 3.2689 | 2.2527
[7 empty] | 7110 | 54 | 3.8536 | 2.6941
[7 empty] | 7111 | 55 | 5.0061 | 3.5642
[7 empty] | 7112 | 56 | 5.2518 | 3.7497
[7 empty] | 7113 | 57 | 6.2094 | 4.4726
[7 empty] | 7114 | 58 | 7.328 | 5.3171
[7 empty] | 7115 | 59 | 8.5482 | 6.2383
[7 empty] | 7116 | 60 | 9.1838 | 6.7181
[7 empty] | 7117 | 61 | 9.8701 | 7.2363
[7 empty] | 7118 | 62 | 9.6668 | 7.0828
[7 empty] | 7119 | 63 | 10.2684 | 7.537
[7 empty] | 7120 | 64 | 11.226 | 8.2599
[7 empty] | 7121 | 65 | 11.853 | 8.7333
[7 empty] | 7122 | 66 | 11.7514 | 8.6565
[7 empty] | 7123 | 67 | 12.4971 | 9.2195
[7 empty] | 7124 | 68 | 12.7428 | 9.405
[7 empty] | 7125 | 69 | 12.2259 | 9.0148
[7 empty] | 7126 | 70 | 9.904 | 7.2619
[7 empty] | 7127 | 71 | 5.3366 | 3.8137
[7 empty] | 7128 | 72 | 4.2398 | 2.9857
[7 empty] | 7129 | 73 | 3.5147 | 2.4382
[7 empty] | 7130 | 74 | 3.2859 | 2.2655
[7 empty] | 7131 | 75 | 3.1842 | 2.1887
[7 empty] | 7132 | 76 | 3.1249 | 2.144
[7 empty] | 7133 | 77 | 3.3028 | 2.2783
[7 empty] | 7134 | 78 | 3.7096 | 2.5854
[7 empty] | 7135 | 79 | 4.8366 | 3.4362
[7 empty] | 7136 | 80 | 5.0146 | 3.5706
[7 empty] | 7137 | 81 | 6.2094 | 4.4726
[7 empty] | 7138 | 82 | 7.311 | 5.3043
[7 empty] | 7139 | 83 | 8.0567 | 5.8673
[7 empty] | 7140 | 84 | 9.3109 | 6.8141
[7 empty] | 7141 | 85 | 9.0058 | 6.5838
[7 empty] | 7142 | 86 | 8.4889 | 6.1935
[7 empty] | 7143 | 87 | 8.938 | 6.5326
[7 empty] | 7144 | 88 | 9.6075 | 7.038
[7 empty] | 7145 | 89 | 10.9718 | 8.068
[7 empty] | 7146 | 90 | 10.3786 | 7.6202
[7 empty] | 7147 | 91 | 11.0734 | 8.1447
[7 empty] | 7148 | 92 | 10.4633 | 7.6841
[7 empty] | 7149 | 93 | 8.0228 | 5.8417
[7 empty] | 7150 | 94 | 7.1076 | 5.1507
[7 empty] | 7151 | 95 | 5.2264 | 3.7305
[7 empty] | 7152 | 96 | 4.2265 | 2.9756
[7 empty] | 7153 | 97 | 4.1757 | 2.9372
[7 empty] | 7154 | 98 | 3.8791 | 2.7133
[7 empty] | 7155 | 99 | 3.8197 | 2.6685
[7 empty] | 7156 | 100 | 3.4638 | 2.3999
[7 empty] | 7157 | 101 | 3.4045 | 2.3551
[7 empty] | 7158 | 102 | 3.6418 | 2.5342
[7 empty] | 7159 | 103 | 4.396 | 3.1036
[7 empty] | 7160 | 104 | 4.6502 | 3.2955
[7 empty] | 7161 | 105 | 5.1417 | 3.6665
[7 empty] | 7162 | 106 | 6.6161 | 4.7797
[7 empty] | 7163 | 107 | 6.9721 | 5.0484
[7 empty] | 7164 | 108 | 8.5652 | 6.2511
[7 empty] | 7165 | 109 | 7.8957 | 5.7457
[7 empty] | 7166 | 110 | 7.4381 | 5.4002
[7 empty] | 7167 | 111 | 7.2771 | 5.2787
[7 empty] | 7168 | 112 | 7.3449 | 5.3299
[7 empty] | 7169 | 113 | 6.9975 | 5.0676
[7 empty] | 7170 | 114 | 7.167 | 5.1955
[7 empty] | 7171 | 115 | 6.7094 | 4.8501
[7 empty] | 7172 | 116 | 7.3958 | 5.3683
[7 empty] | 7173 | 117 | 6.9721 | 5.0484
[7 empty] | 7174 | 118 | 6.1924 | 4.4598
[7 empty] | 7175 | 119 | 4.5824 | 3.2443
[7 empty] | 7176 | 120 | 4.2615 | 3.0021
[7 empty] | 7177 | 121 | 3.5232 | 2.4446
[7 empty] | 7178 | 122 | 3.1079 | 2.1312
[7 empty] | 7179 | 123 | 3.0232 | 2.0672
[7 empty] | 7180 | 124 | 2.9893 | 2.0416
[7 empty] | 7181 | 125 | 2.9469 | 2.0096
[7 empty] | 7182 | 126 | 3.091 | 2.1184
[7 empty] | 7183 | 127 | 4.6163 | 3.2699
[7 empty] | 7184 | 128 | 6.1924 | 4.4598
[7 empty] | 7185 | 129 | 6.8788 | 4.978
[7 empty] | 7186 | 130 | 7.3195 | 5.3107
[7 empty] | 7187 | 131 | 7.4805 | 5.4322
[7 empty] | 7188 | 132 | 7.2263 | 5.2403
[7 empty] | 7189 | 133 | 7.8703 | 5.7265
[7 empty] | 7190 | 134 | 8.1754 | 5.9568
[7 empty] | 7191 | 135 | 8.2431 | 6.008
[7 empty] | 7192 | 136 | 7.4212 | 5.3875
[7 empty] | 7193 | 137 | 7.3195 | 5.3107
[7 empty] | 7194 | 138 | 7.2686 | 5.2723
[7 empty] | 7195 | 139 | 6.9297 | 5.0164
[7 empty] | 7196 | 140 | 6.9382 | 5.0228
[7 empty] | 7197 | 141 | 6.2772 | 4.5238
[7 empty] | 7198 | 142 | 5.6332 | 4.0376
[7 empty] | 7199 | 143 | 4.7434 | 3.3659
[7 empty] | 7200 | 144 | 4.1248 | 2.8989
[7 empty] | 7201 | 145 | 3.6503 | 2.5406
[7 empty] | 7202 | 146 | 3.4384 | 2.3807
[7 empty] | 7203 | 147 | 3.3706 | 2.3295
[7 empty] | 7204 | 148 | 3.3622 | 2.3231
[7 empty] | 7205 | 149 | 3.3622 | 2.3231
[7 empty] | 7206 | 150 | 3.3706 | 2.3295
[7 empty] | 7207 | 151 | 4.4638 | 3.1547
[7 empty] | 7208 | 152 | 6.006 | 4.3191
[7 empty] | 7209 | 153 | 6.6246 | 4.7861
[7 empty] | 7210 | 154 | 7.1924 | 5.2147
[7 empty] | 7211 | 155 | 7.0398 | 5.0996
[7 empty] | 7212 | 156 | 7.2093 | 5.2275
[7 empty] | 7213 | 157 | 7.9296 | 5.7713
[7 empty] | 7214 | 158 | 8.2601 | 6.0208
[7 empty] | 7215 | 159 | 8.5313 | 6.2255
[7 empty] | 7216 | 160 | 8.4041 | 6.1296
[7 empty] | 7217 | 161 | 9.1753 | 6.7117
[7 empty] | 7218 | 162 | 8.6753 | 6.3343
[7 empty] | 7219 | 163 | 9.0397 | 6.6094
[7 empty] | 7220 | 164 | 7.6754 | 5.5794
[7 empty] | 7221 | 165 | 10.8362 | 7.9656
[7 empty] | 7222 | 166 | 8.7685 | 6.4046
[7 empty] | 7223 | 167 | 5.1247 | 3.6537
[7 empty] | 7224 | 168 | 4.4722 | 3.1611
[7 empty] | 7225 | 1 | 2.9978 | 2.048
[7 empty] | 7226 | 2 | 2.8876 | 1.9648
[7 empty] | 7227 | 3 | 2.8791 | 1.9584
[7 empty] | 7228 | 4 | 3.0147 | 2.0608
[7 empty] | 7229 | 5 | 3.0317 | 2.0736
[7 empty] | 7230 | 6 | 3.4638 | 2.3999
[7 empty] | 7231 | 7 | 4.1926 | 2.95
[7 empty] | 7232 | 8 | 4.8705 | 3.4618
[7 empty] | 7233 | 9 | 4.8451 | 3.4426
[7 empty] | 7234 | 10 | 6.3789 | 4.6006
[7 empty] | 7235 | 11 | 8.4804 | 6.1871
[7 empty] | 7236 | 12 | 9.4549 | 6.9228
[7 empty] | 7237 | 13 | 9.8362 | 7.2107
[7 empty] | 7238 | 14 | 9.6159 | 7.0444
[7 empty] | 7239 | 15 | 9.5227 | 6.974
[7 empty] | 7240 | 16 | 10.7175 | 7.8761
[7 empty] | 7241 | 17 | 12.0564 | 8.8868
[7 empty] | 7242 | 18 | 11.8107 | 8.7013
[7 empty] | 7243 | 19 | 12.3445 | 9.1044
[7 empty] | 7244 | 20 | 12.2767 | 9.0532
[7 empty] | 7245 | 21 | 12.853 | 9.4882
[7 empty] | 7246 | 22 | 8.8533 | 6.4686
[7 empty] | 7247 | 23 | 5.04 | 3.5898
[7 empty] | 7248 | 24 | 3.3504 | 2.3142
[7 empty] | 7249 | 25 | 3.252 | 2.2399
[7 empty] | 7250 | 26 | 3.1418 | 2.1567
[7 empty] | 7251 | 27 | 3.0401 | 2.08
[7 empty] | 7252 | 28 | 3.1249 | 2.144
[7 empty] | 7253 | 29 | 3.3706 | 2.3295
[7 empty] | 7254 | 30 | 3.6164 | 2.515
[7 empty] | 7255 | 31 | 4.4722 | 3.1611
[7 empty] | 7256 | 32 | 4.8281 | 3.4298
[7 empty] | 7257 | 33 | 5.4976 | 3.9352
[7 empty] | 7258 | 34 | 6.4043 | 4.6198
[7 empty] | 7259 | 35 | 8.5991 | 6.2767
[7 empty] | 7260 | 36 | 9.6413 | 7.0636
[7 empty] | 7261 | 37 | 9.7176 | 7.1212
[7 empty] | 7262 | 38 | 9.7939 | 7.1787
[7 empty] | 7263 | 39 | 9.4634 | 6.9292
[7 empty] | 7264 | 40 | 10.5311 | 7.7353
[7 empty] | 7265 | 41 | 11.0904 | 8.1575
[7 empty] | 7266 | 42 | 11.1073 | 8.1703
[7 empty] | 7267 | 43 | 11.4802 | 8.4518
[7 empty] | 7268 | 44 | 12.6496 | 9.3347
[7 empty] | 7269 | 45 | 12.2428 | 9.0276
[7 empty] | 7270 | 46 | 9.4634 | 6.9292
[7 empty] | 7271 | 47 | 5.8196 | 4.1783
[7 empty] | 7272 | 48 | 4.3028 | 3.0332
[7 empty] | 7273 | 49 | 3.6333 | 2.5278
[7 empty] | 7274 | 50 | 3.3198 | 2.2911
[7 empty] | 7275 | 51 | 3.2096 | 2.2079
[7 empty] | 7276 | 52 | 3.2435 | 2.2335
[7 empty] | 7277 | 53 | 3.2689 | 2.2527
[7 empty] | 7278 | 54 | 3.8536 | 2.6941
[7 empty] | 7279 | 55 | 5.0061 | 3.5642
[7 empty] | 7280 | 56 | 5.2518 | 3.7497
[7 empty] | 7281 | 57 | 6.2094 | 4.4726
[7 empty] | 7282 | 58 | 7.328 | 5.3171
[7 empty] | 7283 | 59 | 8.5482 | 6.2383
[7 empty] | 7284 | 60 | 9.1838 | 6.7181
[7 empty] | 7285 | 61 | 9.8701 | 7.2363
[7 empty] | 7286 | 62 | 9.6668 | 7.0828
[7 empty] | 7287 | 63 | 10.2684 | 7.537
[7 empty] | 7288 | 64 | 11.226 | 8.2599
[7 empty] | 7289 | 65 | 11.853 | 8.7333
[7 empty] | 7290 | 66 | 11.7514 | 8.6565
[7 empty] | 7291 | 67 | 12.4971 | 9.2195
[7 empty] | 7292 | 68 | 12.7428 | 9.405
[7 empty] | 7293 | 69 | 12.2259 | 9.0148
[7 empty] | 7294 | 70 | 9.904 | 7.2619
[7 empty] | 7295 | 71 | 5.3366 | 3.8137
[7 empty] | 7296 | 72 | 4.2398 | 2.9857
[7 empty] | 7297 | 73 | 3.5147 | 2.4382
[7 empty] | 7298 | 74 | 3.2859 | 2.2655
[7 empty] | 7299 | 75 | 3.1842 | 2.1887
[7 empty] | 7300 | 76 | 3.1249 | 2.144
[7 empty] | 7301 | 77 | 3.3028 | 2.2783
[7 empty] | 7302 | 78 | 3.7096 | 2.5854
[7 empty] | 7303 | 79 | 4.8366 | 3.4362
[7 empty] | 7304 | 80 | 5.0146 | 3.5706
[7 empty] | 7305 | 81 | 6.2094 | 4.4726
[7 empty] | 7306 | 82 | 7.311 | 5.3043
[7 empty] | 7307 | 83 | 8.0567 | 5.8673
[7 empty] | 7308 | 84 | 9.3109 | 6.8141
[7 empty] | 7309 | 85 | 9.0058 | 6.5838
[7 empty] | 7310 | 86 | 8.4889 | 6.1935
[7 empty] | 7311 | 87 | 8.938 | 6.5326
[7 empty] | 7312 | 88 | 9.6075 | 7.038
[7 empty] | 7313 | 89 | 10.9718 | 8.068
[7 empty] | 7314 | 90 | 10.3786 | 7.6202
[7 empty] | 7315 | 91 | 11.0734 | 8.1447
[7 empty] | 7316 | 92 | 10.4633 | 7.6841
[7 empty] | 7317 | 93 | 8.0228 | 5.8417
[7 empty] | 7318 | 94 | 7.1076 | 5.1507
[7 empty] | 7319 | 95 | 5.2264 | 3.7305
[7 empty] | 7320 | 96 | 4.2265 | 2.9756
[7 empty] | 7321 | 97 | 4.1757 | 2.9372
[7 empty] | 7322 | 98 | 3.8791 | 2.7133
[7 empty] | 7323 | 99 | 3.8197 | 2.6685
[7 empty] | 7324 | 100 | 3.4638 | 2.3999
[7 empty] | 7325 | 101 | 3.4045 | 2.3551
[7 empty] | 7326 | 102 | 3.6418 | 2.5342
[7 empty] | 7327 | 103 | 4.396 | 3.1036
[7 empty] | 7328 | 104 | 4.6502 | 3.2955
[7 empty] | 7329 | 105 | 5.1417 | 3.6665
[7 empty] | 7330 | 106 | 6.6161 | 4.7797
[7 empty] | 7331 | 107 | 6.9721 | 5.0484
[7 empty] | 7332 | 108 | 8.5652 | 6.2511
[7 empty] | 7333 | 109 | 7.8957 | 5.7457
[7 empty] | 7334 | 110 | 7.4381 | 5.4002
[7 empty] | 7335 | 111 | 7.2771 | 5.2787
[7 empty] | 7336 | 112 | 7.3449 | 5.3299
[7 empty] | 7337 | 113 | 6.9975 | 5.0676
[7 empty] | 7338 | 114 | 7.167 | 5.1955
[7 empty] | 7339 | 115 | 6.7094 | 4.8501
[7 empty] | 7340 | 116 | 7.3958 | 5.3683
[7 empty] | 7341 | 117 | 6.9721 | 5.0484
[7 empty] | 7342 | 118 | 6.1924 | 4.4598
[7 empty] | 7343 | 119 | 4.5824 | 3.2443
[7 empty] | 7344 | 120 | 4.2615 | 3.0021
[7 empty] | 7345 | 121 | 3.5232 | 2.4446
[7 empty] | 7346 | 122 | 3.1079 | 2.1312
[7 empty] | 7347 | 123 | 3.0232 | 2.0672
[7 empty] | 7348 | 124 | 2.9893 | 2.0416
[7 empty] | 7349 | 125 | 2.9469 | 2.0096
[7 empty] | 7350 | 126 | 3.091 | 2.1184
[7 empty] | 7351 | 127 | 4.6163 | 3.2699
[7 empty] | 7352 | 128 | 6.1924 | 4.4598
[7 empty] | 7353 | 129 | 6.8788 | 4.978
[7 empty] | 7354 | 130 | 7.3195 | 5.3107
[7 empty] | 7355 | 131 | 7.4805 | 5.4322
[7 empty] | 7356 | 132 | 7.2263 | 5.2403
[7 empty] | 7357 | 133 | 7.8703 | 5.7265
[7 empty] | 7358 | 134 | 8.1754 | 5.9568
[7 empty] | 7359 | 135 | 8.2431 | 6.008
[7 empty] | 7360 | 136 | 7.4212 | 5.3875
[7 empty] | 7361 | 137 | 7.3195 | 5.3107
[7 empty] | 7362 | 138 | 7.2686 | 5.2723
[7 empty] | 7363 | 139 | 6.9297 | 5.0164
[7 empty] | 7364 | 140 | 6.9382 | 5.0228
[7 empty] | 7365 | 141 | 6.2772 | 4.5238
[7 empty] | 7366 | 142 | 5.6332 | 4.0376
[7 empty] | 7367 | 143 | 4.7434 | 3.3659
[7 empty] | 7368 | 144 | 4.1248 | 2.8989
[7 empty] | 7369 | 145 | 3.6503 | 2.5406
[7 empty] | 7370 | 146 | 3.4384 | 2.3807
[7 empty] | 7371 | 147 | 3.3706 | 2.3295
[7 empty] | 7372 | 148 | 3.3622 | 2.3231
[7 empty] | 7373 | 149 | 3.3622 | 2.3231
[7 empty] | 7374 | 150 | 3.3706 | 2.3295
[7 empty] | 7375 | 151 | 4.4638 | 3.1547
[7 empty] | 7376 | 152 | 6.006 | 4.3191
[7 empty] | 7377 | 153 | 6.6246 | 4.7861
[7 empty] | 7378 | 154 | 7.1924 | 5.2147
[7 empty] | 7379 | 155 | 7.0398 | 5.0996
[7 empty] | 7380 | 156 | 7.2093 | 5.2275
[7 empty] | 7381 | 157 | 7.9296 | 5.7713
[7 empty] | 7382 | 158 | 8.2601 | 6.0208
[7 empty] | 7383 | 159 | 8.5313 | 6.2255
[7 empty] | 7384 | 160 | 8.4041 | 6.1296
[7 empty] | 7385 | 161 | 9.1753 | 6.7117
[7 empty] | 7386 | 162 | 8.6753 | 6.3343
[7 empty] | 7387 | 163 | 9.0397 | 6.6094
[7 empty] | 7388 | 164 | 7.6754 | 5.5794
[7 empty] | 7389 | 165 | 10.8362 | 7.9656
[7 empty] | 7390 | 166 | 8.7685 | 6.4046
[7 empty] | 7391 | 167 | 5.1247 | 3.6537
[7 empty] | 7392 | 168 | 4.4722 | 3.1611
[7 empty] | 7393 | 1 | 2.9978 | 2.048
[7 empty] | 7394 | 2 | 2.8876 | 1.9648
[7 empty] | 7395 | 3 | 2.8791 | 1.9584
[7 empty] | 7396 | 4 | 3.0147 | 2.0608
[7 empty] | 7397 | 5 | 3.0317 | 2.0736
[7 empty] | 7398 | 6 | 3.4638 | 2.3999
[7 empty] | 7399 | 7 | 4.1926 | 2.95
[7 empty] | 7400 | 8 | 4.8705 | 3.4618
[7 empty] | 7401 | 9 | 4.8451 | 3.4426
[7 empty] | 7402 | 10 | 6.3789 | 4.6006
[7 empty] | 7403 | 11 | 8.4804 | 6.1871
[7 empty] | 7404 | 12 | 9.4549 | 6.9228
[7 empty] | 7405 | 13 | 9.8362 | 7.2107
[7 empty] | 7406 | 14 | 9.6159 | 7.0444
[7 empty] | 7407 | 15 | 9.5227 | 6.974
[7 empty] | 7408 | 16 | 10.7175 | 7.8761
[7 empty] | 7409 | 17 | 12.0564 | 8.8868
[7 empty] | 7410 | 18 | 11.8107 | 8.7013
[7 empty] | 7411 | 19 | 12.3445 | 9.1044
[7 empty] | 7412 | 20 | 12.2767 | 9.0532
[7 empty] | 7413 | 21 | 12.853 | 9.4882
[7 empty] | 7414 | 22 | 8.8533 | 6.4686
[7 empty] | 7415 | 23 | 5.04 | 3.5898
[7 empty] | 7416 | 24 | 3.3504 | 2.3142
[7 empty] | 7417 | 25 | 3.252 | 2.2399
[7 empty] | 7418 | 26 | 3.1418 | 2.1567
[7 empty] | 7419 | 27 | 3.0401 | 2.08
[7 empty] | 7420 | 28 | 3.1249 | 2.144
[7 empty] | 7421 | 29 | 3.3706 | 2.3295
[7 empty] | 7422 | 30 | 3.6164 | 2.515
[7 empty] | 7423 | 31 | 4.4722 | 3.1611
[7 empty] | 7424 | 32 | 4.8281 | 3.4298
[7 empty] | 7425 | 33 | 5.4976 | 3.9352
[7 empty] | 7426 | 34 | 6.4043 | 4.6198
[7 empty] | 7427 | 35 | 8.5991 | 6.2767
[7 empty] | 7428 | 36 | 9.6413 | 7.0636
[7 empty] | 7429 | 37 | 9.7176 | 7.1212
[7 empty] | 7430 | 38 | 9.7939 | 7.1787
[7 empty] | 7431 | 39 | 9.4634 | 6.9292
[7 empty] | 7432 | 40 | 10.5311 | 7.7353
[7 empty] | 7433 | 41 | 11.0904 | 8.1575
[7 empty] | 7434 | 42 | 11.1073 | 8.1703
[7 empty] | 7435 | 43 | 11.4802 | 8.4518
[7 empty] | 7436 | 44 | 12.6496 | 9.3347
[7 empty] | 7437 | 45 | 12.2428 | 9.0276
[7 empty] | 7438 | 46 | 9.4634 | 6.9292
[7 empty] | 7439 | 47 | 5.8196 | 4.1783
[7 empty] | 7440 | 48 | 4.3028 | 3.0332
[7 empty] | 7441 | 49 | 3.6333 | 2.5278
[7 empty] | 7442 | 50 | 3.3198 | 2.2911
[7 empty] | 7443 | 51 | 3.2096 | 2.2079
[7 empty] | 7444 | 52 | 3.2435 | 2.2335
[7 empty] | 7445 | 53 | 3.2689 | 2.2527
[7 empty] | 7446 | 54 | 3.8536 | 2.6941
[7 empty] | 7447 | 55 | 5.0061 | 3.5642
[7 empty] | 7448 | 56 | 5.2518 | 3.7497
[7 empty] | 7449 | 57 | 6.2094 | 4.4726
[7 empty] | 7450 | 58 | 7.328 | 5.3171
[7 empty] | 7451 | 59 | 8.5482 | 6.2383
[7 empty] | 7452 | 60 | 9.1838 | 6.7181
[7 empty] | 7453 | 61 | 9.8701 | 7.2363
[7 empty] | 7454 | 62 | 9.6668 | 7.0828
[7 empty] | 7455 | 63 | 10.2684 | 7.537
[7 empty] | 7456 | 64 | 11.226 | 8.2599
[7 empty] | 7457 | 65 | 11.853 | 8.7333
[7 empty] | 7458 | 66 | 11.7514 | 8.6565
[7 empty] | 7459 | 67 | 12.4971 | 9.2195
[7 empty] | 7460 | 68 | 12.7428 | 9.405
[7 empty] | 7461 | 69 | 12.2259 | 9.0148
[7 empty] | 7462 | 70 | 9.904 | 7.2619
[7 empty] | 7463 | 71 | 5.3366 | 3.8137
[7 empty] | 7464 | 72 | 4.2398 | 2.9857
[7 empty] | 7465 | 73 | 3.5147 | 2.4382
[7 empty] | 7466 | 74 | 3.2859 | 2.2655
[7 empty] | 7467 | 75 | 3.1842 | 2.1887
[7 empty] | 7468 | 76 | 3.1249 | 2.144
[7 empty] | 7469 | 77 | 3.3028 | 2.2783
[7 empty] | 7470 | 78 | 3.7096 | 2.5854
[7 empty] | 7471 | 79 | 4.8366 | 3.4362
[7 empty] | 7472 | 80 | 5.0146 | 3.5706
[7 empty] | 7473 | 81 | 6.2094 | 4.4726
[7 empty] | 7474 | 82 | 7.311 | 5.3043
[7 empty] | 7475 | 83 | 8.0567 | 5.8673
[7 empty] | 7476 | 84 | 9.3109 | 6.8141
[7 empty] | 7477 | 85 | 9.0058 | 6.5838
[7 empty] | 7478 | 86 | 8.4889 | 6.1935
[7 empty] | 7479 | 87 | 8.938 | 6.5326
[7 empty] | 7480 | 88 | 9.6075 | 7.038
[7 empty] | 7481 | 89 | 10.9718 | 8.068
[7 empty] | 7482 | 90 | 10.3786 | 7.6202
[7 empty] | 7483 | 91 | 11.0734 | 8.1447
[7 empty] | 7484 | 92 | 10.4633 | 7.6841
[7 empty] | 7485 | 93 | 8.0228 | 5.8417
[7 empty] | 7486 | 94 | 7.1076 | 5.1507
[7 empty] | 7487 | 95 | 5.2264 | 3.7305
[7 empty] | 7488 | 96 | 4.2265 | 2.9756
[7 empty] | 7489 | 97 | 4.1757 | 2.9372
[7 empty] | 7490 | 98 | 3.8791 | 2.7133
[7 empty] | 7491 | 99 | 3.8197 | 2.6685
[7 empty] | 7492 | 100 | 3.4638 | 2.3999
[7 empty] | 7493 | 101 | 3.4045 | 2.3551
[7 empty] | 7494 | 102 | 3.6418 | 2.5342
[7 empty] | 7495 | 103 | 4.396 | 3.1036
[7 empty] | 7496 | 104 | 4.6502 | 3.2955
[7 empty] | 7497 | 105 | 5.1417 | 3.6665
[7 empty] | 7498 | 106 | 6.6161 | 4.7797
[7 empty] | 7499 | 107 | 6.9721 | 5.0484
[7 empty] | 7500 | 108 | 8.5652 | 6.2511
[7 empty] | 7501 | 109 | 7.8957 | 5.7457
[7 empty] | 7502 | 110 | 7.4381 | 5.4002
[7 empty] | 7503 | 111 | 7.2771 | 5.2787
[7 empty] | 7504 | 112 | 7.3449 | 5.3299
[7 empty] | 7505 | 113 | 6.9975 | 5.0676
[7 empty] | 7506 | 114 | 7.167 | 5.1955
[7 empty] | 7507 | 115 | 6.7094 | 4.8501
[7 empty] | 7508 | 116 | 7.3958 | 5.3683
[7 empty] | 7509 | 117 | 6.9721 | 5.0484
[7 empty] | 7510 | 118 | 6.1924 | 4.4598
[7 empty] | 7511 | 119 | 4.5824 | 3.2443
[7 empty] | 7512 | 120 | 4.2615 | 3.0021
[7 empty] | 7513 | 121 | 3.5232 | 2.4446
[7 empty] | 7514 | 122 | 3.1079 | 2.1312
[7 empty] | 7515 | 123 | 3.0232 | 2.0672
[7 empty] | 7516 | 124 | 2.9893 | 2.0416
[7 empty] | 7517 | 125 | 2.9469 | 2.0096
[7 empty] | 7518 | 126 | 3.091 | 2.1184
[7 empty] | 7519 | 127 | 4.6163 | 3.2699
[7 empty] | 7520 | 128 | 6.1924 | 4.4598
[7 empty] | 7521 | 129 | 6.8788 | 4.978
[7 empty] | 7522 | 130 | 7.3195 | 5.3107
[7 empty] | 7523 | 131 | 7.4805 | 5.4322
[7 empty] | 7524 | 132 | 7.2263 | 5.2403
[7 empty] | 7525 | 133 | 7.8703 | 5.7265
[7 empty] | 7526 | 134 | 8.1754 | 5.9568
[7 empty] | 7527 | 135 | 8.2431 | 6.008
[7 empty] | 7528 | 136 | 7.4212 | 5.3875
[7 empty] | 7529 | 137 | 7.3195 | 5.3107
[7 empty] | 7530 | 138 | 7.2686 | 5.2723
[7 empty] | 7531 | 139 | 6.9297 | 5.0164
[7 empty] | 7532 | 140 | 6.9382 | 5.0228
[7 empty] | 7533 | 141 | 6.2772 | 4.5238
[7 empty] | 7534 | 142 | 5.6332 | 4.0376
[7 empty] | 7535 | 143 | 4.7434 | 3.3659
[7 empty] | 7536 | 144 | 4.1248 | 2.8989
[7 empty] | 7537 | 145 | 3.6503 | 2.5406
[7 empty] | 7538 | 146 | 3.4384 | 2.3807
[7 empty] | 7539 | 147 | 3.3706 | 2.3295
[7 empty] | 7540 | 148 | 3.3622 | 2.3231
[7 empty] | 7541 | 149 | 3.3622 | 2.3231
[7 empty] | 7542 | 150 | 3.3706 | 2.3295
[7 empty] | 7543 | 151 | 4.4638 | 3.1547
[7 empty] | 7544 | 152 | 6.006 | 4.3191
[7 empty] | 7545 | 153 | 6.6246 | 4.7861
[7 empty] | 7546 | 154 | 7.1924 | 5.2147
[7 empty] | 7547 | 155 | 7.0398 | 5.0996
[7 empty] | 7548 | 156 | 7.2093 | 5.2275
[7 empty] | 7549 | 157 | 7.9296 | 5.7713
[7 empty] | 7550 | 158 | 8.2601 | 6.0208
[7 empty] | 7551 | 159 | 8.5313 | 6.2255
[7 empty] | 7552 | 160 | 8.4041 | 6.1296
[7 empty] | 7553 | 161 | 9.1753 | 6.7117
[7 empty] | 7554 | 162 | 8.6753 | 6.3343
[7 empty] | 7555 | 163 | 9.0397 | 6.6094
[7 empty] | 7556 | 164 | 7.6754 | 5.5794
[7 empty] | 7557 | 165 | 10.8362 | 7.9656
[7 empty] | 7558 | 166 | 8.7685 | 6.4046
[7 empty] | 7559 | 167 | 5.1247 | 3.6537
[7 empty] | 7560 | 168 | 4.4722 | 3.1611
[7 empty] | 7561 | 1 | 2.9978 | 2.048
[7 empty] | 7562 | 2 | 2.8876 | 1.9648
[7 empty] | 7563 | 3 | 2.8791 | 1.9584
[7 empty] | 7564 | 4 | 3.0147 | 2.0608
[7 empty] | 7565 | 5 | 3.0317 | 2.0736
[7 empty] | 7566 | 6 | 3.4638 | 2.3999
[7 empty] | 7567 | 7 | 4.1926 | 2.95
[7 empty] | 7568 | 8 | 4.8705 | 3.4618
[7 empty] | 7569 | 9 | 4.8451 | 3.4426
[7 empty] | 7570 | 10 | 6.3789 | 4.6006
[7 empty] | 7571 | 11 | 8.4804 | 6.1871
[7 empty] | 7572 | 12 | 9.4549 | 6.9228
[7 empty] | 7573 | 13 | 9.8362 | 7.2107
[7 empty] | 7574 | 14 | 9.6159 | 7.0444
[7 empty] | 7575 | 15 | 9.5227 | 6.974
[7 empty] | 7576 | 16 | 10.7175 | 7.8761
[7 empty] | 7577 | 17 | 12.0564 | 8.8868
[7 empty] | 7578 | 18 | 11.8107 | 8.7013
[7 empty] | 7579 | 19 | 12.3445 | 9.1044
[7 empty] | 7580 | 20 | 12.2767 | 9.0532
[7 empty] | 7581 | 21 | 12.853 | 9.4882
[7 empty] | 7582 | 22 | 8.8533 | 6.4686
[7 empty] | 7583 | 23 | 5.04 | 3.5898
[7 empty] | 7584 | 24 | 3.3504 | 2.3142
[7 empty] | 7585 | 25 | 3.252 | 2.2399
[7 empty] | 7586 | 26 | 3.1418 | 2.1567
[7 empty] | 7587 | 27 | 3.0401 | 2.08
[7 empty] | 7588 | 28 | 3.1249 | 2.144
[7 empty] | 7589 | 29 | 3.3706 | 2.3295
[7 empty] | 7590 | 30 | 3.6164 | 2.515
[7 empty] | 7591 | 31 | 4.4722 | 3.1611
[7 empty] | 7592 | 32 | 4.8281 | 3.4298
[7 empty] | 7593 | 33 | 5.4976 | 3.9352
[7 empty] | 7594 | 34 | 6.4043 | 4.6198
[7 empty] | 7595 | 35 | 8.5991 | 6.2767
[7 empty] | 7596 | 36 | 9.6413 | 7.0636
[7 empty] | 7597 | 37 | 9.7176 | 7.1212
[7 empty] | 7598 | 38 | 9.7939 | 7.1787
[7 empty] | 7599 | 39 | 9.4634 | 6.9292
[7 empty] | 7600 | 40 | 10.5311 | 7.7353
[7 empty] | 7601 | 41 | 11.0904 | 8.1575
[7 empty] | 7602 | 42 | 11.1073 | 8.1703
[7 empty] | 7603 | 43 | 11.4802 | 8.4518
[7 empty] | 7604 | 44 | 12.6496 | 9.3347
[7 empty] | 7605 | 45 | 12.2428 | 9.0276
[7 empty] | 7606 | 46 | 9.4634 | 6.9292
[7 empty] | 7607 | 47 | 5.8196 | 4.1783
[7 empty] | 7608 | 48 | 4.3028 | 3.0332
[7 empty] | 7609 | 49 | 3.6333 | 2.5278
[7 empty] | 7610 | 50 | 3.3198 | 2.2911
[7 empty] | 7611 | 51 | 3.2096 | 2.2079
[7 empty] | 7612 | 52 | 3.2435 | 2.2335
[7 empty] | 7613 | 53 | 3.2689 | 2.2527
[7 empty] | 7614 | 54 | 3.8536 | 2.6941
[7 empty] | 7615 | 55 | 5.0061 | 3.5642
[7 empty] | 7616 | 56 | 5.2518 | 3.7497
[7 empty] | 7617 | 57 | 6.2094 | 4.4726
[7 empty] | 7618 | 58 | 7.328 | 5.3171
[7 empty] | 7619 | 59 | 8.5482 | 6.2383
[7 empty] | 7620 | 60 | 9.1838 | 6.7181
[7 empty] | 7621 | 61 | 9.8701 | 7.2363
[7 empty] | 7622 | 62 | 9.6668 | 7.0828
[7 empty] | 7623 | 63 | 10.2684 | 7.537
[7 empty] | 7624 | 64 | 11.226 | 8.2599
[7 empty] | 7625 | 65 | 11.853 | 8.7333
[7 empty] | 7626 | 66 | 11.7514 | 8.6565
[7 empty] | 7627 | 67 | 12.4971 | 9.2195
[7 empty] | 7628 | 68 | 12.7428 | 9.405
[7 empty] | 7629 | 69 | 12.2259 | 9.0148
[7 empty] | 7630 | 70 | 9.904 | 7.2619
[7 empty] | 7631 | 71 | 5.3366 | 3.8137
[7 empty] | 7632 | 72 | 4.2398 | 2.9857
[7 empty] | 7633 | 73 | 3.5147 | 2.4382
[7 empty] | 7634 | 74 | 3.2859 | 2.2655
[7 empty] | 7635 | 75 | 3.1842 | 2.1887
[7 empty] | 7636 | 76 | 3.1249 | 2.144
[7 empty] | 7637 | 77 | 3.3028 | 2.2783
[7 empty] | 7638 | 78 | 3.7096 | 2.5854
[7 empty] | 7639 | 79 | 4.8366 | 3.4362
[7 empty] | 7640 | 80 | 5.0146 | 3.5706
[7 empty] | 7641 | 81 | 6.2094 | 4.4726
[7 empty] | 7642 | 82 | 7.311 | 5.3043
[7 empty] | 7643 | 83 | 8.0567 | 5.8673
[7 empty] | 7644 | 84 | 9.3109 | 6.8141
[7 empty] | 7645 | 85 | 9.0058 | 6.5838
[7 empty] | 7646 | 86 | 8.4889 | 6.1935
[7 empty] | 7647 | 87 | 8.938 | 6.5326
[7 empty] | 7648 | 88 | 9.6075 | 7.038
[7 empty] | 7649 | 89 | 10.9718 | 8.068
[7 empty] | 7650 | 90 | 10.3786 | 7.6202
[7 empty] | 7651 | 91 | 11.0734 | 8.1447
[7 empty] | 7652 | 92 | 10.4633 | 7.6841
[7 empty] | 7653 | 93 | 8.0228 | 5.8417
[7 empty] | 7654 | 94 | 7.1076 | 5.1507
[7 empty] | 7655 | 95 | 5.2264 | 3.7305
[7 empty] | 7656 | 96 | 4.2265 | 2.9756
[7 empty] | 7657 | 97 | 4.1757 | 2.9372
[7 empty] | 7658 | 98 | 3.8791 | 2.7133
[7 empty] | 7659 | 99 | 3.8197 | 2.6685
[7 empty] | 7660 | 100 | 3.4638 | 2.3999
[7 empty] | 7661 | 101 | 3.4045 | 2.3551
[7 empty] | 7662 | 102 | 3.6418 | 2.5342
[7 empty] | 7663 | 103 | 4.396 | 3.1036
[7 empty] | 7664 | 104 | 4.6502 | 3.2955
[7 empty] | 7665 | 105 | 5.1417 | 3.6665
[7 empty] | 7666 | 106 | 6.6161 | 4.7797
[7 empty] | 7667 | 107 | 6.9721 | 5.0484
[7 empty] | 7668 | 108 | 8.5652 | 6.2511
[7 empty] | 7669 | 109 | 7.8957 | 5.7457
[7 empty] | 7670 | 110 | 7.4381 | 5.4002
[7 empty] | 7671 | 111 | 7.2771 | 5.2787
[7 empty] | 7672 | 112 | 7.3449 | 5.3299
[7 empty] | 7673 | 113 | 6.9975 | 5.0676
[7 empty] | 7674 | 114 | 7.167 | 5.1955
[7 empty] | 7675 | 115 | 6.7094 | 4.8501
[7 empty] | 7676 | 116 | 7.3958 | 5.3683
[7 empty] | 7677 | 117 | 6.9721 | 5.0484
[7 empty] | 7678 | 118 | 6.1924 | 4.4598
[7 empty] | 7679 | 119 | 4.5824 | 3.2443
[7 empty] | 7680 | 120 | 4.2615 | 3.0021
[7 empty] | 7681 | 121 | 3.5232 | 2.4446
[7 empty] | 7682 | 122 | 3.1079 | 2.1312
[7 empty] | 7683 | 123 | 3.0232 | 2.0672
[7 empty] | 7684 | 124 | 2.9893 | 2.0416
[7 empty] | 7685 | 125 | 2.9469 | 2.0096
[7 empty] | 7686 | 126 | 3.091 | 2.1184
[7 empty] | 7687 | 127 | 4.6163 | 3.2699
[7 empty] | 7688 | 128 | 6.1924 | 4.4598
[7 empty] | 7689 | 129 | 6.8788 | 4.978
[7 empty] | 7690 | 130 | 7.3195 | 5.3107
[7 empty] | 7691 | 131 | 7.4805 | 5.4322
[7 empty] | 7692 | 132 | 7.2263 | 5.2403
[7 empty] | 7693 | 133 | 7.8703 | 5.7265
[7 empty] | 7694 | 134 | 8.1754 | 5.9568
[7 empty] | 7695 | 135 | 8.2431 | 6.008
[7 empty] | 7696 | 136 | 7.4212 | 5.3875
[7 empty] | 7697 | 137 | 7.3195 | 5.3107
[7 empty] | 7698 | 138 | 7.2686 | 5.2723
[7 empty] | 7699 | 139 | 6.9297 | 5.0164
[7 empty] | 7700 | 140 | 6.9382 | 5.0228
[7 empty] | 7701 | 141 | 6.2772 | 4.5238
[7 empty] | 7702 | 142 | 5.6332 | 4.0376
[7 empty] | 7703 | 143 | 4.7434 | 3.3659
[7 empty] | 7704 | 144 | 4.1248 | 2.8989
[7 empty] | 7705 | 145 | 3.6503 | 2.5406
[7 empty] | 7706 | 146 | 3.4384 | 2.3807
[7 empty] | 7707 | 147 | 3.3706 | 2.3295
[7 empty] | 7708 | 148 | 3.3622 | 2.3231
[7 empty] | 7709 | 149 | 3.3622 | 2.3231
[7 empty] | 7710 | 150 | 3.3706 | 2.3295
[7 empty] | 7711 | 151 | 4.4638 | 3.1547
[7 empty] | 7712 | 152 | 6.006 | 4.3191
[7 empty] | 7713 | 153 | 6.6246 | 4.7861
[7 empty] | 7714 | 154 | 7.1924 | 5.2147
[7 empty] | 7715 | 155 | 7.0398 | 5.0996
[7 empty] | 7716 | 156 | 7.2093 | 5.2275
[7 empty] | 7717 | 157 | 7.9296 | 5.7713
[7 empty] | 7718 | 158 | 8.2601 | 6.0208
[7 empty] | 7719 | 159 | 8.5313 | 6.2255
[7 empty] | 7720 | 160 | 8.4041 | 6.1296
[7 empty] | 7721 | 161 | 9.1753 | 6.7117
[7 empty] | 7722 | 162 | 8.6753 | 6.3343
[7 empty] | 7723 | 163 | 9.0397 | 6.6094
[7 empty] | 7724 | 164 | 7.6754 | 5.5794
[7 empty] | 7725 | 165 | 10.8362 | 7.9656
[7 empty] | 7726 | 166 | 8.7685 | 6.4046
[7 empty] | 7727 | 167 | 5.1247 | 3.6537
[7 empty] | 7728 | 168 | 4.4722 | 3.1611
[7 empty] | 7729 | 1 | 2.9978 | 2.048
[7 empty] | 7730 | 2 | 2.8876 | 1.9648
[7 empty] | 7731 | 3 | 2.8791 | 1.9584
[7 empty] | 7732 | 4 | 3.0147 | 2.0608
[7 empty] | 7733 | 5 | 3.0317 | 2.0736
[7 empty] | 7734 | 6 | 3.4638 | 2.3999
[7 empty] | 7735 | 7 | 4.1926 | 2.95
[7 empty] | 7736 | 8 | 4.8705 | 3.4618
[7 empty] | 7737 | 9 | 4.8451 | 3.4426
[7 empty] | 7738 | 10 | 6.3789 | 4.6006
[7 empty] | 7739 | 11 | 8.4804 | 6.1871
[7 empty] | 7740 | 12 | 9.4549 | 6.9228
[7 empty] | 7741 | 13 | 9.8362 | 7.2107
[7 empty] | 7742 | 14 | 9.6159 | 7.0444
[7 empty] | 7743 | 15 | 9.5227 | 6.974
[7 empty] | 7744 | 16 | 10.7175 | 7.8761
[7 empty] | 7745 | 17 | 12.0564 | 8.8868
[7 empty] | 7746 | 18 | 11.8107 | 8.7013
[7 empty] | 7747 | 19 | 12.3445 | 9.1044
[7 empty] | 7748 | 20 | 12.2767 | 9.0532
[7 empty] | 7749 | 21 | 12.853 | 9.4882
[7 empty] | 7750 | 22 | 8.8533 | 6.4686
[7 empty] | 7751 | 23 | 5.04 | 3.5898
[7 empty] | 7752 | 24 | 3.3504 | 2.3142
[7 empty] | 7753 | 25 | 3.252 | 2.2399
[7 empty] | 7754 | 26 | 3.1418 | 2.1567
[7 empty] | 7755 | 27 | 3.0401 | 2.08
[7 empty] | 7756 | 28 | 3.1249 | 2.144
[7 empty] | 7757 | 29 | 3.3706 | 2.3295
[7 empty] | 7758 | 30 | 3.6164 | 2.515
[7 empty] | 7759 | 31 | 4.4722 | 3.1611
[7 empty] | 7760 | 32 | 4.8281 | 3.4298
[7 empty] | 7761 | 33 | 5.4976 | 3.9352
[7 empty] | 7762 | 34 | 6.4043 | 4.6198
[7 empty] | 7763 | 35 | 8.5991 | 6.2767
[7 empty] | 7764 | 36 | 9.6413 | 7.0636
[7 empty] | 7765 | 37 | 9.7176 | 7.1212
[7 empty] | 7766 | 38 | 9.7939 | 7.1787
[7 empty] | 7767 | 39 | 9.4634 | 6.9292
[7 empty] | 7768 | 40 | 10.5311 | 7.7353
[7 empty] | 7769 | 41 | 11.0904 | 8.1575
[7 empty] | 7770 | 42 | 11.1073 | 8.1703
[7 empty] | 7771 | 43 | 11.4802 | 8.4518
[7 empty] | 7772 | 44 | 12.6496 | 9.3347
[7 empty] | 7773 | 45 | 12.2428 | 9.0276
[7 empty] | 7774 | 46 | 9.4634 | 6.9292
[7 empty] | 7775 | 47 | 5.8196 | 4.1783
[7 empty] | 7776 | 48 | 4.3028 | 3.0332
[7 empty] | 7777 | 49 | 3.6333 | 2.5278
[7 empty] | 7778 | 50 | 3.3198 | 2.2911
[7 empty] | 7779 | 51 | 3.2096 | 2.2079
[7 empty] | 7780 | 52 | 3.2435 | 2.2335
[7 empty] | 7781 | 53 | 3.2689 | 2.2527
[7 empty] | 7782 | 54 | 3.8536 | 2.6941
[7 empty] | 7783 | 55 | 5.0061 | 3.5642
[7 empty] | 7784 | 56 | 5.2518 | 3.7497
[7 empty] | 7785 | 57 | 6.2094 | 4.4726
[7 empty] | 7786 | 58 | 7.328 | 5.3171
[7 empty] | 7787 | 59 | 8.5482 | 6.2383
[7 empty] | 7788 | 60 | 9.1838 | 6.7181
[7 empty] | 7789 | 61 | 9.8701 | 7.2363
[7 empty] | 7790 | 62 | 9.6668 | 7.0828
[7 empty] | 7791 | 63 | 10.2684 | 7.537
[7 empty] | 7792 | 64 | 11.226 | 8.2599
[7 empty] | 7793 | 65 | 11.853 | 8.7333
[7 empty] | 7794 | 66 | 11.7514 | 8.6565
[7 empty] | 7795 | 67 | 12.4971 | 9.2195
[7 empty] | 7796 | 68 | 12.7428 | 9.405
[7 empty] | 7797 | 69 | 12.2259 | 9.0148
[7 empty] | 7798 | 70 | 9.904 | 7.2619
[7 empty] | 7799 | 71 | 5.3366 | 3.8137
[7 empty] | 7800 | 72 | 4.2398 | 2.9857
[7 empty] | 7801 | 73 | 3.5147 | 2.4382
[7 empty] | 7802 | 74 | 3.2859 | 2.2655
[7 empty] | 7803 | 75 | 3.1842 | 2.1887
[7 empty] | 7804 | 76 | 3.1249 | 2.144
[7 empty] | 7805 | 77 | 3.3028 | 2.2783
[7 empty] | 7806 | 78 | 3.7096 | 2.5854
[7 empty] | 7807 | 79 | 4.8366 | 3.4362
[7 empty] | 7808 | 80 | 5.0146 | 3.5706
[7 empty] | 7809 | 81 | 6.2094 | 4.4726
[7 empty] | 7810 | 82 | 7.311 | 5.3043
[7 empty] | 7811 | 83 | 8.0567 | 5.8673
[7 empty] | 7812 | 84 | 9.3109 | 6.8141
[7 empty] | 7813 | 85 | 9.0058 | 6.5838
[7 empty] | 7814 | 86 | 8.4889 | 6.1935
[7 empty] | 7815 | 87 | 8.938 | 6.5326
[7 empty] | 7816 | 88 | 9.6075 | 7.038
[7 empty] | 7817 | 89 | 10.9718 | 8.068
[7 empty] | 7818 | 90 | 10.3786 | 7.6202
[7 empty] | 7819 | 91 | 11.0734 | 8.1447
[7 empty] | 7820 | 92 | 10.4633 | 7.6841
[7 empty] | 7821 | 93 | 8.0228 | 5.8417
[7 empty] | 7822 | 94 | 7.1076 | 5.1507
[7 empty] | 7823 | 95 | 5.2264 | 3.7305
[7 empty] | 7824 | 96 | 4.2265 | 2.9756
[7 empty] | 7825 | 97 | 4.1757 | 2.9372
[7 empty] | 7826 | 98 | 3.8791 | 2.7133
[7 empty] | 7827 | 99 | 3.8197 | 2.6685
[7 empty] | 7828 | 100 | 3.4638 | 2.3999
[7 empty] | 7829 | 101 | 3.4045 | 2.3551
[7 empty] | 7830 | 102 | 3.6418 | 2.5342
[7 empty] | 7831 | 103 | 4.396 | 3.1036
[7 empty] | 7832 | 104 | 4.6502 | 3.2955
[7 empty] | 7833 | 105 | 5.1417 | 3.6665
[7 empty] | 7834 | 106 | 6.6161 | 4.7797
[7 empty] | 7835 | 107 | 6.9721 | 5.0484
[7 empty] | 7836 | 108 | 8.5652 | 6.2511
[7 empty] | 7837 | 109 | 7.8957 | 5.7457
[7 empty] | 7838 | 110 | 7.4381 | 5.4002
[7 empty] | 7839 | 111 | 7.2771 | 5.2787
[7 empty] | 7840 | 112 | 7.3449 | 5.3299
[7 empty] | 7841 | 113 | 6.9975 | 5.0676
[7 empty] | 7842 | 114 | 7.167 | 5.1955
[7 empty] | 7843 | 115 | 6.7094 | 4.8501
[7 empty] | 7844 | 116 | 7.3958 | 5.3683
[7 empty] | 7845 | 117 | 6.9721 | 5.0484
[7 empty] | 7846 | 118 | 6.1924 | 4.4598
[7 empty] | 7847 | 119 | 4.5824 | 3.2443
[7 empty] | 7848 | 120 | 4.2615 | 3.0021
[7 empty] | 7849 | 121 | 3.5232 | 2.4446
[7 empty] | 7850 | 122 | 3.1079 | 2.1312
[7 empty] | 7851 | 123 | 3.0232 | 2.0672
[7 empty] | 7852 | 124 | 2.9893 | 2.0416
[7 empty] | 7853 | 125 | 2.9469 | 2.0096
[7 empty] | 7854 | 126 | 3.091 | 2.1184
[7 empty] | 7855 | 127 | 4.6163 | 3.2699
[7 empty] | 7856 | 128 | 6.1924 | 4.4598
[7 empty] | 7857 | 129 | 6.8788 | 4.978
[7 empty] | 7858 | 130 | 7.3195 | 5.3107
[7 empty] | 7859 | 131 | 7.4805 | 5.4322
[7 empty] | 7860 | 132 | 7.2263 | 5.2403
[7 empty] | 7861 | 133 | 7.8703 | 5.7265
[7 empty] | 7862 | 134 | 8.1754 | 5.9568
[7 empty] | 7863 | 135 | 8.2431 | 6.008
[7 empty] | 7864 | 136 | 7.4212 | 5.3875
[7 empty] | 7865 | 137 | 7.3195 | 5.3107
[7 empty] | 7866 | 138 | 7.2686 | 5.2723
[7 empty] | 7867 | 139 | 6.9297 | 5.0164
[7 empty] | 7868 | 140 | 6.9382 | 5.0228
[7 empty] | 7869 | 141 | 6.2772 | 4.5238
[7 empty] | 7870 | 142 | 5.6332 | 4.0376
[7 empty] | 7871 | 143 | 4.7434 | 3.3659
[7 empty] | 7872 | 144 | 4.1248 | 2.8989
[7 empty] | 7873 | 145 | 3.6503 | 2.5406
[7 empty] | 7874 | 146 | 3.4384 | 2.3807
[7 empty] | 7875 | 147 | 3.3706 | 2.3295
[7 empty] | 7876 | 148 | 3.3622 | 2.3231
[7 empty] | 7877 | 149 | 3.3622 | 2.3231
[7 empty] | 7878 | 150 | 3.3706 | 2.3295
[7 empty] | 7879 | 151 | 4.4638 | 3.1547
[7 empty] | 7880 | 152 | 6.006 | 4.3191
[7 empty] | 7881 | 153 | 6.6246 | 4.7861
[7 empty] | 7882 | 154 | 7.1924 | 5.2147
[7 empty] | 7883 | 155 | 7.0398 | 5.0996
[7 empty] | 7884 | 156 | 7.2093 | 5.2275
[7 empty] | 7885 | 157 | 7.9296 | 5.7713
[7 empty] | 7886 | 158 | 8.2601 | 6.0208
[7 empty] | 7887 | 159 | 8.5313 | 6.2255
[7 empty] | 7888 | 160 | 8.4041 | 6.1296
[7 empty] | 7889 | 161 | 9.1753 | 6.7117
[7 empty] | 7890 | 162 | 8.6753 | 6.3343
[7 empty] | 7891 | 163 | 9.0397 | 6.6094
[7 empty] | 7892 | 164 | 7.6754 | 5.5794
[7 empty] | 7893 | 165 | 10.8362 | 7.9656
[7 empty] | 7894 | 166 | 8.7685 | 6.4046
[7 empty] | 7895 | 167 | 5.1247 | 3.6537
[7 empty] | 7896 | 168 | 4.4722 | 3.1611
[7 empty] | 7897 | 1 | 2.9978 | 2.048
[7 empty] | 7898 | 2 | 2.8876 | 1.9648
[7 empty] | 7899 | 3 | 2.8791 | 1.9584
[7 empty] | 7900 | 4 | 3.0147 | 2.0608
[7 empty] | 7901 | 5 | 3.0317 | 2.0736
[7 empty] | 7902 | 6 | 3.4638 | 2.3999
[7 empty] | 7903 | 7 | 4.1926 | 2.95
[7 empty] | 7904 | 8 | 4.8705 | 3.4618
[7 empty] | 7905 | 9 | 4.8451 | 3.4426
[7 empty] | 7906 | 10 | 6.3789 | 4.6006
[7 empty] | 7907 | 11 | 8.4804 | 6.1871
[7 empty] | 7908 | 12 | 9.4549 | 6.9228
[7 empty] | 7909 | 13 | 9.8362 | 7.2107
[7 empty] | 7910 | 14 | 9.6159 | 7.0444
[7 empty] | 7911 | 15 | 9.5227 | 6.974
[7 empty] | 7912 | 16 | 10.7175 | 7.8761
[7 empty] | 7913 | 17 | 12.0564 | 8.8868
[7 empty] | 7914 | 18 | 11.8107 | 8.7013
[7 empty] | 7915 | 19 | 12.3445 | 9.1044
[7 empty] | 7916 | 20 | 12.2767 | 9.0532
[7 empty] | 7917 | 21 | 12.853 | 9.4882
[7 empty] | 7918 | 22 | 8.8533 | 6.4686
[7 empty] | 7919 | 23 | 5.04 | 3.5898
[7 empty] | 7920 | 24 | 3.3504 | 2.3142
[7 empty] | 7921 | 25 | 3.252 | 2.2399
[7 empty] | 7922 | 26 | 3.1418 | 2.1567
[7 empty] | 7923 | 27 | 3.0401 | 2.08
[7 empty] | 7924 | 28 | 3.1249 | 2.144
[7 empty] | 7925 | 29 | 3.3706 | 2.3295
[7 empty] | 7926 | 30 | 3.6164 | 2.515
[7 empty] | 7927 | 31 | 4.4722 | 3.1611
[7 empty] | 7928 | 32 | 4.8281 | 3.4298
[7 empty] | 7929 | 33 | 5.4976 | 3.9352
[7 empty] | 7930 | 34 | 6.4043 | 4.6198
[7 empty] | 7931 | 35 | 8.5991 | 6.2767
[7 empty] | 7932 | 36 | 9.6413 | 7.0636
[7 empty] | 7933 | 37 | 9.7176 | 7.1212
[7 empty] | 7934 | 38 | 9.7939 | 7.1787
[7 empty] | 7935 | 39 | 9.4634 | 6.9292
[7 empty] | 7936 | 40 | 10.5311 | 7.7353
[7 empty] | 7937 | 41 | 11.0904 | 8.1575
[7 empty] | 7938 | 42 | 11.1073 | 8.1703
[7 empty] | 7939 | 43 | 11.4802 | 8.4518
[7 empty] | 7940 | 44 | 12.6496 | 9.3347
[7 empty] | 7941 | 45 | 12.2428 | 9.0276
[7 empty] | 7942 | 46 | 9.4634 | 6.9292
[7 empty] | 7943 | 47 | 5.8196 | 4.1783
[7 empty] | 7944 | 48 | 4.3028 | 3.0332
[7 empty] | 7945 | 49 | 3.6333 | 2.5278
[7 empty] | 7946 | 50 | 3.3198 | 2.2911
[7 empty] | 7947 | 51 | 3.2096 | 2.2079
[7 empty] | 7948 | 52 | 3.2435 | 2.2335
[7 empty] | 7949 | 53 | 3.2689 | 2.2527
[7 empty] | 7950 | 54 | 3.8536 | 2.6941
[7 empty] | 7951 | 55 | 5.0061 | 3.5642
[7 empty] | 7952 | 56 | 5.2518 | 3.7497
[7 empty] | 7953 | 57 | 6.2094 | 4.4726
[7 empty] | 7954 | 58 | 7.328 | 5.3171
[7 empty] | 7955 | 59 | 8.5482 | 6.2383
[7 empty] | 7956 | 60 | 9.1838 | 6.7181
[7 empty] | 7957 | 61 | 9.8701 | 7.2363
[7 empty] | 7958 | 62 | 9.6668 | 7.0828
[7 empty] | 7959 | 63 | 10.2684 | 7.537
[7 empty] | 7960 | 64 | 11.226 | 8.2599
[7 empty] | 7961 | 65 | 11.853 | 8.7333
[7 empty] | 7962 | 66 | 11.7514 | 8.6565
[7 empty] | 7963 | 67 | 12.4971 | 9.2195
[7 empty] | 7964 | 68 | 12.7428 | 9.405
[7 empty] | 7965 | 69 | 12.2259 | 9.0148
[7 empty] | 7966 | 70 | 9.904 | 7.2619
[7 empty] | 7967 | 71 | 5.3366 | 3.8137
[7 empty] | 7968 | 72 | 4.2398 | 2.9857
[7 empty] | 7969 | 73 | 3.5147 | 2.4382
[7 empty] | 7970 | 74 | 3.2859 | 2.2655
[7 empty] | 7971 | 75 | 3.1842 | 2.1887
[7 empty] | 7972 | 76 | 3.1249 | 2.144
[7 empty] | 7973 | 77 | 3.3028 | 2.2783
[7 empty] | 7974 | 78 | 3.7096 | 2.5854
[7 empty] | 7975 | 79 | 4.8366 | 3.4362
[7 empty] | 7976 | 80 | 5.0146 | 3.5706
[7 empty] | 7977 | 81 | 6.2094 | 4.4726
[7 empty] | 7978 | 82 | 7.311 | 5.3043
[7 empty] | 7979 | 83 | 8.0567 | 5.8673
[7 empty] | 7980 | 84 | 9.3109 | 6.8141
[7 empty] | 7981 | 85 | 9.0058 | 6.5838
[7 empty] | 7982 | 86 | 8.4889 | 6.1935
[7 empty] | 7983 | 87 | 8.938 | 6.5326
[7 empty] | 7984 | 88 | 9.6075 | 7.038
[7 empty] | 7985 | 89 | 10.9718 | 8.068
[7 empty] | 7986 | 90 | 10.3786 | 7.6202
[7 empty] | 7987 | 91 | 11.0734 | 8.1447
[7 empty] | 7988 | 92 | 10.4633 | 7.6841
[7 empty] | 7989 | 93 | 8.0228 | 5.8417
[7 empty] | 7990 | 94 | 7.1076 | 5.1507
[7 empty] | 7991 | 95 | 5.2264 | 3.7305
[7 empty] | 7992 | 96 | 4.2265 | 2.9756
[7 empty] | 7993 | 97 | 4.1757 | 2.9372
[7 empty] | 7994 | 98 | 3.8791 | 2.7133
[7 empty] | 7995 | 99 | 3.8197 | 2.6685
[7 empty] | 7996 | 100 | 3.4638 | 2.3999
[7 empty] | 7997 | 101 | 3.4045 | 2.3551
[7 empty] | 7998 | 102 | 3.6418 | 2.5342
[7 empty] | 7999 | 103 | 4.396 | 3.1036
[7 empty] | 8000 | 104 | 4.6502 | 3.2955
[7 empty] | 8001 | 105 | 5.1417 | 3.6665
[7 empty] | 8002 | 106 | 6.6161 | 4.7797
[7 empty] | 8003 | 107 | 6.9721 | 5.0484
[7 empty] | 8004 | 108 | 8.5652 | 6.2511
[7 empty] | 8005 | 109 | 7.8957 | 5.7457
[7 empty] | 8006 | 110 | 7.4381 | 5.4002
[7 empty] | 8007 | 111 | 7.2771 | 5.2787
[7 empty] | 8008 | 112 | 7.3449 | 5.3299
[7 empty] | 8009 | 113 | 6.9975 | 5.0676
[7 empty] | 8010 | 114 | 7.167 | 5.1955
[7 empty] | 8011 | 115 | 6.7094 | 4.8501
[7 empty] | 8012 | 116 | 7.3958 | 5.3683
[7 empty] | 8013 | 117 | 6.9721 | 5.0484
[7 empty] | 8014 | 118 | 6.1924 | 4.4598
[7 empty] | 8015 | 119 | 4.5824 | 3.2443
[7 empty] | 8016 | 120 | 4.2615 | 3.0021
[7 empty] | 8017 | 121 | 3.5232 | 2.4446
[7 empty] | 8018 | 122 | 3.1079 | 2.1312
[7 empty] | 8019 | 123 | 3.0232 | 2.0672
[7 empty] | 8020 | 124 | 2.9893 | 2.0416
[7 empty] | 8021 | 125 | 2.9469 | 2.0096
[7 empty] | 8022 | 126 | 3.091 | 2.1184
[7 empty] | 8023 | 127 | 4.6163 | 3.2699
[7 empty] | 8024 | 128 | 6.1924 | 4.4598
[7 empty] | 8025 | 129 | 6.8788 | 4.978
[7 empty] | 8026 | 130 | 7.3195 | 5.3107
[7 empty] | 8027 | 131 | 7.4805 | 5.4322
[7 empty] | 8028 | 132 | 7.2263 | 5.2403
[7 empty] | 8029 | 133 | 7.8703 | 5.7265
[7 empty] | 8030 | 134 | 8.1754 | 5.9568
[7 empty] | 8031 | 135 | 8.2431 | 6.008
[7 empty] | 8032 | 136 | 7.4212 | 5.3875
[7 empty] | 8033 | 137 | 7.3195 | 5.3107
[7 empty] | 8034 | 138 | 7.2686 | 5.2723
[7 empty] | 8035 | 139 | 6.9297 | 5.0164
[7 empty] | 8036 | 140 | 6.9382 | 5.0228
[7 empty] | 8037 | 141 | 6.2772 | 4.5238
[7 empty] | 8038 | 142 | 5.6332 | 4.0376
[7 empty] | 8039 | 143 | 4.7434 | 3.3659
[7 empty] | 8040 | 144 | 4.1248 | 2.8989
[7 empty] | 8041 | 145 | 3.6503 | 2.5406
[7 empty] | 8042 | 146 | 3.4384 | 2.3807
[7 empty] | 8043 | 147 | 3.3706 | 2.3295
[7 empty] | 8044 | 148 | 3.3622 | 2.3231
[7 empty] | 8045 | 149 | 3.3622 | 2.3231
[7 empty] | 8046 | 150 | 3.3706 | 2.3295
[7 empty] | 8047 | 151 | 4.4638 | 3.1547
[7 empty] | 8048 | 152 | 6.006 | 4.3191
[7 empty] | 8049 | 153 | 6.6246 | 4.7861
[7 empty] | 8050 | 154 | 7.1924 | 5.2147
[7 empty] | 8051 | 155 | 7.0398 | 5.0996
[7 empty] | 8052 | 156 | 7.2093 | 5.2275
[7 empty] | 8053 | 157 | 7.9296 | 5.7713
[7 empty] | 8054 | 158 | 8.2601 | 6.0208
[7 empty] | 8055 | 159 | 8.5313 | 6.2255
[7 empty] | 8056 | 160 | 8.4041 | 6.1296
[7 empty] | 8057 | 161 | 9.1753 | 6.7117
[7 empty] | 8058 | 162 | 8.6753 | 6.3343
[7 empty] | 8059 | 163 | 9.0397 | 6.6094
[7 empty] | 8060 | 164 | 7.6754 | 5.5794
[7 empty] | 8061 | 165 | 10.8362 | 7.9656
[7 empty] | 8062 | 166 | 8.7685 | 6.4046
[7 empty] | 8063 | 167 | 5.1247 | 3.6537
[7 empty] | 8064 | 168 | 4.4722 | 3.1611
[7 empty] | 8065 | 1 | 2.9978 | 2.048
[7 empty] | 8066 | 2 | 2.8876 | 1.9648
[7 empty] | 8067 | 3 | 2.8791 | 1.9584
[7 empty] | 8068 | 4 | 3.0147 | 2.0608
[7 empty] | 8069 | 5 | 3.0317 | 2.0736
[7 empty] | 8070 | 6 | 3.4638 | 2.3999
[7 empty] | 8071 | 7 | 4.1926 | 2.95
[7 empty] | 8072 | 8 | 4.8705 | 3.4618
[7 empty] | 8073 | 9 | 4.8451 | 3.4426
[7 empty] | 8074 | 10 | 6.3789 | 4.6006
[7 empty] | 8075 | 11 | 8.4804 | 6.1871
[7 empty] | 8076 | 12 | 9.4549 | 6.9228
[7 empty] | 8077 | 13 | 9.8362 | 7.2107
[7 empty] | 8078 | 14 | 9.6159 | 7.0444
[7 empty] | 8079 | 15 | 9.5227 | 6.974
[7 empty] | 8080 | 16 | 10.7175 | 7.8761
[7 empty] | 8081 | 17 | 12.0564 | 8.8868
[7 empty] | 8082 | 18 | 11.8107 | 8.7013
[7 empty] | 8083 | 19 | 12.3445 | 9.1044
[7 empty] | 8084 | 20 | 12.2767 | 9.0532
[7 empty] | 8085 | 21 | 12.853 | 9.4882
[7 empty] | 8086 | 22 | 8.8533 | 6.4686
[7 empty] | 8087 | 23 | 5.04 | 3.5898
[7 empty] | 8088 | 24 | 3.3504 | 2.3142
[7 empty] | 8089 | 25 | 3.252 | 2.2399
[7 empty] | 8090 | 26 | 3.1418 | 2.1567
[7 empty] | 8091 | 27 | 3.0401 | 2.08
[7 empty] | 8092 | 28 | 3.1249 | 2.144
[7 empty] | 8093 | 29 | 3.3706 | 2.3295
[7 empty] | 8094 | 30 | 3.6164 | 2.515
[7 empty] | 8095 | 31 | 4.4722 | 3.1611
[7 empty] | 8096 | 32 | 4.8281 | 3.4298
[7 empty] | 8097 | 33 | 5.4976 | 3.9352
[7 empty] | 8098 | 34 | 6.4043 | 4.6198
[7 empty] | 8099 | 35 | 8.5991 | 6.2767
[7 empty] | 8100 | 36 | 9.6413 | 7.0636
[7 empty] | 8101 | 37 | 9.7176 | 7.1212
[7 empty] | 8102 | 38 | 9.7939 | 7.1787
[7 empty] | 8103 | 39 | 9.4634 | 6.9292
[7 empty] | 8104 | 40 | 10.5311 | 7.7353
[7 empty] | 8105 | 41 | 11.0904 | 8.1575
[7 empty] | 8106 | 42 | 11.1073 | 8.1703
[7 empty] | 8107 | 43 | 11.4802 | 8.4518
[7 empty] | 8108 | 44 | 12.6496 | 9.3347
[7 empty] | 8109 | 45 | 12.2428 | 9.0276
[7 empty] | 8110 | 46 | 9.4634 | 6.9292
[7 empty] | 8111 | 47 | 5.8196 | 4.1783
[7 empty] | 8112 | 48 | 4.3028 | 3.0332
[7 empty] | 8113 | 49 | 3.6333 | 2.5278
[7 empty] | 8114 | 50 | 3.3198 | 2.2911
[7 empty] | 8115 | 51 | 3.2096 | 2.2079
[7 empty] | 8116 | 52 | 3.2435 | 2.2335
[7 empty] | 8117 | 53 | 3.2689 | 2.2527
[7 empty] | 8118 | 54 | 3.8536 | 2.6941
[7 empty] | 8119 | 55 | 5.0061 | 3.5642
[7 empty] | 8120 | 56 | 5.2518 | 3.7497
[7 empty] | 8121 | 57 | 6.2094 | 4.4726
[7 empty] | 8122 | 58 | 7.328 | 5.3171
[7 empty] | 8123 | 59 | 8.5482 | 6.2383
[7 empty] | 8124 | 60 | 9.1838 | 6.7181
[7 empty] | 8125 | 61 | 9.8701 | 7.2363
[7 empty] | 8126 | 62 | 9.6668 | 7.0828
[7 empty] | 8127 | 63 | 10.2684 | 7.537
[7 empty] | 8128 | 64 | 11.226 | 8.2599
[7 empty] | 8129 | 65 | 11.853 | 8.7333
[7 empty] | 8130 | 66 | 11.7514 | 8.6565
[7 empty] | 8131 | 67 | 12.4971 | 9.2195
[7 empty] | 8132 | 68 | 12.7428 | 9.405
[7 empty] | 8133 | 69 | 12.2259 | 9.0148
[7 empty] | 8134 | 70 | 9.904 | 7.2619
[7 empty] | 8135 | 71 | 5.3366 | 3.8137
[7 empty] | 8136 | 72 | 4.2398 | 2.9857
[7 empty] | 8137 | 73 | 3.5147 | 2.4382
[7 empty] | 8138 | 74 | 3.2859 | 2.2655
[7 empty] | 8139 | 75 | 3.1842 | 2.1887
[7 empty] | 8140 | 76 | 3.1249 | 2.144
[7 empty] | 8141 | 77 | 3.3028 | 2.2783
[7 empty] | 8142 | 78 | 3.7096 | 2.5854
[7 empty] | 8143 | 79 | 4.8366 | 3.4362
[7 empty] | 8144 | 80 | 5.0146 | 3.5706
[7 empty] | 8145 | 81 | 6.2094 | 4.4726
[7 empty] | 8146 | 82 | 7.311 | 5.3043
[7 empty] | 8147 | 83 | 8.0567 | 5.8673
[7 empty] | 8148 | 84 | 9.3109 | 6.8141
[7 empty] | 8149 | 85 | 9.0058 | 6.5838
[7 empty] | 8150 | 86 | 8.4889 | 6.1935
[7 empty] | 8151 | 87 | 8.938 | 6.5326
[7 empty] | 8152 | 88 | 9.6075 | 7.038
[7 empty] | 8153 | 89 | 10.9718 | 8.068
[7 empty] | 8154 | 90 | 10.3786 | 7.6202
[7 empty] | 8155 | 91 | 11.0734 | 8.1447
[7 empty] | 8156 | 92 | 10.4633 | 7.6841
[7 empty] | 8157 | 93 | 8.0228 | 5.8417
[7 empty] | 8158 | 94 | 7.1076 | 5.1507
[7 empty] | 8159 | 95 | 5.2264 | 3.7305
[7 empty] | 8160 | 96 | 4.2265 | 2.9756
[7 empty] | 8161 | 97 | 4.1757 | 2.9372
[7 empty] | 8162 | 98 | 3.8791 | 2.7133
[7 empty] | 8163 | 99 | 3.8197 | 2.6685
[7 empty] | 8164 | 100 | 3.4638 | 2.3999
[7 empty] | 8165 | 101 | 3.4045 | 2.3551
[7 empty] | 8166 | 102 | 3.6418 | 2.5342
[7 empty] | 8167 | 103 | 4.396 | 3.1036
[7 empty] | 8168 | 104 | 4.6502 | 3.2955
[7 empty] | 8169 | 105 | 5.1417 | 3.6665
[7 empty] | 8170 | 106 | 6.6161 | 4.7797
[7 empty] | 8171 | 107 | 6.9721 | 5.0484
[7 empty] | 8172 | 108 | 8.5652 | 6.2511
[7 empty] | 8173 | 109 | 7.8957 | 5.7457
[7 empty] | 8174 | 110 | 7.4381 | 5.4002
[7 empty] | 8175 | 111 | 7.2771 | 5.2787
[7 empty] | 8176 | 112 | 7.3449 | 5.3299
[7 empty] | 8177 | 113 | 6.9975 | 5.0676
[7 empty] | 8178 | 114 | 7.167 | 5.1955
[7 empty] | 8179 | 115 | 6.7094 | 4.8501
[7 empty] | 8180 | 116 | 7.3958 | 5.3683
[7 empty] | 8181 | 117 | 6.9721 | 5.0484
[7 empty] | 8182 | 118 | 6.1924 | 4.4598
[7 empty] | 8183 | 119 | 4.5824 | 3.2443
[7 empty] | 8184 | 120 | 4.2615 | 3.0021
[7 empty] | 8185 | 121 | 3.5232 | 2.4446
[7 empty] | 8186 | 122 | 3.1079 | 2.1312
[7 empty] | 8187 | 123 | 3.0232 | 2.0672
[7 empty] | 8188 | 124 | 2.9893 | 2.0416
[7 empty] | 8189 | 125 | 2.9469 | 2.0096
[7 empty] | 8190 | 126 | 3.091 | 2.1184
[7 empty] | 8191 | 127 | 4.6163 | 3.2699
[7 empty] | 8192 | 128 | 6.1924 | 4.4598
[7 empty] | 8193 | 129 | 6.8788 | 4.978
[7 empty] | 8194 | 130 | 7.3195 | 5.3107
[7 empty] | 8195 | 131 | 7.4805 | 5.4322
[7 empty] | 8196 | 132 | 7.2263 | 5.2403
[7 empty] | 8197 | 133 | 7.8703 | 5.7265
[7 empty] | 8198 | 134 | 8.1754 | 5.9568
[7 empty] | 8199 | 135 | 8.2431 | 6.008
[7 empty] | 8200 | 136 | 7.4212 | 5.3875
[7 empty] | 8201 | 137 | 7.3195 | 5.3107
[7 empty] | 8202 | 138 | 7.2686 | 5.2723
[7 empty] | 8203 | 139 | 6.9297 | 5.0164
[7 empty] | 8204 | 140 | 6.9382 | 5.0228
[7 empty] | 8205 | 141 | 6.2772 | 4.5238
[7 empty] | 8206 | 142 | 5.6332 | 4.0376
[7 empty] | 8207 | 143 | 4.7434 | 3.3659
[7 empty] | 8208 | 144 | 4.1248 | 2.8989
[7 empty] | 8209 | 145 | 3.6503 | 2.5406
[7 empty] | 8210 | 146 | 3.4384 | 2.3807
[7 empty] | 8211 | 147 | 3.3706 | 2.3295
[7 empty] | 8212 | 148 | 3.3622 | 2.3231
[7 empty] | 8213 | 149 | 3.3622 | 2.3231
[7 empty] | 8214 | 150 | 3.3706 | 2.3295
[7 empty] | 8215 | 151 | 4.4638 | 3.1547
[7 empty] | 8216 | 152 | 6.006 | 4.3191
[7 empty] | 8217 | 153 | 6.6246 | 4.7861
[7 empty] | 8218 | 154 | 7.1924 | 5.2147
[7 empty] | 8219 | 155 | 7.0398 | 5.0996
[7 empty] | 8220 | 156 | 7.2093 | 5.2275
[7 empty] | 8221 | 157 | 7.9296 | 5.7713
[7 empty] | 8222 | 158 | 8.2601 | 6.0208
[7 empty] | 8223 | 159 | 8.5313 | 6.2255
[7 empty] | 8224 | 160 | 8.4041 | 6.1296
[7 empty] | 8225 | 161 | 9.1753 | 6.7117
[7 empty] | 8226 | 162 | 8.6753 | 6.3343
[7 empty] | 8227 | 163 | 9.0397 | 6.6094
[7 empty] | 8228 | 164 | 7.6754 | 5.5794
[7 empty] | 8229 | 165 | 10.8362 | 7.9656
[7 empty] | 8230 | 166 | 8.7685 | 6.4046
[7 empty] | 8231 | 167 | 5.1247 | 3.6537
[7 empty] | 8232 | 168 | 4.4722 | 3.1611
[7 empty] | 8233 | 1 | 2.9978 | 2.048
[7 empty] | 8234 | 2 | 2.8876 | 1.9648
[7 empty] | 8235 | 3 | 2.8791 | 1.9584
[7 empty] | 8236 | 4 | 3.0147 | 2.0608
[7 empty] | 8237 | 5 | 3.0317 | 2.0736
[7 empty] | 8238 | 6 | 3.4638 | 2.3999
[7 empty] | 8239 | 7 | 4.1926 | 2.95
[7 empty] | 8240 | 8 | 4.8705 | 3.4618
[7 empty] | 8241 | 9 | 4.8451 | 3.4426
[7 empty] | 8242 | 10 | 6.3789 | 4.6006
[7 empty] | 8243 | 11 | 8.4804 | 6.1871
[7 empty] | 8244 | 12 | 9.4549 | 6.9228
[7 empty] | 8245 | 13 | 9.8362 | 7.2107
[7 empty] | 8246 | 14 | 9.6159 | 7.0444
[7 empty] | 8247 | 15 | 9.5227 | 6.974
[7 empty] | 8248 | 16 | 10.7175 | 7.8761
[7 empty] | 8249 | 17 | 12.0564 | 8.8868
[7 empty] | 8250 | 18 | 11.8107 | 8.7013
[7 empty] | 8251 | 19 | 12.3445 | 9.1044
[7 empty] | 8252 | 20 | 12.2767 | 9.0532
[7 empty] | 8253 | 21 | 12.853 | 9.4882
[7 empty] | 8254 | 22 | 8.8533 | 6.4686
[7 empty] | 8255 | 23 | 5.04 | 3.5898
[7 empty] | 8256 | 24 | 3.3504 | 2.3142
[7 empty] | 8257 | 25 | 3.252 | 2.2399
[7 empty] | 8258 | 26 | 3.1418 | 2.1567
[7 empty] | 8259 | 27 | 3.0401 | 2.08
[7 empty] | 8260 | 28 | 3.1249 | 2.144
[7 empty] | 8261 | 29 | 3.3706 | 2.3295
[7 empty] | 8262 | 30 | 3.6164 | 2.515
[7 empty] | 8263 | 31 | 4.4722 | 3.1611
[7 empty] | 8264 | 32 | 4.8281 | 3.4298
[7 empty] | 8265 | 33 | 5.4976 | 3.9352
[7 empty] | 8266 | 34 | 6.4043 | 4.6198
[7 empty] | 8267 | 35 | 8.5991 | 6.2767
[7 empty] | 8268 | 36 | 9.6413 | 7.0636
[7 empty] | 8269 | 37 | 9.7176 | 7.1212
[7 empty] | 8270 | 38 | 9.7939 | 7.1787
[7 empty] | 8271 | 39 | 9.4634 | 6.9292
[7 empty] | 8272 | 40 | 10.5311 | 7.7353
[7 empty] | 8273 | 41 | 11.0904 | 8.1575
[7 empty] | 8274 | 42 | 11.1073 | 8.1703
[7 empty] | 8275 | 43 | 11.4802 | 8.4518
[7 empty] | 8276 | 44 | 12.6496 | 9.3347
[7 empty] | 8277 | 45 | 12.2428 | 9.0276
[7 empty] | 8278 | 46 | 9.4634 | 6.9292
[7 empty] | 8279 | 47 | 5.8196 | 4.1783
[7 empty] | 8280 | 48 | 4.3028 | 3.0332
[7 empty] | 8281 | 49 | 3.6333 | 2.5278
[7 empty] | 8282 | 50 | 3.3198 | 2.2911
[7 empty] | 8283 | 51 | 3.2096 | 2.2079
[7 empty] | 8284 | 52 | 3.2435 | 2.2335
[7 empty] | 8285 | 53 | 3.2689 | 2.2527
[7 empty] | 8286 | 54 | 3.8536 | 2.6941
[7 empty] | 8287 | 55 | 5.0061 | 3.5642
[7 empty] | 8288 | 56 | 5.2518 | 3.7497
[7 empty] | 8289 | 57 | 6.2094 | 4.4726
[7 empty] | 8290 | 58 | 7.328 | 5.3171
[7 empty] | 8291 | 59 | 8.5482 | 6.2383
[7 empty] | 8292 | 60 | 9.1838 | 6.7181
[7 empty] | 8293 | 61 | 9.8701 | 7.2363
[7 empty] | 8294 | 62 | 9.6668 | 7.0828
[7 empty] | 8295 | 63 | 10.2684 | 7.537
[7 empty] | 8296 | 64 | 11.226 | 8.2599
[7 empty] | 8297 | 65 | 11.853 | 8.7333
[7 empty] | 8298 | 66 | 11.7514 | 8.6565
[7 empty] | 8299 | 67 | 12.4971 | 9.2195
[7 empty] | 8300 | 68 | 12.7428 | 9.405
[7 empty] | 8301 | 69 | 12.2259 | 9.0148
[7 empty] | 8302 | 70 | 9.904 | 7.2619
[7 empty] | 8303 | 71 | 5.3366 | 3.8137
[7 empty] | 8304 | 72 | 4.2398 | 2.9857
[7 empty] | 8305 | 73 | 3.5147 | 2.4382
[7 empty] | 8306 | 74 | 3.2859 | 2.2655
[7 empty] | 8307 | 75 | 3.1842 | 2.1887
[7 empty] | 8308 | 76 | 3.1249 | 2.144
[7 empty] | 8309 | 77 | 3.3028 | 2.2783
[7 empty] | 8310 | 78 | 3.7096 | 2.5854
[7 empty] | 8311 | 79 | 4.8366 | 3.4362
[7 empty] | 8312 | 80 | 5.0146 | 3.5706
[7 empty] | 8313 | 81 | 6.2094 | 4.4726
[7 empty] | 8314 | 82 | 7.311 | 5.3043
[7 empty] | 8315 | 83 | 8.0567 | 5.8673
[7 empty] | 8316 | 84 | 9.3109 | 6.8141
[7 empty] | 8317 | 85 | 9.0058 | 6.5838
[7 empty] | 8318 | 86 | 8.4889 | 6.1935
[7 empty] | 8319 | 87 | 8.938 | 6.5326
[7 empty] | 8320 | 88 | 9.6075 | 7.038
[7 empty] | 8321 | 89 | 10.9718 | 8.068
[7 empty] | 8322 | 90 | 10.3786 | 7.6202
[7 empty] | 8323 | 91 | 11.0734 | 8.1447
[7 empty] | 8324 | 92 | 10.4633 | 7.6841
[7 empty] | 8325 | 93 | 8.0228 | 5.8417
[7 empty] | 8326 | 94 | 7.1076 | 5.1507
[7 empty] | 8327 | 95 | 5.2264 | 3.7305
[7 empty] | 8328 | 96 | 4.2265 | 2.9756
[7 empty] | 8329 | 97 | 4.1757 | 2.9372
[7 empty] | 8330 | 98 | 3.8791 | 2.7133
[7 empty] | 8331 | 99 | 3.8197 | 2.6685
[7 empty] | 8332 | 100 | 3.4638 | 2.3999
[7 empty] | 8333 | 101 | 3.4045 | 2.3551
[7 empty] | 8334 | 102 | 3.6418 | 2.5342
[7 empty] | 8335 | 103 | 4.396 | 3.1036
[7 empty] | 8336 | 104 | 4.6502 | 3.2955
[7 empty] | 8337 | 105 | 5.1417 | 3.6665
[7 empty] | 8338 | 106 | 6.6161 | 4.7797
[7 empty] | 8339 | 107 | 6.9721 | 5.0484
[7 empty] | 8340 | 108 | 8.5652 | 6.2511
[7 empty] | 8341 | 109 | 7.8957 | 5.7457
[7 empty] | 8342 | 110 | 7.4381 | 5.4002
[7 empty] | 8343 | 111 | 7.2771 | 5.2787
[7 empty] | 8344 | 112 | 7.3449 | 5.3299
[7 empty] | 8345 | 113 | 6.9975 | 5.0676
[7 empty] | 8346 | 114 | 7.167 | 5.1955
[7 empty] | 8347 | 115 | 6.7094 | 4.8501
[7 empty] | 8348 | 116 | 7.3958 | 5.3683
[7 empty] | 8349 | 117 | 6.9721 | 5.0484
[7 empty] | 8350 | 118 | 6.1924 | 4.4598
[7 empty] | 8351 | 119 | 4.5824 | 3.2443
[7 empty] | 8352 | 120 | 4.2615 | 3.0021
[7 empty] | 8353 | 121 | 3.5232 | 2.4446
[7 empty] | 8354 | 122 | 3.1079 | 2.1312
[7 empty] | 8355 | 123 | 3.0232 | 2.0672
[7 empty] | 8356 | 124 | 2.9893 | 2.0416
[7 empty] | 8357 | 125 | 2.9469 | 2.0096
[7 empty] | 8358 | 126 | 3.091 | 2.1184
[7 empty] | 8359 | 127 | 4.6163 | 3.2699
[7 empty] | 8360 | 128 | 6.1924 | 4.4598
[7 empty] | 8361 | 129 | 6.8788 | 4.978
[7 empty] | 8362 | 130 | 7.3195 | 5.3107
[7 empty] | 8363 | 131 | 7.4805 | 5.4322
[7 empty] | 8364 | 132 | 7.2263 | 5.2403
[7 empty] | 8365 | 133 | 7.8703 | 5.7265
[7 empty] | 8366 | 134 | 8.1754 | 5.9568
[7 empty] | 8367 | 135 | 8.2431 | 6.008
[7 empty] | 8368 | 136 | 7.4212 | 5.3875
[7 empty] | 8369 | 137 | 7.3195 | 5.3107
[7 empty] | 8370 | 138 | 7.2686 | 5.2723
[7 empty] | 8371 | 139 | 6.9297 | 5.0164
[7 empty] | 8372 | 140 | 6.9382 | 5.0228
[7 empty] | 8373 | 141 | 6.2772 | 4.5238
[7 empty] | 8374 | 142 | 5.6332 | 4.0376
[7 empty] | 8375 | 143 | 4.7434 | 3.3659
[7 empty] | 8376 | 144 | 4.1248 | 2.8989
[7 empty] | 8377 | 145 | 3.6503 | 2.5406
[7 empty] | 8378 | 146 | 3.4384 | 2.3807
[7 empty] | 8379 | 147 | 3.3706 | 2.3295
[7 empty] | 8380 | 148 | 3.3622 | 2.3231
[7 empty] | 8381 | 149 | 3.3622 | 2.3231
[7 empty] | 8382 | 150 | 3.3706 | 2.3295
[7 empty] | 8383 | 151 | 4.4638 | 3.1547
[7 empty] | 8384 | 152 | 6.006 | 4.3191
[7 empty] | 8385 | 153 | 6.6246 | 4.7861
[7 empty] | 8386 | 154 | 7.1924 | 5.2147
[7 empty] | 8387 | 155 | 7.0398 | 5.0996
[7 empty] | 8388 | 156 | 7.2093 | 5.2275
[7 empty] | 8389 | 157 | 7.9296 | 5.7713
[7 empty] | 8390 | 158 | 8.2601 | 6.0208
[7 empty] | 8391 | 159 | 8.5313 | 6.2255
[7 empty] | 8392 | 160 | 8.4041 | 6.1296
[7 empty] | 8393 | 161 | 9.1753 | 6.7117
[7 empty] | 8394 | 162 | 8.6753 | 6.3343
[7 empty] | 8395 | 163 | 9.0397 | 6.6094
[7 empty] | 8396 | 164 | 7.6754 | 5.5794
[7 empty] | 8397 | 165 | 10.8362 | 7.9656
[7 empty] | 8398 | 166 | 8.7685 | 6.4046
[7 empty] | 8399 | 167 | 5.1247 | 3.6537
[7 empty] | 8400 | 168 | 4.4722 | 3.1611
[7 empty] | 8401 | 1 | 2.9978 | 2.048
[7 empty] | 8402 | 2 | 2.8876 | 1.9648
[7 empty] | 8403 | 3 | 2.8791 | 1.9584
[7 empty] | 8404 | 4 | 3.0147 | 2.0608
[7 empty] | 8405 | 5 | 3.0317 | 2.0736
[7 empty] | 8406 | 6 | 3.4638 | 2.3999
[7 empty] | 8407 | 7 | 4.1926 | 2.95
[7 empty] | 8408 | 8 | 4.8705 | 3.4618
[7 empty] | 8409 | 9 | 4.8451 | 3.4426
[7 empty] | 8410 | 10 | 6.3789 | 4.6006
[7 empty] | 8411 | 11 | 8.4804 | 6.1871
[7 empty] | 8412 | 12 | 9.4549 | 6.9228
[7 empty] | 8413 | 13 | 9.8362 | 7.2107
[7 empty] | 8414 | 14 | 9.6159 | 7.0444
[7 empty] | 8415 | 15 | 9.5227 | 6.974
[7 empty] | 8416 | 16 | 10.7175 | 7.8761
[7 empty] | 8417 | 17 | 12.0564 | 8.8868
[7 empty] | 8418 | 18 | 11.8107 | 8.7013
[7 empty] | 8419 | 19 | 12.3445 | 9.1044
[7 empty] | 8420 | 20 | 12.2767 | 9.0532
[7 empty] | 8421 | 21 | 12.853 | 9.4882
[7 empty] | 8422 | 22 | 8.8533 | 6.4686
[7 empty] | 8423 | 23 | 5.04 | 3.5898
[7 empty] | 8424 | 24 | 3.3504 | 2.3142
[7 empty] | 8425 | 25 | 3.252 | 2.2399
[7 empty] | 8426 | 26 | 3.1418 | 2.1567
[7 empty] | 8427 | 27 | 3.0401 | 2.08
[7 empty] | 8428 | 28 | 3.1249 | 2.144
[7 empty] | 8429 | 29 | 3.3706 | 2.3295
[7 empty] | 8430 | 30 | 3.6164 | 2.515
[7 empty] | 8431 | 31 | 4.4722 | 3.1611
[7 empty] | 8432 | 32 | 4.8281 | 3.4298
[7 empty] | 8433 | 33 | 5.4976 | 3.9352
[7 empty] | 8434 | 34 | 6.4043 | 4.6198
[7 empty] | 8435 | 35 | 8.5991 | 6.2767
[7 empty] | 8436 | 36 | 9.6413 | 7.0636
[7 empty] | 8437 | 37 | 9.7176 | 7.1212
[7 empty] | 8438 | 38 | 9.7939 | 7.1787
[7 empty] | 8439 | 39 | 9.4634 | 6.9292
[7 empty] | 8440 | 40 | 10.5311 | 7.7353
[7 empty] | 8441 | 41 | 11.0904 | 8.1575
[7 empty] | 8442 | 42 | 11.1073 | 8.1703
[7 empty] | 8443 | 43 | 11.4802 | 8.4518
[7 empty] | 8444 | 44 | 12.6496 | 9.3347
[7 empty] | 8445 | 45 | 12.2428 | 9.0276
[7 empty] | 8446 | 46 | 9.4634 | 6.9292
[7 empty] | 8447 | 47 | 5.8196 | 4.1783
[7 empty] | 8448 | 48 | 4.3028 | 3.0332
[7 empty] | 8449 | 49 | 3.6333 | 2.5278
[7 empty] | 8450 | 50 | 3.3198 | 2.2911
[7 empty] | 8451 | 51 | 3.2096 | 2.2079
[7 empty] | 8452 | 52 | 3.2435 | 2.2335
[7 empty] | 8453 | 53 | 3.2689 | 2.2527
[7 empty] | 8454 | 54 | 3.8536 | 2.6941
[7 empty] | 8455 | 55 | 5.0061 | 3.5642
[7 empty] | 8456 | 56 | 5.2518 | 3.7497
[7 empty] | 8457 | 57 | 6.2094 | 4.4726
[7 empty] | 8458 | 58 | 7.328 | 5.3171
[7 empty] | 8459 | 59 | 8.5482 | 6.2383
[7 empty] | 8460 | 60 | 9.1838 | 6.7181
[7 empty] | 8461 | 61 | 9.8701 | 7.2363
[7 empty] | 8462 | 62 | 9.6668 | 7.0828
[7 empty] | 8463 | 63 | 10.2684 | 7.537
[7 empty] | 8464 | 64 | 11.226 | 8.2599
[7 empty] | 8465 | 65 | 11.853 | 8.7333
[7 empty] | 8466 | 66 | 11.7514 | 8.6565
[7 empty] | 8467 | 67 | 12.4971 | 9.2195
[7 empty] | 8468 | 68 | 12.7428 | 9.405
[7 empty] | 8469 | 69 | 12.2259 | 9.0148
[7 empty] | 8470 | 70 | 9.904 | 7.2619
[7 empty] | 8471 | 71 | 5.3366 | 3.8137
[7 empty] | 8472 | 72 | 4.2398 | 2.9857
[7 empty] | 8473 | 73 | 3.5147 | 2.4382
[7 empty] | 8474 | 74 | 3.2859 | 2.2655
[7 empty] | 8475 | 75 | 3.1842 | 2.1887
[7 empty] | 8476 | 76 | 3.1249 | 2.144
[7 empty] | 8477 | 77 | 3.3028 | 2.2783
[7 empty] | 8478 | 78 | 3.7096 | 2.5854
[7 empty] | 8479 | 79 | 4.8366 | 3.4362
[7 empty] | 8480 | 80 | 5.0146 | 3.5706
[7 empty] | 8481 | 81 | 6.2094 | 4.4726
[7 empty] | 8482 | 82 | 7.311 | 5.3043
[7 empty] | 8483 | 83 | 8.0567 | 5.8673
[7 empty] | 8484 | 84 | 9.3109 | 6.8141
[7 empty] | 8485 | 85 | 9.0058 | 6.5838
[7 empty] | 8486 | 86 | 8.4889 | 6.1935
[7 empty] | 8487 | 87 | 8.938 | 6.5326
[7 empty] | 8488 | 88 | 9.6075 | 7.038
[7 empty] | 8489 | 89 | 10.9718 | 8.068
[7 empty] | 8490 | 90 | 10.3786 | 7.6202
[7 empty] | 8491 | 91 | 11.0734 | 8.1447
[7 empty] | 8492 | 92 | 10.4633 | 7.6841
[7 empty] | 8493 | 93 | 8.0228 | 5.8417
[7 empty] | 8494 | 94 | 7.1076 | 5.1507
[7 empty] | 8495 | 95 | 5.2264 | 3.7305
[7 empty] | 8496 | 96 | 4.2265 | 2.9756
[7 empty] | 8497 | 97 | 4.1757 | 2.9372
[7 empty] | 8498 | 98 | 3.8791 | 2.7133
[7 empty] | 8499 | 99 | 3.8197 | 2.6685
[7 empty] | 8500 | 100 | 3.4638 | 2.3999
[7 empty] | 8501 | 101 | 3.4045 | 2.3551
[7 empty] | 8502 | 102 | 3.6418 | 2.5342
[7 empty] | 8503 | 103 | 4.396 | 3.1036
[7 empty] | 8504 | 104 | 4.6502 | 3.2955
[7 empty] | 8505 | 105 | 5.1417 | 3.6665
[7 empty] | 8506 | 106 | 6.6161 | 4.7797
[7 empty] | 8507 | 107 | 6.9721 | 5.0484
[7 empty] | 8508 | 108 | 8.5652 | 6.2511
[7 empty] | 8509 | 109 | 7.8957 | 5.7457
[7 empty] | 8510 | 110 | 7.4381 | 5.4002
[7 empty] | 8511 | 111 | 7.2771 | 5.2787
[7 empty] | 8512 | 112 | 7.3449 | 5.3299
[7 empty] | 8513 | 113 | 6.9975 | 5.0676
[7 empty] | 8514 | 114 | 7.167 | 5.1955
[7 empty] | 8515 | 115 | 6.7094 | 4.8501
[7 empty] | 8516 | 116 | 7.3958 | 5.3683
[7 empty] | 8517 | 117 | 6.9721 | 5.0484
[7 empty] | 8518 | 118 | 6.1924 | 4.4598
[7 empty] | 8519 | 119 | 4.5824 | 3.2443
[7 empty] | 8520 | 120 | 4.2615 | 3.0021
[7 empty] | 8521 | 121 | 3.5232 | 2.4446
[7 empty] | 8522 | 122 | 3.1079 | 2.1312
[7 empty] | 8523 | 123 | 3.0232 | 2.0672
[7 empty] | 8524 | 124 | 2.9893 | 2.0416
[7 empty] | 8525 | 125 | 2.9469 | 2.0096
[7 empty] | 8526 | 126 | 3.091 | 2.1184
[7 empty] | 8527 | 127 | 4.6163 | 3.2699
[7 empty] | 8528 | 128 | 6.1924 | 4.4598
[7 empty] | 8529 | 129 | 6.8788 | 4.978
[7 empty] | 8530 | 130 | 7.3195 | 5.3107
[7 empty] | 8531 | 131 | 7.4805 | 5.4322
[7 empty] | 8532 | 132 | 7.2263 | 5.2403
[7 empty] | 8533 | 133 | 7.8703 | 5.7265
[7 empty] | 8534 | 134 | 8.1754 | 5.9568
[7 empty] | 8535 | 135 | 8.2431 | 6.008
[7 empty] | 8536 | 136 | 7.4212 | 5.3875
[7 empty] | 8537 | 137 | 7.3195 | 5.3107
[7 empty] | 8538 | 138 | 7.2686 | 5.2723
[7 empty] | 8539 | 139 | 6.9297 | 5.0164
[7 empty] | 8540 | 140 | 6.9382 | 5.0228
[7 empty] | 8541 | 141 | 6.2772 | 4.5238
[7 empty] | 8542 | 142 | 5.6332 | 4.0376
[7 empty] | 8543 | 143 | 4.7434 | 3.3659
[7 empty] | 8544 | 144 | 4.1248 | 2.8989
[7 empty] | 8545 | 145 | 3.6503 | 2.5406
[7 empty] | 8546 | 146 | 3.4384 | 2.3807
[7 empty] | 8547 | 147 | 3.3706 | 2.3295
[7 empty] | 8548 | 148 | 3.3622 | 2.3231
[7 empty] | 8549 | 149 | 3.3622 | 2.3231
[7 empty] | 8550 | 150 | 3.3706 | 2.3295
[7 empty] | 8551 | 151 | 4.4638 | 3.1547
[7 empty] | 8552 | 152 | 6.006 | 4.3191
[7 empty] | 8553 | 153 | 6.6246 | 4.7861
[7 empty] | 8554 | 154 | 7.1924 | 5.2147
[7 empty] | 8555 | 155 | 7.0398 | 5.0996
[7 empty] | 8556 | 156 | 7.2093 | 5.2275
[7 empty] | 8557 | 157 | 7.9296 | 5.7713
[7 empty] | 8558 | 158 | 8.2601 | 6.0208
[7 empty] | 8559 | 159 | 8.5313 | 6.2255
[7 empty] | 8560 | 160 | 8.4041 | 6.1296
[7 empty] | 8561 | 161 | 9.1753 | 6.7117
[7 empty] | 8562 | 162 | 8.6753 | 6.3343
[7 empty] | 8563 | 163 | 9.0397 | 6.6094
[7 empty] | 8564 | 164 | 7.6754 | 5.5794
[7 empty] | 8565 | 165 | 10.8362 | 7.9656
[7 empty] | 8566 | 166 | 8.7685 | 6.4046
[7 empty] | 8567 | 167 | 5.1247 | 3.6537
[7 empty] | 8568 | 168 | 4.4722 | 3.1611
[7 empty] | 8569 | 1 | 2.9978 | 2.048
[7 empty] | 8570 | 2 | 2.8876 | 1.9648
[7 empty] | 8571 | 3 | 2.8791 | 1.9584
[7 empty] | 8572 | 4 | 3.0147 | 2.0608
[7 empty] | 8573 | 5 | 3.0317 | 2.0736
[7 empty] | 8574 | 6 | 3.4638 | 2.3999
[7 empty] | 8575 | 7 | 4.1926 | 2.95
[7 empty] | 8576 | 8 | 4.8705 | 3.4618
[7 empty] | 8577 | 9 | 4.8451 | 3.4426
[7 empty] | 8578 | 10 | 6.3789 | 4.6006
[7 empty] | 8579 | 11 | 8.4804 | 6.1871
[7 empty] | 8580 | 12 | 9.4549 | 6.9228
[7 empty] | 8581 | 13 | 9.8362 | 7.2107
[7 empty] | 8582 | 14 | 9.6159 | 7.0444
[7 empty] | 8583 | 15 | 9.5227 | 6.974
[7 empty] | 8584 | 16 | 10.7175 | 7.8761
[7 empty] | 8585 | 17 | 12.0564 | 8.8868
[7 empty] | 8586 | 18 | 11.8107 | 8.7013
[7 empty] | 8587 | 19 | 12.3445 | 9.1044
[7 empty] | 8588 | 20 | 12.2767 | 9.0532
[7 empty] | 8589 | 21 | 12.853 | 9.4882
[7 empty] | 8590 | 22 | 8.8533 | 6.4686
[7 empty] | 8591 | 23 | 5.04 | 3.5898
[7 empty] | 8592 | 24 | 3.3504 | 2.3142
[7 empty] | 8593 | 25 | 3.252 | 2.2399
[7 empty] | 8594 | 26 | 3.1418 | 2.1567
[7 empty] | 8595 | 27 | 3.0401 | 2.08
[7 empty] | 8596 | 28 | 3.1249 | 2.144
[7 empty] | 8597 | 29 | 3.3706 | 2.3295
[7 empty] | 8598 | 30 | 3.6164 | 2.515
[7 empty] | 8599 | 31 | 4.4722 | 3.1611
[7 empty] | 8600 | 32 | 4.8281 | 3.4298
[7 empty] | 8601 | 33 | 5.4976 | 3.9352
[7 empty] | 8602 | 34 | 6.4043 | 4.6198
[7 empty] | 8603 | 35 | 8.5991 | 6.2767
[7 empty] | 8604 | 36 | 9.6413 | 7.0636
[7 empty] | 8605 | 37 | 9.7176 | 7.1212
[7 empty] | 8606 | 38 | 9.7939 | 7.1787
[7 empty] | 8607 | 39 | 9.4634 | 6.9292
[7 empty] | 8608 | 40 | 10.5311 | 7.7353
[7 empty] | 8609 | 41 | 11.0904 | 8.1575
[7 empty] | 8610 | 42 | 11.1073 | 8.1703
[7 empty] | 8611 | 43 | 11.4802 | 8.4518
[7 empty] | 8612 | 44 | 12.6496 | 9.3347
[7 empty] | 8613 | 45 | 12.2428 | 9.0276
[7 empty] | 8614 | 46 | 9.4634 | 6.9292
[7 empty] | 8615 | 47 | 5.8196 | 4.1783
[7 empty] | 8616 | 48 | 4.3028 | 3.0332
[7 empty] | 8617 | 49 | 3.6333 | 2.5278
[7 empty] | 8618 | 50 | 3.3198 | 2.2911
[7 empty] | 8619 | 51 | 3.2096 | 2.2079
[7 empty] | 8620 | 52 | 3.2435 | 2.2335
[7 empty] | 8621 | 53 | 3.2689 | 2.2527
[7 empty] | 8622 | 54 | 3.8536 | 2.6941
[7 empty] | 8623 | 55 | 5.0061 | 3.5642
[7 empty] | 8624 | 56 | 5.2518 | 3.7497
[7 empty] | 8625 | 57 | 6.2094 | 4.4726
[7 empty] | 8626 | 58 | 7.328 | 5.3171
[7 empty] | 8627 | 59 | 8.5482 | 6.2383
[7 empty] | 8628 | 60 | 9.1838 | 6.7181
[7 empty] | 8629 | 61 | 9.8701 | 7.2363
[7 empty] | 8630 | 62 | 9.6668 | 7.0828
[7 empty] | 8631 | 63 | 10.2684 | 7.537
[7 empty] | 8632 | 64 | 11.226 | 8.2599
[7 empty] | 8633 | 65 | 11.853 | 8.7333
[7 empty] | 8634 | 66 | 11.7514 | 8.6565
[7 empty] | 8635 | 67 | 12.4971 | 9.2195
[7 empty] | 8636 | 68 | 12.7428 | 9.405
[7 empty] | 8637 | 69 | 12.2259 | 9.0148
[7 empty] | 8638 | 70 | 9.904 | 7.2619
[7 empty] | 8639 | 71 | 5.3366 | 3.8137
[7 empty] | 8640 | 72 | 4.2398 | 2.9857
[7 empty] | 8641 | 73 | 3.5147 | 2.4382
[7 empty] | 8642 | 74 | 3.2859 | 2.2655
[7 empty] | 8643 | 75 | 3.1842 | 2.1887
[7 empty] | 8644 | 76 | 3.1249 | 2.144
[7 empty] | 8645 | 77 | 3.3028 | 2.2783
[7 empty] | 8646 | 78 | 3.7096 | 2.5854
[7 empty] | 8647 | 79 | 4.8366 | 3.4362
[7 empty] | 8648 | 80 | 5.0146 | 3.5706
[7 empty] | 8649 | 81 | 6.2094 | 4.4726
[7 empty] | 8650 | 82 | 7.311 | 5.3043
[7 empty] | 8651 | 83 | 8.0567 | 5.8673
[7 empty] | 8652 | 84 | 9.3109 | 6.8141
[7 empty] | 8653 | 85 | 9.0058 | 6.5838
[7 empty] | 8654 | 86 | 8.4889 | 6.1935
[7 empty] | 8655 | 87 | 8.938 | 6.5326
[7 empty] | 8656 | 88 | 9.6075 | 7.038
[7 empty] | 8657 | 89 | 10.9718 | 8.068
[7 empty] | 8658 | 90 | 10.3786 | 7.6202
[7 empty] | 8659 | 91 | 11.0734 | 8.1447
[7 empty] | 8660 | 92 | 10.4633 | 7.6841
[7 empty] | 8661 | 93 | 8.0228 | 5.8417
[7 empty] | 8662 | 94 | 7.1076 | 5.1507
[7 empty] | 8663 | 95 | 5.2264 | 3.7305
[7 empty] | 8664 | 96 | 4.2265 | 2.9756
[7 empty] | 8665 | 97 | 4.1757 | 2.9372
[7 empty] | 8666 | 98 | 3.8791 | 2.7133
[7 empty] | 8667 | 99 | 3.8197 | 2.6685
[7 empty] | 8668 | 100 | 3.4638 | 2.3999
[7 empty] | 8669 | 101 | 3.4045 | 2.3551
[7 empty] | 8670 | 102 | 3.6418 | 2.5342
[7 empty] | 8671 | 103 | 4.396 | 3.1036
[7 empty] | 8672 | 104 | 4.6502 | 3.2955
[7 empty] | 8673 | 105 | 5.1417 | 3.6665
[7 empty] | 8674 | 106 | 6.6161 | 4.7797
[7 empty] | 8675 | 107 | 6.9721 | 5.0484
[7 empty] | 8676 | 108 | 8.5652 | 6.2511
[7 empty] | 8677 | 109 | 7.8957 | 5.7457
[7 empty] | 8678 | 110 | 7.4381 | 5.4002
[7 empty] | 8679 | 111 | 7.2771 | 5.2787
[7 empty] | 8680 | 112 | 7.3449 | 5.3299
[7 empty] | 8681 | 113 | 6.9975 | 5.0676
[7 empty] | 8682 | 114 | 7.167 | 5.1955
[7 empty] | 8683 | 115 | 6.7094 | 4.8501
[7 empty] | 8684 | 116 | 7.3958 | 5.3683
[7 empty] | 8685 | 117 | 6.9721 | 5.0484
[7 empty] | 8686 | 118 | 6.1924 | 4.4598
[7 empty] | 8687 | 119 | 4.5824 | 3.2443
[7 empty] | 8688 | 120 | 4.2615 | 3.0021
[7 empty] | 8689 | 121 | 3.5232 | 2.4446
[7 empty] | 8690 | 122 | 3.1079 | 2.1312
[7 empty] | 8691 | 123 | 3.0232 | 2.0672
[7 empty] | 8692 | 124 | 2.9893 | 2.0416
[7 empty] | 8693 | 125 | 2.9469 | 2.0096
[7 empty] | 8694 | 126 | 3.091 | 2.1184
[7 empty] | 8695 | 127 | 4.6163 | 3.2699
[7 empty] | 8696 | 128 | 6.1924 | 4.4598
[7 empty] | 8697 | 129 | 6.8788 | 4.978
[7 empty] | 8698 | 130 | 7.3195 | 5.3107
[7 empty] | 8699 | 131 | 7.4805 | 5.4322
[7 empty] | 8700 | 132 | 7.2263 | 5.2403
[7 empty] | 8701 | 133 | 7.8703 | 5.7265
[7 empty] | 8702 | 134 | 8.1754 | 5.9568
[7 empty] | 8703 | 135 | 8.2431 | 6.008
[7 empty] | 8704 | 136 | 7.4212 | 5.3875
[7 empty] | 8705 | 137 | 7.3195 | 5.3107
[7 empty] | 8706 | 138 | 7.2686 | 5.2723
[7 empty] | 8707 | 139 | 6.9297 | 5.0164
[7 empty] | 8708 | 140 | 6.9382 | 5.0228
[7 empty] | 8709 | 141 | 6.2772 | 4.5238
[7 empty] | 8710 | 142 | 5.6332 | 4.0376
[7 empty] | 8711 | 143 | 4.7434 | 3.3659
[7 empty] | 8712 | 144 | 4.1248 | 2.8989
[7 empty] | 8713 | 145 | 3.6503 | 2.5406
[7 empty] | 8714 | 146 | 3.4384 | 2.3807
[7 empty] | 8715 | 147 | 3.3706 | 2.3295
[7 empty] | 8716 | 148 | 3.3622 | 2.3231
[7 empty] | 8717 | 149 | 3.3622 | 2.3231
[7 empty] | 8718 | 150 | 3.3706 | 2.3295
[7 empty] | 8719 | 151 | 4.4638 | 3.1547
[7 empty] | 8720 | 152 | 6.006 | 4.3191
[7 empty] | 8721 | 153 | 6.6246 | 4.7861
[7 empty] | 8722 | 154 | 7.1924 | 5.2147
[7 empty] | 8723 | 155 | 7.0398 | 5.0996
[7 empty] | 8724 | 156 | 7.2093 | 5.2275
[7 empty] | 8725 | 157 | 7.9296 | 5.7713
[7 empty] | 8726 | 158 | 8.2601 | 6.0208
[7 empty] | 8727 | 159 | 8.5313 | 6.2255
[7 empty] | 8728 | 160 | 8.4041 | 6.1296
[7 empty] | 8729 | 161 | 9.1753 | 6.7117
[7 empty] | 8730 | 162 | 8.6753 | 6.3343
[7 empty] | 8731 | 163 | 9.0397 | 6.6094
[7 empty] | 8732 | 164 | 7.6754 | 5.5794
[7 empty] | 8733 | 165 | 10.8362 | 7.9656
[7 empty] | 8734 | 166 | 8.7685 | 6.4046
[7 empty] | 8735 | 167 | 5.1247 | 3.6537
[7 empty] | 8736 | 168 | 4.4722 | 3.1611
[7 empty] | 8737 | 1 | 2.9978 | 2.048
[7 empty] | 8738 | 2 | 2.8876 | 1.9648
[7 empty] | 8739 | 3 | 2.8791 | 1.9584
[7 empty] | 8740 | 4 | 3.0147 | 2.0608
[7 empty] | 8741 | 5 | 3.0317 | 2.0736
[7 empty] | 8742 | 6 | 3.4638 | 2.3999
[7 empty] | 8743 | 7 | 4.1926 | 2.95
[7 empty] | 8744 | 8 | 4.8705 | 3.4618
[7 empty] | 8745 | 9 | 4.8451 | 3.4426
[7 empty] | 8746 | 10 | 6.3789 | 4.6006
[7 empty] | 8747 | 11 | 8.4804 | 6.1871
[7 empty] | 8748 | 12 | 9.4549 | 6.9228
[7 empty] | 8749 | 13 | 9.8362 | 7.2107
[7 empty] | 8750 | 14 | 9.6159 | 7.0444
[7 empty] | 8751 | 15 | 9.5227 | 6.974
[7 empty] | 8752 | 16 | 10.7175 | 7.8761
[7 empty] | 8753 | 17 | 12.0564 | 8.8868
[7 empty] | 8754 | 18 | 11.8107 | 8.7013
[7 empty] | 8755 | 19 | 12.3445 | 9.1044
[7 empty] | 8756 | 20 | 12.2767 | 9.0532
[7 empty] | 8757 | 21 | 12.853 | 9.4882
[7 empty] | 8758 | 22 | 8.8533 | 6.4686
[7 empty] | 8759 | 23 | 5.04 | 3.5898
[7 empty] | 8760 | 24 | 3.3504 | 2.3142

## DC_2018
Hour | Server | Non-server | Total | Unit: MW | PUE | PUE-Max | Hour-year | Hour-week | Total (MWh) | Server (MWh)
1 | 1.8609 | 0.82475 | 2.6856 |  | 1.341 | 1.3083 | 1 | 1 | 2.6856 | 1.8609
2 | 1.7758 | 0.80131 | 2.5771 |  |  |  | 2 | 2 | 2.5771 | 1.7758
3 | 1.7692 | 0.7995 | 2.5687 |  | Server-Max | Total-Max | 3 | 3 | 2.5687 | 1.7692
4 | 1.874 | 0.82835 | 2.7023 |  | 9.4762 | 12.398 | 4 | 4 | 2.7023 | 1.874
5 | 1.8871 | 0.83196 | 2.719 |  |  |  | 5 | 5 | 2.719 | 1.8871
6 | 2.221 | 0.92392 | 3.1449 |  | Assumed max utilization rate (UR) |  | 6 | 6 | 3.1449 | 2.221
7 | 2.7841 | 1.079 | 3.8631 |  | 65% |  | 7 | 7 | 3.8631 | 2.7841
8 | 3.308 | 1.2232 | 4.5312 |  |  |  | 8 | 8 | 4.5312 | 3.308
9 | 3.2883 | 1.2178 | 4.5062 |  | Servers energy at max UR | Total energy at max UR | 9 | 9 | 4.5062 | 3.2883
10 | 4.4735 | 1.5442 | 6.0177 |  | 6.955 | 9.1825 | 10 | 10 | 6.0177 | 4.4735
11 | 6.0974 | 1.9914 | 8.0888 |  |  |  | 11 | 11 | 8.0888 | 6.0974
12 | 6.8504 | 2.1987 | 9.0492 |  | Non-server power linear model scaling factor |  | 12 | 12 | 9.0492 | 6.8504
13 | 7.1451 | 2.2799 | 9.425 |  | 0.26294 |  | 13 | 13 | 9.425 | 7.1451
14 | 6.9748 | 2.233 | 9.2079 |  |  |  | 14 | 14 | 9.2079 | 6.9748
15 | 6.9028 | 2.2132 | 9.116 |  |  |  | 15 | 15 | 9.116 | 6.9028
16 | 7.8261 | 2.4674 | 10.2935 |  |  |  | 16 | 16 | 10.2935 | 7.8261
17 | 8.8607 | 2.7523 | 11.613 |  |  |  | 17 | 17 | 11.613 | 8.8607
18 | 8.6708 | 2.7 | 11.3708 |  |  |  | 18 | 18 | 11.3708 | 8.6708
19 | 9.0833 | 2.8136 | 11.8969 |  |  |  | 19 | 19 | 11.8969 | 9.0833
20 | 9.0309 | 2.7992 | 11.8301 |  |  |  | 20 | 20 | 11.8301 | 9.0309
21 | 9.4762 | 2.9218 | 12.398 |  |  |  | 21 | 21 | 12.398 | 9.4762
22 | 6.3855 | 2.0707 | 8.4563 |  |  |  | 22 | 22 | 8.4563 | 6.3855
23 | 3.4389 | 1.2593 | 4.6983 |  |  |  | 23 | 23 | 4.6983 | 3.4389
24 | 2.1333 | 0.89977 | 3.0331 |  |  |  | 24 | 24 | 3.0331 | 2.1333
25 | 2.0573 | 0.87884 | 2.9362 |  |  |  | 25 | 25 | 2.9362 | 2.0573
26 | 1.9722 | 0.8554 | 2.8276 |  |  |  | 26 | 26 | 2.8276 | 1.9722
27 | 1.8936 | 0.83376 | 2.7274 |  |  |  | 27 | 27 | 2.7274 | 1.8936
28 | 1.9591 | 0.85179 | 2.8109 |  |  |  | 28 | 28 | 2.8109 | 1.9591
29 | 2.149 | 0.90409 | 3.0531 |  |  |  | 29 | 29 | 3.0531 | 2.149
30 | 2.3389 | 0.95638 | 3.2953 |  |  |  | 30 | 30 | 3.2953 | 2.3389
31 | 3.0002 | 1.1385 | 4.1387 |  |  |  | 31 | 31 | 4.1387 | 3.0002
32 | 3.2752 | 1.2142 | 4.4895 |  |  |  | 32 | 32 | 4.4895 | 3.2752
33 | 3.7925 | 1.3567 | 5.1492 |  |  |  | 33 | 33 | 5.1492 | 3.7925
34 | 4.4932 | 1.5496 | 6.0428 |  |  |  | 34 | 34 | 6.0428 | 4.4932
35 | 6.1891 | 2.0166 | 8.2057 |  |  |  | 35 | 35 | 8.2057 | 6.1891
36 | 6.9945 | 2.2384 | 9.2329 |  |  |  | 36 | 36 | 9.2329 | 6.9945
37 | 7.0534 | 2.2546 | 9.3081 |  |  |  | 37 | 37 | 9.3081 | 7.0534
38 | 7.1123 | 2.2709 | 9.3832 |  |  |  | 38 | 38 | 9.3832 | 7.1123
39 | 6.857 | 2.2006 | 9.0575 |  |  |  | 39 | 39 | 9.0575 | 6.857
40 | 7.682 | 2.4277 | 10.1098 |  |  |  | 40 | 40 | 10.1098 | 7.682
41 | 8.1142 | 2.5468 | 10.6609 |  |  |  | 41 | 41 | 10.6609 | 8.1142
42 | 8.1273 | 2.5504 | 10.6776 |  |  |  | 42 | 42 | 10.6776 | 8.1273
43 | 8.4154 | 2.6297 | 11.0451 |  |  |  | 43 | 43 | 11.0451 | 8.4154
44 | 9.319 | 2.8785 | 12.1975 |  |  |  | 44 | 44 | 12.1975 | 9.319
45 | 9.0047 | 2.792 | 11.7967 |  |  |  | 45 | 45 | 11.7967 | 9.0047
46 | 6.857 | 2.2006 | 9.0575 |  |  |  | 46 | 46 | 9.0575 | 6.857
47 | 4.0414 | 1.4252 | 5.4666 |  |  |  | 47 | 47 | 5.4666 | 4.0414
48 | 2.8693 | 1.1024 | 3.9717 |  |  |  | 48 | 48 | 3.9717 | 2.8693
49 | 2.352 | 0.95998 | 3.312 |  |  |  | 49 | 49 | 3.312 | 2.352
50 | 2.1097 | 0.89327 | 3.003 |  |  |  | 50 | 50 | 3.003 | 2.1097
51 | 2.0246 | 0.86983 | 2.8944 |  |  |  | 51 | 51 | 2.8944 | 2.0246
52 | 2.0508 | 0.87704 | 2.9278 |  |  |  | 52 | 52 | 2.9278 | 2.0508
53 | 2.0704 | 0.88245 | 2.9529 |  |  |  | 53 | 53 | 2.9529 | 2.0704
54 | 2.5222 | 1.0069 | 3.5291 |  |  |  | 54 | 54 | 3.5291 | 2.5222
55 | 3.4128 | 1.2521 | 4.6648 |  |  |  | 55 | 55 | 4.6648 | 3.4128
56 | 3.6026 | 1.3044 | 4.907 |  |  |  | 56 | 56 | 4.907 | 3.6026
57 | 4.3426 | 1.5081 | 5.8507 |  |  |  | 57 | 57 | 5.8507 | 4.3426
58 | 5.2069 | 1.7462 | 6.9531 |  |  |  | 58 | 58 | 6.9531 | 5.2069
59 | 6.1498 | 2.0058 | 8.1556 |  |  |  | 59 | 59 | 8.1556 | 6.1498
60 | 6.6409 | 2.141 | 8.7819 |  |  |  | 60 | 60 | 8.7819 | 6.6409
61 | 7.1713 | 2.2871 | 9.4584 |  |  |  | 61 | 61 | 9.4584 | 7.1713
62 | 7.0141 | 2.2438 | 9.258 |  |  |  | 62 | 62 | 9.258 | 7.0141
63 | 7.479 | 2.3719 | 9.8509 |  |  |  | 63 | 63 | 9.8509 | 7.479
64 | 8.219 | 2.5756 | 10.7946 |  |  |  | 64 | 64 | 10.7946 | 8.219
65 | 8.7035 | 2.709 | 11.4125 |  |  |  | 65 | 65 | 11.4125 | 8.7035
66 | 8.6249 | 2.6874 | 11.3123 |  |  |  | 66 | 66 | 11.3123 | 8.6249
67 | 9.2011 | 2.8461 | 12.0472 |  |  |  | 67 | 67 | 12.0472 | 9.2011
68 | 9.391 | 2.8984 | 12.2894 |  |  |  | 68 | 68 | 12.2894 | 9.391
69 | 8.9916 | 2.7884 | 11.78 |  |  |  | 69 | 69 | 11.78 | 8.9916
70 | 7.1975 | 2.2943 | 9.4918 |  |  |  | 70 | 70 | 9.4918 | 7.1975
71 | 3.6681 | 1.3224 | 4.9905 |  |  |  | 71 | 71 | 4.9905 | 3.6681
72 | 2.8206 | 1.089 | 3.9097 |  |  |  | 72 | 72 | 3.9097 | 2.8206
73 | 2.2603 | 0.93474 | 3.1951 |  |  |  | 73 | 73 | 3.1951 | 2.2603
74 | 2.0835 | 0.88605 | 2.9696 |  |  |  | 74 | 74 | 2.9696 | 2.0835
75 | 2.0049 | 0.86442 | 2.8694 |  |  |  | 75 | 75 | 2.8694 | 2.0049
76 | 1.9591 | 0.85179 | 2.8109 |  |  |  | 76 | 76 | 2.8109 | 1.9591
77 | 2.0966 | 0.88966 | 2.9863 |  |  |  | 77 | 77 | 2.9863 | 2.0966
78 | 2.4109 | 0.97621 | 3.3871 |  |  |  | 78 | 78 | 3.3871 | 2.4109
79 | 3.2818 | 1.216 | 4.4978 |  |  |  | 79 | 79 | 4.4978 | 3.2818
80 | 3.4193 | 1.2539 | 4.6732 |  |  |  | 80 | 80 | 4.6732 | 3.4193
81 | 4.3426 | 1.5081 | 5.8507 |  |  |  | 81 | 81 | 5.8507 | 4.3426
82 | 5.1938 | 1.7426 | 6.9363 |  |  |  | 82 | 82 | 6.9363 | 5.1938
83 | 5.77 | 1.9012 | 7.6712 |  |  |  | 83 | 83 | 7.6712 | 5.77
84 | 6.7391 | 2.1681 | 8.9072 |  |  |  | 84 | 84 | 8.9072 | 6.7391
85 | 6.5034 | 2.1032 | 8.6066 |  |  |  | 85 | 85 | 8.6066 | 6.5034
86 | 6.104 | 1.9932 | 8.0972 |  |  |  | 86 | 86 | 8.0972 | 6.104
87 | 6.451 | 2.0888 | 8.5398 |  |  |  | 87 | 87 | 8.5398 | 6.451
88 | 6.9683 | 2.2312 | 9.1995 |  |  |  | 88 | 88 | 9.1995 | 6.9683
89 | 8.0225 | 2.5215 | 10.544 |  |  |  | 89 | 89 | 10.544 | 8.0225
90 | 7.5642 | 2.3953 | 9.9595 |  |  |  | 90 | 90 | 9.9595 | 7.5642
91 | 8.1011 | 2.5432 | 10.6442 |  |  |  | 91 | 91 | 10.6442 | 8.1011
92 | 7.6296 | 2.4133 | 10.043 |  |  |  | 92 | 92 | 10.043 | 7.6296
93 | 5.7438 | 1.894 | 7.6378 |  |  |  | 93 | 93 | 7.6378 | 5.7438
94 | 5.0366 | 1.6993 | 6.7359 |  |  |  | 94 | 94 | 6.7359 | 5.0366
95 | 3.583 | 1.299 | 4.882 |  |  |  | 95 | 95 | 4.882 | 3.583
96 | 2.8103 | 1.0862 | 3.8965 |  |  |  | 96 | 96 | 3.8965 | 2.8103
97 | 2.7711 | 1.0754 | 3.8464 |  |  |  | 97 | 97 | 3.8464 | 2.7711
98 | 2.5419 | 1.0123 | 3.5541 |  |  |  | 98 | 98 | 3.5541 | 2.5419
99 | 2.496 | 0.99965 | 3.4957 |  |  |  | 99 | 99 | 3.4957 | 2.496
100 | 2.221 | 0.92392 | 3.1449 |  |  |  | 100 | 100 | 3.1449 | 2.221
101 | 2.1752 | 0.9113 | 3.0865 |  |  |  | 101 | 101 | 3.0865 | 2.1752
102 | 2.3585 | 0.96179 | 3.3203 |  |  |  | 102 | 102 | 3.3203 | 2.3585
103 | 2.9413 | 1.1223 | 4.0636 |  |  |  | 103 | 103 | 4.0636 | 2.9413
104 | 3.1377 | 1.1764 | 4.3141 |  |  |  | 104 | 104 | 4.3141 | 3.1377
105 | 3.5175 | 1.2809 | 4.7985 |  |  |  | 105 | 105 | 4.7985 | 3.5175
106 | 4.6569 | 1.5947 | 6.2516 |  |  |  | 106 | 106 | 6.2516 | 4.6569
107 | 4.9319 | 1.6704 | 6.6023 |  |  |  | 107 | 107 | 6.6023 | 4.9319
108 | 6.1629 | 2.0094 | 8.1723 |  |  |  | 108 | 108 | 8.1723 | 6.1629
109 | 5.6456 | 1.867 | 7.5126 |  |  |  | 109 | 109 | 7.5126 | 5.6456
110 | 5.292 | 1.7696 | 7.0616 |  |  |  | 110 | 110 | 7.0616 | 5.292
111 | 5.1676 | 1.7353 | 6.9029 |  |  |  | 111 | 111 | 6.9029 | 5.1676
112 | 5.22 | 1.7498 | 6.9698 |  |  |  | 112 | 112 | 6.9698 | 5.22
113 | 4.9515 | 1.6758 | 6.6274 |  |  |  | 113 | 113 | 6.6274 | 4.9515
114 | 5.0825 | 1.7119 | 6.7944 |  |  |  | 114 | 114 | 6.7944 | 5.0825
115 | 4.7289 | 1.6145 | 6.3434 |  |  |  | 115 | 115 | 6.3434 | 4.7289
116 | 5.2593 | 1.7606 | 7.0199 |  |  |  | 116 | 116 | 7.0199 | 5.2593
117 | 4.9319 | 1.6704 | 6.6023 |  |  |  | 117 | 117 | 6.6023 | 4.9319
118 | 4.3295 | 1.5045 | 5.834 |  |  |  | 118 | 118 | 5.834 | 4.3295
119 | 3.0854 | 1.1619 | 4.2473 |  |  |  | 119 | 119 | 4.2473 | 3.0854
120 | 2.8374 | 1.0937 | 3.9311 |  |  |  | 120 | 120 | 3.9311 | 2.8374
121 | 2.2669 | 0.93654 | 3.2034 |  |  |  | 121 | 121 | 3.2034 | 2.2669
122 | 1.946 | 0.84819 | 2.7942 |  |  |  | 122 | 122 | 2.7942 | 1.946
123 | 1.8805 | 0.83016 | 2.7107 |  |  |  | 123 | 123 | 2.7107 | 1.8805
124 | 1.8543 | 0.82294 | 2.6773 |  |  |  | 124 | 124 | 2.6773 | 1.8543
125 | 1.8216 | 0.81393 | 2.6355 |  |  |  | 125 | 125 | 2.6355 | 1.8216
126 | 1.9329 | 0.84458 | 2.7775 |  |  |  | 126 | 126 | 2.7775 | 1.9329
127 | 3.1115 | 1.1691 | 4.2807 |  |  |  | 127 | 127 | 4.2807 | 3.1115
128 | 4.3295 | 1.5045 | 5.834 |  |  |  | 128 | 128 | 5.834 | 4.3295
129 | 4.8599 | 1.6506 | 6.5104 |  |  |  | 129 | 129 | 6.5104 | 4.8599
130 | 5.2003 | 1.7444 | 6.9447 |  |  |  | 130 | 130 | 6.9447 | 5.2003
131 | 5.3248 | 1.7786 | 7.1034 |  |  |  | 131 | 131 | 7.1034 | 5.3248
132 | 5.1283 | 1.7245 | 6.8528 |  |  |  | 132 | 132 | 6.8528 | 5.1283
133 | 5.626 | 1.8616 | 7.4875 |  |  |  | 133 | 133 | 7.4875 | 5.626
134 | 5.8617 | 1.9265 | 7.7882 |  |  |  | 134 | 134 | 7.7882 | 5.8617
135 | 5.9141 | 1.9409 | 7.855 |  |  |  | 135 | 135 | 7.855 | 5.9141
136 | 5.2789 | 1.766 | 7.0449 |  |  |  | 136 | 136 | 7.0449 | 5.2789
137 | 5.2003 | 1.7444 | 6.9447 |  |  |  | 137 | 137 | 6.9447 | 5.2003
138 | 5.1611 | 1.7335 | 6.8946 |  |  |  | 138 | 138 | 6.8946 | 5.1611
139 | 4.8991 | 1.6614 | 6.5605 |  |  |  | 139 | 139 | 6.5605 | 4.8991
140 | 4.9057 | 1.6632 | 6.5689 |  |  |  | 140 | 140 | 6.5689 | 4.9057
141 | 4.3949 | 1.5226 | 5.9175 |  |  |  | 141 | 141 | 5.9175 | 4.3949
142 | 3.8973 | 1.3855 | 5.2828 |  |  |  | 142 | 142 | 5.2828 | 3.8973
143 | 3.2098 | 1.1962 | 4.406 |  |  |  | 143 | 143 | 4.406 | 3.2098
144 | 2.7318 | 1.0646 | 3.7963 |  |  |  | 144 | 144 | 3.7963 | 2.7318
145 | 2.3651 | 0.96359 | 3.3287 |  |  |  | 145 | 145 | 3.3287 | 2.3651
146 | 2.2014 | 0.91851 | 3.1199 |  |  |  | 146 | 146 | 3.1199 | 2.2014
147 | 2.149 | 0.90409 | 3.0531 |  |  |  | 147 | 147 | 3.0531 | 2.149
148 | 2.1424 | 0.90228 | 3.0447 |  |  |  | 148 | 148 | 3.0447 | 2.1424
149 | 2.1424 | 0.90228 | 3.0447 |  |  |  | 149 | 149 | 3.0447 | 2.1424
150 | 2.149 | 0.90409 | 3.0531 |  |  |  | 150 | 150 | 3.0531 | 2.149
151 | 2.9937 | 1.1367 | 4.1304 |  |  |  | 151 | 151 | 4.1304 | 2.9937
152 | 4.1854 | 1.4649 | 5.6503 |  |  |  | 152 | 152 | 5.6503 | 4.1854
153 | 4.6634 | 1.5965 | 6.2599 |  |  |  | 153 | 153 | 6.2599 | 4.6634
154 | 5.1021 | 1.7173 | 6.8194 |  |  |  | 154 | 154 | 6.8194 | 5.1021
155 | 4.9843 | 1.6849 | 6.6691 |  |  |  | 155 | 155 | 6.6691 | 4.9843
156 | 5.1152 | 1.7209 | 6.8361 |  |  |  | 156 | 156 | 6.8361 | 5.1152
157 | 5.6718 | 1.8742 | 7.546 |  |  |  | 157 | 157 | 7.546 | 5.6718
158 | 5.9272 | 1.9445 | 7.8717 |  |  |  | 158 | 158 | 7.8717 | 5.9272
159 | 6.1367 | 2.0022 | 8.1389 |  |  |  | 159 | 159 | 8.1389 | 6.1367
160 | 6.0385 | 1.9752 | 8.0136 |  |  |  | 160 | 160 | 8.0136 | 6.0385
161 | 6.6343 | 2.1392 | 8.7736 |  |  |  | 161 | 161 | 8.7736 | 6.6343
162 | 6.248 | 2.0329 | 8.2809 |  |  |  | 162 | 162 | 8.2809 | 6.248
163 | 6.5296 | 2.1104 | 8.64 |  |  |  | 163 | 163 | 8.64 | 6.5296
164 | 5.4754 | 1.8201 | 7.2954 |  |  |  | 164 | 164 | 7.2954 | 5.4754
165 | 7.9177 | 2.4927 | 10.4104 |  |  |  | 165 | 165 | 10.4104 | 7.9177
166 | 6.32 | 2.0527 | 8.3727 |  |  |  | 166 | 166 | 8.3727 | 6.32
167 | 3.5044 | 1.2773 | 4.7818 |  |  |  | 167 | 167 | 4.7818 | 3.5044
168 | 3.0002 | 1.1385 | 4.1387 |  |  |  | 168 | 168 | 4.1387 | 3.0002
[7 empty] | 169 | 1 | 2.6856 | 1.8609
[7 empty] | 170 | 2 | 2.5771 | 1.7758
[7 empty] | 171 | 3 | 2.5687 | 1.7692
[7 empty] | 172 | 4 | 2.7023 | 1.874
[7 empty] | 173 | 5 | 2.719 | 1.8871
[7 empty] | 174 | 6 | 3.1449 | 2.221
[7 empty] | 175 | 7 | 3.8631 | 2.7841
[7 empty] | 176 | 8 | 4.5312 | 3.308
[7 empty] | 177 | 9 | 4.5062 | 3.2883
[7 empty] | 178 | 10 | 6.0177 | 4.4735
[7 empty] | 179 | 11 | 8.0888 | 6.0974
[7 empty] | 180 | 12 | 9.0492 | 6.8504
[7 empty] | 181 | 13 | 9.425 | 7.1451
[7 empty] | 182 | 14 | 9.2079 | 6.9748
[7 empty] | 183 | 15 | 9.116 | 6.9028
[7 empty] | 184 | 16 | 10.2935 | 7.8261
[7 empty] | 185 | 17 | 11.613 | 8.8607
[7 empty] | 186 | 18 | 11.3708 | 8.6708
[7 empty] | 187 | 19 | 11.8969 | 9.0833
[7 empty] | 188 | 20 | 11.8301 | 9.0309
[7 empty] | 189 | 21 | 12.398 | 9.4762
[7 empty] | 190 | 22 | 8.4563 | 6.3855
[7 empty] | 191 | 23 | 4.6983 | 3.4389
[7 empty] | 192 | 24 | 3.0331 | 2.1333
[7 empty] | 193 | 25 | 2.9362 | 2.0573
[7 empty] | 194 | 26 | 2.8276 | 1.9722
[7 empty] | 195 | 27 | 2.7274 | 1.8936
[7 empty] | 196 | 28 | 2.8109 | 1.9591
[7 empty] | 197 | 29 | 3.0531 | 2.149
[7 empty] | 198 | 30 | 3.2953 | 2.3389
[7 empty] | 199 | 31 | 4.1387 | 3.0002
[7 empty] | 200 | 32 | 4.4895 | 3.2752
[7 empty] | 201 | 33 | 5.1492 | 3.7925
[7 empty] | 202 | 34 | 6.0428 | 4.4932
[7 empty] | 203 | 35 | 8.2057 | 6.1891
[7 empty] | 204 | 36 | 9.2329 | 6.9945
[7 empty] | 205 | 37 | 9.3081 | 7.0534
[7 empty] | 206 | 38 | 9.3832 | 7.1123
[7 empty] | 207 | 39 | 9.0575 | 6.857
[7 empty] | 208 | 40 | 10.1098 | 7.682
[7 empty] | 209 | 41 | 10.6609 | 8.1142
[7 empty] | 210 | 42 | 10.6776 | 8.1273
[7 empty] | 211 | 43 | 11.0451 | 8.4154
[7 empty] | 212 | 44 | 12.1975 | 9.319
[7 empty] | 213 | 45 | 11.7967 | 9.0047
[7 empty] | 214 | 46 | 9.0575 | 6.857
[7 empty] | 215 | 47 | 5.4666 | 4.0414
[7 empty] | 216 | 48 | 3.9717 | 2.8693
[7 empty] | 217 | 49 | 3.312 | 2.352
[7 empty] | 218 | 50 | 3.003 | 2.1097
[7 empty] | 219 | 51 | 2.8944 | 2.0246
[7 empty] | 220 | 52 | 2.9278 | 2.0508
[7 empty] | 221 | 53 | 2.9529 | 2.0704
[7 empty] | 222 | 54 | 3.5291 | 2.5222
[7 empty] | 223 | 55 | 4.6648 | 3.4128
[7 empty] | 224 | 56 | 4.907 | 3.6026
[7 empty] | 225 | 57 | 5.8507 | 4.3426
[7 empty] | 226 | 58 | 6.9531 | 5.2069
[7 empty] | 227 | 59 | 8.1556 | 6.1498
[7 empty] | 228 | 60 | 8.7819 | 6.6409
[7 empty] | 229 | 61 | 9.4584 | 7.1713
[7 empty] | 230 | 62 | 9.258 | 7.0141
[7 empty] | 231 | 63 | 9.8509 | 7.479
[7 empty] | 232 | 64 | 10.7946 | 8.219
[7 empty] | 233 | 65 | 11.4125 | 8.7035
[7 empty] | 234 | 66 | 11.3123 | 8.6249
[7 empty] | 235 | 67 | 12.0472 | 9.2011
[7 empty] | 236 | 68 | 12.2894 | 9.391
[7 empty] | 237 | 69 | 11.78 | 8.9916
[7 empty] | 238 | 70 | 9.4918 | 7.1975
[7 empty] | 239 | 71 | 4.9905 | 3.6681
[7 empty] | 240 | 72 | 3.9097 | 2.8206
[7 empty] | 241 | 73 | 3.1951 | 2.2603
[7 empty] | 242 | 74 | 2.9696 | 2.0835
[7 empty] | 243 | 75 | 2.8694 | 2.0049
[7 empty] | 244 | 76 | 2.8109 | 1.9591
[7 empty] | 245 | 77 | 2.9863 | 2.0966
[7 empty] | 246 | 78 | 3.3871 | 2.4109
[7 empty] | 247 | 79 | 4.4978 | 3.2818
[7 empty] | 248 | 80 | 4.6732 | 3.4193
[7 empty] | 249 | 81 | 5.8507 | 4.3426
[7 empty] | 250 | 82 | 6.9363 | 5.1938
[7 empty] | 251 | 83 | 7.6712 | 5.77
[7 empty] | 252 | 84 | 8.9072 | 6.7391
[7 empty] | 253 | 85 | 8.6066 | 6.5034
[7 empty] | 254 | 86 | 8.0972 | 6.104
[7 empty] | 255 | 87 | 8.5398 | 6.451
[7 empty] | 256 | 88 | 9.1995 | 6.9683
[7 empty] | 257 | 89 | 10.544 | 8.0225
[7 empty] | 258 | 90 | 9.9595 | 7.5642
[7 empty] | 259 | 91 | 10.6442 | 8.1011
[7 empty] | 260 | 92 | 10.043 | 7.6296
[7 empty] | 261 | 93 | 7.6378 | 5.7438
[7 empty] | 262 | 94 | 6.7359 | 5.0366
[7 empty] | 263 | 95 | 4.882 | 3.583
[7 empty] | 264 | 96 | 3.8965 | 2.8103
[7 empty] | 265 | 97 | 3.8464 | 2.7711
[7 empty] | 266 | 98 | 3.5541 | 2.5419
[7 empty] | 267 | 99 | 3.4957 | 2.496
[7 empty] | 268 | 100 | 3.1449 | 2.221
[7 empty] | 269 | 101 | 3.0865 | 2.1752
[7 empty] | 270 | 102 | 3.3203 | 2.3585
[7 empty] | 271 | 103 | 4.0636 | 2.9413
[7 empty] | 272 | 104 | 4.3141 | 3.1377
[7 empty] | 273 | 105 | 4.7985 | 3.5175
[7 empty] | 274 | 106 | 6.2516 | 4.6569
[7 empty] | 275 | 107 | 6.6023 | 4.9319
[7 empty] | 276 | 108 | 8.1723 | 6.1629
[7 empty] | 277 | 109 | 7.5126 | 5.6456
[7 empty] | 278 | 110 | 7.0616 | 5.292
[7 empty] | 279 | 111 | 6.9029 | 5.1676
[7 empty] | 280 | 112 | 6.9698 | 5.22
[7 empty] | 281 | 113 | 6.6274 | 4.9515
[7 empty] | 282 | 114 | 6.7944 | 5.0825
[7 empty] | 283 | 115 | 6.3434 | 4.7289
[7 empty] | 284 | 116 | 7.0199 | 5.2593
[7 empty] | 285 | 117 | 6.6023 | 4.9319
[7 empty] | 286 | 118 | 5.834 | 4.3295
[7 empty] | 287 | 119 | 4.2473 | 3.0854
[7 empty] | 288 | 120 | 3.9311 | 2.8374
[7 empty] | 289 | 121 | 3.2034 | 2.2669
[7 empty] | 290 | 122 | 2.7942 | 1.946
[7 empty] | 291 | 123 | 2.7107 | 1.8805
[7 empty] | 292 | 124 | 2.6773 | 1.8543
[7 empty] | 293 | 125 | 2.6355 | 1.8216
[7 empty] | 294 | 126 | 2.7775 | 1.9329
[7 empty] | 295 | 127 | 4.2807 | 3.1115
[7 empty] | 296 | 128 | 5.834 | 4.3295
[7 empty] | 297 | 129 | 6.5104 | 4.8599
[7 empty] | 298 | 130 | 6.9447 | 5.2003
[7 empty] | 299 | 131 | 7.1034 | 5.3248
[7 empty] | 300 | 132 | 6.8528 | 5.1283
[7 empty] | 301 | 133 | 7.4875 | 5.626
[7 empty] | 302 | 134 | 7.7882 | 5.8617
[7 empty] | 303 | 135 | 7.855 | 5.9141
[7 empty] | 304 | 136 | 7.0449 | 5.2789
[7 empty] | 305 | 137 | 6.9447 | 5.2003
[7 empty] | 306 | 138 | 6.8946 | 5.1611
[7 empty] | 307 | 139 | 6.5605 | 4.8991
[7 empty] | 308 | 140 | 6.5689 | 4.9057
[7 empty] | 309 | 141 | 5.9175 | 4.3949
[7 empty] | 310 | 142 | 5.2828 | 3.8973
[7 empty] | 311 | 143 | 4.406 | 3.2098
[7 empty] | 312 | 144 | 3.7963 | 2.7318
[7 empty] | 313 | 145 | 3.3287 | 2.3651
[7 empty] | 314 | 146 | 3.1199 | 2.2014
[7 empty] | 315 | 147 | 3.0531 | 2.149
[7 empty] | 316 | 148 | 3.0447 | 2.1424
[7 empty] | 317 | 149 | 3.0447 | 2.1424
[7 empty] | 318 | 150 | 3.0531 | 2.149
[7 empty] | 319 | 151 | 4.1304 | 2.9937
[7 empty] | 320 | 152 | 5.6503 | 4.1854
[7 empty] | 321 | 153 | 6.2599 | 4.6634
[7 empty] | 322 | 154 | 6.8194 | 5.1021
[7 empty] | 323 | 155 | 6.6691 | 4.9843
[7 empty] | 324 | 156 | 6.8361 | 5.1152
[7 empty] | 325 | 157 | 7.546 | 5.6718
[7 empty] | 326 | 158 | 7.8717 | 5.9272
[7 empty] | 327 | 159 | 8.1389 | 6.1367
[7 empty] | 328 | 160 | 8.0136 | 6.0385
[7 empty] | 329 | 161 | 8.7736 | 6.6343
[7 empty] | 330 | 162 | 8.2809 | 6.248
[7 empty] | 331 | 163 | 8.64 | 6.5296
[7 empty] | 332 | 164 | 7.2954 | 5.4754
[7 empty] | 333 | 165 | 10.4104 | 7.9177
[7 empty] | 334 | 166 | 8.3727 | 6.32
[7 empty] | 335 | 167 | 4.7818 | 3.5044
[7 empty] | 336 | 168 | 4.1387 | 3.0002
[7 empty] | 337 | 1 | 2.6856 | 1.8609
[7 empty] | 338 | 2 | 2.5771 | 1.7758
[7 empty] | 339 | 3 | 2.5687 | 1.7692
[7 empty] | 340 | 4 | 2.7023 | 1.874
[7 empty] | 341 | 5 | 2.719 | 1.8871
[7 empty] | 342 | 6 | 3.1449 | 2.221
[7 empty] | 343 | 7 | 3.8631 | 2.7841
[7 empty] | 344 | 8 | 4.5312 | 3.308
[7 empty] | 345 | 9 | 4.5062 | 3.2883
[7 empty] | 346 | 10 | 6.0177 | 4.4735
[7 empty] | 347 | 11 | 8.0888 | 6.0974
[7 empty] | 348 | 12 | 9.0492 | 6.8504
[7 empty] | 349 | 13 | 9.425 | 7.1451
[7 empty] | 350 | 14 | 9.2079 | 6.9748
[7 empty] | 351 | 15 | 9.116 | 6.9028
[7 empty] | 352 | 16 | 10.2935 | 7.8261
[7 empty] | 353 | 17 | 11.613 | 8.8607
[7 empty] | 354 | 18 | 11.3708 | 8.6708
[7 empty] | 355 | 19 | 11.8969 | 9.0833
[7 empty] | 356 | 20 | 11.8301 | 9.0309
[7 empty] | 357 | 21 | 12.398 | 9.4762
[7 empty] | 358 | 22 | 8.4563 | 6.3855
[7 empty] | 359 | 23 | 4.6983 | 3.4389
[7 empty] | 360 | 24 | 3.0331 | 2.1333
[7 empty] | 361 | 25 | 2.9362 | 2.0573
[7 empty] | 362 | 26 | 2.8276 | 1.9722
[7 empty] | 363 | 27 | 2.7274 | 1.8936
[7 empty] | 364 | 28 | 2.8109 | 1.9591
[7 empty] | 365 | 29 | 3.0531 | 2.149
[7 empty] | 366 | 30 | 3.2953 | 2.3389
[7 empty] | 367 | 31 | 4.1387 | 3.0002
[7 empty] | 368 | 32 | 4.4895 | 3.2752
[7 empty] | 369 | 33 | 5.1492 | 3.7925
[7 empty] | 370 | 34 | 6.0428 | 4.4932
[7 empty] | 371 | 35 | 8.2057 | 6.1891
[7 empty] | 372 | 36 | 9.2329 | 6.9945
[7 empty] | 373 | 37 | 9.3081 | 7.0534
[7 empty] | 374 | 38 | 9.3832 | 7.1123
[7 empty] | 375 | 39 | 9.0575 | 6.857
[7 empty] | 376 | 40 | 10.1098 | 7.682
[7 empty] | 377 | 41 | 10.6609 | 8.1142
[7 empty] | 378 | 42 | 10.6776 | 8.1273
[7 empty] | 379 | 43 | 11.0451 | 8.4154
[7 empty] | 380 | 44 | 12.1975 | 9.319
[7 empty] | 381 | 45 | 11.7967 | 9.0047
[7 empty] | 382 | 46 | 9.0575 | 6.857
[7 empty] | 383 | 47 | 5.4666 | 4.0414
[7 empty] | 384 | 48 | 3.9717 | 2.8693
[7 empty] | 385 | 49 | 3.312 | 2.352
[7 empty] | 386 | 50 | 3.003 | 2.1097
[7 empty] | 387 | 51 | 2.8944 | 2.0246
[7 empty] | 388 | 52 | 2.9278 | 2.0508
[7 empty] | 389 | 53 | 2.9529 | 2.0704
[7 empty] | 390 | 54 | 3.5291 | 2.5222
[7 empty] | 391 | 55 | 4.6648 | 3.4128
[7 empty] | 392 | 56 | 4.907 | 3.6026
[7 empty] | 393 | 57 | 5.8507 | 4.3426
[7 empty] | 394 | 58 | 6.9531 | 5.2069
[7 empty] | 395 | 59 | 8.1556 | 6.1498
[7 empty] | 396 | 60 | 8.7819 | 6.6409
[7 empty] | 397 | 61 | 9.4584 | 7.1713
[7 empty] | 398 | 62 | 9.258 | 7.0141
[7 empty] | 399 | 63 | 9.8509 | 7.479
[7 empty] | 400 | 64 | 10.7946 | 8.219
[7 empty] | 401 | 65 | 11.4125 | 8.7035
[7 empty] | 402 | 66 | 11.3123 | 8.6249
[7 empty] | 403 | 67 | 12.0472 | 9.2011
[7 empty] | 404 | 68 | 12.2894 | 9.391
[7 empty] | 405 | 69 | 11.78 | 8.9916
[7 empty] | 406 | 70 | 9.4918 | 7.1975
[7 empty] | 407 | 71 | 4.9905 | 3.6681
[7 empty] | 408 | 72 | 3.9097 | 2.8206
[7 empty] | 409 | 73 | 3.1951 | 2.2603
[7 empty] | 410 | 74 | 2.9696 | 2.0835
[7 empty] | 411 | 75 | 2.8694 | 2.0049
[7 empty] | 412 | 76 | 2.8109 | 1.9591
[7 empty] | 413 | 77 | 2.9863 | 2.0966
[7 empty] | 414 | 78 | 3.3871 | 2.4109
[7 empty] | 415 | 79 | 4.4978 | 3.2818
[7 empty] | 416 | 80 | 4.6732 | 3.4193
[7 empty] | 417 | 81 | 5.8507 | 4.3426
[7 empty] | 418 | 82 | 6.9363 | 5.1938
[7 empty] | 419 | 83 | 7.6712 | 5.77
[7 empty] | 420 | 84 | 8.9072 | 6.7391
[7 empty] | 421 | 85 | 8.6066 | 6.5034
[7 empty] | 422 | 86 | 8.0972 | 6.104
[7 empty] | 423 | 87 | 8.5398 | 6.451
[7 empty] | 424 | 88 | 9.1995 | 6.9683
[7 empty] | 425 | 89 | 10.544 | 8.0225
[7 empty] | 426 | 90 | 9.9595 | 7.5642
[7 empty] | 427 | 91 | 10.6442 | 8.1011
[7 empty] | 428 | 92 | 10.043 | 7.6296
[7 empty] | 429 | 93 | 7.6378 | 5.7438
[7 empty] | 430 | 94 | 6.7359 | 5.0366
[7 empty] | 431 | 95 | 4.882 | 3.583
[7 empty] | 432 | 96 | 3.8965 | 2.8103
[7 empty] | 433 | 97 | 3.8464 | 2.7711
[7 empty] | 434 | 98 | 3.5541 | 2.5419
[7 empty] | 435 | 99 | 3.4957 | 2.496
[7 empty] | 436 | 100 | 3.1449 | 2.221
[7 empty] | 437 | 101 | 3.0865 | 2.1752
[7 empty] | 438 | 102 | 3.3203 | 2.3585
[7 empty] | 439 | 103 | 4.0636 | 2.9413
[7 empty] | 440 | 104 | 4.3141 | 3.1377
[7 empty] | 441 | 105 | 4.7985 | 3.5175
[7 empty] | 442 | 106 | 6.2516 | 4.6569
[7 empty] | 443 | 107 | 6.6023 | 4.9319
[7 empty] | 444 | 108 | 8.1723 | 6.1629
[7 empty] | 445 | 109 | 7.5126 | 5.6456
[7 empty] | 446 | 110 | 7.0616 | 5.292
[7 empty] | 447 | 111 | 6.9029 | 5.1676
[7 empty] | 448 | 112 | 6.9698 | 5.22
[7 empty] | 449 | 113 | 6.6274 | 4.9515
[7 empty] | 450 | 114 | 6.7944 | 5.0825
[7 empty] | 451 | 115 | 6.3434 | 4.7289
[7 empty] | 452 | 116 | 7.0199 | 5.2593
[7 empty] | 453 | 117 | 6.6023 | 4.9319
[7 empty] | 454 | 118 | 5.834 | 4.3295
[7 empty] | 455 | 119 | 4.2473 | 3.0854
[7 empty] | 456 | 120 | 3.9311 | 2.8374
[7 empty] | 457 | 121 | 3.2034 | 2.2669
[7 empty] | 458 | 122 | 2.7942 | 1.946
[7 empty] | 459 | 123 | 2.7107 | 1.8805
[7 empty] | 460 | 124 | 2.6773 | 1.8543
[7 empty] | 461 | 125 | 2.6355 | 1.8216
[7 empty] | 462 | 126 | 2.7775 | 1.9329
[7 empty] | 463 | 127 | 4.2807 | 3.1115
[7 empty] | 464 | 128 | 5.834 | 4.3295
[7 empty] | 465 | 129 | 6.5104 | 4.8599
[7 empty] | 466 | 130 | 6.9447 | 5.2003
[7 empty] | 467 | 131 | 7.1034 | 5.3248
[7 empty] | 468 | 132 | 6.8528 | 5.1283
[7 empty] | 469 | 133 | 7.4875 | 5.626
[7 empty] | 470 | 134 | 7.7882 | 5.8617
[7 empty] | 471 | 135 | 7.855 | 5.9141
[7 empty] | 472 | 136 | 7.0449 | 5.2789
[7 empty] | 473 | 137 | 6.9447 | 5.2003
[7 empty] | 474 | 138 | 6.8946 | 5.1611
[7 empty] | 475 | 139 | 6.5605 | 4.8991
[7 empty] | 476 | 140 | 6.5689 | 4.9057
[7 empty] | 477 | 141 | 5.9175 | 4.3949
[7 empty] | 478 | 142 | 5.2828 | 3.8973
[7 empty] | 479 | 143 | 4.406 | 3.2098
[7 empty] | 480 | 144 | 3.7963 | 2.7318
[7 empty] | 481 | 145 | 3.3287 | 2.3651
[7 empty] | 482 | 146 | 3.1199 | 2.2014
[7 empty] | 483 | 147 | 3.0531 | 2.149
[7 empty] | 484 | 148 | 3.0447 | 2.1424
[7 empty] | 485 | 149 | 3.0447 | 2.1424
[7 empty] | 486 | 150 | 3.0531 | 2.149
[7 empty] | 487 | 151 | 4.1304 | 2.9937
[7 empty] | 488 | 152 | 5.6503 | 4.1854
[7 empty] | 489 | 153 | 6.2599 | 4.6634
[7 empty] | 490 | 154 | 6.8194 | 5.1021
[7 empty] | 491 | 155 | 6.6691 | 4.9843
[7 empty] | 492 | 156 | 6.8361 | 5.1152
[7 empty] | 493 | 157 | 7.546 | 5.6718
[7 empty] | 494 | 158 | 7.8717 | 5.9272
[7 empty] | 495 | 159 | 8.1389 | 6.1367
[7 empty] | 496 | 160 | 8.0136 | 6.0385
[7 empty] | 497 | 161 | 8.7736 | 6.6343
[7 empty] | 498 | 162 | 8.2809 | 6.248
[7 empty] | 499 | 163 | 8.64 | 6.5296
[7 empty] | 500 | 164 | 7.2954 | 5.4754
[7 empty] | 501 | 165 | 10.4104 | 7.9177
[7 empty] | 502 | 166 | 8.3727 | 6.32
[7 empty] | 503 | 167 | 4.7818 | 3.5044
[7 empty] | 504 | 168 | 4.1387 | 3.0002
[7 empty] | 505 | 1 | 2.6856 | 1.8609
[7 empty] | 506 | 2 | 2.5771 | 1.7758
[7 empty] | 507 | 3 | 2.5687 | 1.7692
[7 empty] | 508 | 4 | 2.7023 | 1.874
[7 empty] | 509 | 5 | 2.719 | 1.8871
[7 empty] | 510 | 6 | 3.1449 | 2.221
[7 empty] | 511 | 7 | 3.8631 | 2.7841
[7 empty] | 512 | 8 | 4.5312 | 3.308
[7 empty] | 513 | 9 | 4.5062 | 3.2883
[7 empty] | 514 | 10 | 6.0177 | 4.4735
[7 empty] | 515 | 11 | 8.0888 | 6.0974
[7 empty] | 516 | 12 | 9.0492 | 6.8504
[7 empty] | 517 | 13 | 9.425 | 7.1451
[7 empty] | 518 | 14 | 9.2079 | 6.9748
[7 empty] | 519 | 15 | 9.116 | 6.9028
[7 empty] | 520 | 16 | 10.2935 | 7.8261
[7 empty] | 521 | 17 | 11.613 | 8.8607
[7 empty] | 522 | 18 | 11.3708 | 8.6708
[7 empty] | 523 | 19 | 11.8969 | 9.0833
[7 empty] | 524 | 20 | 11.8301 | 9.0309
[7 empty] | 525 | 21 | 12.398 | 9.4762
[7 empty] | 526 | 22 | 8.4563 | 6.3855
[7 empty] | 527 | 23 | 4.6983 | 3.4389
[7 empty] | 528 | 24 | 3.0331 | 2.1333
[7 empty] | 529 | 25 | 2.9362 | 2.0573
[7 empty] | 530 | 26 | 2.8276 | 1.9722
[7 empty] | 531 | 27 | 2.7274 | 1.8936
[7 empty] | 532 | 28 | 2.8109 | 1.9591
[7 empty] | 533 | 29 | 3.0531 | 2.149
[7 empty] | 534 | 30 | 3.2953 | 2.3389
[7 empty] | 535 | 31 | 4.1387 | 3.0002
[7 empty] | 536 | 32 | 4.4895 | 3.2752
[7 empty] | 537 | 33 | 5.1492 | 3.7925
[7 empty] | 538 | 34 | 6.0428 | 4.4932
[7 empty] | 539 | 35 | 8.2057 | 6.1891
[7 empty] | 540 | 36 | 9.2329 | 6.9945
[7 empty] | 541 | 37 | 9.3081 | 7.0534
[7 empty] | 542 | 38 | 9.3832 | 7.1123
[7 empty] | 543 | 39 | 9.0575 | 6.857
[7 empty] | 544 | 40 | 10.1098 | 7.682
[7 empty] | 545 | 41 | 10.6609 | 8.1142
[7 empty] | 546 | 42 | 10.6776 | 8.1273
[7 empty] | 547 | 43 | 11.0451 | 8.4154
[7 empty] | 548 | 44 | 12.1975 | 9.319
[7 empty] | 549 | 45 | 11.7967 | 9.0047
[7 empty] | 550 | 46 | 9.0575 | 6.857
[7 empty] | 551 | 47 | 5.4666 | 4.0414
[7 empty] | 552 | 48 | 3.9717 | 2.8693
[7 empty] | 553 | 49 | 3.312 | 2.352
[7 empty] | 554 | 50 | 3.003 | 2.1097
[7 empty] | 555 | 51 | 2.8944 | 2.0246
[7 empty] | 556 | 52 | 2.9278 | 2.0508
[7 empty] | 557 | 53 | 2.9529 | 2.0704
[7 empty] | 558 | 54 | 3.5291 | 2.5222
[7 empty] | 559 | 55 | 4.6648 | 3.4128
[7 empty] | 560 | 56 | 4.907 | 3.6026
[7 empty] | 561 | 57 | 5.8507 | 4.3426
[7 empty] | 562 | 58 | 6.9531 | 5.2069
[7 empty] | 563 | 59 | 8.1556 | 6.1498
[7 empty] | 564 | 60 | 8.7819 | 6.6409
[7 empty] | 565 | 61 | 9.4584 | 7.1713
[7 empty] | 566 | 62 | 9.258 | 7.0141
[7 empty] | 567 | 63 | 9.8509 | 7.479
[7 empty] | 568 | 64 | 10.7946 | 8.219
[7 empty] | 569 | 65 | 11.4125 | 8.7035
[7 empty] | 570 | 66 | 11.3123 | 8.6249
[7 empty] | 571 | 67 | 12.0472 | 9.2011
[7 empty] | 572 | 68 | 12.2894 | 9.391
[7 empty] | 573 | 69 | 11.78 | 8.9916
[7 empty] | 574 | 70 | 9.4918 | 7.1975
[7 empty] | 575 | 71 | 4.9905 | 3.6681
[7 empty] | 576 | 72 | 3.9097 | 2.8206
[7 empty] | 577 | 73 | 3.1951 | 2.2603
[7 empty] | 578 | 74 | 2.9696 | 2.0835
[7 empty] | 579 | 75 | 2.8694 | 2.0049
[7 empty] | 580 | 76 | 2.8109 | 1.9591
[7 empty] | 581 | 77 | 2.9863 | 2.0966
[7 empty] | 582 | 78 | 3.3871 | 2.4109
[7 empty] | 583 | 79 | 4.4978 | 3.2818
[7 empty] | 584 | 80 | 4.6732 | 3.4193
[7 empty] | 585 | 81 | 5.8507 | 4.3426
[7 empty] | 586 | 82 | 6.9363 | 5.1938
[7 empty] | 587 | 83 | 7.6712 | 5.77
[7 empty] | 588 | 84 | 8.9072 | 6.7391
[7 empty] | 589 | 85 | 8.6066 | 6.5034
[7 empty] | 590 | 86 | 8.0972 | 6.104
[7 empty] | 591 | 87 | 8.5398 | 6.451
[7 empty] | 592 | 88 | 9.1995 | 6.9683
[7 empty] | 593 | 89 | 10.544 | 8.0225
[7 empty] | 594 | 90 | 9.9595 | 7.5642
[7 empty] | 595 | 91 | 10.6442 | 8.1011
[7 empty] | 596 | 92 | 10.043 | 7.6296
[7 empty] | 597 | 93 | 7.6378 | 5.7438
[7 empty] | 598 | 94 | 6.7359 | 5.0366
[7 empty] | 599 | 95 | 4.882 | 3.583
[7 empty] | 600 | 96 | 3.8965 | 2.8103
[7 empty] | 601 | 97 | 3.8464 | 2.7711
[7 empty] | 602 | 98 | 3.5541 | 2.5419
[7 empty] | 603 | 99 | 3.4957 | 2.496
[7 empty] | 604 | 100 | 3.1449 | 2.221
[7 empty] | 605 | 101 | 3.0865 | 2.1752
[7 empty] | 606 | 102 | 3.3203 | 2.3585
[7 empty] | 607 | 103 | 4.0636 | 2.9413
[7 empty] | 608 | 104 | 4.3141 | 3.1377
[7 empty] | 609 | 105 | 4.7985 | 3.5175
[7 empty] | 610 | 106 | 6.2516 | 4.6569
[7 empty] | 611 | 107 | 6.6023 | 4.9319
[7 empty] | 612 | 108 | 8.1723 | 6.1629
[7 empty] | 613 | 109 | 7.5126 | 5.6456
[7 empty] | 614 | 110 | 7.0616 | 5.292
[7 empty] | 615 | 111 | 6.9029 | 5.1676
[7 empty] | 616 | 112 | 6.9698 | 5.22
[7 empty] | 617 | 113 | 6.6274 | 4.9515
[7 empty] | 618 | 114 | 6.7944 | 5.0825
[7 empty] | 619 | 115 | 6.3434 | 4.7289
[7 empty] | 620 | 116 | 7.0199 | 5.2593
[7 empty] | 621 | 117 | 6.6023 | 4.9319
[7 empty] | 622 | 118 | 5.834 | 4.3295
[7 empty] | 623 | 119 | 4.2473 | 3.0854
[7 empty] | 624 | 120 | 3.9311 | 2.8374
[7 empty] | 625 | 121 | 3.2034 | 2.2669
[7 empty] | 626 | 122 | 2.7942 | 1.946
[7 empty] | 627 | 123 | 2.7107 | 1.8805
[7 empty] | 628 | 124 | 2.6773 | 1.8543
[7 empty] | 629 | 125 | 2.6355 | 1.8216
[7 empty] | 630 | 126 | 2.7775 | 1.9329
[7 empty] | 631 | 127 | 4.2807 | 3.1115
[7 empty] | 632 | 128 | 5.834 | 4.3295
[7 empty] | 633 | 129 | 6.5104 | 4.8599
[7 empty] | 634 | 130 | 6.9447 | 5.2003
[7 empty] | 635 | 131 | 7.1034 | 5.3248
[7 empty] | 636 | 132 | 6.8528 | 5.1283
[7 empty] | 637 | 133 | 7.4875 | 5.626
[7 empty] | 638 | 134 | 7.7882 | 5.8617
[7 empty] | 639 | 135 | 7.855 | 5.9141
[7 empty] | 640 | 136 | 7.0449 | 5.2789
[7 empty] | 641 | 137 | 6.9447 | 5.2003
[7 empty] | 642 | 138 | 6.8946 | 5.1611
[7 empty] | 643 | 139 | 6.5605 | 4.8991
[7 empty] | 644 | 140 | 6.5689 | 4.9057
[7 empty] | 645 | 141 | 5.9175 | 4.3949
[7 empty] | 646 | 142 | 5.2828 | 3.8973
[7 empty] | 647 | 143 | 4.406 | 3.2098
[7 empty] | 648 | 144 | 3.7963 | 2.7318
[7 empty] | 649 | 145 | 3.3287 | 2.3651
[7 empty] | 650 | 146 | 3.1199 | 2.2014
[7 empty] | 651 | 147 | 3.0531 | 2.149
[7 empty] | 652 | 148 | 3.0447 | 2.1424
[7 empty] | 653 | 149 | 3.0447 | 2.1424
[7 empty] | 654 | 150 | 3.0531 | 2.149
[7 empty] | 655 | 151 | 4.1304 | 2.9937
[7 empty] | 656 | 152 | 5.6503 | 4.1854
[7 empty] | 657 | 153 | 6.2599 | 4.6634
[7 empty] | 658 | 154 | 6.8194 | 5.1021
[7 empty] | 659 | 155 | 6.6691 | 4.9843
[7 empty] | 660 | 156 | 6.8361 | 5.1152
[7 empty] | 661 | 157 | 7.546 | 5.6718
[7 empty] | 662 | 158 | 7.8717 | 5.9272
[7 empty] | 663 | 159 | 8.1389 | 6.1367
[7 empty] | 664 | 160 | 8.0136 | 6.0385
[7 empty] | 665 | 161 | 8.7736 | 6.6343
[7 empty] | 666 | 162 | 8.2809 | 6.248
[7 empty] | 667 | 163 | 8.64 | 6.5296
[7 empty] | 668 | 164 | 7.2954 | 5.4754
[7 empty] | 669 | 165 | 10.4104 | 7.9177
[7 empty] | 670 | 166 | 8.3727 | 6.32
[7 empty] | 671 | 167 | 4.7818 | 3.5044
[7 empty] | 672 | 168 | 4.1387 | 3.0002
[7 empty] | 673 | 1 | 2.6856 | 1.8609
[7 empty] | 674 | 2 | 2.5771 | 1.7758
[7 empty] | 675 | 3 | 2.5687 | 1.7692
[7 empty] | 676 | 4 | 2.7023 | 1.874
[7 empty] | 677 | 5 | 2.719 | 1.8871
[7 empty] | 678 | 6 | 3.1449 | 2.221
[7 empty] | 679 | 7 | 3.8631 | 2.7841
[7 empty] | 680 | 8 | 4.5312 | 3.308
[7 empty] | 681 | 9 | 4.5062 | 3.2883
[7 empty] | 682 | 10 | 6.0177 | 4.4735
[7 empty] | 683 | 11 | 8.0888 | 6.0974
[7 empty] | 684 | 12 | 9.0492 | 6.8504
[7 empty] | 685 | 13 | 9.425 | 7.1451
[7 empty] | 686 | 14 | 9.2079 | 6.9748
[7 empty] | 687 | 15 | 9.116 | 6.9028
[7 empty] | 688 | 16 | 10.2935 | 7.8261
[7 empty] | 689 | 17 | 11.613 | 8.8607
[7 empty] | 690 | 18 | 11.3708 | 8.6708
[7 empty] | 691 | 19 | 11.8969 | 9.0833
[7 empty] | 692 | 20 | 11.8301 | 9.0309
[7 empty] | 693 | 21 | 12.398 | 9.4762
[7 empty] | 694 | 22 | 8.4563 | 6.3855
[7 empty] | 695 | 23 | 4.6983 | 3.4389
[7 empty] | 696 | 24 | 3.0331 | 2.1333
[7 empty] | 697 | 25 | 2.9362 | 2.0573
[7 empty] | 698 | 26 | 2.8276 | 1.9722
[7 empty] | 699 | 27 | 2.7274 | 1.8936
[7 empty] | 700 | 28 | 2.8109 | 1.9591
[7 empty] | 701 | 29 | 3.0531 | 2.149
[7 empty] | 702 | 30 | 3.2953 | 2.3389
[7 empty] | 703 | 31 | 4.1387 | 3.0002
[7 empty] | 704 | 32 | 4.4895 | 3.2752
[7 empty] | 705 | 33 | 5.1492 | 3.7925
[7 empty] | 706 | 34 | 6.0428 | 4.4932
[7 empty] | 707 | 35 | 8.2057 | 6.1891
[7 empty] | 708 | 36 | 9.2329 | 6.9945
[7 empty] | 709 | 37 | 9.3081 | 7.0534
[7 empty] | 710 | 38 | 9.3832 | 7.1123
[7 empty] | 711 | 39 | 9.0575 | 6.857
[7 empty] | 712 | 40 | 10.1098 | 7.682
[7 empty] | 713 | 41 | 10.6609 | 8.1142
[7 empty] | 714 | 42 | 10.6776 | 8.1273
[7 empty] | 715 | 43 | 11.0451 | 8.4154
[7 empty] | 716 | 44 | 12.1975 | 9.319
[7 empty] | 717 | 45 | 11.7967 | 9.0047
[7 empty] | 718 | 46 | 9.0575 | 6.857
[7 empty] | 719 | 47 | 5.4666 | 4.0414
[7 empty] | 720 | 48 | 3.9717 | 2.8693
[7 empty] | 721 | 49 | 3.312 | 2.352
[7 empty] | 722 | 50 | 3.003 | 2.1097
[7 empty] | 723 | 51 | 2.8944 | 2.0246
[7 empty] | 724 | 52 | 2.9278 | 2.0508
[7 empty] | 725 | 53 | 2.9529 | 2.0704
[7 empty] | 726 | 54 | 3.5291 | 2.5222
[7 empty] | 727 | 55 | 4.6648 | 3.4128
[7 empty] | 728 | 56 | 4.907 | 3.6026
[7 empty] | 729 | 57 | 5.8507 | 4.3426
[7 empty] | 730 | 58 | 6.9531 | 5.2069
[7 empty] | 731 | 59 | 8.1556 | 6.1498
[7 empty] | 732 | 60 | 8.7819 | 6.6409
[7 empty] | 733 | 61 | 9.4584 | 7.1713
[7 empty] | 734 | 62 | 9.258 | 7.0141
[7 empty] | 735 | 63 | 9.8509 | 7.479
[7 empty] | 736 | 64 | 10.7946 | 8.219
[7 empty] | 737 | 65 | 11.4125 | 8.7035
[7 empty] | 738 | 66 | 11.3123 | 8.6249
[7 empty] | 739 | 67 | 12.0472 | 9.2011
[7 empty] | 740 | 68 | 12.2894 | 9.391
[7 empty] | 741 | 69 | 11.78 | 8.9916
[7 empty] | 742 | 70 | 9.4918 | 7.1975
[7 empty] | 743 | 71 | 4.9905 | 3.6681
[7 empty] | 744 | 72 | 3.9097 | 2.8206
[7 empty] | 745 | 73 | 3.1951 | 2.2603
[7 empty] | 746 | 74 | 2.9696 | 2.0835
[7 empty] | 747 | 75 | 2.8694 | 2.0049
[7 empty] | 748 | 76 | 2.8109 | 1.9591
[7 empty] | 749 | 77 | 2.9863 | 2.0966
[7 empty] | 750 | 78 | 3.3871 | 2.4109
[7 empty] | 751 | 79 | 4.4978 | 3.2818
[7 empty] | 752 | 80 | 4.6732 | 3.4193
[7 empty] | 753 | 81 | 5.8507 | 4.3426
[7 empty] | 754 | 82 | 6.9363 | 5.1938
[7 empty] | 755 | 83 | 7.6712 | 5.77
[7 empty] | 756 | 84 | 8.9072 | 6.7391
[7 empty] | 757 | 85 | 8.6066 | 6.5034
[7 empty] | 758 | 86 | 8.0972 | 6.104
[7 empty] | 759 | 87 | 8.5398 | 6.451
[7 empty] | 760 | 88 | 9.1995 | 6.9683
[7 empty] | 761 | 89 | 10.544 | 8.0225
[7 empty] | 762 | 90 | 9.9595 | 7.5642
[7 empty] | 763 | 91 | 10.6442 | 8.1011
[7 empty] | 764 | 92 | 10.043 | 7.6296
[7 empty] | 765 | 93 | 7.6378 | 5.7438
[7 empty] | 766 | 94 | 6.7359 | 5.0366
[7 empty] | 767 | 95 | 4.882 | 3.583
[7 empty] | 768 | 96 | 3.8965 | 2.8103
[7 empty] | 769 | 97 | 3.8464 | 2.7711
[7 empty] | 770 | 98 | 3.5541 | 2.5419
[7 empty] | 771 | 99 | 3.4957 | 2.496
[7 empty] | 772 | 100 | 3.1449 | 2.221
[7 empty] | 773 | 101 | 3.0865 | 2.1752
[7 empty] | 774 | 102 | 3.3203 | 2.3585
[7 empty] | 775 | 103 | 4.0636 | 2.9413
[7 empty] | 776 | 104 | 4.3141 | 3.1377
[7 empty] | 777 | 105 | 4.7985 | 3.5175
[7 empty] | 778 | 106 | 6.2516 | 4.6569
[7 empty] | 779 | 107 | 6.6023 | 4.9319
[7 empty] | 780 | 108 | 8.1723 | 6.1629
[7 empty] | 781 | 109 | 7.5126 | 5.6456
[7 empty] | 782 | 110 | 7.0616 | 5.292
[7 empty] | 783 | 111 | 6.9029 | 5.1676
[7 empty] | 784 | 112 | 6.9698 | 5.22
[7 empty] | 785 | 113 | 6.6274 | 4.9515
[7 empty] | 786 | 114 | 6.7944 | 5.0825
[7 empty] | 787 | 115 | 6.3434 | 4.7289
[7 empty] | 788 | 116 | 7.0199 | 5.2593
[7 empty] | 789 | 117 | 6.6023 | 4.9319
[7 empty] | 790 | 118 | 5.834 | 4.3295
[7 empty] | 791 | 119 | 4.2473 | 3.0854
[7 empty] | 792 | 120 | 3.9311 | 2.8374
[7 empty] | 793 | 121 | 3.2034 | 2.2669
[7 empty] | 794 | 122 | 2.7942 | 1.946
[7 empty] | 795 | 123 | 2.7107 | 1.8805
[7 empty] | 796 | 124 | 2.6773 | 1.8543
[7 empty] | 797 | 125 | 2.6355 | 1.8216
[7 empty] | 798 | 126 | 2.7775 | 1.9329
[7 empty] | 799 | 127 | 4.2807 | 3.1115
[7 empty] | 800 | 128 | 5.834 | 4.3295
[7 empty] | 801 | 129 | 6.5104 | 4.8599
[7 empty] | 802 | 130 | 6.9447 | 5.2003
[7 empty] | 803 | 131 | 7.1034 | 5.3248
[7 empty] | 804 | 132 | 6.8528 | 5.1283
[7 empty] | 805 | 133 | 7.4875 | 5.626
[7 empty] | 806 | 134 | 7.7882 | 5.8617
[7 empty] | 807 | 135 | 7.855 | 5.9141
[7 empty] | 808 | 136 | 7.0449 | 5.2789
[7 empty] | 809 | 137 | 6.9447 | 5.2003
[7 empty] | 810 | 138 | 6.8946 | 5.1611
[7 empty] | 811 | 139 | 6.5605 | 4.8991
[7 empty] | 812 | 140 | 6.5689 | 4.9057
[7 empty] | 813 | 141 | 5.9175 | 4.3949
[7 empty] | 814 | 142 | 5.2828 | 3.8973
[7 empty] | 815 | 143 | 4.406 | 3.2098
[7 empty] | 816 | 144 | 3.7963 | 2.7318
[7 empty] | 817 | 145 | 3.3287 | 2.3651
[7 empty] | 818 | 146 | 3.1199 | 2.2014
[7 empty] | 819 | 147 | 3.0531 | 2.149
[7 empty] | 820 | 148 | 3.0447 | 2.1424
[7 empty] | 821 | 149 | 3.0447 | 2.1424
[7 empty] | 822 | 150 | 3.0531 | 2.149
[7 empty] | 823 | 151 | 4.1304 | 2.9937
[7 empty] | 824 | 152 | 5.6503 | 4.1854
[7 empty] | 825 | 153 | 6.2599 | 4.6634
[7 empty] | 826 | 154 | 6.8194 | 5.1021
[7 empty] | 827 | 155 | 6.6691 | 4.9843
[7 empty] | 828 | 156 | 6.8361 | 5.1152
[7 empty] | 829 | 157 | 7.546 | 5.6718
[7 empty] | 830 | 158 | 7.8717 | 5.9272
[7 empty] | 831 | 159 | 8.1389 | 6.1367
[7 empty] | 832 | 160 | 8.0136 | 6.0385
[7 empty] | 833 | 161 | 8.7736 | 6.6343
[7 empty] | 834 | 162 | 8.2809 | 6.248
[7 empty] | 835 | 163 | 8.64 | 6.5296
[7 empty] | 836 | 164 | 7.2954 | 5.4754
[7 empty] | 837 | 165 | 10.4104 | 7.9177
[7 empty] | 838 | 166 | 8.3727 | 6.32
[7 empty] | 839 | 167 | 4.7818 | 3.5044
[7 empty] | 840 | 168 | 4.1387 | 3.0002
[7 empty] | 841 | 1 | 2.6856 | 1.8609
[7 empty] | 842 | 2 | 2.5771 | 1.7758
[7 empty] | 843 | 3 | 2.5687 | 1.7692
[7 empty] | 844 | 4 | 2.7023 | 1.874
[7 empty] | 845 | 5 | 2.719 | 1.8871
[7 empty] | 846 | 6 | 3.1449 | 2.221
[7 empty] | 847 | 7 | 3.8631 | 2.7841
[7 empty] | 848 | 8 | 4.5312 | 3.308
[7 empty] | 849 | 9 | 4.5062 | 3.2883
[7 empty] | 850 | 10 | 6.0177 | 4.4735
[7 empty] | 851 | 11 | 8.0888 | 6.0974
[7 empty] | 852 | 12 | 9.0492 | 6.8504
[7 empty] | 853 | 13 | 9.425 | 7.1451
[7 empty] | 854 | 14 | 9.2079 | 6.9748
[7 empty] | 855 | 15 | 9.116 | 6.9028
[7 empty] | 856 | 16 | 10.2935 | 7.8261
[7 empty] | 857 | 17 | 11.613 | 8.8607
[7 empty] | 858 | 18 | 11.3708 | 8.6708
[7 empty] | 859 | 19 | 11.8969 | 9.0833
[7 empty] | 860 | 20 | 11.8301 | 9.0309
[7 empty] | 861 | 21 | 12.398 | 9.4762
[7 empty] | 862 | 22 | 8.4563 | 6.3855
[7 empty] | 863 | 23 | 4.6983 | 3.4389
[7 empty] | 864 | 24 | 3.0331 | 2.1333
[7 empty] | 865 | 25 | 2.9362 | 2.0573
[7 empty] | 866 | 26 | 2.8276 | 1.9722
[7 empty] | 867 | 27 | 2.7274 | 1.8936
[7 empty] | 868 | 28 | 2.8109 | 1.9591
[7 empty] | 869 | 29 | 3.0531 | 2.149
[7 empty] | 870 | 30 | 3.2953 | 2.3389
[7 empty] | 871 | 31 | 4.1387 | 3.0002
[7 empty] | 872 | 32 | 4.4895 | 3.2752
[7 empty] | 873 | 33 | 5.1492 | 3.7925
[7 empty] | 874 | 34 | 6.0428 | 4.4932
[7 empty] | 875 | 35 | 8.2057 | 6.1891
[7 empty] | 876 | 36 | 9.2329 | 6.9945
[7 empty] | 877 | 37 | 9.3081 | 7.0534
[7 empty] | 878 | 38 | 9.3832 | 7.1123
[7 empty] | 879 | 39 | 9.0575 | 6.857
[7 empty] | 880 | 40 | 10.1098 | 7.682
[7 empty] | 881 | 41 | 10.6609 | 8.1142
[7 empty] | 882 | 42 | 10.6776 | 8.1273
[7 empty] | 883 | 43 | 11.0451 | 8.4154
[7 empty] | 884 | 44 | 12.1975 | 9.319
[7 empty] | 885 | 45 | 11.7967 | 9.0047
[7 empty] | 886 | 46 | 9.0575 | 6.857
[7 empty] | 887 | 47 | 5.4666 | 4.0414
[7 empty] | 888 | 48 | 3.9717 | 2.8693
[7 empty] | 889 | 49 | 3.312 | 2.352
[7 empty] | 890 | 50 | 3.003 | 2.1097
[7 empty] | 891 | 51 | 2.8944 | 2.0246
[7 empty] | 892 | 52 | 2.9278 | 2.0508
[7 empty] | 893 | 53 | 2.9529 | 2.0704
[7 empty] | 894 | 54 | 3.5291 | 2.5222
[7 empty] | 895 | 55 | 4.6648 | 3.4128
[7 empty] | 896 | 56 | 4.907 | 3.6026
[7 empty] | 897 | 57 | 5.8507 | 4.3426
[7 empty] | 898 | 58 | 6.9531 | 5.2069
[7 empty] | 899 | 59 | 8.1556 | 6.1498
[7 empty] | 900 | 60 | 8.7819 | 6.6409
[7 empty] | 901 | 61 | 9.4584 | 7.1713
[7 empty] | 902 | 62 | 9.258 | 7.0141
[7 empty] | 903 | 63 | 9.8509 | 7.479
[7 empty] | 904 | 64 | 10.7946 | 8.219
[7 empty] | 905 | 65 | 11.4125 | 8.7035
[7 empty] | 906 | 66 | 11.3123 | 8.6249
[7 empty] | 907 | 67 | 12.0472 | 9.2011
[7 empty] | 908 | 68 | 12.2894 | 9.391
[7 empty] | 909 | 69 | 11.78 | 8.9916
[7 empty] | 910 | 70 | 9.4918 | 7.1975
[7 empty] | 911 | 71 | 4.9905 | 3.6681
[7 empty] | 912 | 72 | 3.9097 | 2.8206
[7 empty] | 913 | 73 | 3.1951 | 2.2603
[7 empty] | 914 | 74 | 2.9696 | 2.0835
[7 empty] | 915 | 75 | 2.8694 | 2.0049
[7 empty] | 916 | 76 | 2.8109 | 1.9591
[7 empty] | 917 | 77 | 2.9863 | 2.0966
[7 empty] | 918 | 78 | 3.3871 | 2.4109
[7 empty] | 919 | 79 | 4.4978 | 3.2818
[7 empty] | 920 | 80 | 4.6732 | 3.4193
[7 empty] | 921 | 81 | 5.8507 | 4.3426
[7 empty] | 922 | 82 | 6.9363 | 5.1938
[7 empty] | 923 | 83 | 7.6712 | 5.77
[7 empty] | 924 | 84 | 8.9072 | 6.7391
[7 empty] | 925 | 85 | 8.6066 | 6.5034
[7 empty] | 926 | 86 | 8.0972 | 6.104
[7 empty] | 927 | 87 | 8.5398 | 6.451
[7 empty] | 928 | 88 | 9.1995 | 6.9683
[7 empty] | 929 | 89 | 10.544 | 8.0225
[7 empty] | 930 | 90 | 9.9595 | 7.5642
[7 empty] | 931 | 91 | 10.6442 | 8.1011
[7 empty] | 932 | 92 | 10.043 | 7.6296
[7 empty] | 933 | 93 | 7.6378 | 5.7438
[7 empty] | 934 | 94 | 6.7359 | 5.0366
[7 empty] | 935 | 95 | 4.882 | 3.583
[7 empty] | 936 | 96 | 3.8965 | 2.8103
[7 empty] | 937 | 97 | 3.8464 | 2.7711
[7 empty] | 938 | 98 | 3.5541 | 2.5419
[7 empty] | 939 | 99 | 3.4957 | 2.496
[7 empty] | 940 | 100 | 3.1449 | 2.221
[7 empty] | 941 | 101 | 3.0865 | 2.1752
[7 empty] | 942 | 102 | 3.3203 | 2.3585
[7 empty] | 943 | 103 | 4.0636 | 2.9413
[7 empty] | 944 | 104 | 4.3141 | 3.1377
[7 empty] | 945 | 105 | 4.7985 | 3.5175
[7 empty] | 946 | 106 | 6.2516 | 4.6569
[7 empty] | 947 | 107 | 6.6023 | 4.9319
[7 empty] | 948 | 108 | 8.1723 | 6.1629
[7 empty] | 949 | 109 | 7.5126 | 5.6456
[7 empty] | 950 | 110 | 7.0616 | 5.292
[7 empty] | 951 | 111 | 6.9029 | 5.1676
[7 empty] | 952 | 112 | 6.9698 | 5.22
[7 empty] | 953 | 113 | 6.6274 | 4.9515
[7 empty] | 954 | 114 | 6.7944 | 5.0825
[7 empty] | 955 | 115 | 6.3434 | 4.7289
[7 empty] | 956 | 116 | 7.0199 | 5.2593
[7 empty] | 957 | 117 | 6.6023 | 4.9319
[7 empty] | 958 | 118 | 5.834 | 4.3295
[7 empty] | 959 | 119 | 4.2473 | 3.0854
[7 empty] | 960 | 120 | 3.9311 | 2.8374
[7 empty] | 961 | 121 | 3.2034 | 2.2669
[7 empty] | 962 | 122 | 2.7942 | 1.946
[7 empty] | 963 | 123 | 2.7107 | 1.8805
[7 empty] | 964 | 124 | 2.6773 | 1.8543
[7 empty] | 965 | 125 | 2.6355 | 1.8216
[7 empty] | 966 | 126 | 2.7775 | 1.9329
[7 empty] | 967 | 127 | 4.2807 | 3.1115
[7 empty] | 968 | 128 | 5.834 | 4.3295
[7 empty] | 969 | 129 | 6.5104 | 4.8599
[7 empty] | 970 | 130 | 6.9447 | 5.2003
[7 empty] | 971 | 131 | 7.1034 | 5.3248
[7 empty] | 972 | 132 | 6.8528 | 5.1283
[7 empty] | 973 | 133 | 7.4875 | 5.626
[7 empty] | 974 | 134 | 7.7882 | 5.8617
[7 empty] | 975 | 135 | 7.855 | 5.9141
[7 empty] | 976 | 136 | 7.0449 | 5.2789
[7 empty] | 977 | 137 | 6.9447 | 5.2003
[7 empty] | 978 | 138 | 6.8946 | 5.1611
[7 empty] | 979 | 139 | 6.5605 | 4.8991
[7 empty] | 980 | 140 | 6.5689 | 4.9057
[7 empty] | 981 | 141 | 5.9175 | 4.3949
[7 empty] | 982 | 142 | 5.2828 | 3.8973
[7 empty] | 983 | 143 | 4.406 | 3.2098
[7 empty] | 984 | 144 | 3.7963 | 2.7318
[7 empty] | 985 | 145 | 3.3287 | 2.3651
[7 empty] | 986 | 146 | 3.1199 | 2.2014
[7 empty] | 987 | 147 | 3.0531 | 2.149
[7 empty] | 988 | 148 | 3.0447 | 2.1424
[7 empty] | 989 | 149 | 3.0447 | 2.1424
[7 empty] | 990 | 150 | 3.0531 | 2.149
[7 empty] | 991 | 151 | 4.1304 | 2.9937
[7 empty] | 992 | 152 | 5.6503 | 4.1854
[7 empty] | 993 | 153 | 6.2599 | 4.6634
[7 empty] | 994 | 154 | 6.8194 | 5.1021
[7 empty] | 995 | 155 | 6.6691 | 4.9843
[7 empty] | 996 | 156 | 6.8361 | 5.1152
[7 empty] | 997 | 157 | 7.546 | 5.6718
[7 empty] | 998 | 158 | 7.8717 | 5.9272
[7 empty] | 999 | 159 | 8.1389 | 6.1367
[7 empty] | 1000 | 160 | 8.0136 | 6.0385
[7 empty] | 1001 | 161 | 8.7736 | 6.6343
[7 empty] | 1002 | 162 | 8.2809 | 6.248
[7 empty] | 1003 | 163 | 8.64 | 6.5296
[7 empty] | 1004 | 164 | 7.2954 | 5.4754
[7 empty] | 1005 | 165 | 10.4104 | 7.9177
[7 empty] | 1006 | 166 | 8.3727 | 6.32
[7 empty] | 1007 | 167 | 4.7818 | 3.5044
[7 empty] | 1008 | 168 | 4.1387 | 3.0002
[7 empty] | 1009 | 1 | 2.6856 | 1.8609
[7 empty] | 1010 | 2 | 2.5771 | 1.7758
[7 empty] | 1011 | 3 | 2.5687 | 1.7692
[7 empty] | 1012 | 4 | 2.7023 | 1.874
[7 empty] | 1013 | 5 | 2.719 | 1.8871
[7 empty] | 1014 | 6 | 3.1449 | 2.221
[7 empty] | 1015 | 7 | 3.8631 | 2.7841
[7 empty] | 1016 | 8 | 4.5312 | 3.308
[7 empty] | 1017 | 9 | 4.5062 | 3.2883
[7 empty] | 1018 | 10 | 6.0177 | 4.4735
[7 empty] | 1019 | 11 | 8.0888 | 6.0974
[7 empty] | 1020 | 12 | 9.0492 | 6.8504
[7 empty] | 1021 | 13 | 9.425 | 7.1451
[7 empty] | 1022 | 14 | 9.2079 | 6.9748
[7 empty] | 1023 | 15 | 9.116 | 6.9028
[7 empty] | 1024 | 16 | 10.2935 | 7.8261
[7 empty] | 1025 | 17 | 11.613 | 8.8607
[7 empty] | 1026 | 18 | 11.3708 | 8.6708
[7 empty] | 1027 | 19 | 11.8969 | 9.0833
[7 empty] | 1028 | 20 | 11.8301 | 9.0309
[7 empty] | 1029 | 21 | 12.398 | 9.4762
[7 empty] | 1030 | 22 | 8.4563 | 6.3855
[7 empty] | 1031 | 23 | 4.6983 | 3.4389
[7 empty] | 1032 | 24 | 3.0331 | 2.1333
[7 empty] | 1033 | 25 | 2.9362 | 2.0573
[7 empty] | 1034 | 26 | 2.8276 | 1.9722
[7 empty] | 1035 | 27 | 2.7274 | 1.8936
[7 empty] | 1036 | 28 | 2.8109 | 1.9591
[7 empty] | 1037 | 29 | 3.0531 | 2.149
[7 empty] | 1038 | 30 | 3.2953 | 2.3389
[7 empty] | 1039 | 31 | 4.1387 | 3.0002
[7 empty] | 1040 | 32 | 4.4895 | 3.2752
[7 empty] | 1041 | 33 | 5.1492 | 3.7925
[7 empty] | 1042 | 34 | 6.0428 | 4.4932
[7 empty] | 1043 | 35 | 8.2057 | 6.1891
[7 empty] | 1044 | 36 | 9.2329 | 6.9945
[7 empty] | 1045 | 37 | 9.3081 | 7.0534
[7 empty] | 1046 | 38 | 9.3832 | 7.1123
[7 empty] | 1047 | 39 | 9.0575 | 6.857
[7 empty] | 1048 | 40 | 10.1098 | 7.682
[7 empty] | 1049 | 41 | 10.6609 | 8.1142
[7 empty] | 1050 | 42 | 10.6776 | 8.1273
[7 empty] | 1051 | 43 | 11.0451 | 8.4154
[7 empty] | 1052 | 44 | 12.1975 | 9.319
[7 empty] | 1053 | 45 | 11.7967 | 9.0047
[7 empty] | 1054 | 46 | 9.0575 | 6.857
[7 empty] | 1055 | 47 | 5.4666 | 4.0414
[7 empty] | 1056 | 48 | 3.9717 | 2.8693
[7 empty] | 1057 | 49 | 3.312 | 2.352
[7 empty] | 1058 | 50 | 3.003 | 2.1097
[7 empty] | 1059 | 51 | 2.8944 | 2.0246
[7 empty] | 1060 | 52 | 2.9278 | 2.0508
[7 empty] | 1061 | 53 | 2.9529 | 2.0704
[7 empty] | 1062 | 54 | 3.5291 | 2.5222
[7 empty] | 1063 | 55 | 4.6648 | 3.4128
[7 empty] | 1064 | 56 | 4.907 | 3.6026
[7 empty] | 1065 | 57 | 5.8507 | 4.3426
[7 empty] | 1066 | 58 | 6.9531 | 5.2069
[7 empty] | 1067 | 59 | 8.1556 | 6.1498
[7 empty] | 1068 | 60 | 8.7819 | 6.6409
[7 empty] | 1069 | 61 | 9.4584 | 7.1713
[7 empty] | 1070 | 62 | 9.258 | 7.0141
[7 empty] | 1071 | 63 | 9.8509 | 7.479
[7 empty] | 1072 | 64 | 10.7946 | 8.219
[7 empty] | 1073 | 65 | 11.4125 | 8.7035
[7 empty] | 1074 | 66 | 11.3123 | 8.6249
[7 empty] | 1075 | 67 | 12.0472 | 9.2011
[7 empty] | 1076 | 68 | 12.2894 | 9.391
[7 empty] | 1077 | 69 | 11.78 | 8.9916
[7 empty] | 1078 | 70 | 9.4918 | 7.1975
[7 empty] | 1079 | 71 | 4.9905 | 3.6681
[7 empty] | 1080 | 72 | 3.9097 | 2.8206
[7 empty] | 1081 | 73 | 3.1951 | 2.2603
[7 empty] | 1082 | 74 | 2.9696 | 2.0835
[7 empty] | 1083 | 75 | 2.8694 | 2.0049
[7 empty] | 1084 | 76 | 2.8109 | 1.9591
[7 empty] | 1085 | 77 | 2.9863 | 2.0966
[7 empty] | 1086 | 78 | 3.3871 | 2.4109
[7 empty] | 1087 | 79 | 4.4978 | 3.2818
[7 empty] | 1088 | 80 | 4.6732 | 3.4193
[7 empty] | 1089 | 81 | 5.8507 | 4.3426
[7 empty] | 1090 | 82 | 6.9363 | 5.1938
[7 empty] | 1091 | 83 | 7.6712 | 5.77
[7 empty] | 1092 | 84 | 8.9072 | 6.7391
[7 empty] | 1093 | 85 | 8.6066 | 6.5034
[7 empty] | 1094 | 86 | 8.0972 | 6.104
[7 empty] | 1095 | 87 | 8.5398 | 6.451
[7 empty] | 1096 | 88 | 9.1995 | 6.9683
[7 empty] | 1097 | 89 | 10.544 | 8.0225
[7 empty] | 1098 | 90 | 9.9595 | 7.5642
[7 empty] | 1099 | 91 | 10.6442 | 8.1011
[7 empty] | 1100 | 92 | 10.043 | 7.6296
[7 empty] | 1101 | 93 | 7.6378 | 5.7438
[7 empty] | 1102 | 94 | 6.7359 | 5.0366
[7 empty] | 1103 | 95 | 4.882 | 3.583
[7 empty] | 1104 | 96 | 3.8965 | 2.8103
[7 empty] | 1105 | 97 | 3.8464 | 2.7711
[7 empty] | 1106 | 98 | 3.5541 | 2.5419
[7 empty] | 1107 | 99 | 3.4957 | 2.496
[7 empty] | 1108 | 100 | 3.1449 | 2.221
[7 empty] | 1109 | 101 | 3.0865 | 2.1752
[7 empty] | 1110 | 102 | 3.3203 | 2.3585
[7 empty] | 1111 | 103 | 4.0636 | 2.9413
[7 empty] | 1112 | 104 | 4.3141 | 3.1377
[7 empty] | 1113 | 105 | 4.7985 | 3.5175
[7 empty] | 1114 | 106 | 6.2516 | 4.6569
[7 empty] | 1115 | 107 | 6.6023 | 4.9319
[7 empty] | 1116 | 108 | 8.1723 | 6.1629
[7 empty] | 1117 | 109 | 7.5126 | 5.6456
[7 empty] | 1118 | 110 | 7.0616 | 5.292
[7 empty] | 1119 | 111 | 6.9029 | 5.1676
[7 empty] | 1120 | 112 | 6.9698 | 5.22
[7 empty] | 1121 | 113 | 6.6274 | 4.9515
[7 empty] | 1122 | 114 | 6.7944 | 5.0825
[7 empty] | 1123 | 115 | 6.3434 | 4.7289
[7 empty] | 1124 | 116 | 7.0199 | 5.2593
[7 empty] | 1125 | 117 | 6.6023 | 4.9319
[7 empty] | 1126 | 118 | 5.834 | 4.3295
[7 empty] | 1127 | 119 | 4.2473 | 3.0854
[7 empty] | 1128 | 120 | 3.9311 | 2.8374
[7 empty] | 1129 | 121 | 3.2034 | 2.2669
[7 empty] | 1130 | 122 | 2.7942 | 1.946
[7 empty] | 1131 | 123 | 2.7107 | 1.8805
[7 empty] | 1132 | 124 | 2.6773 | 1.8543
[7 empty] | 1133 | 125 | 2.6355 | 1.8216
[7 empty] | 1134 | 126 | 2.7775 | 1.9329
[7 empty] | 1135 | 127 | 4.2807 | 3.1115
[7 empty] | 1136 | 128 | 5.834 | 4.3295
[7 empty] | 1137 | 129 | 6.5104 | 4.8599
[7 empty] | 1138 | 130 | 6.9447 | 5.2003
[7 empty] | 1139 | 131 | 7.1034 | 5.3248
[7 empty] | 1140 | 132 | 6.8528 | 5.1283
[7 empty] | 1141 | 133 | 7.4875 | 5.626
[7 empty] | 1142 | 134 | 7.7882 | 5.8617
[7 empty] | 1143 | 135 | 7.855 | 5.9141
[7 empty] | 1144 | 136 | 7.0449 | 5.2789
[7 empty] | 1145 | 137 | 6.9447 | 5.2003
[7 empty] | 1146 | 138 | 6.8946 | 5.1611
[7 empty] | 1147 | 139 | 6.5605 | 4.8991
[7 empty] | 1148 | 140 | 6.5689 | 4.9057
[7 empty] | 1149 | 141 | 5.9175 | 4.3949
[7 empty] | 1150 | 142 | 5.2828 | 3.8973
[7 empty] | 1151 | 143 | 4.406 | 3.2098
[7 empty] | 1152 | 144 | 3.7963 | 2.7318
[7 empty] | 1153 | 145 | 3.3287 | 2.3651
[7 empty] | 1154 | 146 | 3.1199 | 2.2014
[7 empty] | 1155 | 147 | 3.0531 | 2.149
[7 empty] | 1156 | 148 | 3.0447 | 2.1424
[7 empty] | 1157 | 149 | 3.0447 | 2.1424
[7 empty] | 1158 | 150 | 3.0531 | 2.149
[7 empty] | 1159 | 151 | 4.1304 | 2.9937
[7 empty] | 1160 | 152 | 5.6503 | 4.1854
[7 empty] | 1161 | 153 | 6.2599 | 4.6634
[7 empty] | 1162 | 154 | 6.8194 | 5.1021
[7 empty] | 1163 | 155 | 6.6691 | 4.9843
[7 empty] | 1164 | 156 | 6.8361 | 5.1152
[7 empty] | 1165 | 157 | 7.546 | 5.6718
[7 empty] | 1166 | 158 | 7.8717 | 5.9272
[7 empty] | 1167 | 159 | 8.1389 | 6.1367
[7 empty] | 1168 | 160 | 8.0136 | 6.0385
[7 empty] | 1169 | 161 | 8.7736 | 6.6343
[7 empty] | 1170 | 162 | 8.2809 | 6.248
[7 empty] | 1171 | 163 | 8.64 | 6.5296
[7 empty] | 1172 | 164 | 7.2954 | 5.4754
[7 empty] | 1173 | 165 | 10.4104 | 7.9177
[7 empty] | 1174 | 166 | 8.3727 | 6.32
[7 empty] | 1175 | 167 | 4.7818 | 3.5044
[7 empty] | 1176 | 168 | 4.1387 | 3.0002
[7 empty] | 1177 | 1 | 2.6856 | 1.8609
[7 empty] | 1178 | 2 | 2.5771 | 1.7758
[7 empty] | 1179 | 3 | 2.5687 | 1.7692
[7 empty] | 1180 | 4 | 2.7023 | 1.874
[7 empty] | 1181 | 5 | 2.719 | 1.8871
[7 empty] | 1182 | 6 | 3.1449 | 2.221
[7 empty] | 1183 | 7 | 3.8631 | 2.7841
[7 empty] | 1184 | 8 | 4.5312 | 3.308
[7 empty] | 1185 | 9 | 4.5062 | 3.2883
[7 empty] | 1186 | 10 | 6.0177 | 4.4735
[7 empty] | 1187 | 11 | 8.0888 | 6.0974
[7 empty] | 1188 | 12 | 9.0492 | 6.8504
[7 empty] | 1189 | 13 | 9.425 | 7.1451
[7 empty] | 1190 | 14 | 9.2079 | 6.9748
[7 empty] | 1191 | 15 | 9.116 | 6.9028
[7 empty] | 1192 | 16 | 10.2935 | 7.8261
[7 empty] | 1193 | 17 | 11.613 | 8.8607
[7 empty] | 1194 | 18 | 11.3708 | 8.6708
[7 empty] | 1195 | 19 | 11.8969 | 9.0833
[7 empty] | 1196 | 20 | 11.8301 | 9.0309
[7 empty] | 1197 | 21 | 12.398 | 9.4762
[7 empty] | 1198 | 22 | 8.4563 | 6.3855
[7 empty] | 1199 | 23 | 4.6983 | 3.4389
[7 empty] | 1200 | 24 | 3.0331 | 2.1333
[7 empty] | 1201 | 25 | 2.9362 | 2.0573
[7 empty] | 1202 | 26 | 2.8276 | 1.9722
[7 empty] | 1203 | 27 | 2.7274 | 1.8936
[7 empty] | 1204 | 28 | 2.8109 | 1.9591
[7 empty] | 1205 | 29 | 3.0531 | 2.149
[7 empty] | 1206 | 30 | 3.2953 | 2.3389
[7 empty] | 1207 | 31 | 4.1387 | 3.0002
[7 empty] | 1208 | 32 | 4.4895 | 3.2752
[7 empty] | 1209 | 33 | 5.1492 | 3.7925
[7 empty] | 1210 | 34 | 6.0428 | 4.4932
[7 empty] | 1211 | 35 | 8.2057 | 6.1891
[7 empty] | 1212 | 36 | 9.2329 | 6.9945
[7 empty] | 1213 | 37 | 9.3081 | 7.0534
[7 empty] | 1214 | 38 | 9.3832 | 7.1123
[7 empty] | 1215 | 39 | 9.0575 | 6.857
[7 empty] | 1216 | 40 | 10.1098 | 7.682
[7 empty] | 1217 | 41 | 10.6609 | 8.1142
[7 empty] | 1218 | 42 | 10.6776 | 8.1273
[7 empty] | 1219 | 43 | 11.0451 | 8.4154
[7 empty] | 1220 | 44 | 12.1975 | 9.319
[7 empty] | 1221 | 45 | 11.7967 | 9.0047
[7 empty] | 1222 | 46 | 9.0575 | 6.857
[7 empty] | 1223 | 47 | 5.4666 | 4.0414
[7 empty] | 1224 | 48 | 3.9717 | 2.8693
[7 empty] | 1225 | 49 | 3.312 | 2.352
[7 empty] | 1226 | 50 | 3.003 | 2.1097
[7 empty] | 1227 | 51 | 2.8944 | 2.0246
[7 empty] | 1228 | 52 | 2.9278 | 2.0508
[7 empty] | 1229 | 53 | 2.9529 | 2.0704
[7 empty] | 1230 | 54 | 3.5291 | 2.5222
[7 empty] | 1231 | 55 | 4.6648 | 3.4128
[7 empty] | 1232 | 56 | 4.907 | 3.6026
[7 empty] | 1233 | 57 | 5.8507 | 4.3426
[7 empty] | 1234 | 58 | 6.9531 | 5.2069
[7 empty] | 1235 | 59 | 8.1556 | 6.1498
[7 empty] | 1236 | 60 | 8.7819 | 6.6409
[7 empty] | 1237 | 61 | 9.4584 | 7.1713
[7 empty] | 1238 | 62 | 9.258 | 7.0141
[7 empty] | 1239 | 63 | 9.8509 | 7.479
[7 empty] | 1240 | 64 | 10.7946 | 8.219
[7 empty] | 1241 | 65 | 11.4125 | 8.7035
[7 empty] | 1242 | 66 | 11.3123 | 8.6249
[7 empty] | 1243 | 67 | 12.0472 | 9.2011
[7 empty] | 1244 | 68 | 12.2894 | 9.391
[7 empty] | 1245 | 69 | 11.78 | 8.9916
[7 empty] | 1246 | 70 | 9.4918 | 7.1975
[7 empty] | 1247 | 71 | 4.9905 | 3.6681
[7 empty] | 1248 | 72 | 3.9097 | 2.8206
[7 empty] | 1249 | 73 | 3.1951 | 2.2603
[7 empty] | 1250 | 74 | 2.9696 | 2.0835
[7 empty] | 1251 | 75 | 2.8694 | 2.0049
[7 empty] | 1252 | 76 | 2.8109 | 1.9591
[7 empty] | 1253 | 77 | 2.9863 | 2.0966
[7 empty] | 1254 | 78 | 3.3871 | 2.4109
[7 empty] | 1255 | 79 | 4.4978 | 3.2818
[7 empty] | 1256 | 80 | 4.6732 | 3.4193
[7 empty] | 1257 | 81 | 5.8507 | 4.3426
[7 empty] | 1258 | 82 | 6.9363 | 5.1938
[7 empty] | 1259 | 83 | 7.6712 | 5.77
[7 empty] | 1260 | 84 | 8.9072 | 6.7391
[7 empty] | 1261 | 85 | 8.6066 | 6.5034
[7 empty] | 1262 | 86 | 8.0972 | 6.104
[7 empty] | 1263 | 87 | 8.5398 | 6.451
[7 empty] | 1264 | 88 | 9.1995 | 6.9683
[7 empty] | 1265 | 89 | 10.544 | 8.0225
[7 empty] | 1266 | 90 | 9.9595 | 7.5642
[7 empty] | 1267 | 91 | 10.6442 | 8.1011
[7 empty] | 1268 | 92 | 10.043 | 7.6296
[7 empty] | 1269 | 93 | 7.6378 | 5.7438
[7 empty] | 1270 | 94 | 6.7359 | 5.0366
[7 empty] | 1271 | 95 | 4.882 | 3.583
[7 empty] | 1272 | 96 | 3.8965 | 2.8103
[7 empty] | 1273 | 97 | 3.8464 | 2.7711
[7 empty] | 1274 | 98 | 3.5541 | 2.5419
[7 empty] | 1275 | 99 | 3.4957 | 2.496
[7 empty] | 1276 | 100 | 3.1449 | 2.221
[7 empty] | 1277 | 101 | 3.0865 | 2.1752
[7 empty] | 1278 | 102 | 3.3203 | 2.3585
[7 empty] | 1279 | 103 | 4.0636 | 2.9413
[7 empty] | 1280 | 104 | 4.3141 | 3.1377
[7 empty] | 1281 | 105 | 4.7985 | 3.5175
[7 empty] | 1282 | 106 | 6.2516 | 4.6569
[7 empty] | 1283 | 107 | 6.6023 | 4.9319
[7 empty] | 1284 | 108 | 8.1723 | 6.1629
[7 empty] | 1285 | 109 | 7.5126 | 5.6456
[7 empty] | 1286 | 110 | 7.0616 | 5.292
[7 empty] | 1287 | 111 | 6.9029 | 5.1676
[7 empty] | 1288 | 112 | 6.9698 | 5.22
[7 empty] | 1289 | 113 | 6.6274 | 4.9515
[7 empty] | 1290 | 114 | 6.7944 | 5.0825
[7 empty] | 1291 | 115 | 6.3434 | 4.7289
[7 empty] | 1292 | 116 | 7.0199 | 5.2593
[7 empty] | 1293 | 117 | 6.6023 | 4.9319
[7 empty] | 1294 | 118 | 5.834 | 4.3295
[7 empty] | 1295 | 119 | 4.2473 | 3.0854
[7 empty] | 1296 | 120 | 3.9311 | 2.8374
[7 empty] | 1297 | 121 | 3.2034 | 2.2669
[7 empty] | 1298 | 122 | 2.7942 | 1.946
[7 empty] | 1299 | 123 | 2.7107 | 1.8805
[7 empty] | 1300 | 124 | 2.6773 | 1.8543
[7 empty] | 1301 | 125 | 2.6355 | 1.8216
[7 empty] | 1302 | 126 | 2.7775 | 1.9329
[7 empty] | 1303 | 127 | 4.2807 | 3.1115
[7 empty] | 1304 | 128 | 5.834 | 4.3295
[7 empty] | 1305 | 129 | 6.5104 | 4.8599
[7 empty] | 1306 | 130 | 6.9447 | 5.2003
[7 empty] | 1307 | 131 | 7.1034 | 5.3248
[7 empty] | 1308 | 132 | 6.8528 | 5.1283
[7 empty] | 1309 | 133 | 7.4875 | 5.626
[7 empty] | 1310 | 134 | 7.7882 | 5.8617
[7 empty] | 1311 | 135 | 7.855 | 5.9141
[7 empty] | 1312 | 136 | 7.0449 | 5.2789
[7 empty] | 1313 | 137 | 6.9447 | 5.2003
[7 empty] | 1314 | 138 | 6.8946 | 5.1611
[7 empty] | 1315 | 139 | 6.5605 | 4.8991
[7 empty] | 1316 | 140 | 6.5689 | 4.9057
[7 empty] | 1317 | 141 | 5.9175 | 4.3949
[7 empty] | 1318 | 142 | 5.2828 | 3.8973
[7 empty] | 1319 | 143 | 4.406 | 3.2098
[7 empty] | 1320 | 144 | 3.7963 | 2.7318
[7 empty] | 1321 | 145 | 3.3287 | 2.3651
[7 empty] | 1322 | 146 | 3.1199 | 2.2014
[7 empty] | 1323 | 147 | 3.0531 | 2.149
[7 empty] | 1324 | 148 | 3.0447 | 2.1424
[7 empty] | 1325 | 149 | 3.0447 | 2.1424
[7 empty] | 1326 | 150 | 3.0531 | 2.149
[7 empty] | 1327 | 151 | 4.1304 | 2.9937
[7 empty] | 1328 | 152 | 5.6503 | 4.1854
[7 empty] | 1329 | 153 | 6.2599 | 4.6634
[7 empty] | 1330 | 154 | 6.8194 | 5.1021
[7 empty] | 1331 | 155 | 6.6691 | 4.9843
[7 empty] | 1332 | 156 | 6.8361 | 5.1152
[7 empty] | 1333 | 157 | 7.546 | 5.6718
[7 empty] | 1334 | 158 | 7.8717 | 5.9272
[7 empty] | 1335 | 159 | 8.1389 | 6.1367
[7 empty] | 1336 | 160 | 8.0136 | 6.0385
[7 empty] | 1337 | 161 | 8.7736 | 6.6343
[7 empty] | 1338 | 162 | 8.2809 | 6.248
[7 empty] | 1339 | 163 | 8.64 | 6.5296
[7 empty] | 1340 | 164 | 7.2954 | 5.4754
[7 empty] | 1341 | 165 | 10.4104 | 7.9177
[7 empty] | 1342 | 166 | 8.3727 | 6.32
[7 empty] | 1343 | 167 | 4.7818 | 3.5044
[7 empty] | 1344 | 168 | 4.1387 | 3.0002
[7 empty] | 1345 | 1 | 2.6856 | 1.8609
[7 empty] | 1346 | 2 | 2.5771 | 1.7758
[7 empty] | 1347 | 3 | 2.5687 | 1.7692
[7 empty] | 1348 | 4 | 2.7023 | 1.874
[7 empty] | 1349 | 5 | 2.719 | 1.8871
[7 empty] | 1350 | 6 | 3.1449 | 2.221
[7 empty] | 1351 | 7 | 3.8631 | 2.7841
[7 empty] | 1352 | 8 | 4.5312 | 3.308
[7 empty] | 1353 | 9 | 4.5062 | 3.2883
[7 empty] | 1354 | 10 | 6.0177 | 4.4735
[7 empty] | 1355 | 11 | 8.0888 | 6.0974
[7 empty] | 1356 | 12 | 9.0492 | 6.8504
[7 empty] | 1357 | 13 | 9.425 | 7.1451
[7 empty] | 1358 | 14 | 9.2079 | 6.9748
[7 empty] | 1359 | 15 | 9.116 | 6.9028
[7 empty] | 1360 | 16 | 10.2935 | 7.8261
[7 empty] | 1361 | 17 | 11.613 | 8.8607
[7 empty] | 1362 | 18 | 11.3708 | 8.6708
[7 empty] | 1363 | 19 | 11.8969 | 9.0833
[7 empty] | 1364 | 20 | 11.8301 | 9.0309
[7 empty] | 1365 | 21 | 12.398 | 9.4762
[7 empty] | 1366 | 22 | 8.4563 | 6.3855
[7 empty] | 1367 | 23 | 4.6983 | 3.4389
[7 empty] | 1368 | 24 | 3.0331 | 2.1333
[7 empty] | 1369 | 25 | 2.9362 | 2.0573
[7 empty] | 1370 | 26 | 2.8276 | 1.9722
[7 empty] | 1371 | 27 | 2.7274 | 1.8936
[7 empty] | 1372 | 28 | 2.8109 | 1.9591
[7 empty] | 1373 | 29 | 3.0531 | 2.149
[7 empty] | 1374 | 30 | 3.2953 | 2.3389
[7 empty] | 1375 | 31 | 4.1387 | 3.0002
[7 empty] | 1376 | 32 | 4.4895 | 3.2752
[7 empty] | 1377 | 33 | 5.1492 | 3.7925
[7 empty] | 1378 | 34 | 6.0428 | 4.4932
[7 empty] | 1379 | 35 | 8.2057 | 6.1891
[7 empty] | 1380 | 36 | 9.2329 | 6.9945
[7 empty] | 1381 | 37 | 9.3081 | 7.0534
[7 empty] | 1382 | 38 | 9.3832 | 7.1123
[7 empty] | 1383 | 39 | 9.0575 | 6.857
[7 empty] | 1384 | 40 | 10.1098 | 7.682
[7 empty] | 1385 | 41 | 10.6609 | 8.1142
[7 empty] | 1386 | 42 | 10.6776 | 8.1273
[7 empty] | 1387 | 43 | 11.0451 | 8.4154
[7 empty] | 1388 | 44 | 12.1975 | 9.319
[7 empty] | 1389 | 45 | 11.7967 | 9.0047
[7 empty] | 1390 | 46 | 9.0575 | 6.857
[7 empty] | 1391 | 47 | 5.4666 | 4.0414
[7 empty] | 1392 | 48 | 3.9717 | 2.8693
[7 empty] | 1393 | 49 | 3.312 | 2.352
[7 empty] | 1394 | 50 | 3.003 | 2.1097
[7 empty] | 1395 | 51 | 2.8944 | 2.0246
[7 empty] | 1396 | 52 | 2.9278 | 2.0508
[7 empty] | 1397 | 53 | 2.9529 | 2.0704
[7 empty] | 1398 | 54 | 3.5291 | 2.5222
[7 empty] | 1399 | 55 | 4.6648 | 3.4128
[7 empty] | 1400 | 56 | 4.907 | 3.6026
[7 empty] | 1401 | 57 | 5.8507 | 4.3426
[7 empty] | 1402 | 58 | 6.9531 | 5.2069
[7 empty] | 1403 | 59 | 8.1556 | 6.1498
[7 empty] | 1404 | 60 | 8.7819 | 6.6409
[7 empty] | 1405 | 61 | 9.4584 | 7.1713
[7 empty] | 1406 | 62 | 9.258 | 7.0141
[7 empty] | 1407 | 63 | 9.8509 | 7.479
[7 empty] | 1408 | 64 | 10.7946 | 8.219
[7 empty] | 1409 | 65 | 11.4125 | 8.7035
[7 empty] | 1410 | 66 | 11.3123 | 8.6249
[7 empty] | 1411 | 67 | 12.0472 | 9.2011
[7 empty] | 1412 | 68 | 12.2894 | 9.391
[7 empty] | 1413 | 69 | 11.78 | 8.9916
[7 empty] | 1414 | 70 | 9.4918 | 7.1975
[7 empty] | 1415 | 71 | 4.9905 | 3.6681
[7 empty] | 1416 | 72 | 3.9097 | 2.8206
[7 empty] | 1417 | 73 | 3.1951 | 2.2603
[7 empty] | 1418 | 74 | 2.9696 | 2.0835
[7 empty] | 1419 | 75 | 2.8694 | 2.0049
[7 empty] | 1420 | 76 | 2.8109 | 1.9591
[7 empty] | 1421 | 77 | 2.9863 | 2.0966
[7 empty] | 1422 | 78 | 3.3871 | 2.4109
[7 empty] | 1423 | 79 | 4.4978 | 3.2818
[7 empty] | 1424 | 80 | 4.6732 | 3.4193
[7 empty] | 1425 | 81 | 5.8507 | 4.3426
[7 empty] | 1426 | 82 | 6.9363 | 5.1938
[7 empty] | 1427 | 83 | 7.6712 | 5.77
[7 empty] | 1428 | 84 | 8.9072 | 6.7391
[7 empty] | 1429 | 85 | 8.6066 | 6.5034
[7 empty] | 1430 | 86 | 8.0972 | 6.104
[7 empty] | 1431 | 87 | 8.5398 | 6.451
[7 empty] | 1432 | 88 | 9.1995 | 6.9683
[7 empty] | 1433 | 89 | 10.544 | 8.0225
[7 empty] | 1434 | 90 | 9.9595 | 7.5642
[7 empty] | 1435 | 91 | 10.6442 | 8.1011
[7 empty] | 1436 | 92 | 10.043 | 7.6296
[7 empty] | 1437 | 93 | 7.6378 | 5.7438
[7 empty] | 1438 | 94 | 6.7359 | 5.0366
[7 empty] | 1439 | 95 | 4.882 | 3.583
[7 empty] | 1440 | 96 | 3.8965 | 2.8103
[7 empty] | 1441 | 97 | 3.8464 | 2.7711
[7 empty] | 1442 | 98 | 3.5541 | 2.5419
[7 empty] | 1443 | 99 | 3.4957 | 2.496
[7 empty] | 1444 | 100 | 3.1449 | 2.221
[7 empty] | 1445 | 101 | 3.0865 | 2.1752
[7 empty] | 1446 | 102 | 3.3203 | 2.3585
[7 empty] | 1447 | 103 | 4.0636 | 2.9413
[7 empty] | 1448 | 104 | 4.3141 | 3.1377
[7 empty] | 1449 | 105 | 4.7985 | 3.5175
[7 empty] | 1450 | 106 | 6.2516 | 4.6569
[7 empty] | 1451 | 107 | 6.6023 | 4.9319
[7 empty] | 1452 | 108 | 8.1723 | 6.1629
[7 empty] | 1453 | 109 | 7.5126 | 5.6456
[7 empty] | 1454 | 110 | 7.0616 | 5.292
[7 empty] | 1455 | 111 | 6.9029 | 5.1676
[7 empty] | 1456 | 112 | 6.9698 | 5.22
[7 empty] | 1457 | 113 | 6.6274 | 4.9515
[7 empty] | 1458 | 114 | 6.7944 | 5.0825
[7 empty] | 1459 | 115 | 6.3434 | 4.7289
[7 empty] | 1460 | 116 | 7.0199 | 5.2593
[7 empty] | 1461 | 117 | 6.6023 | 4.9319
[7 empty] | 1462 | 118 | 5.834 | 4.3295
[7 empty] | 1463 | 119 | 4.2473 | 3.0854
[7 empty] | 1464 | 120 | 3.9311 | 2.8374
[7 empty] | 1465 | 121 | 3.2034 | 2.2669
[7 empty] | 1466 | 122 | 2.7942 | 1.946
[7 empty] | 1467 | 123 | 2.7107 | 1.8805
[7 empty] | 1468 | 124 | 2.6773 | 1.8543
[7 empty] | 1469 | 125 | 2.6355 | 1.8216
[7 empty] | 1470 | 126 | 2.7775 | 1.9329
[7 empty] | 1471 | 127 | 4.2807 | 3.1115
[7 empty] | 1472 | 128 | 5.834 | 4.3295
[7 empty] | 1473 | 129 | 6.5104 | 4.8599
[7 empty] | 1474 | 130 | 6.9447 | 5.2003
[7 empty] | 1475 | 131 | 7.1034 | 5.3248
[7 empty] | 1476 | 132 | 6.8528 | 5.1283
[7 empty] | 1477 | 133 | 7.4875 | 5.626
[7 empty] | 1478 | 134 | 7.7882 | 5.8617
[7 empty] | 1479 | 135 | 7.855 | 5.9141
[7 empty] | 1480 | 136 | 7.0449 | 5.2789
[7 empty] | 1481 | 137 | 6.9447 | 5.2003
[7 empty] | 1482 | 138 | 6.8946 | 5.1611
[7 empty] | 1483 | 139 | 6.5605 | 4.8991
[7 empty] | 1484 | 140 | 6.5689 | 4.9057
[7 empty] | 1485 | 141 | 5.9175 | 4.3949
[7 empty] | 1486 | 142 | 5.2828 | 3.8973
[7 empty] | 1487 | 143 | 4.406 | 3.2098
[7 empty] | 1488 | 144 | 3.7963 | 2.7318
[7 empty] | 1489 | 145 | 3.3287 | 2.3651
[7 empty] | 1490 | 146 | 3.1199 | 2.2014
[7 empty] | 1491 | 147 | 3.0531 | 2.149
[7 empty] | 1492 | 148 | 3.0447 | 2.1424
[7 empty] | 1493 | 149 | 3.0447 | 2.1424
[7 empty] | 1494 | 150 | 3.0531 | 2.149
[7 empty] | 1495 | 151 | 4.1304 | 2.9937
[7 empty] | 1496 | 152 | 5.6503 | 4.1854
[7 empty] | 1497 | 153 | 6.2599 | 4.6634
[7 empty] | 1498 | 154 | 6.8194 | 5.1021
[7 empty] | 1499 | 155 | 6.6691 | 4.9843
[7 empty] | 1500 | 156 | 6.8361 | 5.1152
[7 empty] | 1501 | 157 | 7.546 | 5.6718
[7 empty] | 1502 | 158 | 7.8717 | 5.9272
[7 empty] | 1503 | 159 | 8.1389 | 6.1367
[7 empty] | 1504 | 160 | 8.0136 | 6.0385
[7 empty] | 1505 | 161 | 8.7736 | 6.6343
[7 empty] | 1506 | 162 | 8.2809 | 6.248
[7 empty] | 1507 | 163 | 8.64 | 6.5296
[7 empty] | 1508 | 164 | 7.2954 | 5.4754
[7 empty] | 1509 | 165 | 10.4104 | 7.9177
[7 empty] | 1510 | 166 | 8.3727 | 6.32
[7 empty] | 1511 | 167 | 4.7818 | 3.5044
[7 empty] | 1512 | 168 | 4.1387 | 3.0002
[7 empty] | 1513 | 1 | 2.6856 | 1.8609
[7 empty] | 1514 | 2 | 2.5771 | 1.7758
[7 empty] | 1515 | 3 | 2.5687 | 1.7692
[7 empty] | 1516 | 4 | 2.7023 | 1.874
[7 empty] | 1517 | 5 | 2.719 | 1.8871
[7 empty] | 1518 | 6 | 3.1449 | 2.221
[7 empty] | 1519 | 7 | 3.8631 | 2.7841
[7 empty] | 1520 | 8 | 4.5312 | 3.308
[7 empty] | 1521 | 9 | 4.5062 | 3.2883
[7 empty] | 1522 | 10 | 6.0177 | 4.4735
[7 empty] | 1523 | 11 | 8.0888 | 6.0974
[7 empty] | 1524 | 12 | 9.0492 | 6.8504
[7 empty] | 1525 | 13 | 9.425 | 7.1451
[7 empty] | 1526 | 14 | 9.2079 | 6.9748
[7 empty] | 1527 | 15 | 9.116 | 6.9028
[7 empty] | 1528 | 16 | 10.2935 | 7.8261
[7 empty] | 1529 | 17 | 11.613 | 8.8607
[7 empty] | 1530 | 18 | 11.3708 | 8.6708
[7 empty] | 1531 | 19 | 11.8969 | 9.0833
[7 empty] | 1532 | 20 | 11.8301 | 9.0309
[7 empty] | 1533 | 21 | 12.398 | 9.4762
[7 empty] | 1534 | 22 | 8.4563 | 6.3855
[7 empty] | 1535 | 23 | 4.6983 | 3.4389
[7 empty] | 1536 | 24 | 3.0331 | 2.1333
[7 empty] | 1537 | 25 | 2.9362 | 2.0573
[7 empty] | 1538 | 26 | 2.8276 | 1.9722
[7 empty] | 1539 | 27 | 2.7274 | 1.8936
[7 empty] | 1540 | 28 | 2.8109 | 1.9591
[7 empty] | 1541 | 29 | 3.0531 | 2.149
[7 empty] | 1542 | 30 | 3.2953 | 2.3389
[7 empty] | 1543 | 31 | 4.1387 | 3.0002
[7 empty] | 1544 | 32 | 4.4895 | 3.2752
[7 empty] | 1545 | 33 | 5.1492 | 3.7925
[7 empty] | 1546 | 34 | 6.0428 | 4.4932
[7 empty] | 1547 | 35 | 8.2057 | 6.1891
[7 empty] | 1548 | 36 | 9.2329 | 6.9945
[7 empty] | 1549 | 37 | 9.3081 | 7.0534
[7 empty] | 1550 | 38 | 9.3832 | 7.1123
[7 empty] | 1551 | 39 | 9.0575 | 6.857
[7 empty] | 1552 | 40 | 10.1098 | 7.682
[7 empty] | 1553 | 41 | 10.6609 | 8.1142
[7 empty] | 1554 | 42 | 10.6776 | 8.1273
[7 empty] | 1555 | 43 | 11.0451 | 8.4154
[7 empty] | 1556 | 44 | 12.1975 | 9.319
[7 empty] | 1557 | 45 | 11.7967 | 9.0047
[7 empty] | 1558 | 46 | 9.0575 | 6.857
[7 empty] | 1559 | 47 | 5.4666 | 4.0414
[7 empty] | 1560 | 48 | 3.9717 | 2.8693
[7 empty] | 1561 | 49 | 3.312 | 2.352
[7 empty] | 1562 | 50 | 3.003 | 2.1097
[7 empty] | 1563 | 51 | 2.8944 | 2.0246
[7 empty] | 1564 | 52 | 2.9278 | 2.0508
[7 empty] | 1565 | 53 | 2.9529 | 2.0704
[7 empty] | 1566 | 54 | 3.5291 | 2.5222
[7 empty] | 1567 | 55 | 4.6648 | 3.4128
[7 empty] | 1568 | 56 | 4.907 | 3.6026
[7 empty] | 1569 | 57 | 5.8507 | 4.3426
[7 empty] | 1570 | 58 | 6.9531 | 5.2069
[7 empty] | 1571 | 59 | 8.1556 | 6.1498
[7 empty] | 1572 | 60 | 8.7819 | 6.6409
[7 empty] | 1573 | 61 | 9.4584 | 7.1713
[7 empty] | 1574 | 62 | 9.258 | 7.0141
[7 empty] | 1575 | 63 | 9.8509 | 7.479
[7 empty] | 1576 | 64 | 10.7946 | 8.219
[7 empty] | 1577 | 65 | 11.4125 | 8.7035
[7 empty] | 1578 | 66 | 11.3123 | 8.6249
[7 empty] | 1579 | 67 | 12.0472 | 9.2011
[7 empty] | 1580 | 68 | 12.2894 | 9.391
[7 empty] | 1581 | 69 | 11.78 | 8.9916
[7 empty] | 1582 | 70 | 9.4918 | 7.1975
[7 empty] | 1583 | 71 | 4.9905 | 3.6681
[7 empty] | 1584 | 72 | 3.9097 | 2.8206
[7 empty] | 1585 | 73 | 3.1951 | 2.2603
[7 empty] | 1586 | 74 | 2.9696 | 2.0835
[7 empty] | 1587 | 75 | 2.8694 | 2.0049
[7 empty] | 1588 | 76 | 2.8109 | 1.9591
[7 empty] | 1589 | 77 | 2.9863 | 2.0966
[7 empty] | 1590 | 78 | 3.3871 | 2.4109
[7 empty] | 1591 | 79 | 4.4978 | 3.2818
[7 empty] | 1592 | 80 | 4.6732 | 3.4193
[7 empty] | 1593 | 81 | 5.8507 | 4.3426
[7 empty] | 1594 | 82 | 6.9363 | 5.1938
[7 empty] | 1595 | 83 | 7.6712 | 5.77
[7 empty] | 1596 | 84 | 8.9072 | 6.7391
[7 empty] | 1597 | 85 | 8.6066 | 6.5034
[7 empty] | 1598 | 86 | 8.0972 | 6.104
[7 empty] | 1599 | 87 | 8.5398 | 6.451
[7 empty] | 1600 | 88 | 9.1995 | 6.9683
[7 empty] | 1601 | 89 | 10.544 | 8.0225
[7 empty] | 1602 | 90 | 9.9595 | 7.5642
[7 empty] | 1603 | 91 | 10.6442 | 8.1011
[7 empty] | 1604 | 92 | 10.043 | 7.6296
[7 empty] | 1605 | 93 | 7.6378 | 5.7438
[7 empty] | 1606 | 94 | 6.7359 | 5.0366
[7 empty] | 1607 | 95 | 4.882 | 3.583
[7 empty] | 1608 | 96 | 3.8965 | 2.8103
[7 empty] | 1609 | 97 | 3.8464 | 2.7711
[7 empty] | 1610 | 98 | 3.5541 | 2.5419
[7 empty] | 1611 | 99 | 3.4957 | 2.496
[7 empty] | 1612 | 100 | 3.1449 | 2.221
[7 empty] | 1613 | 101 | 3.0865 | 2.1752
[7 empty] | 1614 | 102 | 3.3203 | 2.3585
[7 empty] | 1615 | 103 | 4.0636 | 2.9413
[7 empty] | 1616 | 104 | 4.3141 | 3.1377
[7 empty] | 1617 | 105 | 4.7985 | 3.5175
[7 empty] | 1618 | 106 | 6.2516 | 4.6569
[7 empty] | 1619 | 107 | 6.6023 | 4.9319
[7 empty] | 1620 | 108 | 8.1723 | 6.1629
[7 empty] | 1621 | 109 | 7.5126 | 5.6456
[7 empty] | 1622 | 110 | 7.0616 | 5.292
[7 empty] | 1623 | 111 | 6.9029 | 5.1676
[7 empty] | 1624 | 112 | 6.9698 | 5.22
[7 empty] | 1625 | 113 | 6.6274 | 4.9515
[7 empty] | 1626 | 114 | 6.7944 | 5.0825
[7 empty] | 1627 | 115 | 6.3434 | 4.7289
[7 empty] | 1628 | 116 | 7.0199 | 5.2593
[7 empty] | 1629 | 117 | 6.6023 | 4.9319
[7 empty] | 1630 | 118 | 5.834 | 4.3295
[7 empty] | 1631 | 119 | 4.2473 | 3.0854
[7 empty] | 1632 | 120 | 3.9311 | 2.8374
[7 empty] | 1633 | 121 | 3.2034 | 2.2669
[7 empty] | 1634 | 122 | 2.7942 | 1.946
[7 empty] | 1635 | 123 | 2.7107 | 1.8805
[7 empty] | 1636 | 124 | 2.6773 | 1.8543
[7 empty] | 1637 | 125 | 2.6355 | 1.8216
[7 empty] | 1638 | 126 | 2.7775 | 1.9329
[7 empty] | 1639 | 127 | 4.2807 | 3.1115
[7 empty] | 1640 | 128 | 5.834 | 4.3295
[7 empty] | 1641 | 129 | 6.5104 | 4.8599
[7 empty] | 1642 | 130 | 6.9447 | 5.2003
[7 empty] | 1643 | 131 | 7.1034 | 5.3248
[7 empty] | 1644 | 132 | 6.8528 | 5.1283
[7 empty] | 1645 | 133 | 7.4875 | 5.626
[7 empty] | 1646 | 134 | 7.7882 | 5.8617
[7 empty] | 1647 | 135 | 7.855 | 5.9141
[7 empty] | 1648 | 136 | 7.0449 | 5.2789
[7 empty] | 1649 | 137 | 6.9447 | 5.2003
[7 empty] | 1650 | 138 | 6.8946 | 5.1611
[7 empty] | 1651 | 139 | 6.5605 | 4.8991
[7 empty] | 1652 | 140 | 6.5689 | 4.9057
[7 empty] | 1653 | 141 | 5.9175 | 4.3949
[7 empty] | 1654 | 142 | 5.2828 | 3.8973
[7 empty] | 1655 | 143 | 4.406 | 3.2098
[7 empty] | 1656 | 144 | 3.7963 | 2.7318
[7 empty] | 1657 | 145 | 3.3287 | 2.3651
[7 empty] | 1658 | 146 | 3.1199 | 2.2014
[7 empty] | 1659 | 147 | 3.0531 | 2.149
[7 empty] | 1660 | 148 | 3.0447 | 2.1424
[7 empty] | 1661 | 149 | 3.0447 | 2.1424
[7 empty] | 1662 | 150 | 3.0531 | 2.149
[7 empty] | 1663 | 151 | 4.1304 | 2.9937
[7 empty] | 1664 | 152 | 5.6503 | 4.1854
[7 empty] | 1665 | 153 | 6.2599 | 4.6634
[7 empty] | 1666 | 154 | 6.8194 | 5.1021
[7 empty] | 1667 | 155 | 6.6691 | 4.9843
[7 empty] | 1668 | 156 | 6.8361 | 5.1152
[7 empty] | 1669 | 157 | 7.546 | 5.6718
[7 empty] | 1670 | 158 | 7.8717 | 5.9272
[7 empty] | 1671 | 159 | 8.1389 | 6.1367
[7 empty] | 1672 | 160 | 8.0136 | 6.0385
[7 empty] | 1673 | 161 | 8.7736 | 6.6343
[7 empty] | 1674 | 162 | 8.2809 | 6.248
[7 empty] | 1675 | 163 | 8.64 | 6.5296
[7 empty] | 1676 | 164 | 7.2954 | 5.4754
[7 empty] | 1677 | 165 | 10.4104 | 7.9177
[7 empty] | 1678 | 166 | 8.3727 | 6.32
[7 empty] | 1679 | 167 | 4.7818 | 3.5044
[7 empty] | 1680 | 168 | 4.1387 | 3.0002
[7 empty] | 1681 | 1 | 2.6856 | 1.8609
[7 empty] | 1682 | 2 | 2.5771 | 1.7758
[7 empty] | 1683 | 3 | 2.5687 | 1.7692
[7 empty] | 1684 | 4 | 2.7023 | 1.874
[7 empty] | 1685 | 5 | 2.719 | 1.8871
[7 empty] | 1686 | 6 | 3.1449 | 2.221
[7 empty] | 1687 | 7 | 3.8631 | 2.7841
[7 empty] | 1688 | 8 | 4.5312 | 3.308
[7 empty] | 1689 | 9 | 4.5062 | 3.2883
[7 empty] | 1690 | 10 | 6.0177 | 4.4735
[7 empty] | 1691 | 11 | 8.0888 | 6.0974
[7 empty] | 1692 | 12 | 9.0492 | 6.8504
[7 empty] | 1693 | 13 | 9.425 | 7.1451
[7 empty] | 1694 | 14 | 9.2079 | 6.9748
[7 empty] | 1695 | 15 | 9.116 | 6.9028
[7 empty] | 1696 | 16 | 10.2935 | 7.8261
[7 empty] | 1697 | 17 | 11.613 | 8.8607
[7 empty] | 1698 | 18 | 11.3708 | 8.6708
[7 empty] | 1699 | 19 | 11.8969 | 9.0833
[7 empty] | 1700 | 20 | 11.8301 | 9.0309
[7 empty] | 1701 | 21 | 12.398 | 9.4762
[7 empty] | 1702 | 22 | 8.4563 | 6.3855
[7 empty] | 1703 | 23 | 4.6983 | 3.4389
[7 empty] | 1704 | 24 | 3.0331 | 2.1333
[7 empty] | 1705 | 25 | 2.9362 | 2.0573
[7 empty] | 1706 | 26 | 2.8276 | 1.9722
[7 empty] | 1707 | 27 | 2.7274 | 1.8936
[7 empty] | 1708 | 28 | 2.8109 | 1.9591
[7 empty] | 1709 | 29 | 3.0531 | 2.149
[7 empty] | 1710 | 30 | 3.2953 | 2.3389
[7 empty] | 1711 | 31 | 4.1387 | 3.0002
[7 empty] | 1712 | 32 | 4.4895 | 3.2752
[7 empty] | 1713 | 33 | 5.1492 | 3.7925
[7 empty] | 1714 | 34 | 6.0428 | 4.4932
[7 empty] | 1715 | 35 | 8.2057 | 6.1891
[7 empty] | 1716 | 36 | 9.2329 | 6.9945
[7 empty] | 1717 | 37 | 9.3081 | 7.0534
[7 empty] | 1718 | 38 | 9.3832 | 7.1123
[7 empty] | 1719 | 39 | 9.0575 | 6.857
[7 empty] | 1720 | 40 | 10.1098 | 7.682
[7 empty] | 1721 | 41 | 10.6609 | 8.1142
[7 empty] | 1722 | 42 | 10.6776 | 8.1273
[7 empty] | 1723 | 43 | 11.0451 | 8.4154
[7 empty] | 1724 | 44 | 12.1975 | 9.319
[7 empty] | 1725 | 45 | 11.7967 | 9.0047
[7 empty] | 1726 | 46 | 9.0575 | 6.857
[7 empty] | 1727 | 47 | 5.4666 | 4.0414
[7 empty] | 1728 | 48 | 3.9717 | 2.8693
[7 empty] | 1729 | 49 | 3.312 | 2.352
[7 empty] | 1730 | 50 | 3.003 | 2.1097
[7 empty] | 1731 | 51 | 2.8944 | 2.0246
[7 empty] | 1732 | 52 | 2.9278 | 2.0508
[7 empty] | 1733 | 53 | 2.9529 | 2.0704
[7 empty] | 1734 | 54 | 3.5291 | 2.5222
[7 empty] | 1735 | 55 | 4.6648 | 3.4128
[7 empty] | 1736 | 56 | 4.907 | 3.6026
[7 empty] | 1737 | 57 | 5.8507 | 4.3426
[7 empty] | 1738 | 58 | 6.9531 | 5.2069
[7 empty] | 1739 | 59 | 8.1556 | 6.1498
[7 empty] | 1740 | 60 | 8.7819 | 6.6409
[7 empty] | 1741 | 61 | 9.4584 | 7.1713
[7 empty] | 1742 | 62 | 9.258 | 7.0141
[7 empty] | 1743 | 63 | 9.8509 | 7.479
[7 empty] | 1744 | 64 | 10.7946 | 8.219
[7 empty] | 1745 | 65 | 11.4125 | 8.7035
[7 empty] | 1746 | 66 | 11.3123 | 8.6249
[7 empty] | 1747 | 67 | 12.0472 | 9.2011
[7 empty] | 1748 | 68 | 12.2894 | 9.391
[7 empty] | 1749 | 69 | 11.78 | 8.9916
[7 empty] | 1750 | 70 | 9.4918 | 7.1975
[7 empty] | 1751 | 71 | 4.9905 | 3.6681
[7 empty] | 1752 | 72 | 3.9097 | 2.8206
[7 empty] | 1753 | 73 | 3.1951 | 2.2603
[7 empty] | 1754 | 74 | 2.9696 | 2.0835
[7 empty] | 1755 | 75 | 2.8694 | 2.0049
[7 empty] | 1756 | 76 | 2.8109 | 1.9591
[7 empty] | 1757 | 77 | 2.9863 | 2.0966
[7 empty] | 1758 | 78 | 3.3871 | 2.4109
[7 empty] | 1759 | 79 | 4.4978 | 3.2818
[7 empty] | 1760 | 80 | 4.6732 | 3.4193
[7 empty] | 1761 | 81 | 5.8507 | 4.3426
[7 empty] | 1762 | 82 | 6.9363 | 5.1938
[7 empty] | 1763 | 83 | 7.6712 | 5.77
[7 empty] | 1764 | 84 | 8.9072 | 6.7391
[7 empty] | 1765 | 85 | 8.6066 | 6.5034
[7 empty] | 1766 | 86 | 8.0972 | 6.104
[7 empty] | 1767 | 87 | 8.5398 | 6.451
[7 empty] | 1768 | 88 | 9.1995 | 6.9683
[7 empty] | 1769 | 89 | 10.544 | 8.0225
[7 empty] | 1770 | 90 | 9.9595 | 7.5642
[7 empty] | 1771 | 91 | 10.6442 | 8.1011
[7 empty] | 1772 | 92 | 10.043 | 7.6296
[7 empty] | 1773 | 93 | 7.6378 | 5.7438
[7 empty] | 1774 | 94 | 6.7359 | 5.0366
[7 empty] | 1775 | 95 | 4.882 | 3.583
[7 empty] | 1776 | 96 | 3.8965 | 2.8103
[7 empty] | 1777 | 97 | 3.8464 | 2.7711
[7 empty] | 1778 | 98 | 3.5541 | 2.5419
[7 empty] | 1779 | 99 | 3.4957 | 2.496
[7 empty] | 1780 | 100 | 3.1449 | 2.221
[7 empty] | 1781 | 101 | 3.0865 | 2.1752
[7 empty] | 1782 | 102 | 3.3203 | 2.3585
[7 empty] | 1783 | 103 | 4.0636 | 2.9413
[7 empty] | 1784 | 104 | 4.3141 | 3.1377
[7 empty] | 1785 | 105 | 4.7985 | 3.5175
[7 empty] | 1786 | 106 | 6.2516 | 4.6569
[7 empty] | 1787 | 107 | 6.6023 | 4.9319
[7 empty] | 1788 | 108 | 8.1723 | 6.1629
[7 empty] | 1789 | 109 | 7.5126 | 5.6456
[7 empty] | 1790 | 110 | 7.0616 | 5.292
[7 empty] | 1791 | 111 | 6.9029 | 5.1676
[7 empty] | 1792 | 112 | 6.9698 | 5.22
[7 empty] | 1793 | 113 | 6.6274 | 4.9515
[7 empty] | 1794 | 114 | 6.7944 | 5.0825
[7 empty] | 1795 | 115 | 6.3434 | 4.7289
[7 empty] | 1796 | 116 | 7.0199 | 5.2593
[7 empty] | 1797 | 117 | 6.6023 | 4.9319
[7 empty] | 1798 | 118 | 5.834 | 4.3295
[7 empty] | 1799 | 119 | 4.2473 | 3.0854
[7 empty] | 1800 | 120 | 3.9311 | 2.8374
[7 empty] | 1801 | 121 | 3.2034 | 2.2669
[7 empty] | 1802 | 122 | 2.7942 | 1.946
[7 empty] | 1803 | 123 | 2.7107 | 1.8805
[7 empty] | 1804 | 124 | 2.6773 | 1.8543
[7 empty] | 1805 | 125 | 2.6355 | 1.8216
[7 empty] | 1806 | 126 | 2.7775 | 1.9329
[7 empty] | 1807 | 127 | 4.2807 | 3.1115
[7 empty] | 1808 | 128 | 5.834 | 4.3295
[7 empty] | 1809 | 129 | 6.5104 | 4.8599
[7 empty] | 1810 | 130 | 6.9447 | 5.2003
[7 empty] | 1811 | 131 | 7.1034 | 5.3248
[7 empty] | 1812 | 132 | 6.8528 | 5.1283
[7 empty] | 1813 | 133 | 7.4875 | 5.626
[7 empty] | 1814 | 134 | 7.7882 | 5.8617
[7 empty] | 1815 | 135 | 7.855 | 5.9141
[7 empty] | 1816 | 136 | 7.0449 | 5.2789
[7 empty] | 1817 | 137 | 6.9447 | 5.2003
[7 empty] | 1818 | 138 | 6.8946 | 5.1611
[7 empty] | 1819 | 139 | 6.5605 | 4.8991
[7 empty] | 1820 | 140 | 6.5689 | 4.9057
[7 empty] | 1821 | 141 | 5.9175 | 4.3949
[7 empty] | 1822 | 142 | 5.2828 | 3.8973
[7 empty] | 1823 | 143 | 4.406 | 3.2098
[7 empty] | 1824 | 144 | 3.7963 | 2.7318
[7 empty] | 1825 | 145 | 3.3287 | 2.3651
[7 empty] | 1826 | 146 | 3.1199 | 2.2014
[7 empty] | 1827 | 147 | 3.0531 | 2.149
[7 empty] | 1828 | 148 | 3.0447 | 2.1424
[7 empty] | 1829 | 149 | 3.0447 | 2.1424
[7 empty] | 1830 | 150 | 3.0531 | 2.149
[7 empty] | 1831 | 151 | 4.1304 | 2.9937
[7 empty] | 1832 | 152 | 5.6503 | 4.1854
[7 empty] | 1833 | 153 | 6.2599 | 4.6634
[7 empty] | 1834 | 154 | 6.8194 | 5.1021
[7 empty] | 1835 | 155 | 6.6691 | 4.9843
[7 empty] | 1836 | 156 | 6.8361 | 5.1152
[7 empty] | 1837 | 157 | 7.546 | 5.6718
[7 empty] | 1838 | 158 | 7.8717 | 5.9272
[7 empty] | 1839 | 159 | 8.1389 | 6.1367
[7 empty] | 1840 | 160 | 8.0136 | 6.0385
[7 empty] | 1841 | 161 | 8.7736 | 6.6343
[7 empty] | 1842 | 162 | 8.2809 | 6.248
[7 empty] | 1843 | 163 | 8.64 | 6.5296
[7 empty] | 1844 | 164 | 7.2954 | 5.4754
[7 empty] | 1845 | 165 | 10.4104 | 7.9177
[7 empty] | 1846 | 166 | 8.3727 | 6.32
[7 empty] | 1847 | 167 | 4.7818 | 3.5044
[7 empty] | 1848 | 168 | 4.1387 | 3.0002
[7 empty] | 1849 | 1 | 2.6856 | 1.8609
[7 empty] | 1850 | 2 | 2.5771 | 1.7758
[7 empty] | 1851 | 3 | 2.5687 | 1.7692
[7 empty] | 1852 | 4 | 2.7023 | 1.874
[7 empty] | 1853 | 5 | 2.719 | 1.8871
[7 empty] | 1854 | 6 | 3.1449 | 2.221
[7 empty] | 1855 | 7 | 3.8631 | 2.7841
[7 empty] | 1856 | 8 | 4.5312 | 3.308
[7 empty] | 1857 | 9 | 4.5062 | 3.2883
[7 empty] | 1858 | 10 | 6.0177 | 4.4735
[7 empty] | 1859 | 11 | 8.0888 | 6.0974
[7 empty] | 1860 | 12 | 9.0492 | 6.8504
[7 empty] | 1861 | 13 | 9.425 | 7.1451
[7 empty] | 1862 | 14 | 9.2079 | 6.9748
[7 empty] | 1863 | 15 | 9.116 | 6.9028
[7 empty] | 1864 | 16 | 10.2935 | 7.8261
[7 empty] | 1865 | 17 | 11.613 | 8.8607
[7 empty] | 1866 | 18 | 11.3708 | 8.6708
[7 empty] | 1867 | 19 | 11.8969 | 9.0833
[7 empty] | 1868 | 20 | 11.8301 | 9.0309
[7 empty] | 1869 | 21 | 12.398 | 9.4762
[7 empty] | 1870 | 22 | 8.4563 | 6.3855
[7 empty] | 1871 | 23 | 4.6983 | 3.4389
[7 empty] | 1872 | 24 | 3.0331 | 2.1333
[7 empty] | 1873 | 25 | 2.9362 | 2.0573
[7 empty] | 1874 | 26 | 2.8276 | 1.9722
[7 empty] | 1875 | 27 | 2.7274 | 1.8936
[7 empty] | 1876 | 28 | 2.8109 | 1.9591
[7 empty] | 1877 | 29 | 3.0531 | 2.149
[7 empty] | 1878 | 30 | 3.2953 | 2.3389
[7 empty] | 1879 | 31 | 4.1387 | 3.0002
[7 empty] | 1880 | 32 | 4.4895 | 3.2752
[7 empty] | 1881 | 33 | 5.1492 | 3.7925
[7 empty] | 1882 | 34 | 6.0428 | 4.4932
[7 empty] | 1883 | 35 | 8.2057 | 6.1891
[7 empty] | 1884 | 36 | 9.2329 | 6.9945
[7 empty] | 1885 | 37 | 9.3081 | 7.0534
[7 empty] | 1886 | 38 | 9.3832 | 7.1123
[7 empty] | 1887 | 39 | 9.0575 | 6.857
[7 empty] | 1888 | 40 | 10.1098 | 7.682
[7 empty] | 1889 | 41 | 10.6609 | 8.1142
[7 empty] | 1890 | 42 | 10.6776 | 8.1273
[7 empty] | 1891 | 43 | 11.0451 | 8.4154
[7 empty] | 1892 | 44 | 12.1975 | 9.319
[7 empty] | 1893 | 45 | 11.7967 | 9.0047
[7 empty] | 1894 | 46 | 9.0575 | 6.857
[7 empty] | 1895 | 47 | 5.4666 | 4.0414
[7 empty] | 1896 | 48 | 3.9717 | 2.8693
[7 empty] | 1897 | 49 | 3.312 | 2.352
[7 empty] | 1898 | 50 | 3.003 | 2.1097
[7 empty] | 1899 | 51 | 2.8944 | 2.0246
[7 empty] | 1900 | 52 | 2.9278 | 2.0508
[7 empty] | 1901 | 53 | 2.9529 | 2.0704
[7 empty] | 1902 | 54 | 3.5291 | 2.5222
[7 empty] | 1903 | 55 | 4.6648 | 3.4128
[7 empty] | 1904 | 56 | 4.907 | 3.6026
[7 empty] | 1905 | 57 | 5.8507 | 4.3426
[7 empty] | 1906 | 58 | 6.9531 | 5.2069
[7 empty] | 1907 | 59 | 8.1556 | 6.1498
[7 empty] | 1908 | 60 | 8.7819 | 6.6409
[7 empty] | 1909 | 61 | 9.4584 | 7.1713
[7 empty] | 1910 | 62 | 9.258 | 7.0141
[7 empty] | 1911 | 63 | 9.8509 | 7.479
[7 empty] | 1912 | 64 | 10.7946 | 8.219
[7 empty] | 1913 | 65 | 11.4125 | 8.7035
[7 empty] | 1914 | 66 | 11.3123 | 8.6249
[7 empty] | 1915 | 67 | 12.0472 | 9.2011
[7 empty] | 1916 | 68 | 12.2894 | 9.391
[7 empty] | 1917 | 69 | 11.78 | 8.9916
[7 empty] | 1918 | 70 | 9.4918 | 7.1975
[7 empty] | 1919 | 71 | 4.9905 | 3.6681
[7 empty] | 1920 | 72 | 3.9097 | 2.8206
[7 empty] | 1921 | 73 | 3.1951 | 2.2603
[7 empty] | 1922 | 74 | 2.9696 | 2.0835
[7 empty] | 1923 | 75 | 2.8694 | 2.0049
[7 empty] | 1924 | 76 | 2.8109 | 1.9591
[7 empty] | 1925 | 77 | 2.9863 | 2.0966
[7 empty] | 1926 | 78 | 3.3871 | 2.4109
[7 empty] | 1927 | 79 | 4.4978 | 3.2818
[7 empty] | 1928 | 80 | 4.6732 | 3.4193
[7 empty] | 1929 | 81 | 5.8507 | 4.3426
[7 empty] | 1930 | 82 | 6.9363 | 5.1938
[7 empty] | 1931 | 83 | 7.6712 | 5.77
[7 empty] | 1932 | 84 | 8.9072 | 6.7391
[7 empty] | 1933 | 85 | 8.6066 | 6.5034
[7 empty] | 1934 | 86 | 8.0972 | 6.104
[7 empty] | 1935 | 87 | 8.5398 | 6.451
[7 empty] | 1936 | 88 | 9.1995 | 6.9683
[7 empty] | 1937 | 89 | 10.544 | 8.0225
[7 empty] | 1938 | 90 | 9.9595 | 7.5642
[7 empty] | 1939 | 91 | 10.6442 | 8.1011
[7 empty] | 1940 | 92 | 10.043 | 7.6296
[7 empty] | 1941 | 93 | 7.6378 | 5.7438
[7 empty] | 1942 | 94 | 6.7359 | 5.0366
[7 empty] | 1943 | 95 | 4.882 | 3.583
[7 empty] | 1944 | 96 | 3.8965 | 2.8103
[7 empty] | 1945 | 97 | 3.8464 | 2.7711
[7 empty] | 1946 | 98 | 3.5541 | 2.5419
[7 empty] | 1947 | 99 | 3.4957 | 2.496
[7 empty] | 1948 | 100 | 3.1449 | 2.221
[7 empty] | 1949 | 101 | 3.0865 | 2.1752
[7 empty] | 1950 | 102 | 3.3203 | 2.3585
[7 empty] | 1951 | 103 | 4.0636 | 2.9413
[7 empty] | 1952 | 104 | 4.3141 | 3.1377
[7 empty] | 1953 | 105 | 4.7985 | 3.5175
[7 empty] | 1954 | 106 | 6.2516 | 4.6569
[7 empty] | 1955 | 107 | 6.6023 | 4.9319
[7 empty] | 1956 | 108 | 8.1723 | 6.1629
[7 empty] | 1957 | 109 | 7.5126 | 5.6456
[7 empty] | 1958 | 110 | 7.0616 | 5.292
[7 empty] | 1959 | 111 | 6.9029 | 5.1676
[7 empty] | 1960 | 112 | 6.9698 | 5.22
[7 empty] | 1961 | 113 | 6.6274 | 4.9515
[7 empty] | 1962 | 114 | 6.7944 | 5.0825
[7 empty] | 1963 | 115 | 6.3434 | 4.7289
[7 empty] | 1964 | 116 | 7.0199 | 5.2593
[7 empty] | 1965 | 117 | 6.6023 | 4.9319
[7 empty] | 1966 | 118 | 5.834 | 4.3295
[7 empty] | 1967 | 119 | 4.2473 | 3.0854
[7 empty] | 1968 | 120 | 3.9311 | 2.8374
[7 empty] | 1969 | 121 | 3.2034 | 2.2669
[7 empty] | 1970 | 122 | 2.7942 | 1.946
[7 empty] | 1971 | 123 | 2.7107 | 1.8805
[7 empty] | 1972 | 124 | 2.6773 | 1.8543
[7 empty] | 1973 | 125 | 2.6355 | 1.8216
[7 empty] | 1974 | 126 | 2.7775 | 1.9329
[7 empty] | 1975 | 127 | 4.2807 | 3.1115
[7 empty] | 1976 | 128 | 5.834 | 4.3295
[7 empty] | 1977 | 129 | 6.5104 | 4.8599
[7 empty] | 1978 | 130 | 6.9447 | 5.2003
[7 empty] | 1979 | 131 | 7.1034 | 5.3248
[7 empty] | 1980 | 132 | 6.8528 | 5.1283
[7 empty] | 1981 | 133 | 7.4875 | 5.626
[7 empty] | 1982 | 134 | 7.7882 | 5.8617
[7 empty] | 1983 | 135 | 7.855 | 5.9141
[7 empty] | 1984 | 136 | 7.0449 | 5.2789
[7 empty] | 1985 | 137 | 6.9447 | 5.2003
[7 empty] | 1986 | 138 | 6.8946 | 5.1611
[7 empty] | 1987 | 139 | 6.5605 | 4.8991
[7 empty] | 1988 | 140 | 6.5689 | 4.9057
[7 empty] | 1989 | 141 | 5.9175 | 4.3949
[7 empty] | 1990 | 142 | 5.2828 | 3.8973
[7 empty] | 1991 | 143 | 4.406 | 3.2098
[7 empty] | 1992 | 144 | 3.7963 | 2.7318
[7 empty] | 1993 | 145 | 3.3287 | 2.3651
[7 empty] | 1994 | 146 | 3.1199 | 2.2014
[7 empty] | 1995 | 147 | 3.0531 | 2.149
[7 empty] | 1996 | 148 | 3.0447 | 2.1424
[7 empty] | 1997 | 149 | 3.0447 | 2.1424
[7 empty] | 1998 | 150 | 3.0531 | 2.149
[7 empty] | 1999 | 151 | 4.1304 | 2.9937
[7 empty] | 2000 | 152 | 5.6503 | 4.1854
[7 empty] | 2001 | 153 | 6.2599 | 4.6634
[7 empty] | 2002 | 154 | 6.8194 | 5.1021
[7 empty] | 2003 | 155 | 6.6691 | 4.9843
[7 empty] | 2004 | 156 | 6.8361 | 5.1152
[7 empty] | 2005 | 157 | 7.546 | 5.6718
[7 empty] | 2006 | 158 | 7.8717 | 5.9272
[7 empty] | 2007 | 159 | 8.1389 | 6.1367
[7 empty] | 2008 | 160 | 8.0136 | 6.0385
[7 empty] | 2009 | 161 | 8.7736 | 6.6343
[7 empty] | 2010 | 162 | 8.2809 | 6.248
[7 empty] | 2011 | 163 | 8.64 | 6.5296
[7 empty] | 2012 | 164 | 7.2954 | 5.4754
[7 empty] | 2013 | 165 | 10.4104 | 7.9177
[7 empty] | 2014 | 166 | 8.3727 | 6.32
[7 empty] | 2015 | 167 | 4.7818 | 3.5044
[7 empty] | 2016 | 168 | 4.1387 | 3.0002
[7 empty] | 2017 | 1 | 2.6856 | 1.8609
[7 empty] | 2018 | 2 | 2.5771 | 1.7758
[7 empty] | 2019 | 3 | 2.5687 | 1.7692
[7 empty] | 2020 | 4 | 2.7023 | 1.874
[7 empty] | 2021 | 5 | 2.719 | 1.8871
[7 empty] | 2022 | 6 | 3.1449 | 2.221
[7 empty] | 2023 | 7 | 3.8631 | 2.7841
[7 empty] | 2024 | 8 | 4.5312 | 3.308
[7 empty] | 2025 | 9 | 4.5062 | 3.2883
[7 empty] | 2026 | 10 | 6.0177 | 4.4735
[7 empty] | 2027 | 11 | 8.0888 | 6.0974
[7 empty] | 2028 | 12 | 9.0492 | 6.8504
[7 empty] | 2029 | 13 | 9.425 | 7.1451
[7 empty] | 2030 | 14 | 9.2079 | 6.9748
[7 empty] | 2031 | 15 | 9.116 | 6.9028
[7 empty] | 2032 | 16 | 10.2935 | 7.8261
[7 empty] | 2033 | 17 | 11.613 | 8.8607
[7 empty] | 2034 | 18 | 11.3708 | 8.6708
[7 empty] | 2035 | 19 | 11.8969 | 9.0833
[7 empty] | 2036 | 20 | 11.8301 | 9.0309
[7 empty] | 2037 | 21 | 12.398 | 9.4762
[7 empty] | 2038 | 22 | 8.4563 | 6.3855
[7 empty] | 2039 | 23 | 4.6983 | 3.4389
[7 empty] | 2040 | 24 | 3.0331 | 2.1333
[7 empty] | 2041 | 25 | 2.9362 | 2.0573
[7 empty] | 2042 | 26 | 2.8276 | 1.9722
[7 empty] | 2043 | 27 | 2.7274 | 1.8936
[7 empty] | 2044 | 28 | 2.8109 | 1.9591
[7 empty] | 2045 | 29 | 3.0531 | 2.149
[7 empty] | 2046 | 30 | 3.2953 | 2.3389
[7 empty] | 2047 | 31 | 4.1387 | 3.0002
[7 empty] | 2048 | 32 | 4.4895 | 3.2752
[7 empty] | 2049 | 33 | 5.1492 | 3.7925
[7 empty] | 2050 | 34 | 6.0428 | 4.4932
[7 empty] | 2051 | 35 | 8.2057 | 6.1891
[7 empty] | 2052 | 36 | 9.2329 | 6.9945
[7 empty] | 2053 | 37 | 9.3081 | 7.0534
[7 empty] | 2054 | 38 | 9.3832 | 7.1123
[7 empty] | 2055 | 39 | 9.0575 | 6.857
[7 empty] | 2056 | 40 | 10.1098 | 7.682
[7 empty] | 2057 | 41 | 10.6609 | 8.1142
[7 empty] | 2058 | 42 | 10.6776 | 8.1273
[7 empty] | 2059 | 43 | 11.0451 | 8.4154
[7 empty] | 2060 | 44 | 12.1975 | 9.319
[7 empty] | 2061 | 45 | 11.7967 | 9.0047
[7 empty] | 2062 | 46 | 9.0575 | 6.857
[7 empty] | 2063 | 47 | 5.4666 | 4.0414
[7 empty] | 2064 | 48 | 3.9717 | 2.8693
[7 empty] | 2065 | 49 | 3.312 | 2.352
[7 empty] | 2066 | 50 | 3.003 | 2.1097
[7 empty] | 2067 | 51 | 2.8944 | 2.0246
[7 empty] | 2068 | 52 | 2.9278 | 2.0508
[7 empty] | 2069 | 53 | 2.9529 | 2.0704
[7 empty] | 2070 | 54 | 3.5291 | 2.5222
[7 empty] | 2071 | 55 | 4.6648 | 3.4128
[7 empty] | 2072 | 56 | 4.907 | 3.6026
[7 empty] | 2073 | 57 | 5.8507 | 4.3426
[7 empty] | 2074 | 58 | 6.9531 | 5.2069
[7 empty] | 2075 | 59 | 8.1556 | 6.1498
[7 empty] | 2076 | 60 | 8.7819 | 6.6409
[7 empty] | 2077 | 61 | 9.4584 | 7.1713
[7 empty] | 2078 | 62 | 9.258 | 7.0141
[7 empty] | 2079 | 63 | 9.8509 | 7.479
[7 empty] | 2080 | 64 | 10.7946 | 8.219
[7 empty] | 2081 | 65 | 11.4125 | 8.7035
[7 empty] | 2082 | 66 | 11.3123 | 8.6249
[7 empty] | 2083 | 67 | 12.0472 | 9.2011
[7 empty] | 2084 | 68 | 12.2894 | 9.391
[7 empty] | 2085 | 69 | 11.78 | 8.9916
[7 empty] | 2086 | 70 | 9.4918 | 7.1975
[7 empty] | 2087 | 71 | 4.9905 | 3.6681
[7 empty] | 2088 | 72 | 3.9097 | 2.8206
[7 empty] | 2089 | 73 | 3.1951 | 2.2603
[7 empty] | 2090 | 74 | 2.9696 | 2.0835
[7 empty] | 2091 | 75 | 2.8694 | 2.0049
[7 empty] | 2092 | 76 | 2.8109 | 1.9591
[7 empty] | 2093 | 77 | 2.9863 | 2.0966
[7 empty] | 2094 | 78 | 3.3871 | 2.4109
[7 empty] | 2095 | 79 | 4.4978 | 3.2818
[7 empty] | 2096 | 80 | 4.6732 | 3.4193
[7 empty] | 2097 | 81 | 5.8507 | 4.3426
[7 empty] | 2098 | 82 | 6.9363 | 5.1938
[7 empty] | 2099 | 83 | 7.6712 | 5.77
[7 empty] | 2100 | 84 | 8.9072 | 6.7391
[7 empty] | 2101 | 85 | 8.6066 | 6.5034
[7 empty] | 2102 | 86 | 8.0972 | 6.104
[7 empty] | 2103 | 87 | 8.5398 | 6.451
[7 empty] | 2104 | 88 | 9.1995 | 6.9683
[7 empty] | 2105 | 89 | 10.544 | 8.0225
[7 empty] | 2106 | 90 | 9.9595 | 7.5642
[7 empty] | 2107 | 91 | 10.6442 | 8.1011
[7 empty] | 2108 | 92 | 10.043 | 7.6296
[7 empty] | 2109 | 93 | 7.6378 | 5.7438
[7 empty] | 2110 | 94 | 6.7359 | 5.0366
[7 empty] | 2111 | 95 | 4.882 | 3.583
[7 empty] | 2112 | 96 | 3.8965 | 2.8103
[7 empty] | 2113 | 97 | 3.8464 | 2.7711
[7 empty] | 2114 | 98 | 3.5541 | 2.5419
[7 empty] | 2115 | 99 | 3.4957 | 2.496
[7 empty] | 2116 | 100 | 3.1449 | 2.221
[7 empty] | 2117 | 101 | 3.0865 | 2.1752
[7 empty] | 2118 | 102 | 3.3203 | 2.3585
[7 empty] | 2119 | 103 | 4.0636 | 2.9413
[7 empty] | 2120 | 104 | 4.3141 | 3.1377
[7 empty] | 2121 | 105 | 4.7985 | 3.5175
[7 empty] | 2122 | 106 | 6.2516 | 4.6569
[7 empty] | 2123 | 107 | 6.6023 | 4.9319
[7 empty] | 2124 | 108 | 8.1723 | 6.1629
[7 empty] | 2125 | 109 | 7.5126 | 5.6456
[7 empty] | 2126 | 110 | 7.0616 | 5.292
[7 empty] | 2127 | 111 | 6.9029 | 5.1676
[7 empty] | 2128 | 112 | 6.9698 | 5.22
[7 empty] | 2129 | 113 | 6.6274 | 4.9515
[7 empty] | 2130 | 114 | 6.7944 | 5.0825
[7 empty] | 2131 | 115 | 6.3434 | 4.7289
[7 empty] | 2132 | 116 | 7.0199 | 5.2593
[7 empty] | 2133 | 117 | 6.6023 | 4.9319
[7 empty] | 2134 | 118 | 5.834 | 4.3295
[7 empty] | 2135 | 119 | 4.2473 | 3.0854
[7 empty] | 2136 | 120 | 3.9311 | 2.8374
[7 empty] | 2137 | 121 | 3.2034 | 2.2669
[7 empty] | 2138 | 122 | 2.7942 | 1.946
[7 empty] | 2139 | 123 | 2.7107 | 1.8805
[7 empty] | 2140 | 124 | 2.6773 | 1.8543
[7 empty] | 2141 | 125 | 2.6355 | 1.8216
[7 empty] | 2142 | 126 | 2.7775 | 1.9329
[7 empty] | 2143 | 127 | 4.2807 | 3.1115
[7 empty] | 2144 | 128 | 5.834 | 4.3295
[7 empty] | 2145 | 129 | 6.5104 | 4.8599
[7 empty] | 2146 | 130 | 6.9447 | 5.2003
[7 empty] | 2147 | 131 | 7.1034 | 5.3248
[7 empty] | 2148 | 132 | 6.8528 | 5.1283
[7 empty] | 2149 | 133 | 7.4875 | 5.626
[7 empty] | 2150 | 134 | 7.7882 | 5.8617
[7 empty] | 2151 | 135 | 7.855 | 5.9141
[7 empty] | 2152 | 136 | 7.0449 | 5.2789
[7 empty] | 2153 | 137 | 6.9447 | 5.2003
[7 empty] | 2154 | 138 | 6.8946 | 5.1611
[7 empty] | 2155 | 139 | 6.5605 | 4.8991
[7 empty] | 2156 | 140 | 6.5689 | 4.9057
[7 empty] | 2157 | 141 | 5.9175 | 4.3949
[7 empty] | 2158 | 142 | 5.2828 | 3.8973
[7 empty] | 2159 | 143 | 4.406 | 3.2098
[7 empty] | 2160 | 144 | 3.7963 | 2.7318
[7 empty] | 2161 | 145 | 3.3287 | 2.3651
[7 empty] | 2162 | 146 | 3.1199 | 2.2014
[7 empty] | 2163 | 147 | 3.0531 | 2.149
[7 empty] | 2164 | 148 | 3.0447 | 2.1424
[7 empty] | 2165 | 149 | 3.0447 | 2.1424
[7 empty] | 2166 | 150 | 3.0531 | 2.149
[7 empty] | 2167 | 151 | 4.1304 | 2.9937
[7 empty] | 2168 | 152 | 5.6503 | 4.1854
[7 empty] | 2169 | 153 | 6.2599 | 4.6634
[7 empty] | 2170 | 154 | 6.8194 | 5.1021
[7 empty] | 2171 | 155 | 6.6691 | 4.9843
[7 empty] | 2172 | 156 | 6.8361 | 5.1152
[7 empty] | 2173 | 157 | 7.546 | 5.6718
[7 empty] | 2174 | 158 | 7.8717 | 5.9272
[7 empty] | 2175 | 159 | 8.1389 | 6.1367
[7 empty] | 2176 | 160 | 8.0136 | 6.0385
[7 empty] | 2177 | 161 | 8.7736 | 6.6343
[7 empty] | 2178 | 162 | 8.2809 | 6.248
[7 empty] | 2179 | 163 | 8.64 | 6.5296
[7 empty] | 2180 | 164 | 7.2954 | 5.4754
[7 empty] | 2181 | 165 | 10.4104 | 7.9177
[7 empty] | 2182 | 166 | 8.3727 | 6.32
[7 empty] | 2183 | 167 | 4.7818 | 3.5044
[7 empty] | 2184 | 168 | 4.1387 | 3.0002
[7 empty] | 2185 | 1 | 2.6856 | 1.8609
[7 empty] | 2186 | 2 | 2.5771 | 1.7758
[7 empty] | 2187 | 3 | 2.5687 | 1.7692
[7 empty] | 2188 | 4 | 2.7023 | 1.874
[7 empty] | 2189 | 5 | 2.719 | 1.8871
[7 empty] | 2190 | 6 | 3.1449 | 2.221
[7 empty] | 2191 | 7 | 3.8631 | 2.7841
[7 empty] | 2192 | 8 | 4.5312 | 3.308
[7 empty] | 2193 | 9 | 4.5062 | 3.2883
[7 empty] | 2194 | 10 | 6.0177 | 4.4735
[7 empty] | 2195 | 11 | 8.0888 | 6.0974
[7 empty] | 2196 | 12 | 9.0492 | 6.8504
[7 empty] | 2197 | 13 | 9.425 | 7.1451
[7 empty] | 2198 | 14 | 9.2079 | 6.9748
[7 empty] | 2199 | 15 | 9.116 | 6.9028
[7 empty] | 2200 | 16 | 10.2935 | 7.8261
[7 empty] | 2201 | 17 | 11.613 | 8.8607
[7 empty] | 2202 | 18 | 11.3708 | 8.6708
[7 empty] | 2203 | 19 | 11.8969 | 9.0833
[7 empty] | 2204 | 20 | 11.8301 | 9.0309
[7 empty] | 2205 | 21 | 12.398 | 9.4762
[7 empty] | 2206 | 22 | 8.4563 | 6.3855
[7 empty] | 2207 | 23 | 4.6983 | 3.4389
[7 empty] | 2208 | 24 | 3.0331 | 2.1333
[7 empty] | 2209 | 25 | 2.9362 | 2.0573
[7 empty] | 2210 | 26 | 2.8276 | 1.9722
[7 empty] | 2211 | 27 | 2.7274 | 1.8936
[7 empty] | 2212 | 28 | 2.8109 | 1.9591
[7 empty] | 2213 | 29 | 3.0531 | 2.149
[7 empty] | 2214 | 30 | 3.2953 | 2.3389
[7 empty] | 2215 | 31 | 4.1387 | 3.0002
[7 empty] | 2216 | 32 | 4.4895 | 3.2752
[7 empty] | 2217 | 33 | 5.1492 | 3.7925
[7 empty] | 2218 | 34 | 6.0428 | 4.4932
[7 empty] | 2219 | 35 | 8.2057 | 6.1891
[7 empty] | 2220 | 36 | 9.2329 | 6.9945
[7 empty] | 2221 | 37 | 9.3081 | 7.0534
[7 empty] | 2222 | 38 | 9.3832 | 7.1123
[7 empty] | 2223 | 39 | 9.0575 | 6.857
[7 empty] | 2224 | 40 | 10.1098 | 7.682
[7 empty] | 2225 | 41 | 10.6609 | 8.1142
[7 empty] | 2226 | 42 | 10.6776 | 8.1273
[7 empty] | 2227 | 43 | 11.0451 | 8.4154
[7 empty] | 2228 | 44 | 12.1975 | 9.319
[7 empty] | 2229 | 45 | 11.7967 | 9.0047
[7 empty] | 2230 | 46 | 9.0575 | 6.857
[7 empty] | 2231 | 47 | 5.4666 | 4.0414
[7 empty] | 2232 | 48 | 3.9717 | 2.8693
[7 empty] | 2233 | 49 | 3.312 | 2.352
[7 empty] | 2234 | 50 | 3.003 | 2.1097
[7 empty] | 2235 | 51 | 2.8944 | 2.0246
[7 empty] | 2236 | 52 | 2.9278 | 2.0508
[7 empty] | 2237 | 53 | 2.9529 | 2.0704
[7 empty] | 2238 | 54 | 3.5291 | 2.5222
[7 empty] | 2239 | 55 | 4.6648 | 3.4128
[7 empty] | 2240 | 56 | 4.907 | 3.6026
[7 empty] | 2241 | 57 | 5.8507 | 4.3426
[7 empty] | 2242 | 58 | 6.9531 | 5.2069
[7 empty] | 2243 | 59 | 8.1556 | 6.1498
[7 empty] | 2244 | 60 | 8.7819 | 6.6409
[7 empty] | 2245 | 61 | 9.4584 | 7.1713
[7 empty] | 2246 | 62 | 9.258 | 7.0141
[7 empty] | 2247 | 63 | 9.8509 | 7.479
[7 empty] | 2248 | 64 | 10.7946 | 8.219
[7 empty] | 2249 | 65 | 11.4125 | 8.7035
[7 empty] | 2250 | 66 | 11.3123 | 8.6249
[7 empty] | 2251 | 67 | 12.0472 | 9.2011
[7 empty] | 2252 | 68 | 12.2894 | 9.391
[7 empty] | 2253 | 69 | 11.78 | 8.9916
[7 empty] | 2254 | 70 | 9.4918 | 7.1975
[7 empty] | 2255 | 71 | 4.9905 | 3.6681
[7 empty] | 2256 | 72 | 3.9097 | 2.8206
[7 empty] | 2257 | 73 | 3.1951 | 2.2603
[7 empty] | 2258 | 74 | 2.9696 | 2.0835
[7 empty] | 2259 | 75 | 2.8694 | 2.0049
[7 empty] | 2260 | 76 | 2.8109 | 1.9591
[7 empty] | 2261 | 77 | 2.9863 | 2.0966
[7 empty] | 2262 | 78 | 3.3871 | 2.4109
[7 empty] | 2263 | 79 | 4.4978 | 3.2818
[7 empty] | 2264 | 80 | 4.6732 | 3.4193
[7 empty] | 2265 | 81 | 5.8507 | 4.3426
[7 empty] | 2266 | 82 | 6.9363 | 5.1938
[7 empty] | 2267 | 83 | 7.6712 | 5.77
[7 empty] | 2268 | 84 | 8.9072 | 6.7391
[7 empty] | 2269 | 85 | 8.6066 | 6.5034
[7 empty] | 2270 | 86 | 8.0972 | 6.104
[7 empty] | 2271 | 87 | 8.5398 | 6.451
[7 empty] | 2272 | 88 | 9.1995 | 6.9683
[7 empty] | 2273 | 89 | 10.544 | 8.0225
[7 empty] | 2274 | 90 | 9.9595 | 7.5642
[7 empty] | 2275 | 91 | 10.6442 | 8.1011
[7 empty] | 2276 | 92 | 10.043 | 7.6296
[7 empty] | 2277 | 93 | 7.6378 | 5.7438
[7 empty] | 2278 | 94 | 6.7359 | 5.0366
[7 empty] | 2279 | 95 | 4.882 | 3.583
[7 empty] | 2280 | 96 | 3.8965 | 2.8103
[7 empty] | 2281 | 97 | 3.8464 | 2.7711
[7 empty] | 2282 | 98 | 3.5541 | 2.5419
[7 empty] | 2283 | 99 | 3.4957 | 2.496
[7 empty] | 2284 | 100 | 3.1449 | 2.221
[7 empty] | 2285 | 101 | 3.0865 | 2.1752
[7 empty] | 2286 | 102 | 3.3203 | 2.3585
[7 empty] | 2287 | 103 | 4.0636 | 2.9413
[7 empty] | 2288 | 104 | 4.3141 | 3.1377
[7 empty] | 2289 | 105 | 4.7985 | 3.5175
[7 empty] | 2290 | 106 | 6.2516 | 4.6569
[7 empty] | 2291 | 107 | 6.6023 | 4.9319
[7 empty] | 2292 | 108 | 8.1723 | 6.1629
[7 empty] | 2293 | 109 | 7.5126 | 5.6456
[7 empty] | 2294 | 110 | 7.0616 | 5.292
[7 empty] | 2295 | 111 | 6.9029 | 5.1676
[7 empty] | 2296 | 112 | 6.9698 | 5.22
[7 empty] | 2297 | 113 | 6.6274 | 4.9515
[7 empty] | 2298 | 114 | 6.7944 | 5.0825
[7 empty] | 2299 | 115 | 6.3434 | 4.7289
[7 empty] | 2300 | 116 | 7.0199 | 5.2593
[7 empty] | 2301 | 117 | 6.6023 | 4.9319
[7 empty] | 2302 | 118 | 5.834 | 4.3295
[7 empty] | 2303 | 119 | 4.2473 | 3.0854
[7 empty] | 2304 | 120 | 3.9311 | 2.8374
[7 empty] | 2305 | 121 | 3.2034 | 2.2669
[7 empty] | 2306 | 122 | 2.7942 | 1.946
[7 empty] | 2307 | 123 | 2.7107 | 1.8805
[7 empty] | 2308 | 124 | 2.6773 | 1.8543
[7 empty] | 2309 | 125 | 2.6355 | 1.8216
[7 empty] | 2310 | 126 | 2.7775 | 1.9329
[7 empty] | 2311 | 127 | 4.2807 | 3.1115
[7 empty] | 2312 | 128 | 5.834 | 4.3295
[7 empty] | 2313 | 129 | 6.5104 | 4.8599
[7 empty] | 2314 | 130 | 6.9447 | 5.2003
[7 empty] | 2315 | 131 | 7.1034 | 5.3248
[7 empty] | 2316 | 132 | 6.8528 | 5.1283
[7 empty] | 2317 | 133 | 7.4875 | 5.626
[7 empty] | 2318 | 134 | 7.7882 | 5.8617
[7 empty] | 2319 | 135 | 7.855 | 5.9141
[7 empty] | 2320 | 136 | 7.0449 | 5.2789
[7 empty] | 2321 | 137 | 6.9447 | 5.2003
[7 empty] | 2322 | 138 | 6.8946 | 5.1611
[7 empty] | 2323 | 139 | 6.5605 | 4.8991
[7 empty] | 2324 | 140 | 6.5689 | 4.9057
[7 empty] | 2325 | 141 | 5.9175 | 4.3949
[7 empty] | 2326 | 142 | 5.2828 | 3.8973
[7 empty] | 2327 | 143 | 4.406 | 3.2098
[7 empty] | 2328 | 144 | 3.7963 | 2.7318
[7 empty] | 2329 | 145 | 3.3287 | 2.3651
[7 empty] | 2330 | 146 | 3.1199 | 2.2014
[7 empty] | 2331 | 147 | 3.0531 | 2.149
[7 empty] | 2332 | 148 | 3.0447 | 2.1424
[7 empty] | 2333 | 149 | 3.0447 | 2.1424
[7 empty] | 2334 | 150 | 3.0531 | 2.149
[7 empty] | 2335 | 151 | 4.1304 | 2.9937
[7 empty] | 2336 | 152 | 5.6503 | 4.1854
[7 empty] | 2337 | 153 | 6.2599 | 4.6634
[7 empty] | 2338 | 154 | 6.8194 | 5.1021
[7 empty] | 2339 | 155 | 6.6691 | 4.9843
[7 empty] | 2340 | 156 | 6.8361 | 5.1152
[7 empty] | 2341 | 157 | 7.546 | 5.6718
[7 empty] | 2342 | 158 | 7.8717 | 5.9272
[7 empty] | 2343 | 159 | 8.1389 | 6.1367
[7 empty] | 2344 | 160 | 8.0136 | 6.0385
[7 empty] | 2345 | 161 | 8.7736 | 6.6343
[7 empty] | 2346 | 162 | 8.2809 | 6.248
[7 empty] | 2347 | 163 | 8.64 | 6.5296
[7 empty] | 2348 | 164 | 7.2954 | 5.4754
[7 empty] | 2349 | 165 | 10.4104 | 7.9177
[7 empty] | 2350 | 166 | 8.3727 | 6.32
[7 empty] | 2351 | 167 | 4.7818 | 3.5044
[7 empty] | 2352 | 168 | 4.1387 | 3.0002
[7 empty] | 2353 | 1 | 2.6856 | 1.8609
[7 empty] | 2354 | 2 | 2.5771 | 1.7758
[7 empty] | 2355 | 3 | 2.5687 | 1.7692
[7 empty] | 2356 | 4 | 2.7023 | 1.874
[7 empty] | 2357 | 5 | 2.719 | 1.8871
[7 empty] | 2358 | 6 | 3.1449 | 2.221
[7 empty] | 2359 | 7 | 3.8631 | 2.7841
[7 empty] | 2360 | 8 | 4.5312 | 3.308
[7 empty] | 2361 | 9 | 4.5062 | 3.2883
[7 empty] | 2362 | 10 | 6.0177 | 4.4735
[7 empty] | 2363 | 11 | 8.0888 | 6.0974
[7 empty] | 2364 | 12 | 9.0492 | 6.8504
[7 empty] | 2365 | 13 | 9.425 | 7.1451
[7 empty] | 2366 | 14 | 9.2079 | 6.9748
[7 empty] | 2367 | 15 | 9.116 | 6.9028
[7 empty] | 2368 | 16 | 10.2935 | 7.8261
[7 empty] | 2369 | 17 | 11.613 | 8.8607
[7 empty] | 2370 | 18 | 11.3708 | 8.6708
[7 empty] | 2371 | 19 | 11.8969 | 9.0833
[7 empty] | 2372 | 20 | 11.8301 | 9.0309
[7 empty] | 2373 | 21 | 12.398 | 9.4762
[7 empty] | 2374 | 22 | 8.4563 | 6.3855
[7 empty] | 2375 | 23 | 4.6983 | 3.4389
[7 empty] | 2376 | 24 | 3.0331 | 2.1333
[7 empty] | 2377 | 25 | 2.9362 | 2.0573
[7 empty] | 2378 | 26 | 2.8276 | 1.9722
[7 empty] | 2379 | 27 | 2.7274 | 1.8936
[7 empty] | 2380 | 28 | 2.8109 | 1.9591
[7 empty] | 2381 | 29 | 3.0531 | 2.149
[7 empty] | 2382 | 30 | 3.2953 | 2.3389
[7 empty] | 2383 | 31 | 4.1387 | 3.0002
[7 empty] | 2384 | 32 | 4.4895 | 3.2752
[7 empty] | 2385 | 33 | 5.1492 | 3.7925
[7 empty] | 2386 | 34 | 6.0428 | 4.4932
[7 empty] | 2387 | 35 | 8.2057 | 6.1891
[7 empty] | 2388 | 36 | 9.2329 | 6.9945
[7 empty] | 2389 | 37 | 9.3081 | 7.0534
[7 empty] | 2390 | 38 | 9.3832 | 7.1123
[7 empty] | 2391 | 39 | 9.0575 | 6.857
[7 empty] | 2392 | 40 | 10.1098 | 7.682
[7 empty] | 2393 | 41 | 10.6609 | 8.1142
[7 empty] | 2394 | 42 | 10.6776 | 8.1273
[7 empty] | 2395 | 43 | 11.0451 | 8.4154
[7 empty] | 2396 | 44 | 12.1975 | 9.319
[7 empty] | 2397 | 45 | 11.7967 | 9.0047
[7 empty] | 2398 | 46 | 9.0575 | 6.857
[7 empty] | 2399 | 47 | 5.4666 | 4.0414
[7 empty] | 2400 | 48 | 3.9717 | 2.8693
[7 empty] | 2401 | 49 | 3.312 | 2.352
[7 empty] | 2402 | 50 | 3.003 | 2.1097
[7 empty] | 2403 | 51 | 2.8944 | 2.0246
[7 empty] | 2404 | 52 | 2.9278 | 2.0508
[7 empty] | 2405 | 53 | 2.9529 | 2.0704
[7 empty] | 2406 | 54 | 3.5291 | 2.5222
[7 empty] | 2407 | 55 | 4.6648 | 3.4128
[7 empty] | 2408 | 56 | 4.907 | 3.6026
[7 empty] | 2409 | 57 | 5.8507 | 4.3426
[7 empty] | 2410 | 58 | 6.9531 | 5.2069
[7 empty] | 2411 | 59 | 8.1556 | 6.1498
[7 empty] | 2412 | 60 | 8.7819 | 6.6409
[7 empty] | 2413 | 61 | 9.4584 | 7.1713
[7 empty] | 2414 | 62 | 9.258 | 7.0141
[7 empty] | 2415 | 63 | 9.8509 | 7.479
[7 empty] | 2416 | 64 | 10.7946 | 8.219
[7 empty] | 2417 | 65 | 11.4125 | 8.7035
[7 empty] | 2418 | 66 | 11.3123 | 8.6249
[7 empty] | 2419 | 67 | 12.0472 | 9.2011
[7 empty] | 2420 | 68 | 12.2894 | 9.391
[7 empty] | 2421 | 69 | 11.78 | 8.9916
[7 empty] | 2422 | 70 | 9.4918 | 7.1975
[7 empty] | 2423 | 71 | 4.9905 | 3.6681
[7 empty] | 2424 | 72 | 3.9097 | 2.8206
[7 empty] | 2425 | 73 | 3.1951 | 2.2603
[7 empty] | 2426 | 74 | 2.9696 | 2.0835
[7 empty] | 2427 | 75 | 2.8694 | 2.0049
[7 empty] | 2428 | 76 | 2.8109 | 1.9591
[7 empty] | 2429 | 77 | 2.9863 | 2.0966
[7 empty] | 2430 | 78 | 3.3871 | 2.4109
[7 empty] | 2431 | 79 | 4.4978 | 3.2818
[7 empty] | 2432 | 80 | 4.6732 | 3.4193
[7 empty] | 2433 | 81 | 5.8507 | 4.3426
[7 empty] | 2434 | 82 | 6.9363 | 5.1938
[7 empty] | 2435 | 83 | 7.6712 | 5.77
[7 empty] | 2436 | 84 | 8.9072 | 6.7391
[7 empty] | 2437 | 85 | 8.6066 | 6.5034
[7 empty] | 2438 | 86 | 8.0972 | 6.104
[7 empty] | 2439 | 87 | 8.5398 | 6.451
[7 empty] | 2440 | 88 | 9.1995 | 6.9683
[7 empty] | 2441 | 89 | 10.544 | 8.0225
[7 empty] | 2442 | 90 | 9.9595 | 7.5642
[7 empty] | 2443 | 91 | 10.6442 | 8.1011
[7 empty] | 2444 | 92 | 10.043 | 7.6296
[7 empty] | 2445 | 93 | 7.6378 | 5.7438
[7 empty] | 2446 | 94 | 6.7359 | 5.0366
[7 empty] | 2447 | 95 | 4.882 | 3.583
[7 empty] | 2448 | 96 | 3.8965 | 2.8103
[7 empty] | 2449 | 97 | 3.8464 | 2.7711
[7 empty] | 2450 | 98 | 3.5541 | 2.5419
[7 empty] | 2451 | 99 | 3.4957 | 2.496
[7 empty] | 2452 | 100 | 3.1449 | 2.221
[7 empty] | 2453 | 101 | 3.0865 | 2.1752
[7 empty] | 2454 | 102 | 3.3203 | 2.3585
[7 empty] | 2455 | 103 | 4.0636 | 2.9413
[7 empty] | 2456 | 104 | 4.3141 | 3.1377
[7 empty] | 2457 | 105 | 4.7985 | 3.5175
[7 empty] | 2458 | 106 | 6.2516 | 4.6569
[7 empty] | 2459 | 107 | 6.6023 | 4.9319
[7 empty] | 2460 | 108 | 8.1723 | 6.1629
[7 empty] | 2461 | 109 | 7.5126 | 5.6456
[7 empty] | 2462 | 110 | 7.0616 | 5.292
[7 empty] | 2463 | 111 | 6.9029 | 5.1676
[7 empty] | 2464 | 112 | 6.9698 | 5.22
[7 empty] | 2465 | 113 | 6.6274 | 4.9515
[7 empty] | 2466 | 114 | 6.7944 | 5.0825
[7 empty] | 2467 | 115 | 6.3434 | 4.7289
[7 empty] | 2468 | 116 | 7.0199 | 5.2593
[7 empty] | 2469 | 117 | 6.6023 | 4.9319
[7 empty] | 2470 | 118 | 5.834 | 4.3295
[7 empty] | 2471 | 119 | 4.2473 | 3.0854
[7 empty] | 2472 | 120 | 3.9311 | 2.8374
[7 empty] | 2473 | 121 | 3.2034 | 2.2669
[7 empty] | 2474 | 122 | 2.7942 | 1.946
[7 empty] | 2475 | 123 | 2.7107 | 1.8805
[7 empty] | 2476 | 124 | 2.6773 | 1.8543
[7 empty] | 2477 | 125 | 2.6355 | 1.8216
[7 empty] | 2478 | 126 | 2.7775 | 1.9329
[7 empty] | 2479 | 127 | 4.2807 | 3.1115
[7 empty] | 2480 | 128 | 5.834 | 4.3295
[7 empty] | 2481 | 129 | 6.5104 | 4.8599
[7 empty] | 2482 | 130 | 6.9447 | 5.2003
[7 empty] | 2483 | 131 | 7.1034 | 5.3248
[7 empty] | 2484 | 132 | 6.8528 | 5.1283
[7 empty] | 2485 | 133 | 7.4875 | 5.626
[7 empty] | 2486 | 134 | 7.7882 | 5.8617
[7 empty] | 2487 | 135 | 7.855 | 5.9141
[7 empty] | 2488 | 136 | 7.0449 | 5.2789
[7 empty] | 2489 | 137 | 6.9447 | 5.2003
[7 empty] | 2490 | 138 | 6.8946 | 5.1611
[7 empty] | 2491 | 139 | 6.5605 | 4.8991
[7 empty] | 2492 | 140 | 6.5689 | 4.9057
[7 empty] | 2493 | 141 | 5.9175 | 4.3949
[7 empty] | 2494 | 142 | 5.2828 | 3.8973
[7 empty] | 2495 | 143 | 4.406 | 3.2098
[7 empty] | 2496 | 144 | 3.7963 | 2.7318
[7 empty] | 2497 | 145 | 3.3287 | 2.3651
[7 empty] | 2498 | 146 | 3.1199 | 2.2014
[7 empty] | 2499 | 147 | 3.0531 | 2.149
[7 empty] | 2500 | 148 | 3.0447 | 2.1424
[7 empty] | 2501 | 149 | 3.0447 | 2.1424
[7 empty] | 2502 | 150 | 3.0531 | 2.149
[7 empty] | 2503 | 151 | 4.1304 | 2.9937
[7 empty] | 2504 | 152 | 5.6503 | 4.1854
[7 empty] | 2505 | 153 | 6.2599 | 4.6634
[7 empty] | 2506 | 154 | 6.8194 | 5.1021
[7 empty] | 2507 | 155 | 6.6691 | 4.9843
[7 empty] | 2508 | 156 | 6.8361 | 5.1152
[7 empty] | 2509 | 157 | 7.546 | 5.6718
[7 empty] | 2510 | 158 | 7.8717 | 5.9272
[7 empty] | 2511 | 159 | 8.1389 | 6.1367
[7 empty] | 2512 | 160 | 8.0136 | 6.0385
[7 empty] | 2513 | 161 | 8.7736 | 6.6343
[7 empty] | 2514 | 162 | 8.2809 | 6.248
[7 empty] | 2515 | 163 | 8.64 | 6.5296
[7 empty] | 2516 | 164 | 7.2954 | 5.4754
[7 empty] | 2517 | 165 | 10.4104 | 7.9177
[7 empty] | 2518 | 166 | 8.3727 | 6.32
[7 empty] | 2519 | 167 | 4.7818 | 3.5044
[7 empty] | 2520 | 168 | 4.1387 | 3.0002
[7 empty] | 2521 | 1 | 2.6856 | 1.8609
[7 empty] | 2522 | 2 | 2.5771 | 1.7758
[7 empty] | 2523 | 3 | 2.5687 | 1.7692
[7 empty] | 2524 | 4 | 2.7023 | 1.874
[7 empty] | 2525 | 5 | 2.719 | 1.8871
[7 empty] | 2526 | 6 | 3.1449 | 2.221
[7 empty] | 2527 | 7 | 3.8631 | 2.7841
[7 empty] | 2528 | 8 | 4.5312 | 3.308
[7 empty] | 2529 | 9 | 4.5062 | 3.2883
[7 empty] | 2530 | 10 | 6.0177 | 4.4735
[7 empty] | 2531 | 11 | 8.0888 | 6.0974
[7 empty] | 2532 | 12 | 9.0492 | 6.8504
[7 empty] | 2533 | 13 | 9.425 | 7.1451
[7 empty] | 2534 | 14 | 9.2079 | 6.9748
[7 empty] | 2535 | 15 | 9.116 | 6.9028
[7 empty] | 2536 | 16 | 10.2935 | 7.8261
[7 empty] | 2537 | 17 | 11.613 | 8.8607
[7 empty] | 2538 | 18 | 11.3708 | 8.6708
[7 empty] | 2539 | 19 | 11.8969 | 9.0833
[7 empty] | 2540 | 20 | 11.8301 | 9.0309
[7 empty] | 2541 | 21 | 12.398 | 9.4762
[7 empty] | 2542 | 22 | 8.4563 | 6.3855
[7 empty] | 2543 | 23 | 4.6983 | 3.4389
[7 empty] | 2544 | 24 | 3.0331 | 2.1333
[7 empty] | 2545 | 25 | 2.9362 | 2.0573
[7 empty] | 2546 | 26 | 2.8276 | 1.9722
[7 empty] | 2547 | 27 | 2.7274 | 1.8936
[7 empty] | 2548 | 28 | 2.8109 | 1.9591
[7 empty] | 2549 | 29 | 3.0531 | 2.149
[7 empty] | 2550 | 30 | 3.2953 | 2.3389
[7 empty] | 2551 | 31 | 4.1387 | 3.0002
[7 empty] | 2552 | 32 | 4.4895 | 3.2752
[7 empty] | 2553 | 33 | 5.1492 | 3.7925
[7 empty] | 2554 | 34 | 6.0428 | 4.4932
[7 empty] | 2555 | 35 | 8.2057 | 6.1891
[7 empty] | 2556 | 36 | 9.2329 | 6.9945
[7 empty] | 2557 | 37 | 9.3081 | 7.0534
[7 empty] | 2558 | 38 | 9.3832 | 7.1123
[7 empty] | 2559 | 39 | 9.0575 | 6.857
[7 empty] | 2560 | 40 | 10.1098 | 7.682
[7 empty] | 2561 | 41 | 10.6609 | 8.1142
[7 empty] | 2562 | 42 | 10.6776 | 8.1273
[7 empty] | 2563 | 43 | 11.0451 | 8.4154
[7 empty] | 2564 | 44 | 12.1975 | 9.319
[7 empty] | 2565 | 45 | 11.7967 | 9.0047
[7 empty] | 2566 | 46 | 9.0575 | 6.857
[7 empty] | 2567 | 47 | 5.4666 | 4.0414
[7 empty] | 2568 | 48 | 3.9717 | 2.8693
[7 empty] | 2569 | 49 | 3.312 | 2.352
[7 empty] | 2570 | 50 | 3.003 | 2.1097
[7 empty] | 2571 | 51 | 2.8944 | 2.0246
[7 empty] | 2572 | 52 | 2.9278 | 2.0508
[7 empty] | 2573 | 53 | 2.9529 | 2.0704
[7 empty] | 2574 | 54 | 3.5291 | 2.5222
[7 empty] | 2575 | 55 | 4.6648 | 3.4128
[7 empty] | 2576 | 56 | 4.907 | 3.6026
[7 empty] | 2577 | 57 | 5.8507 | 4.3426
[7 empty] | 2578 | 58 | 6.9531 | 5.2069
[7 empty] | 2579 | 59 | 8.1556 | 6.1498
[7 empty] | 2580 | 60 | 8.7819 | 6.6409
[7 empty] | 2581 | 61 | 9.4584 | 7.1713
[7 empty] | 2582 | 62 | 9.258 | 7.0141
[7 empty] | 2583 | 63 | 9.8509 | 7.479
[7 empty] | 2584 | 64 | 10.7946 | 8.219
[7 empty] | 2585 | 65 | 11.4125 | 8.7035
[7 empty] | 2586 | 66 | 11.3123 | 8.6249
[7 empty] | 2587 | 67 | 12.0472 | 9.2011
[7 empty] | 2588 | 68 | 12.2894 | 9.391
[7 empty] | 2589 | 69 | 11.78 | 8.9916
[7 empty] | 2590 | 70 | 9.4918 | 7.1975
[7 empty] | 2591 | 71 | 4.9905 | 3.6681
[7 empty] | 2592 | 72 | 3.9097 | 2.8206
[7 empty] | 2593 | 73 | 3.1951 | 2.2603
[7 empty] | 2594 | 74 | 2.9696 | 2.0835
[7 empty] | 2595 | 75 | 2.8694 | 2.0049
[7 empty] | 2596 | 76 | 2.8109 | 1.9591
[7 empty] | 2597 | 77 | 2.9863 | 2.0966
[7 empty] | 2598 | 78 | 3.3871 | 2.4109
[7 empty] | 2599 | 79 | 4.4978 | 3.2818
[7 empty] | 2600 | 80 | 4.6732 | 3.4193
[7 empty] | 2601 | 81 | 5.8507 | 4.3426
[7 empty] | 2602 | 82 | 6.9363 | 5.1938
[7 empty] | 2603 | 83 | 7.6712 | 5.77
[7 empty] | 2604 | 84 | 8.9072 | 6.7391
[7 empty] | 2605 | 85 | 8.6066 | 6.5034
[7 empty] | 2606 | 86 | 8.0972 | 6.104
[7 empty] | 2607 | 87 | 8.5398 | 6.451
[7 empty] | 2608 | 88 | 9.1995 | 6.9683
[7 empty] | 2609 | 89 | 10.544 | 8.0225
[7 empty] | 2610 | 90 | 9.9595 | 7.5642
[7 empty] | 2611 | 91 | 10.6442 | 8.1011
[7 empty] | 2612 | 92 | 10.043 | 7.6296
[7 empty] | 2613 | 93 | 7.6378 | 5.7438
[7 empty] | 2614 | 94 | 6.7359 | 5.0366
[7 empty] | 2615 | 95 | 4.882 | 3.583
[7 empty] | 2616 | 96 | 3.8965 | 2.8103
[7 empty] | 2617 | 97 | 3.8464 | 2.7711
[7 empty] | 2618 | 98 | 3.5541 | 2.5419
[7 empty] | 2619 | 99 | 3.4957 | 2.496
[7 empty] | 2620 | 100 | 3.1449 | 2.221
[7 empty] | 2621 | 101 | 3.0865 | 2.1752
[7 empty] | 2622 | 102 | 3.3203 | 2.3585
[7 empty] | 2623 | 103 | 4.0636 | 2.9413
[7 empty] | 2624 | 104 | 4.3141 | 3.1377
[7 empty] | 2625 | 105 | 4.7985 | 3.5175
[7 empty] | 2626 | 106 | 6.2516 | 4.6569
[7 empty] | 2627 | 107 | 6.6023 | 4.9319
[7 empty] | 2628 | 108 | 8.1723 | 6.1629
[7 empty] | 2629 | 109 | 7.5126 | 5.6456
[7 empty] | 2630 | 110 | 7.0616 | 5.292
[7 empty] | 2631 | 111 | 6.9029 | 5.1676
[7 empty] | 2632 | 112 | 6.9698 | 5.22
[7 empty] | 2633 | 113 | 6.6274 | 4.9515
[7 empty] | 2634 | 114 | 6.7944 | 5.0825
[7 empty] | 2635 | 115 | 6.3434 | 4.7289
[7 empty] | 2636 | 116 | 7.0199 | 5.2593
[7 empty] | 2637 | 117 | 6.6023 | 4.9319
[7 empty] | 2638 | 118 | 5.834 | 4.3295
[7 empty] | 2639 | 119 | 4.2473 | 3.0854
[7 empty] | 2640 | 120 | 3.9311 | 2.8374
[7 empty] | 2641 | 121 | 3.2034 | 2.2669
[7 empty] | 2642 | 122 | 2.7942 | 1.946
[7 empty] | 2643 | 123 | 2.7107 | 1.8805
[7 empty] | 2644 | 124 | 2.6773 | 1.8543
[7 empty] | 2645 | 125 | 2.6355 | 1.8216
[7 empty] | 2646 | 126 | 2.7775 | 1.9329
[7 empty] | 2647 | 127 | 4.2807 | 3.1115
[7 empty] | 2648 | 128 | 5.834 | 4.3295
[7 empty] | 2649 | 129 | 6.5104 | 4.8599
[7 empty] | 2650 | 130 | 6.9447 | 5.2003
[7 empty] | 2651 | 131 | 7.1034 | 5.3248
[7 empty] | 2652 | 132 | 6.8528 | 5.1283
[7 empty] | 2653 | 133 | 7.4875 | 5.626
[7 empty] | 2654 | 134 | 7.7882 | 5.8617
[7 empty] | 2655 | 135 | 7.855 | 5.9141
[7 empty] | 2656 | 136 | 7.0449 | 5.2789
[7 empty] | 2657 | 137 | 6.9447 | 5.2003
[7 empty] | 2658 | 138 | 6.8946 | 5.1611
[7 empty] | 2659 | 139 | 6.5605 | 4.8991
[7 empty] | 2660 | 140 | 6.5689 | 4.9057
[7 empty] | 2661 | 141 | 5.9175 | 4.3949
[7 empty] | 2662 | 142 | 5.2828 | 3.8973
[7 empty] | 2663 | 143 | 4.406 | 3.2098
[7 empty] | 2664 | 144 | 3.7963 | 2.7318
[7 empty] | 2665 | 145 | 3.3287 | 2.3651
[7 empty] | 2666 | 146 | 3.1199 | 2.2014
[7 empty] | 2667 | 147 | 3.0531 | 2.149
[7 empty] | 2668 | 148 | 3.0447 | 2.1424
[7 empty] | 2669 | 149 | 3.0447 | 2.1424
[7 empty] | 2670 | 150 | 3.0531 | 2.149
[7 empty] | 2671 | 151 | 4.1304 | 2.9937
[7 empty] | 2672 | 152 | 5.6503 | 4.1854
[7 empty] | 2673 | 153 | 6.2599 | 4.6634
[7 empty] | 2674 | 154 | 6.8194 | 5.1021
[7 empty] | 2675 | 155 | 6.6691 | 4.9843
[7 empty] | 2676 | 156 | 6.8361 | 5.1152
[7 empty] | 2677 | 157 | 7.546 | 5.6718
[7 empty] | 2678 | 158 | 7.8717 | 5.9272
[7 empty] | 2679 | 159 | 8.1389 | 6.1367
[7 empty] | 2680 | 160 | 8.0136 | 6.0385
[7 empty] | 2681 | 161 | 8.7736 | 6.6343
[7 empty] | 2682 | 162 | 8.2809 | 6.248
[7 empty] | 2683 | 163 | 8.64 | 6.5296
[7 empty] | 2684 | 164 | 7.2954 | 5.4754
[7 empty] | 2685 | 165 | 10.4104 | 7.9177
[7 empty] | 2686 | 166 | 8.3727 | 6.32
[7 empty] | 2687 | 167 | 4.7818 | 3.5044
[7 empty] | 2688 | 168 | 4.1387 | 3.0002
[7 empty] | 2689 | 1 | 2.6856 | 1.8609
[7 empty] | 2690 | 2 | 2.5771 | 1.7758
[7 empty] | 2691 | 3 | 2.5687 | 1.7692
[7 empty] | 2692 | 4 | 2.7023 | 1.874
[7 empty] | 2693 | 5 | 2.719 | 1.8871
[7 empty] | 2694 | 6 | 3.1449 | 2.221
[7 empty] | 2695 | 7 | 3.8631 | 2.7841
[7 empty] | 2696 | 8 | 4.5312 | 3.308
[7 empty] | 2697 | 9 | 4.5062 | 3.2883
[7 empty] | 2698 | 10 | 6.0177 | 4.4735
[7 empty] | 2699 | 11 | 8.0888 | 6.0974
[7 empty] | 2700 | 12 | 9.0492 | 6.8504
[7 empty] | 2701 | 13 | 9.425 | 7.1451
[7 empty] | 2702 | 14 | 9.2079 | 6.9748
[7 empty] | 2703 | 15 | 9.116 | 6.9028
[7 empty] | 2704 | 16 | 10.2935 | 7.8261
[7 empty] | 2705 | 17 | 11.613 | 8.8607
[7 empty] | 2706 | 18 | 11.3708 | 8.6708
[7 empty] | 2707 | 19 | 11.8969 | 9.0833
[7 empty] | 2708 | 20 | 11.8301 | 9.0309
[7 empty] | 2709 | 21 | 12.398 | 9.4762
[7 empty] | 2710 | 22 | 8.4563 | 6.3855
[7 empty] | 2711 | 23 | 4.6983 | 3.4389
[7 empty] | 2712 | 24 | 3.0331 | 2.1333
[7 empty] | 2713 | 25 | 2.9362 | 2.0573
[7 empty] | 2714 | 26 | 2.8276 | 1.9722
[7 empty] | 2715 | 27 | 2.7274 | 1.8936
[7 empty] | 2716 | 28 | 2.8109 | 1.9591
[7 empty] | 2717 | 29 | 3.0531 | 2.149
[7 empty] | 2718 | 30 | 3.2953 | 2.3389
[7 empty] | 2719 | 31 | 4.1387 | 3.0002
[7 empty] | 2720 | 32 | 4.4895 | 3.2752
[7 empty] | 2721 | 33 | 5.1492 | 3.7925
[7 empty] | 2722 | 34 | 6.0428 | 4.4932
[7 empty] | 2723 | 35 | 8.2057 | 6.1891
[7 empty] | 2724 | 36 | 9.2329 | 6.9945
[7 empty] | 2725 | 37 | 9.3081 | 7.0534
[7 empty] | 2726 | 38 | 9.3832 | 7.1123
[7 empty] | 2727 | 39 | 9.0575 | 6.857
[7 empty] | 2728 | 40 | 10.1098 | 7.682
[7 empty] | 2729 | 41 | 10.6609 | 8.1142
[7 empty] | 2730 | 42 | 10.6776 | 8.1273
[7 empty] | 2731 | 43 | 11.0451 | 8.4154
[7 empty] | 2732 | 44 | 12.1975 | 9.319
[7 empty] | 2733 | 45 | 11.7967 | 9.0047
[7 empty] | 2734 | 46 | 9.0575 | 6.857
[7 empty] | 2735 | 47 | 5.4666 | 4.0414
[7 empty] | 2736 | 48 | 3.9717 | 2.8693
[7 empty] | 2737 | 49 | 3.312 | 2.352
[7 empty] | 2738 | 50 | 3.003 | 2.1097
[7 empty] | 2739 | 51 | 2.8944 | 2.0246
[7 empty] | 2740 | 52 | 2.9278 | 2.0508
[7 empty] | 2741 | 53 | 2.9529 | 2.0704
[7 empty] | 2742 | 54 | 3.5291 | 2.5222
[7 empty] | 2743 | 55 | 4.6648 | 3.4128
[7 empty] | 2744 | 56 | 4.907 | 3.6026
[7 empty] | 2745 | 57 | 5.8507 | 4.3426
[7 empty] | 2746 | 58 | 6.9531 | 5.2069
[7 empty] | 2747 | 59 | 8.1556 | 6.1498
[7 empty] | 2748 | 60 | 8.7819 | 6.6409
[7 empty] | 2749 | 61 | 9.4584 | 7.1713
[7 empty] | 2750 | 62 | 9.258 | 7.0141
[7 empty] | 2751 | 63 | 9.8509 | 7.479
[7 empty] | 2752 | 64 | 10.7946 | 8.219
[7 empty] | 2753 | 65 | 11.4125 | 8.7035
[7 empty] | 2754 | 66 | 11.3123 | 8.6249
[7 empty] | 2755 | 67 | 12.0472 | 9.2011
[7 empty] | 2756 | 68 | 12.2894 | 9.391
[7 empty] | 2757 | 69 | 11.78 | 8.9916
[7 empty] | 2758 | 70 | 9.4918 | 7.1975
[7 empty] | 2759 | 71 | 4.9905 | 3.6681
[7 empty] | 2760 | 72 | 3.9097 | 2.8206
[7 empty] | 2761 | 73 | 3.1951 | 2.2603
[7 empty] | 2762 | 74 | 2.9696 | 2.0835
[7 empty] | 2763 | 75 | 2.8694 | 2.0049
[7 empty] | 2764 | 76 | 2.8109 | 1.9591
[7 empty] | 2765 | 77 | 2.9863 | 2.0966
[7 empty] | 2766 | 78 | 3.3871 | 2.4109
[7 empty] | 2767 | 79 | 4.4978 | 3.2818
[7 empty] | 2768 | 80 | 4.6732 | 3.4193
[7 empty] | 2769 | 81 | 5.8507 | 4.3426
[7 empty] | 2770 | 82 | 6.9363 | 5.1938
[7 empty] | 2771 | 83 | 7.6712 | 5.77
[7 empty] | 2772 | 84 | 8.9072 | 6.7391
[7 empty] | 2773 | 85 | 8.6066 | 6.5034
[7 empty] | 2774 | 86 | 8.0972 | 6.104
[7 empty] | 2775 | 87 | 8.5398 | 6.451
[7 empty] | 2776 | 88 | 9.1995 | 6.9683
[7 empty] | 2777 | 89 | 10.544 | 8.0225
[7 empty] | 2778 | 90 | 9.9595 | 7.5642
[7 empty] | 2779 | 91 | 10.6442 | 8.1011
[7 empty] | 2780 | 92 | 10.043 | 7.6296
[7 empty] | 2781 | 93 | 7.6378 | 5.7438
[7 empty] | 2782 | 94 | 6.7359 | 5.0366
[7 empty] | 2783 | 95 | 4.882 | 3.583
[7 empty] | 2784 | 96 | 3.8965 | 2.8103
[7 empty] | 2785 | 97 | 3.8464 | 2.7711
[7 empty] | 2786 | 98 | 3.5541 | 2.5419
[7 empty] | 2787 | 99 | 3.4957 | 2.496
[7 empty] | 2788 | 100 | 3.1449 | 2.221
[7 empty] | 2789 | 101 | 3.0865 | 2.1752
[7 empty] | 2790 | 102 | 3.3203 | 2.3585
[7 empty] | 2791 | 103 | 4.0636 | 2.9413
[7 empty] | 2792 | 104 | 4.3141 | 3.1377
[7 empty] | 2793 | 105 | 4.7985 | 3.5175
[7 empty] | 2794 | 106 | 6.2516 | 4.6569
[7 empty] | 2795 | 107 | 6.6023 | 4.9319
[7 empty] | 2796 | 108 | 8.1723 | 6.1629
[7 empty] | 2797 | 109 | 7.5126 | 5.6456
[7 empty] | 2798 | 110 | 7.0616 | 5.292
[7 empty] | 2799 | 111 | 6.9029 | 5.1676
[7 empty] | 2800 | 112 | 6.9698 | 5.22
[7 empty] | 2801 | 113 | 6.6274 | 4.9515
[7 empty] | 2802 | 114 | 6.7944 | 5.0825
[7 empty] | 2803 | 115 | 6.3434 | 4.7289
[7 empty] | 2804 | 116 | 7.0199 | 5.2593
[7 empty] | 2805 | 117 | 6.6023 | 4.9319
[7 empty] | 2806 | 118 | 5.834 | 4.3295
[7 empty] | 2807 | 119 | 4.2473 | 3.0854
[7 empty] | 2808 | 120 | 3.9311 | 2.8374
[7 empty] | 2809 | 121 | 3.2034 | 2.2669
[7 empty] | 2810 | 122 | 2.7942 | 1.946
[7 empty] | 2811 | 123 | 2.7107 | 1.8805
[7 empty] | 2812 | 124 | 2.6773 | 1.8543
[7 empty] | 2813 | 125 | 2.6355 | 1.8216
[7 empty] | 2814 | 126 | 2.7775 | 1.9329
[7 empty] | 2815 | 127 | 4.2807 | 3.1115
[7 empty] | 2816 | 128 | 5.834 | 4.3295
[7 empty] | 2817 | 129 | 6.5104 | 4.8599
[7 empty] | 2818 | 130 | 6.9447 | 5.2003
[7 empty] | 2819 | 131 | 7.1034 | 5.3248
[7 empty] | 2820 | 132 | 6.8528 | 5.1283
[7 empty] | 2821 | 133 | 7.4875 | 5.626
[7 empty] | 2822 | 134 | 7.7882 | 5.8617
[7 empty] | 2823 | 135 | 7.855 | 5.9141
[7 empty] | 2824 | 136 | 7.0449 | 5.2789
[7 empty] | 2825 | 137 | 6.9447 | 5.2003
[7 empty] | 2826 | 138 | 6.8946 | 5.1611
[7 empty] | 2827 | 139 | 6.5605 | 4.8991
[7 empty] | 2828 | 140 | 6.5689 | 4.9057
[7 empty] | 2829 | 141 | 5.9175 | 4.3949
[7 empty] | 2830 | 142 | 5.2828 | 3.8973
[7 empty] | 2831 | 143 | 4.406 | 3.2098
[7 empty] | 2832 | 144 | 3.7963 | 2.7318
[7 empty] | 2833 | 145 | 3.3287 | 2.3651
[7 empty] | 2834 | 146 | 3.1199 | 2.2014
[7 empty] | 2835 | 147 | 3.0531 | 2.149
[7 empty] | 2836 | 148 | 3.0447 | 2.1424
[7 empty] | 2837 | 149 | 3.0447 | 2.1424
[7 empty] | 2838 | 150 | 3.0531 | 2.149
[7 empty] | 2839 | 151 | 4.1304 | 2.9937
[7 empty] | 2840 | 152 | 5.6503 | 4.1854
[7 empty] | 2841 | 153 | 6.2599 | 4.6634
[7 empty] | 2842 | 154 | 6.8194 | 5.1021
[7 empty] | 2843 | 155 | 6.6691 | 4.9843
[7 empty] | 2844 | 156 | 6.8361 | 5.1152
[7 empty] | 2845 | 157 | 7.546 | 5.6718
[7 empty] | 2846 | 158 | 7.8717 | 5.9272
[7 empty] | 2847 | 159 | 8.1389 | 6.1367
[7 empty] | 2848 | 160 | 8.0136 | 6.0385
[7 empty] | 2849 | 161 | 8.7736 | 6.6343
[7 empty] | 2850 | 162 | 8.2809 | 6.248
[7 empty] | 2851 | 163 | 8.64 | 6.5296
[7 empty] | 2852 | 164 | 7.2954 | 5.4754
[7 empty] | 2853 | 165 | 10.4104 | 7.9177
[7 empty] | 2854 | 166 | 8.3727 | 6.32
[7 empty] | 2855 | 167 | 4.7818 | 3.5044
[7 empty] | 2856 | 168 | 4.1387 | 3.0002
[7 empty] | 2857 | 1 | 2.6856 | 1.8609
[7 empty] | 2858 | 2 | 2.5771 | 1.7758
[7 empty] | 2859 | 3 | 2.5687 | 1.7692
[7 empty] | 2860 | 4 | 2.7023 | 1.874
[7 empty] | 2861 | 5 | 2.719 | 1.8871
[7 empty] | 2862 | 6 | 3.1449 | 2.221
[7 empty] | 2863 | 7 | 3.8631 | 2.7841
[7 empty] | 2864 | 8 | 4.5312 | 3.308
[7 empty] | 2865 | 9 | 4.5062 | 3.2883
[7 empty] | 2866 | 10 | 6.0177 | 4.4735
[7 empty] | 2867 | 11 | 8.0888 | 6.0974
[7 empty] | 2868 | 12 | 9.0492 | 6.8504
[7 empty] | 2869 | 13 | 9.425 | 7.1451
[7 empty] | 2870 | 14 | 9.2079 | 6.9748
[7 empty] | 2871 | 15 | 9.116 | 6.9028
[7 empty] | 2872 | 16 | 10.2935 | 7.8261
[7 empty] | 2873 | 17 | 11.613 | 8.8607
[7 empty] | 2874 | 18 | 11.3708 | 8.6708
[7 empty] | 2875 | 19 | 11.8969 | 9.0833
[7 empty] | 2876 | 20 | 11.8301 | 9.0309
[7 empty] | 2877 | 21 | 12.398 | 9.4762
[7 empty] | 2878 | 22 | 8.4563 | 6.3855
[7 empty] | 2879 | 23 | 4.6983 | 3.4389
[7 empty] | 2880 | 24 | 3.0331 | 2.1333
[7 empty] | 2881 | 25 | 2.9362 | 2.0573
[7 empty] | 2882 | 26 | 2.8276 | 1.9722
[7 empty] | 2883 | 27 | 2.7274 | 1.8936
[7 empty] | 2884 | 28 | 2.8109 | 1.9591
[7 empty] | 2885 | 29 | 3.0531 | 2.149
[7 empty] | 2886 | 30 | 3.2953 | 2.3389
[7 empty] | 2887 | 31 | 4.1387 | 3.0002
[7 empty] | 2888 | 32 | 4.4895 | 3.2752
[7 empty] | 2889 | 33 | 5.1492 | 3.7925
[7 empty] | 2890 | 34 | 6.0428 | 4.4932
[7 empty] | 2891 | 35 | 8.2057 | 6.1891
[7 empty] | 2892 | 36 | 9.2329 | 6.9945
[7 empty] | 2893 | 37 | 9.3081 | 7.0534
[7 empty] | 2894 | 38 | 9.3832 | 7.1123
[7 empty] | 2895 | 39 | 9.0575 | 6.857
[7 empty] | 2896 | 40 | 10.1098 | 7.682
[7 empty] | 2897 | 41 | 10.6609 | 8.1142
[7 empty] | 2898 | 42 | 10.6776 | 8.1273
[7 empty] | 2899 | 43 | 11.0451 | 8.4154
[7 empty] | 2900 | 44 | 12.1975 | 9.319
[7 empty] | 2901 | 45 | 11.7967 | 9.0047
[7 empty] | 2902 | 46 | 9.0575 | 6.857
[7 empty] | 2903 | 47 | 5.4666 | 4.0414
[7 empty] | 2904 | 48 | 3.9717 | 2.8693
[7 empty] | 2905 | 49 | 3.312 | 2.352
[7 empty] | 2906 | 50 | 3.003 | 2.1097
[7 empty] | 2907 | 51 | 2.8944 | 2.0246
[7 empty] | 2908 | 52 | 2.9278 | 2.0508
[7 empty] | 2909 | 53 | 2.9529 | 2.0704
[7 empty] | 2910 | 54 | 3.5291 | 2.5222
[7 empty] | 2911 | 55 | 4.6648 | 3.4128
[7 empty] | 2912 | 56 | 4.907 | 3.6026
[7 empty] | 2913 | 57 | 5.8507 | 4.3426
[7 empty] | 2914 | 58 | 6.9531 | 5.2069
[7 empty] | 2915 | 59 | 8.1556 | 6.1498
[7 empty] | 2916 | 60 | 8.7819 | 6.6409
[7 empty] | 2917 | 61 | 9.4584 | 7.1713
[7 empty] | 2918 | 62 | 9.258 | 7.0141
[7 empty] | 2919 | 63 | 9.8509 | 7.479
[7 empty] | 2920 | 64 | 10.7946 | 8.219
[7 empty] | 2921 | 65 | 11.4125 | 8.7035
[7 empty] | 2922 | 66 | 11.3123 | 8.6249
[7 empty] | 2923 | 67 | 12.0472 | 9.2011
[7 empty] | 2924 | 68 | 12.2894 | 9.391
[7 empty] | 2925 | 69 | 11.78 | 8.9916
[7 empty] | 2926 | 70 | 9.4918 | 7.1975
[7 empty] | 2927 | 71 | 4.9905 | 3.6681
[7 empty] | 2928 | 72 | 3.9097 | 2.8206
[7 empty] | 2929 | 73 | 3.1951 | 2.2603
[7 empty] | 2930 | 74 | 2.9696 | 2.0835
[7 empty] | 2931 | 75 | 2.8694 | 2.0049
[7 empty] | 2932 | 76 | 2.8109 | 1.9591
[7 empty] | 2933 | 77 | 2.9863 | 2.0966
[7 empty] | 2934 | 78 | 3.3871 | 2.4109
[7 empty] | 2935 | 79 | 4.4978 | 3.2818
[7 empty] | 2936 | 80 | 4.6732 | 3.4193
[7 empty] | 2937 | 81 | 5.8507 | 4.3426
[7 empty] | 2938 | 82 | 6.9363 | 5.1938
[7 empty] | 2939 | 83 | 7.6712 | 5.77
[7 empty] | 2940 | 84 | 8.9072 | 6.7391
[7 empty] | 2941 | 85 | 8.6066 | 6.5034
[7 empty] | 2942 | 86 | 8.0972 | 6.104
[7 empty] | 2943 | 87 | 8.5398 | 6.451
[7 empty] | 2944 | 88 | 9.1995 | 6.9683
[7 empty] | 2945 | 89 | 10.544 | 8.0225
[7 empty] | 2946 | 90 | 9.9595 | 7.5642
[7 empty] | 2947 | 91 | 10.6442 | 8.1011
[7 empty] | 2948 | 92 | 10.043 | 7.6296
[7 empty] | 2949 | 93 | 7.6378 | 5.7438
[7 empty] | 2950 | 94 | 6.7359 | 5.0366
[7 empty] | 2951 | 95 | 4.882 | 3.583
[7 empty] | 2952 | 96 | 3.8965 | 2.8103
[7 empty] | 2953 | 97 | 3.8464 | 2.7711
[7 empty] | 2954 | 98 | 3.5541 | 2.5419
[7 empty] | 2955 | 99 | 3.4957 | 2.496
[7 empty] | 2956 | 100 | 3.1449 | 2.221
[7 empty] | 2957 | 101 | 3.0865 | 2.1752
[7 empty] | 2958 | 102 | 3.3203 | 2.3585
[7 empty] | 2959 | 103 | 4.0636 | 2.9413
[7 empty] | 2960 | 104 | 4.3141 | 3.1377
[7 empty] | 2961 | 105 | 4.7985 | 3.5175
[7 empty] | 2962 | 106 | 6.2516 | 4.6569
[7 empty] | 2963 | 107 | 6.6023 | 4.9319
[7 empty] | 2964 | 108 | 8.1723 | 6.1629
[7 empty] | 2965 | 109 | 7.5126 | 5.6456
[7 empty] | 2966 | 110 | 7.0616 | 5.292
[7 empty] | 2967 | 111 | 6.9029 | 5.1676
[7 empty] | 2968 | 112 | 6.9698 | 5.22
[7 empty] | 2969 | 113 | 6.6274 | 4.9515
[7 empty] | 2970 | 114 | 6.7944 | 5.0825
[7 empty] | 2971 | 115 | 6.3434 | 4.7289
[7 empty] | 2972 | 116 | 7.0199 | 5.2593
[7 empty] | 2973 | 117 | 6.6023 | 4.9319
[7 empty] | 2974 | 118 | 5.834 | 4.3295
[7 empty] | 2975 | 119 | 4.2473 | 3.0854
[7 empty] | 2976 | 120 | 3.9311 | 2.8374
[7 empty] | 2977 | 121 | 3.2034 | 2.2669
[7 empty] | 2978 | 122 | 2.7942 | 1.946
[7 empty] | 2979 | 123 | 2.7107 | 1.8805
[7 empty] | 2980 | 124 | 2.6773 | 1.8543
[7 empty] | 2981 | 125 | 2.6355 | 1.8216
[7 empty] | 2982 | 126 | 2.7775 | 1.9329
[7 empty] | 2983 | 127 | 4.2807 | 3.1115
[7 empty] | 2984 | 128 | 5.834 | 4.3295
[7 empty] | 2985 | 129 | 6.5104 | 4.8599
[7 empty] | 2986 | 130 | 6.9447 | 5.2003
[7 empty] | 2987 | 131 | 7.1034 | 5.3248
[7 empty] | 2988 | 132 | 6.8528 | 5.1283
[7 empty] | 2989 | 133 | 7.4875 | 5.626
[7 empty] | 2990 | 134 | 7.7882 | 5.8617
[7 empty] | 2991 | 135 | 7.855 | 5.9141
[7 empty] | 2992 | 136 | 7.0449 | 5.2789
[7 empty] | 2993 | 137 | 6.9447 | 5.2003
[7 empty] | 2994 | 138 | 6.8946 | 5.1611
[7 empty] | 2995 | 139 | 6.5605 | 4.8991
[7 empty] | 2996 | 140 | 6.5689 | 4.9057
[7 empty] | 2997 | 141 | 5.9175 | 4.3949
[7 empty] | 2998 | 142 | 5.2828 | 3.8973
[7 empty] | 2999 | 143 | 4.406 | 3.2098
[7 empty] | 3000 | 144 | 3.7963 | 2.7318
[7 empty] | 3001 | 145 | 3.3287 | 2.3651
[7 empty] | 3002 | 146 | 3.1199 | 2.2014
[7 empty] | 3003 | 147 | 3.0531 | 2.149
[7 empty] | 3004 | 148 | 3.0447 | 2.1424
[7 empty] | 3005 | 149 | 3.0447 | 2.1424
[7 empty] | 3006 | 150 | 3.0531 | 2.149
[7 empty] | 3007 | 151 | 4.1304 | 2.9937
[7 empty] | 3008 | 152 | 5.6503 | 4.1854
[7 empty] | 3009 | 153 | 6.2599 | 4.6634
[7 empty] | 3010 | 154 | 6.8194 | 5.1021
[7 empty] | 3011 | 155 | 6.6691 | 4.9843
[7 empty] | 3012 | 156 | 6.8361 | 5.1152
[7 empty] | 3013 | 157 | 7.546 | 5.6718
[7 empty] | 3014 | 158 | 7.8717 | 5.9272
[7 empty] | 3015 | 159 | 8.1389 | 6.1367
[7 empty] | 3016 | 160 | 8.0136 | 6.0385
[7 empty] | 3017 | 161 | 8.7736 | 6.6343
[7 empty] | 3018 | 162 | 8.2809 | 6.248
[7 empty] | 3019 | 163 | 8.64 | 6.5296
[7 empty] | 3020 | 164 | 7.2954 | 5.4754
[7 empty] | 3021 | 165 | 10.4104 | 7.9177
[7 empty] | 3022 | 166 | 8.3727 | 6.32
[7 empty] | 3023 | 167 | 4.7818 | 3.5044
[7 empty] | 3024 | 168 | 4.1387 | 3.0002
[7 empty] | 3025 | 1 | 2.6856 | 1.8609
[7 empty] | 3026 | 2 | 2.5771 | 1.7758
[7 empty] | 3027 | 3 | 2.5687 | 1.7692
[7 empty] | 3028 | 4 | 2.7023 | 1.874
[7 empty] | 3029 | 5 | 2.719 | 1.8871
[7 empty] | 3030 | 6 | 3.1449 | 2.221
[7 empty] | 3031 | 7 | 3.8631 | 2.7841
[7 empty] | 3032 | 8 | 4.5312 | 3.308
[7 empty] | 3033 | 9 | 4.5062 | 3.2883
[7 empty] | 3034 | 10 | 6.0177 | 4.4735
[7 empty] | 3035 | 11 | 8.0888 | 6.0974
[7 empty] | 3036 | 12 | 9.0492 | 6.8504
[7 empty] | 3037 | 13 | 9.425 | 7.1451
[7 empty] | 3038 | 14 | 9.2079 | 6.9748
[7 empty] | 3039 | 15 | 9.116 | 6.9028
[7 empty] | 3040 | 16 | 10.2935 | 7.8261
[7 empty] | 3041 | 17 | 11.613 | 8.8607
[7 empty] | 3042 | 18 | 11.3708 | 8.6708
[7 empty] | 3043 | 19 | 11.8969 | 9.0833
[7 empty] | 3044 | 20 | 11.8301 | 9.0309
[7 empty] | 3045 | 21 | 12.398 | 9.4762
[7 empty] | 3046 | 22 | 8.4563 | 6.3855
[7 empty] | 3047 | 23 | 4.6983 | 3.4389
[7 empty] | 3048 | 24 | 3.0331 | 2.1333
[7 empty] | 3049 | 25 | 2.9362 | 2.0573
[7 empty] | 3050 | 26 | 2.8276 | 1.9722
[7 empty] | 3051 | 27 | 2.7274 | 1.8936
[7 empty] | 3052 | 28 | 2.8109 | 1.9591
[7 empty] | 3053 | 29 | 3.0531 | 2.149
[7 empty] | 3054 | 30 | 3.2953 | 2.3389
[7 empty] | 3055 | 31 | 4.1387 | 3.0002
[7 empty] | 3056 | 32 | 4.4895 | 3.2752
[7 empty] | 3057 | 33 | 5.1492 | 3.7925
[7 empty] | 3058 | 34 | 6.0428 | 4.4932
[7 empty] | 3059 | 35 | 8.2057 | 6.1891
[7 empty] | 3060 | 36 | 9.2329 | 6.9945
[7 empty] | 3061 | 37 | 9.3081 | 7.0534
[7 empty] | 3062 | 38 | 9.3832 | 7.1123
[7 empty] | 3063 | 39 | 9.0575 | 6.857
[7 empty] | 3064 | 40 | 10.1098 | 7.682
[7 empty] | 3065 | 41 | 10.6609 | 8.1142
[7 empty] | 3066 | 42 | 10.6776 | 8.1273
[7 empty] | 3067 | 43 | 11.0451 | 8.4154
[7 empty] | 3068 | 44 | 12.1975 | 9.319
[7 empty] | 3069 | 45 | 11.7967 | 9.0047
[7 empty] | 3070 | 46 | 9.0575 | 6.857
[7 empty] | 3071 | 47 | 5.4666 | 4.0414
[7 empty] | 3072 | 48 | 3.9717 | 2.8693
[7 empty] | 3073 | 49 | 3.312 | 2.352
[7 empty] | 3074 | 50 | 3.003 | 2.1097
[7 empty] | 3075 | 51 | 2.8944 | 2.0246
[7 empty] | 3076 | 52 | 2.9278 | 2.0508
[7 empty] | 3077 | 53 | 2.9529 | 2.0704
[7 empty] | 3078 | 54 | 3.5291 | 2.5222
[7 empty] | 3079 | 55 | 4.6648 | 3.4128
[7 empty] | 3080 | 56 | 4.907 | 3.6026
[7 empty] | 3081 | 57 | 5.8507 | 4.3426
[7 empty] | 3082 | 58 | 6.9531 | 5.2069
[7 empty] | 3083 | 59 | 8.1556 | 6.1498
[7 empty] | 3084 | 60 | 8.7819 | 6.6409
[7 empty] | 3085 | 61 | 9.4584 | 7.1713
[7 empty] | 3086 | 62 | 9.258 | 7.0141
[7 empty] | 3087 | 63 | 9.8509 | 7.479
[7 empty] | 3088 | 64 | 10.7946 | 8.219
[7 empty] | 3089 | 65 | 11.4125 | 8.7035
[7 empty] | 3090 | 66 | 11.3123 | 8.6249
[7 empty] | 3091 | 67 | 12.0472 | 9.2011
[7 empty] | 3092 | 68 | 12.2894 | 9.391
[7 empty] | 3093 | 69 | 11.78 | 8.9916
[7 empty] | 3094 | 70 | 9.4918 | 7.1975
[7 empty] | 3095 | 71 | 4.9905 | 3.6681
[7 empty] | 3096 | 72 | 3.9097 | 2.8206
[7 empty] | 3097 | 73 | 3.1951 | 2.2603
[7 empty] | 3098 | 74 | 2.9696 | 2.0835
[7 empty] | 3099 | 75 | 2.8694 | 2.0049
[7 empty] | 3100 | 76 | 2.8109 | 1.9591
[7 empty] | 3101 | 77 | 2.9863 | 2.0966
[7 empty] | 3102 | 78 | 3.3871 | 2.4109
[7 empty] | 3103 | 79 | 4.4978 | 3.2818
[7 empty] | 3104 | 80 | 4.6732 | 3.4193
[7 empty] | 3105 | 81 | 5.8507 | 4.3426
[7 empty] | 3106 | 82 | 6.9363 | 5.1938
[7 empty] | 3107 | 83 | 7.6712 | 5.77
[7 empty] | 3108 | 84 | 8.9072 | 6.7391
[7 empty] | 3109 | 85 | 8.6066 | 6.5034
[7 empty] | 3110 | 86 | 8.0972 | 6.104
[7 empty] | 3111 | 87 | 8.5398 | 6.451
[7 empty] | 3112 | 88 | 9.1995 | 6.9683
[7 empty] | 3113 | 89 | 10.544 | 8.0225
[7 empty] | 3114 | 90 | 9.9595 | 7.5642
[7 empty] | 3115 | 91 | 10.6442 | 8.1011
[7 empty] | 3116 | 92 | 10.043 | 7.6296
[7 empty] | 3117 | 93 | 7.6378 | 5.7438
[7 empty] | 3118 | 94 | 6.7359 | 5.0366
[7 empty] | 3119 | 95 | 4.882 | 3.583
[7 empty] | 3120 | 96 | 3.8965 | 2.8103
[7 empty] | 3121 | 97 | 3.8464 | 2.7711
[7 empty] | 3122 | 98 | 3.5541 | 2.5419
[7 empty] | 3123 | 99 | 3.4957 | 2.496
[7 empty] | 3124 | 100 | 3.1449 | 2.221
[7 empty] | 3125 | 101 | 3.0865 | 2.1752
[7 empty] | 3126 | 102 | 3.3203 | 2.3585
[7 empty] | 3127 | 103 | 4.0636 | 2.9413
[7 empty] | 3128 | 104 | 4.3141 | 3.1377
[7 empty] | 3129 | 105 | 4.7985 | 3.5175
[7 empty] | 3130 | 106 | 6.2516 | 4.6569
[7 empty] | 3131 | 107 | 6.6023 | 4.9319
[7 empty] | 3132 | 108 | 8.1723 | 6.1629
[7 empty] | 3133 | 109 | 7.5126 | 5.6456
[7 empty] | 3134 | 110 | 7.0616 | 5.292
[7 empty] | 3135 | 111 | 6.9029 | 5.1676
[7 empty] | 3136 | 112 | 6.9698 | 5.22
[7 empty] | 3137 | 113 | 6.6274 | 4.9515
[7 empty] | 3138 | 114 | 6.7944 | 5.0825
[7 empty] | 3139 | 115 | 6.3434 | 4.7289
[7 empty] | 3140 | 116 | 7.0199 | 5.2593
[7 empty] | 3141 | 117 | 6.6023 | 4.9319
[7 empty] | 3142 | 118 | 5.834 | 4.3295
[7 empty] | 3143 | 119 | 4.2473 | 3.0854
[7 empty] | 3144 | 120 | 3.9311 | 2.8374
[7 empty] | 3145 | 121 | 3.2034 | 2.2669
[7 empty] | 3146 | 122 | 2.7942 | 1.946
[7 empty] | 3147 | 123 | 2.7107 | 1.8805
[7 empty] | 3148 | 124 | 2.6773 | 1.8543
[7 empty] | 3149 | 125 | 2.6355 | 1.8216
[7 empty] | 3150 | 126 | 2.7775 | 1.9329
[7 empty] | 3151 | 127 | 4.2807 | 3.1115
[7 empty] | 3152 | 128 | 5.834 | 4.3295
[7 empty] | 3153 | 129 | 6.5104 | 4.8599
[7 empty] | 3154 | 130 | 6.9447 | 5.2003
[7 empty] | 3155 | 131 | 7.1034 | 5.3248
[7 empty] | 3156 | 132 | 6.8528 | 5.1283
[7 empty] | 3157 | 133 | 7.4875 | 5.626
[7 empty] | 3158 | 134 | 7.7882 | 5.8617
[7 empty] | 3159 | 135 | 7.855 | 5.9141
[7 empty] | 3160 | 136 | 7.0449 | 5.2789
[7 empty] | 3161 | 137 | 6.9447 | 5.2003
[7 empty] | 3162 | 138 | 6.8946 | 5.1611
[7 empty] | 3163 | 139 | 6.5605 | 4.8991
[7 empty] | 3164 | 140 | 6.5689 | 4.9057
[7 empty] | 3165 | 141 | 5.9175 | 4.3949
[7 empty] | 3166 | 142 | 5.2828 | 3.8973
[7 empty] | 3167 | 143 | 4.406 | 3.2098
[7 empty] | 3168 | 144 | 3.7963 | 2.7318
[7 empty] | 3169 | 145 | 3.3287 | 2.3651
[7 empty] | 3170 | 146 | 3.1199 | 2.2014
[7 empty] | 3171 | 147 | 3.0531 | 2.149
[7 empty] | 3172 | 148 | 3.0447 | 2.1424
[7 empty] | 3173 | 149 | 3.0447 | 2.1424
[7 empty] | 3174 | 150 | 3.0531 | 2.149
[7 empty] | 3175 | 151 | 4.1304 | 2.9937
[7 empty] | 3176 | 152 | 5.6503 | 4.1854
[7 empty] | 3177 | 153 | 6.2599 | 4.6634
[7 empty] | 3178 | 154 | 6.8194 | 5.1021
[7 empty] | 3179 | 155 | 6.6691 | 4.9843
[7 empty] | 3180 | 156 | 6.8361 | 5.1152
[7 empty] | 3181 | 157 | 7.546 | 5.6718
[7 empty] | 3182 | 158 | 7.8717 | 5.9272
[7 empty] | 3183 | 159 | 8.1389 | 6.1367
[7 empty] | 3184 | 160 | 8.0136 | 6.0385
[7 empty] | 3185 | 161 | 8.7736 | 6.6343
[7 empty] | 3186 | 162 | 8.2809 | 6.248
[7 empty] | 3187 | 163 | 8.64 | 6.5296
[7 empty] | 3188 | 164 | 7.2954 | 5.4754
[7 empty] | 3189 | 165 | 10.4104 | 7.9177
[7 empty] | 3190 | 166 | 8.3727 | 6.32
[7 empty] | 3191 | 167 | 4.7818 | 3.5044
[7 empty] | 3192 | 168 | 4.1387 | 3.0002
[7 empty] | 3193 | 1 | 2.6856 | 1.8609
[7 empty] | 3194 | 2 | 2.5771 | 1.7758
[7 empty] | 3195 | 3 | 2.5687 | 1.7692
[7 empty] | 3196 | 4 | 2.7023 | 1.874
[7 empty] | 3197 | 5 | 2.719 | 1.8871
[7 empty] | 3198 | 6 | 3.1449 | 2.221
[7 empty] | 3199 | 7 | 3.8631 | 2.7841
[7 empty] | 3200 | 8 | 4.5312 | 3.308
[7 empty] | 3201 | 9 | 4.5062 | 3.2883
[7 empty] | 3202 | 10 | 6.0177 | 4.4735
[7 empty] | 3203 | 11 | 8.0888 | 6.0974
[7 empty] | 3204 | 12 | 9.0492 | 6.8504
[7 empty] | 3205 | 13 | 9.425 | 7.1451
[7 empty] | 3206 | 14 | 9.2079 | 6.9748
[7 empty] | 3207 | 15 | 9.116 | 6.9028
[7 empty] | 3208 | 16 | 10.2935 | 7.8261
[7 empty] | 3209 | 17 | 11.613 | 8.8607
[7 empty] | 3210 | 18 | 11.3708 | 8.6708
[7 empty] | 3211 | 19 | 11.8969 | 9.0833
[7 empty] | 3212 | 20 | 11.8301 | 9.0309
[7 empty] | 3213 | 21 | 12.398 | 9.4762
[7 empty] | 3214 | 22 | 8.4563 | 6.3855
[7 empty] | 3215 | 23 | 4.6983 | 3.4389
[7 empty] | 3216 | 24 | 3.0331 | 2.1333
[7 empty] | 3217 | 25 | 2.9362 | 2.0573
[7 empty] | 3218 | 26 | 2.8276 | 1.9722
[7 empty] | 3219 | 27 | 2.7274 | 1.8936
[7 empty] | 3220 | 28 | 2.8109 | 1.9591
[7 empty] | 3221 | 29 | 3.0531 | 2.149
[7 empty] | 3222 | 30 | 3.2953 | 2.3389
[7 empty] | 3223 | 31 | 4.1387 | 3.0002
[7 empty] | 3224 | 32 | 4.4895 | 3.2752
[7 empty] | 3225 | 33 | 5.1492 | 3.7925
[7 empty] | 3226 | 34 | 6.0428 | 4.4932
[7 empty] | 3227 | 35 | 8.2057 | 6.1891
[7 empty] | 3228 | 36 | 9.2329 | 6.9945
[7 empty] | 3229 | 37 | 9.3081 | 7.0534
[7 empty] | 3230 | 38 | 9.3832 | 7.1123
[7 empty] | 3231 | 39 | 9.0575 | 6.857
[7 empty] | 3232 | 40 | 10.1098 | 7.682
[7 empty] | 3233 | 41 | 10.6609 | 8.1142
[7 empty] | 3234 | 42 | 10.6776 | 8.1273
[7 empty] | 3235 | 43 | 11.0451 | 8.4154
[7 empty] | 3236 | 44 | 12.1975 | 9.319
[7 empty] | 3237 | 45 | 11.7967 | 9.0047
[7 empty] | 3238 | 46 | 9.0575 | 6.857
[7 empty] | 3239 | 47 | 5.4666 | 4.0414
[7 empty] | 3240 | 48 | 3.9717 | 2.8693
[7 empty] | 3241 | 49 | 3.312 | 2.352
[7 empty] | 3242 | 50 | 3.003 | 2.1097
[7 empty] | 3243 | 51 | 2.8944 | 2.0246
[7 empty] | 3244 | 52 | 2.9278 | 2.0508
[7 empty] | 3245 | 53 | 2.9529 | 2.0704
[7 empty] | 3246 | 54 | 3.5291 | 2.5222
[7 empty] | 3247 | 55 | 4.6648 | 3.4128
[7 empty] | 3248 | 56 | 4.907 | 3.6026
[7 empty] | 3249 | 57 | 5.8507 | 4.3426
[7 empty] | 3250 | 58 | 6.9531 | 5.2069
[7 empty] | 3251 | 59 | 8.1556 | 6.1498
[7 empty] | 3252 | 60 | 8.7819 | 6.6409
[7 empty] | 3253 | 61 | 9.4584 | 7.1713
[7 empty] | 3254 | 62 | 9.258 | 7.0141
[7 empty] | 3255 | 63 | 9.8509 | 7.479
[7 empty] | 3256 | 64 | 10.7946 | 8.219
[7 empty] | 3257 | 65 | 11.4125 | 8.7035
[7 empty] | 3258 | 66 | 11.3123 | 8.6249
[7 empty] | 3259 | 67 | 12.0472 | 9.2011
[7 empty] | 3260 | 68 | 12.2894 | 9.391
[7 empty] | 3261 | 69 | 11.78 | 8.9916
[7 empty] | 3262 | 70 | 9.4918 | 7.1975
[7 empty] | 3263 | 71 | 4.9905 | 3.6681
[7 empty] | 3264 | 72 | 3.9097 | 2.8206
[7 empty] | 3265 | 73 | 3.1951 | 2.2603
[7 empty] | 3266 | 74 | 2.9696 | 2.0835
[7 empty] | 3267 | 75 | 2.8694 | 2.0049
[7 empty] | 3268 | 76 | 2.8109 | 1.9591
[7 empty] | 3269 | 77 | 2.9863 | 2.0966
[7 empty] | 3270 | 78 | 3.3871 | 2.4109
[7 empty] | 3271 | 79 | 4.4978 | 3.2818
[7 empty] | 3272 | 80 | 4.6732 | 3.4193
[7 empty] | 3273 | 81 | 5.8507 | 4.3426
[7 empty] | 3274 | 82 | 6.9363 | 5.1938
[7 empty] | 3275 | 83 | 7.6712 | 5.77
[7 empty] | 3276 | 84 | 8.9072 | 6.7391
[7 empty] | 3277 | 85 | 8.6066 | 6.5034
[7 empty] | 3278 | 86 | 8.0972 | 6.104
[7 empty] | 3279 | 87 | 8.5398 | 6.451
[7 empty] | 3280 | 88 | 9.1995 | 6.9683
[7 empty] | 3281 | 89 | 10.544 | 8.0225
[7 empty] | 3282 | 90 | 9.9595 | 7.5642
[7 empty] | 3283 | 91 | 10.6442 | 8.1011
[7 empty] | 3284 | 92 | 10.043 | 7.6296
[7 empty] | 3285 | 93 | 7.6378 | 5.7438
[7 empty] | 3286 | 94 | 6.7359 | 5.0366
[7 empty] | 3287 | 95 | 4.882 | 3.583
[7 empty] | 3288 | 96 | 3.8965 | 2.8103
[7 empty] | 3289 | 97 | 3.8464 | 2.7711
[7 empty] | 3290 | 98 | 3.5541 | 2.5419
[7 empty] | 3291 | 99 | 3.4957 | 2.496
[7 empty] | 3292 | 100 | 3.1449 | 2.221
[7 empty] | 3293 | 101 | 3.0865 | 2.1752
[7 empty] | 3294 | 102 | 3.3203 | 2.3585
[7 empty] | 3295 | 103 | 4.0636 | 2.9413
[7 empty] | 3296 | 104 | 4.3141 | 3.1377
[7 empty] | 3297 | 105 | 4.7985 | 3.5175
[7 empty] | 3298 | 106 | 6.2516 | 4.6569
[7 empty] | 3299 | 107 | 6.6023 | 4.9319
[7 empty] | 3300 | 108 | 8.1723 | 6.1629
[7 empty] | 3301 | 109 | 7.5126 | 5.6456
[7 empty] | 3302 | 110 | 7.0616 | 5.292
[7 empty] | 3303 | 111 | 6.9029 | 5.1676
[7 empty] | 3304 | 112 | 6.9698 | 5.22
[7 empty] | 3305 | 113 | 6.6274 | 4.9515
[7 empty] | 3306 | 114 | 6.7944 | 5.0825
[7 empty] | 3307 | 115 | 6.3434 | 4.7289
[7 empty] | 3308 | 116 | 7.0199 | 5.2593
[7 empty] | 3309 | 117 | 6.6023 | 4.9319
[7 empty] | 3310 | 118 | 5.834 | 4.3295
[7 empty] | 3311 | 119 | 4.2473 | 3.0854
[7 empty] | 3312 | 120 | 3.9311 | 2.8374
[7 empty] | 3313 | 121 | 3.2034 | 2.2669
[7 empty] | 3314 | 122 | 2.7942 | 1.946
[7 empty] | 3315 | 123 | 2.7107 | 1.8805
[7 empty] | 3316 | 124 | 2.6773 | 1.8543
[7 empty] | 3317 | 125 | 2.6355 | 1.8216
[7 empty] | 3318 | 126 | 2.7775 | 1.9329
[7 empty] | 3319 | 127 | 4.2807 | 3.1115
[7 empty] | 3320 | 128 | 5.834 | 4.3295
[7 empty] | 3321 | 129 | 6.5104 | 4.8599
[7 empty] | 3322 | 130 | 6.9447 | 5.2003
[7 empty] | 3323 | 131 | 7.1034 | 5.3248
[7 empty] | 3324 | 132 | 6.8528 | 5.1283
[7 empty] | 3325 | 133 | 7.4875 | 5.626
[7 empty] | 3326 | 134 | 7.7882 | 5.8617
[7 empty] | 3327 | 135 | 7.855 | 5.9141
[7 empty] | 3328 | 136 | 7.0449 | 5.2789
[7 empty] | 3329 | 137 | 6.9447 | 5.2003
[7 empty] | 3330 | 138 | 6.8946 | 5.1611
[7 empty] | 3331 | 139 | 6.5605 | 4.8991
[7 empty] | 3332 | 140 | 6.5689 | 4.9057
[7 empty] | 3333 | 141 | 5.9175 | 4.3949
[7 empty] | 3334 | 142 | 5.2828 | 3.8973
[7 empty] | 3335 | 143 | 4.406 | 3.2098
[7 empty] | 3336 | 144 | 3.7963 | 2.7318
[7 empty] | 3337 | 145 | 3.3287 | 2.3651
[7 empty] | 3338 | 146 | 3.1199 | 2.2014
[7 empty] | 3339 | 147 | 3.0531 | 2.149
[7 empty] | 3340 | 148 | 3.0447 | 2.1424
[7 empty] | 3341 | 149 | 3.0447 | 2.1424
[7 empty] | 3342 | 150 | 3.0531 | 2.149
[7 empty] | 3343 | 151 | 4.1304 | 2.9937
[7 empty] | 3344 | 152 | 5.6503 | 4.1854
[7 empty] | 3345 | 153 | 6.2599 | 4.6634
[7 empty] | 3346 | 154 | 6.8194 | 5.1021
[7 empty] | 3347 | 155 | 6.6691 | 4.9843
[7 empty] | 3348 | 156 | 6.8361 | 5.1152
[7 empty] | 3349 | 157 | 7.546 | 5.6718
[7 empty] | 3350 | 158 | 7.8717 | 5.9272
[7 empty] | 3351 | 159 | 8.1389 | 6.1367
[7 empty] | 3352 | 160 | 8.0136 | 6.0385
[7 empty] | 3353 | 161 | 8.7736 | 6.6343
[7 empty] | 3354 | 162 | 8.2809 | 6.248
[7 empty] | 3355 | 163 | 8.64 | 6.5296
[7 empty] | 3356 | 164 | 7.2954 | 5.4754
[7 empty] | 3357 | 165 | 10.4104 | 7.9177
[7 empty] | 3358 | 166 | 8.3727 | 6.32
[7 empty] | 3359 | 167 | 4.7818 | 3.5044
[7 empty] | 3360 | 168 | 4.1387 | 3.0002
[7 empty] | 3361 | 1 | 2.6856 | 1.8609
[7 empty] | 3362 | 2 | 2.5771 | 1.7758
[7 empty] | 3363 | 3 | 2.5687 | 1.7692
[7 empty] | 3364 | 4 | 2.7023 | 1.874
[7 empty] | 3365 | 5 | 2.719 | 1.8871
[7 empty] | 3366 | 6 | 3.1449 | 2.221
[7 empty] | 3367 | 7 | 3.8631 | 2.7841
[7 empty] | 3368 | 8 | 4.5312 | 3.308
[7 empty] | 3369 | 9 | 4.5062 | 3.2883
[7 empty] | 3370 | 10 | 6.0177 | 4.4735
[7 empty] | 3371 | 11 | 8.0888 | 6.0974
[7 empty] | 3372 | 12 | 9.0492 | 6.8504
[7 empty] | 3373 | 13 | 9.425 | 7.1451
[7 empty] | 3374 | 14 | 9.2079 | 6.9748
[7 empty] | 3375 | 15 | 9.116 | 6.9028
[7 empty] | 3376 | 16 | 10.2935 | 7.8261
[7 empty] | 3377 | 17 | 11.613 | 8.8607
[7 empty] | 3378 | 18 | 11.3708 | 8.6708
[7 empty] | 3379 | 19 | 11.8969 | 9.0833
[7 empty] | 3380 | 20 | 11.8301 | 9.0309
[7 empty] | 3381 | 21 | 12.398 | 9.4762
[7 empty] | 3382 | 22 | 8.4563 | 6.3855
[7 empty] | 3383 | 23 | 4.6983 | 3.4389
[7 empty] | 3384 | 24 | 3.0331 | 2.1333
[7 empty] | 3385 | 25 | 2.9362 | 2.0573
[7 empty] | 3386 | 26 | 2.8276 | 1.9722
[7 empty] | 3387 | 27 | 2.7274 | 1.8936
[7 empty] | 3388 | 28 | 2.8109 | 1.9591
[7 empty] | 3389 | 29 | 3.0531 | 2.149
[7 empty] | 3390 | 30 | 3.2953 | 2.3389
[7 empty] | 3391 | 31 | 4.1387 | 3.0002
[7 empty] | 3392 | 32 | 4.4895 | 3.2752
[7 empty] | 3393 | 33 | 5.1492 | 3.7925
[7 empty] | 3394 | 34 | 6.0428 | 4.4932
[7 empty] | 3395 | 35 | 8.2057 | 6.1891
[7 empty] | 3396 | 36 | 9.2329 | 6.9945
[7 empty] | 3397 | 37 | 9.3081 | 7.0534
[7 empty] | 3398 | 38 | 9.3832 | 7.1123
[7 empty] | 3399 | 39 | 9.0575 | 6.857
[7 empty] | 3400 | 40 | 10.1098 | 7.682
[7 empty] | 3401 | 41 | 10.6609 | 8.1142
[7 empty] | 3402 | 42 | 10.6776 | 8.1273
[7 empty] | 3403 | 43 | 11.0451 | 8.4154
[7 empty] | 3404 | 44 | 12.1975 | 9.319
[7 empty] | 3405 | 45 | 11.7967 | 9.0047
[7 empty] | 3406 | 46 | 9.0575 | 6.857
[7 empty] | 3407 | 47 | 5.4666 | 4.0414
[7 empty] | 3408 | 48 | 3.9717 | 2.8693
[7 empty] | 3409 | 49 | 3.312 | 2.352
[7 empty] | 3410 | 50 | 3.003 | 2.1097
[7 empty] | 3411 | 51 | 2.8944 | 2.0246
[7 empty] | 3412 | 52 | 2.9278 | 2.0508
[7 empty] | 3413 | 53 | 2.9529 | 2.0704
[7 empty] | 3414 | 54 | 3.5291 | 2.5222
[7 empty] | 3415 | 55 | 4.6648 | 3.4128
[7 empty] | 3416 | 56 | 4.907 | 3.6026
[7 empty] | 3417 | 57 | 5.8507 | 4.3426
[7 empty] | 3418 | 58 | 6.9531 | 5.2069
[7 empty] | 3419 | 59 | 8.1556 | 6.1498
[7 empty] | 3420 | 60 | 8.7819 | 6.6409
[7 empty] | 3421 | 61 | 9.4584 | 7.1713
[7 empty] | 3422 | 62 | 9.258 | 7.0141
[7 empty] | 3423 | 63 | 9.8509 | 7.479
[7 empty] | 3424 | 64 | 10.7946 | 8.219
[7 empty] | 3425 | 65 | 11.4125 | 8.7035
[7 empty] | 3426 | 66 | 11.3123 | 8.6249
[7 empty] | 3427 | 67 | 12.0472 | 9.2011
[7 empty] | 3428 | 68 | 12.2894 | 9.391
[7 empty] | 3429 | 69 | 11.78 | 8.9916
[7 empty] | 3430 | 70 | 9.4918 | 7.1975
[7 empty] | 3431 | 71 | 4.9905 | 3.6681
[7 empty] | 3432 | 72 | 3.9097 | 2.8206
[7 empty] | 3433 | 73 | 3.1951 | 2.2603
[7 empty] | 3434 | 74 | 2.9696 | 2.0835
[7 empty] | 3435 | 75 | 2.8694 | 2.0049
[7 empty] | 3436 | 76 | 2.8109 | 1.9591
[7 empty] | 3437 | 77 | 2.9863 | 2.0966
[7 empty] | 3438 | 78 | 3.3871 | 2.4109
[7 empty] | 3439 | 79 | 4.4978 | 3.2818
[7 empty] | 3440 | 80 | 4.6732 | 3.4193
[7 empty] | 3441 | 81 | 5.8507 | 4.3426
[7 empty] | 3442 | 82 | 6.9363 | 5.1938
[7 empty] | 3443 | 83 | 7.6712 | 5.77
[7 empty] | 3444 | 84 | 8.9072 | 6.7391
[7 empty] | 3445 | 85 | 8.6066 | 6.5034
[7 empty] | 3446 | 86 | 8.0972 | 6.104
[7 empty] | 3447 | 87 | 8.5398 | 6.451
[7 empty] | 3448 | 88 | 9.1995 | 6.9683
[7 empty] | 3449 | 89 | 10.544 | 8.0225
[7 empty] | 3450 | 90 | 9.9595 | 7.5642
[7 empty] | 3451 | 91 | 10.6442 | 8.1011
[7 empty] | 3452 | 92 | 10.043 | 7.6296
[7 empty] | 3453 | 93 | 7.6378 | 5.7438
[7 empty] | 3454 | 94 | 6.7359 | 5.0366
[7 empty] | 3455 | 95 | 4.882 | 3.583
[7 empty] | 3456 | 96 | 3.8965 | 2.8103
[7 empty] | 3457 | 97 | 3.8464 | 2.7711
[7 empty] | 3458 | 98 | 3.5541 | 2.5419
[7 empty] | 3459 | 99 | 3.4957 | 2.496
[7 empty] | 3460 | 100 | 3.1449 | 2.221
[7 empty] | 3461 | 101 | 3.0865 | 2.1752
[7 empty] | 3462 | 102 | 3.3203 | 2.3585
[7 empty] | 3463 | 103 | 4.0636 | 2.9413
[7 empty] | 3464 | 104 | 4.3141 | 3.1377
[7 empty] | 3465 | 105 | 4.7985 | 3.5175
[7 empty] | 3466 | 106 | 6.2516 | 4.6569
[7 empty] | 3467 | 107 | 6.6023 | 4.9319
[7 empty] | 3468 | 108 | 8.1723 | 6.1629
[7 empty] | 3469 | 109 | 7.5126 | 5.6456
[7 empty] | 3470 | 110 | 7.0616 | 5.292
[7 empty] | 3471 | 111 | 6.9029 | 5.1676
[7 empty] | 3472 | 112 | 6.9698 | 5.22
[7 empty] | 3473 | 113 | 6.6274 | 4.9515
[7 empty] | 3474 | 114 | 6.7944 | 5.0825
[7 empty] | 3475 | 115 | 6.3434 | 4.7289
[7 empty] | 3476 | 116 | 7.0199 | 5.2593
[7 empty] | 3477 | 117 | 6.6023 | 4.9319
[7 empty] | 3478 | 118 | 5.834 | 4.3295
[7 empty] | 3479 | 119 | 4.2473 | 3.0854
[7 empty] | 3480 | 120 | 3.9311 | 2.8374
[7 empty] | 3481 | 121 | 3.2034 | 2.2669
[7 empty] | 3482 | 122 | 2.7942 | 1.946
[7 empty] | 3483 | 123 | 2.7107 | 1.8805
[7 empty] | 3484 | 124 | 2.6773 | 1.8543
[7 empty] | 3485 | 125 | 2.6355 | 1.8216
[7 empty] | 3486 | 126 | 2.7775 | 1.9329
[7 empty] | 3487 | 127 | 4.2807 | 3.1115
[7 empty] | 3488 | 128 | 5.834 | 4.3295
[7 empty] | 3489 | 129 | 6.5104 | 4.8599
[7 empty] | 3490 | 130 | 6.9447 | 5.2003
[7 empty] | 3491 | 131 | 7.1034 | 5.3248
[7 empty] | 3492 | 132 | 6.8528 | 5.1283
[7 empty] | 3493 | 133 | 7.4875 | 5.626
[7 empty] | 3494 | 134 | 7.7882 | 5.8617
[7 empty] | 3495 | 135 | 7.855 | 5.9141
[7 empty] | 3496 | 136 | 7.0449 | 5.2789
[7 empty] | 3497 | 137 | 6.9447 | 5.2003
[7 empty] | 3498 | 138 | 6.8946 | 5.1611
[7 empty] | 3499 | 139 | 6.5605 | 4.8991
[7 empty] | 3500 | 140 | 6.5689 | 4.9057
[7 empty] | 3501 | 141 | 5.9175 | 4.3949
[7 empty] | 3502 | 142 | 5.2828 | 3.8973
[7 empty] | 3503 | 143 | 4.406 | 3.2098
[7 empty] | 3504 | 144 | 3.7963 | 2.7318
[7 empty] | 3505 | 145 | 3.3287 | 2.3651
[7 empty] | 3506 | 146 | 3.1199 | 2.2014
[7 empty] | 3507 | 147 | 3.0531 | 2.149
[7 empty] | 3508 | 148 | 3.0447 | 2.1424
[7 empty] | 3509 | 149 | 3.0447 | 2.1424
[7 empty] | 3510 | 150 | 3.0531 | 2.149
[7 empty] | 3511 | 151 | 4.1304 | 2.9937
[7 empty] | 3512 | 152 | 5.6503 | 4.1854
[7 empty] | 3513 | 153 | 6.2599 | 4.6634
[7 empty] | 3514 | 154 | 6.8194 | 5.1021
[7 empty] | 3515 | 155 | 6.6691 | 4.9843
[7 empty] | 3516 | 156 | 6.8361 | 5.1152
[7 empty] | 3517 | 157 | 7.546 | 5.6718
[7 empty] | 3518 | 158 | 7.8717 | 5.9272
[7 empty] | 3519 | 159 | 8.1389 | 6.1367
[7 empty] | 3520 | 160 | 8.0136 | 6.0385
[7 empty] | 3521 | 161 | 8.7736 | 6.6343
[7 empty] | 3522 | 162 | 8.2809 | 6.248
[7 empty] | 3523 | 163 | 8.64 | 6.5296
[7 empty] | 3524 | 164 | 7.2954 | 5.4754
[7 empty] | 3525 | 165 | 10.4104 | 7.9177
[7 empty] | 3526 | 166 | 8.3727 | 6.32
[7 empty] | 3527 | 167 | 4.7818 | 3.5044
[7 empty] | 3528 | 168 | 4.1387 | 3.0002
[7 empty] | 3529 | 1 | 2.6856 | 1.8609
[7 empty] | 3530 | 2 | 2.5771 | 1.7758
[7 empty] | 3531 | 3 | 2.5687 | 1.7692
[7 empty] | 3532 | 4 | 2.7023 | 1.874
[7 empty] | 3533 | 5 | 2.719 | 1.8871
[7 empty] | 3534 | 6 | 3.1449 | 2.221
[7 empty] | 3535 | 7 | 3.8631 | 2.7841
[7 empty] | 3536 | 8 | 4.5312 | 3.308
[7 empty] | 3537 | 9 | 4.5062 | 3.2883
[7 empty] | 3538 | 10 | 6.0177 | 4.4735
[7 empty] | 3539 | 11 | 8.0888 | 6.0974
[7 empty] | 3540 | 12 | 9.0492 | 6.8504
[7 empty] | 3541 | 13 | 9.425 | 7.1451
[7 empty] | 3542 | 14 | 9.2079 | 6.9748
[7 empty] | 3543 | 15 | 9.116 | 6.9028
[7 empty] | 3544 | 16 | 10.2935 | 7.8261
[7 empty] | 3545 | 17 | 11.613 | 8.8607
[7 empty] | 3546 | 18 | 11.3708 | 8.6708
[7 empty] | 3547 | 19 | 11.8969 | 9.0833
[7 empty] | 3548 | 20 | 11.8301 | 9.0309
[7 empty] | 3549 | 21 | 12.398 | 9.4762
[7 empty] | 3550 | 22 | 8.4563 | 6.3855
[7 empty] | 3551 | 23 | 4.6983 | 3.4389
[7 empty] | 3552 | 24 | 3.0331 | 2.1333
[7 empty] | 3553 | 25 | 2.9362 | 2.0573
[7 empty] | 3554 | 26 | 2.8276 | 1.9722
[7 empty] | 3555 | 27 | 2.7274 | 1.8936
[7 empty] | 3556 | 28 | 2.8109 | 1.9591
[7 empty] | 3557 | 29 | 3.0531 | 2.149
[7 empty] | 3558 | 30 | 3.2953 | 2.3389
[7 empty] | 3559 | 31 | 4.1387 | 3.0002
[7 empty] | 3560 | 32 | 4.4895 | 3.2752
[7 empty] | 3561 | 33 | 5.1492 | 3.7925
[7 empty] | 3562 | 34 | 6.0428 | 4.4932
[7 empty] | 3563 | 35 | 8.2057 | 6.1891
[7 empty] | 3564 | 36 | 9.2329 | 6.9945
[7 empty] | 3565 | 37 | 9.3081 | 7.0534
[7 empty] | 3566 | 38 | 9.3832 | 7.1123
[7 empty] | 3567 | 39 | 9.0575 | 6.857
[7 empty] | 3568 | 40 | 10.1098 | 7.682
[7 empty] | 3569 | 41 | 10.6609 | 8.1142
[7 empty] | 3570 | 42 | 10.6776 | 8.1273
[7 empty] | 3571 | 43 | 11.0451 | 8.4154
[7 empty] | 3572 | 44 | 12.1975 | 9.319
[7 empty] | 3573 | 45 | 11.7967 | 9.0047
[7 empty] | 3574 | 46 | 9.0575 | 6.857
[7 empty] | 3575 | 47 | 5.4666 | 4.0414
[7 empty] | 3576 | 48 | 3.9717 | 2.8693
[7 empty] | 3577 | 49 | 3.312 | 2.352
[7 empty] | 3578 | 50 | 3.003 | 2.1097
[7 empty] | 3579 | 51 | 2.8944 | 2.0246
[7 empty] | 3580 | 52 | 2.9278 | 2.0508
[7 empty] | 3581 | 53 | 2.9529 | 2.0704
[7 empty] | 3582 | 54 | 3.5291 | 2.5222
[7 empty] | 3583 | 55 | 4.6648 | 3.4128
[7 empty] | 3584 | 56 | 4.907 | 3.6026
[7 empty] | 3585 | 57 | 5.8507 | 4.3426
[7 empty] | 3586 | 58 | 6.9531 | 5.2069
[7 empty] | 3587 | 59 | 8.1556 | 6.1498
[7 empty] | 3588 | 60 | 8.7819 | 6.6409
[7 empty] | 3589 | 61 | 9.4584 | 7.1713
[7 empty] | 3590 | 62 | 9.258 | 7.0141
[7 empty] | 3591 | 63 | 9.8509 | 7.479
[7 empty] | 3592 | 64 | 10.7946 | 8.219
[7 empty] | 3593 | 65 | 11.4125 | 8.7035
[7 empty] | 3594 | 66 | 11.3123 | 8.6249
[7 empty] | 3595 | 67 | 12.0472 | 9.2011
[7 empty] | 3596 | 68 | 12.2894 | 9.391
[7 empty] | 3597 | 69 | 11.78 | 8.9916
[7 empty] | 3598 | 70 | 9.4918 | 7.1975
[7 empty] | 3599 | 71 | 4.9905 | 3.6681
[7 empty] | 3600 | 72 | 3.9097 | 2.8206
[7 empty] | 3601 | 73 | 3.1951 | 2.2603
[7 empty] | 3602 | 74 | 2.9696 | 2.0835
[7 empty] | 3603 | 75 | 2.8694 | 2.0049
[7 empty] | 3604 | 76 | 2.8109 | 1.9591
[7 empty] | 3605 | 77 | 2.9863 | 2.0966
[7 empty] | 3606 | 78 | 3.3871 | 2.4109
[7 empty] | 3607 | 79 | 4.4978 | 3.2818
[7 empty] | 3608 | 80 | 4.6732 | 3.4193
[7 empty] | 3609 | 81 | 5.8507 | 4.3426
[7 empty] | 3610 | 82 | 6.9363 | 5.1938
[7 empty] | 3611 | 83 | 7.6712 | 5.77
[7 empty] | 3612 | 84 | 8.9072 | 6.7391
[7 empty] | 3613 | 85 | 8.6066 | 6.5034
[7 empty] | 3614 | 86 | 8.0972 | 6.104
[7 empty] | 3615 | 87 | 8.5398 | 6.451
[7 empty] | 3616 | 88 | 9.1995 | 6.9683
[7 empty] | 3617 | 89 | 10.544 | 8.0225
[7 empty] | 3618 | 90 | 9.9595 | 7.5642
[7 empty] | 3619 | 91 | 10.6442 | 8.1011
[7 empty] | 3620 | 92 | 10.043 | 7.6296
[7 empty] | 3621 | 93 | 7.6378 | 5.7438
[7 empty] | 3622 | 94 | 6.7359 | 5.0366
[7 empty] | 3623 | 95 | 4.882 | 3.583
[7 empty] | 3624 | 96 | 3.8965 | 2.8103
[7 empty] | 3625 | 97 | 3.8464 | 2.7711
[7 empty] | 3626 | 98 | 3.5541 | 2.5419
[7 empty] | 3627 | 99 | 3.4957 | 2.496
[7 empty] | 3628 | 100 | 3.1449 | 2.221
[7 empty] | 3629 | 101 | 3.0865 | 2.1752
[7 empty] | 3630 | 102 | 3.3203 | 2.3585
[7 empty] | 3631 | 103 | 4.0636 | 2.9413
[7 empty] | 3632 | 104 | 4.3141 | 3.1377
[7 empty] | 3633 | 105 | 4.7985 | 3.5175
[7 empty] | 3634 | 106 | 6.2516 | 4.6569
[7 empty] | 3635 | 107 | 6.6023 | 4.9319
[7 empty] | 3636 | 108 | 8.1723 | 6.1629
[7 empty] | 3637 | 109 | 7.5126 | 5.6456
[7 empty] | 3638 | 110 | 7.0616 | 5.292
[7 empty] | 3639 | 111 | 6.9029 | 5.1676
[7 empty] | 3640 | 112 | 6.9698 | 5.22
[7 empty] | 3641 | 113 | 6.6274 | 4.9515
[7 empty] | 3642 | 114 | 6.7944 | 5.0825
[7 empty] | 3643 | 115 | 6.3434 | 4.7289
[7 empty] | 3644 | 116 | 7.0199 | 5.2593
[7 empty] | 3645 | 117 | 6.6023 | 4.9319
[7 empty] | 3646 | 118 | 5.834 | 4.3295
[7 empty] | 3647 | 119 | 4.2473 | 3.0854
[7 empty] | 3648 | 120 | 3.9311 | 2.8374
[7 empty] | 3649 | 121 | 3.2034 | 2.2669
[7 empty] | 3650 | 122 | 2.7942 | 1.946
[7 empty] | 3651 | 123 | 2.7107 | 1.8805
[7 empty] | 3652 | 124 | 2.6773 | 1.8543
[7 empty] | 3653 | 125 | 2.6355 | 1.8216
[7 empty] | 3654 | 126 | 2.7775 | 1.9329
[7 empty] | 3655 | 127 | 4.2807 | 3.1115
[7 empty] | 3656 | 128 | 5.834 | 4.3295
[7 empty] | 3657 | 129 | 6.5104 | 4.8599
[7 empty] | 3658 | 130 | 6.9447 | 5.2003
[7 empty] | 3659 | 131 | 7.1034 | 5.3248
[7 empty] | 3660 | 132 | 6.8528 | 5.1283
[7 empty] | 3661 | 133 | 7.4875 | 5.626
[7 empty] | 3662 | 134 | 7.7882 | 5.8617
[7 empty] | 3663 | 135 | 7.855 | 5.9141
[7 empty] | 3664 | 136 | 7.0449 | 5.2789
[7 empty] | 3665 | 137 | 6.9447 | 5.2003
[7 empty] | 3666 | 138 | 6.8946 | 5.1611
[7 empty] | 3667 | 139 | 6.5605 | 4.8991
[7 empty] | 3668 | 140 | 6.5689 | 4.9057
[7 empty] | 3669 | 141 | 5.9175 | 4.3949
[7 empty] | 3670 | 142 | 5.2828 | 3.8973
[7 empty] | 3671 | 143 | 4.406 | 3.2098
[7 empty] | 3672 | 144 | 3.7963 | 2.7318
[7 empty] | 3673 | 145 | 3.3287 | 2.3651
[7 empty] | 3674 | 146 | 3.1199 | 2.2014
[7 empty] | 3675 | 147 | 3.0531 | 2.149
[7 empty] | 3676 | 148 | 3.0447 | 2.1424
[7 empty] | 3677 | 149 | 3.0447 | 2.1424
[7 empty] | 3678 | 150 | 3.0531 | 2.149
[7 empty] | 3679 | 151 | 4.1304 | 2.9937
[7 empty] | 3680 | 152 | 5.6503 | 4.1854
[7 empty] | 3681 | 153 | 6.2599 | 4.6634
[7 empty] | 3682 | 154 | 6.8194 | 5.1021
[7 empty] | 3683 | 155 | 6.6691 | 4.9843
[7 empty] | 3684 | 156 | 6.8361 | 5.1152
[7 empty] | 3685 | 157 | 7.546 | 5.6718
[7 empty] | 3686 | 158 | 7.8717 | 5.9272
[7 empty] | 3687 | 159 | 8.1389 | 6.1367
[7 empty] | 3688 | 160 | 8.0136 | 6.0385
[7 empty] | 3689 | 161 | 8.7736 | 6.6343
[7 empty] | 3690 | 162 | 8.2809 | 6.248
[7 empty] | 3691 | 163 | 8.64 | 6.5296
[7 empty] | 3692 | 164 | 7.2954 | 5.4754
[7 empty] | 3693 | 165 | 10.4104 | 7.9177
[7 empty] | 3694 | 166 | 8.3727 | 6.32
[7 empty] | 3695 | 167 | 4.7818 | 3.5044
[7 empty] | 3696 | 168 | 4.1387 | 3.0002
[7 empty] | 3697 | 1 | 2.6856 | 1.8609
[7 empty] | 3698 | 2 | 2.5771 | 1.7758
[7 empty] | 3699 | 3 | 2.5687 | 1.7692
[7 empty] | 3700 | 4 | 2.7023 | 1.874
[7 empty] | 3701 | 5 | 2.719 | 1.8871
[7 empty] | 3702 | 6 | 3.1449 | 2.221
[7 empty] | 3703 | 7 | 3.8631 | 2.7841
[7 empty] | 3704 | 8 | 4.5312 | 3.308
[7 empty] | 3705 | 9 | 4.5062 | 3.2883
[7 empty] | 3706 | 10 | 6.0177 | 4.4735
[7 empty] | 3707 | 11 | 8.0888 | 6.0974
[7 empty] | 3708 | 12 | 9.0492 | 6.8504
[7 empty] | 3709 | 13 | 9.425 | 7.1451
[7 empty] | 3710 | 14 | 9.2079 | 6.9748
[7 empty] | 3711 | 15 | 9.116 | 6.9028
[7 empty] | 3712 | 16 | 10.2935 | 7.8261
[7 empty] | 3713 | 17 | 11.613 | 8.8607
[7 empty] | 3714 | 18 | 11.3708 | 8.6708
[7 empty] | 3715 | 19 | 11.8969 | 9.0833
[7 empty] | 3716 | 20 | 11.8301 | 9.0309
[7 empty] | 3717 | 21 | 12.398 | 9.4762
[7 empty] | 3718 | 22 | 8.4563 | 6.3855
[7 empty] | 3719 | 23 | 4.6983 | 3.4389
[7 empty] | 3720 | 24 | 3.0331 | 2.1333
[7 empty] | 3721 | 25 | 2.9362 | 2.0573
[7 empty] | 3722 | 26 | 2.8276 | 1.9722
[7 empty] | 3723 | 27 | 2.7274 | 1.8936
[7 empty] | 3724 | 28 | 2.8109 | 1.9591
[7 empty] | 3725 | 29 | 3.0531 | 2.149
[7 empty] | 3726 | 30 | 3.2953 | 2.3389
[7 empty] | 3727 | 31 | 4.1387 | 3.0002
[7 empty] | 3728 | 32 | 4.4895 | 3.2752
[7 empty] | 3729 | 33 | 5.1492 | 3.7925
[7 empty] | 3730 | 34 | 6.0428 | 4.4932
[7 empty] | 3731 | 35 | 8.2057 | 6.1891
[7 empty] | 3732 | 36 | 9.2329 | 6.9945
[7 empty] | 3733 | 37 | 9.3081 | 7.0534
[7 empty] | 3734 | 38 | 9.3832 | 7.1123
[7 empty] | 3735 | 39 | 9.0575 | 6.857
[7 empty] | 3736 | 40 | 10.1098 | 7.682
[7 empty] | 3737 | 41 | 10.6609 | 8.1142
[7 empty] | 3738 | 42 | 10.6776 | 8.1273
[7 empty] | 3739 | 43 | 11.0451 | 8.4154
[7 empty] | 3740 | 44 | 12.1975 | 9.319
[7 empty] | 3741 | 45 | 11.7967 | 9.0047
[7 empty] | 3742 | 46 | 9.0575 | 6.857
[7 empty] | 3743 | 47 | 5.4666 | 4.0414
[7 empty] | 3744 | 48 | 3.9717 | 2.8693
[7 empty] | 3745 | 49 | 3.312 | 2.352
[7 empty] | 3746 | 50 | 3.003 | 2.1097
[7 empty] | 3747 | 51 | 2.8944 | 2.0246
[7 empty] | 3748 | 52 | 2.9278 | 2.0508
[7 empty] | 3749 | 53 | 2.9529 | 2.0704
[7 empty] | 3750 | 54 | 3.5291 | 2.5222
[7 empty] | 3751 | 55 | 4.6648 | 3.4128
[7 empty] | 3752 | 56 | 4.907 | 3.6026
[7 empty] | 3753 | 57 | 5.8507 | 4.3426
[7 empty] | 3754 | 58 | 6.9531 | 5.2069
[7 empty] | 3755 | 59 | 8.1556 | 6.1498
[7 empty] | 3756 | 60 | 8.7819 | 6.6409
[7 empty] | 3757 | 61 | 9.4584 | 7.1713
[7 empty] | 3758 | 62 | 9.258 | 7.0141
[7 empty] | 3759 | 63 | 9.8509 | 7.479
[7 empty] | 3760 | 64 | 10.7946 | 8.219
[7 empty] | 3761 | 65 | 11.4125 | 8.7035
[7 empty] | 3762 | 66 | 11.3123 | 8.6249
[7 empty] | 3763 | 67 | 12.0472 | 9.2011
[7 empty] | 3764 | 68 | 12.2894 | 9.391
[7 empty] | 3765 | 69 | 11.78 | 8.9916
[7 empty] | 3766 | 70 | 9.4918 | 7.1975
[7 empty] | 3767 | 71 | 4.9905 | 3.6681
[7 empty] | 3768 | 72 | 3.9097 | 2.8206
[7 empty] | 3769 | 73 | 3.1951 | 2.2603
[7 empty] | 3770 | 74 | 2.9696 | 2.0835
[7 empty] | 3771 | 75 | 2.8694 | 2.0049
[7 empty] | 3772 | 76 | 2.8109 | 1.9591
[7 empty] | 3773 | 77 | 2.9863 | 2.0966
[7 empty] | 3774 | 78 | 3.3871 | 2.4109
[7 empty] | 3775 | 79 | 4.4978 | 3.2818
[7 empty] | 3776 | 80 | 4.6732 | 3.4193
[7 empty] | 3777 | 81 | 5.8507 | 4.3426
[7 empty] | 3778 | 82 | 6.9363 | 5.1938
[7 empty] | 3779 | 83 | 7.6712 | 5.77
[7 empty] | 3780 | 84 | 8.9072 | 6.7391
[7 empty] | 3781 | 85 | 8.6066 | 6.5034
[7 empty] | 3782 | 86 | 8.0972 | 6.104
[7 empty] | 3783 | 87 | 8.5398 | 6.451
[7 empty] | 3784 | 88 | 9.1995 | 6.9683
[7 empty] | 3785 | 89 | 10.544 | 8.0225
[7 empty] | 3786 | 90 | 9.9595 | 7.5642
[7 empty] | 3787 | 91 | 10.6442 | 8.1011
[7 empty] | 3788 | 92 | 10.043 | 7.6296
[7 empty] | 3789 | 93 | 7.6378 | 5.7438
[7 empty] | 3790 | 94 | 6.7359 | 5.0366
[7 empty] | 3791 | 95 | 4.882 | 3.583
[7 empty] | 3792 | 96 | 3.8965 | 2.8103
[7 empty] | 3793 | 97 | 3.8464 | 2.7711
[7 empty] | 3794 | 98 | 3.5541 | 2.5419
[7 empty] | 3795 | 99 | 3.4957 | 2.496
[7 empty] | 3796 | 100 | 3.1449 | 2.221
[7 empty] | 3797 | 101 | 3.0865 | 2.1752
[7 empty] | 3798 | 102 | 3.3203 | 2.3585
[7 empty] | 3799 | 103 | 4.0636 | 2.9413
[7 empty] | 3800 | 104 | 4.3141 | 3.1377
[7 empty] | 3801 | 105 | 4.7985 | 3.5175
[7 empty] | 3802 | 106 | 6.2516 | 4.6569
[7 empty] | 3803 | 107 | 6.6023 | 4.9319
[7 empty] | 3804 | 108 | 8.1723 | 6.1629
[7 empty] | 3805 | 109 | 7.5126 | 5.6456
[7 empty] | 3806 | 110 | 7.0616 | 5.292
[7 empty] | 3807 | 111 | 6.9029 | 5.1676
[7 empty] | 3808 | 112 | 6.9698 | 5.22
[7 empty] | 3809 | 113 | 6.6274 | 4.9515
[7 empty] | 3810 | 114 | 6.7944 | 5.0825
[7 empty] | 3811 | 115 | 6.3434 | 4.7289
[7 empty] | 3812 | 116 | 7.0199 | 5.2593
[7 empty] | 3813 | 117 | 6.6023 | 4.9319
[7 empty] | 3814 | 118 | 5.834 | 4.3295
[7 empty] | 3815 | 119 | 4.2473 | 3.0854
[7 empty] | 3816 | 120 | 3.9311 | 2.8374
[7 empty] | 3817 | 121 | 3.2034 | 2.2669
[7 empty] | 3818 | 122 | 2.7942 | 1.946
[7 empty] | 3819 | 123 | 2.7107 | 1.8805
[7 empty] | 3820 | 124 | 2.6773 | 1.8543
[7 empty] | 3821 | 125 | 2.6355 | 1.8216
[7 empty] | 3822 | 126 | 2.7775 | 1.9329
[7 empty] | 3823 | 127 | 4.2807 | 3.1115
[7 empty] | 3824 | 128 | 5.834 | 4.3295
[7 empty] | 3825 | 129 | 6.5104 | 4.8599
[7 empty] | 3826 | 130 | 6.9447 | 5.2003
[7 empty] | 3827 | 131 | 7.1034 | 5.3248
[7 empty] | 3828 | 132 | 6.8528 | 5.1283
[7 empty] | 3829 | 133 | 7.4875 | 5.626
[7 empty] | 3830 | 134 | 7.7882 | 5.8617
[7 empty] | 3831 | 135 | 7.855 | 5.9141
[7 empty] | 3832 | 136 | 7.0449 | 5.2789
[7 empty] | 3833 | 137 | 6.9447 | 5.2003
[7 empty] | 3834 | 138 | 6.8946 | 5.1611
[7 empty] | 3835 | 139 | 6.5605 | 4.8991
[7 empty] | 3836 | 140 | 6.5689 | 4.9057
[7 empty] | 3837 | 141 | 5.9175 | 4.3949
[7 empty] | 3838 | 142 | 5.2828 | 3.8973
[7 empty] | 3839 | 143 | 4.406 | 3.2098
[7 empty] | 3840 | 144 | 3.7963 | 2.7318
[7 empty] | 3841 | 145 | 3.3287 | 2.3651
[7 empty] | 3842 | 146 | 3.1199 | 2.2014
[7 empty] | 3843 | 147 | 3.0531 | 2.149
[7 empty] | 3844 | 148 | 3.0447 | 2.1424
[7 empty] | 3845 | 149 | 3.0447 | 2.1424
[7 empty] | 3846 | 150 | 3.0531 | 2.149
[7 empty] | 3847 | 151 | 4.1304 | 2.9937
[7 empty] | 3848 | 152 | 5.6503 | 4.1854
[7 empty] | 3849 | 153 | 6.2599 | 4.6634
[7 empty] | 3850 | 154 | 6.8194 | 5.1021
[7 empty] | 3851 | 155 | 6.6691 | 4.9843
[7 empty] | 3852 | 156 | 6.8361 | 5.1152
[7 empty] | 3853 | 157 | 7.546 | 5.6718
[7 empty] | 3854 | 158 | 7.8717 | 5.9272
[7 empty] | 3855 | 159 | 8.1389 | 6.1367
[7 empty] | 3856 | 160 | 8.0136 | 6.0385
[7 empty] | 3857 | 161 | 8.7736 | 6.6343
[7 empty] | 3858 | 162 | 8.2809 | 6.248
[7 empty] | 3859 | 163 | 8.64 | 6.5296
[7 empty] | 3860 | 164 | 7.2954 | 5.4754
[7 empty] | 3861 | 165 | 10.4104 | 7.9177
[7 empty] | 3862 | 166 | 8.3727 | 6.32
[7 empty] | 3863 | 167 | 4.7818 | 3.5044
[7 empty] | 3864 | 168 | 4.1387 | 3.0002
[7 empty] | 3865 | 1 | 2.6856 | 1.8609
[7 empty] | 3866 | 2 | 2.5771 | 1.7758
[7 empty] | 3867 | 3 | 2.5687 | 1.7692
[7 empty] | 3868 | 4 | 2.7023 | 1.874
[7 empty] | 3869 | 5 | 2.719 | 1.8871
[7 empty] | 3870 | 6 | 3.1449 | 2.221
[7 empty] | 3871 | 7 | 3.8631 | 2.7841
[7 empty] | 3872 | 8 | 4.5312 | 3.308
[7 empty] | 3873 | 9 | 4.5062 | 3.2883
[7 empty] | 3874 | 10 | 6.0177 | 4.4735
[7 empty] | 3875 | 11 | 8.0888 | 6.0974
[7 empty] | 3876 | 12 | 9.0492 | 6.8504
[7 empty] | 3877 | 13 | 9.425 | 7.1451
[7 empty] | 3878 | 14 | 9.2079 | 6.9748
[7 empty] | 3879 | 15 | 9.116 | 6.9028
[7 empty] | 3880 | 16 | 10.2935 | 7.8261
[7 empty] | 3881 | 17 | 11.613 | 8.8607
[7 empty] | 3882 | 18 | 11.3708 | 8.6708
[7 empty] | 3883 | 19 | 11.8969 | 9.0833
[7 empty] | 3884 | 20 | 11.8301 | 9.0309
[7 empty] | 3885 | 21 | 12.398 | 9.4762
[7 empty] | 3886 | 22 | 8.4563 | 6.3855
[7 empty] | 3887 | 23 | 4.6983 | 3.4389
[7 empty] | 3888 | 24 | 3.0331 | 2.1333
[7 empty] | 3889 | 25 | 2.9362 | 2.0573
[7 empty] | 3890 | 26 | 2.8276 | 1.9722
[7 empty] | 3891 | 27 | 2.7274 | 1.8936
[7 empty] | 3892 | 28 | 2.8109 | 1.9591
[7 empty] | 3893 | 29 | 3.0531 | 2.149
[7 empty] | 3894 | 30 | 3.2953 | 2.3389
[7 empty] | 3895 | 31 | 4.1387 | 3.0002
[7 empty] | 3896 | 32 | 4.4895 | 3.2752
[7 empty] | 3897 | 33 | 5.1492 | 3.7925
[7 empty] | 3898 | 34 | 6.0428 | 4.4932
[7 empty] | 3899 | 35 | 8.2057 | 6.1891
[7 empty] | 3900 | 36 | 9.2329 | 6.9945
[7 empty] | 3901 | 37 | 9.3081 | 7.0534
[7 empty] | 3902 | 38 | 9.3832 | 7.1123
[7 empty] | 3903 | 39 | 9.0575 | 6.857
[7 empty] | 3904 | 40 | 10.1098 | 7.682
[7 empty] | 3905 | 41 | 10.6609 | 8.1142
[7 empty] | 3906 | 42 | 10.6776 | 8.1273
[7 empty] | 3907 | 43 | 11.0451 | 8.4154
[7 empty] | 3908 | 44 | 12.1975 | 9.319
[7 empty] | 3909 | 45 | 11.7967 | 9.0047
[7 empty] | 3910 | 46 | 9.0575 | 6.857
[7 empty] | 3911 | 47 | 5.4666 | 4.0414
[7 empty] | 3912 | 48 | 3.9717 | 2.8693
[7 empty] | 3913 | 49 | 3.312 | 2.352
[7 empty] | 3914 | 50 | 3.003 | 2.1097
[7 empty] | 3915 | 51 | 2.8944 | 2.0246
[7 empty] | 3916 | 52 | 2.9278 | 2.0508
[7 empty] | 3917 | 53 | 2.9529 | 2.0704
[7 empty] | 3918 | 54 | 3.5291 | 2.5222
[7 empty] | 3919 | 55 | 4.6648 | 3.4128
[7 empty] | 3920 | 56 | 4.907 | 3.6026
[7 empty] | 3921 | 57 | 5.8507 | 4.3426
[7 empty] | 3922 | 58 | 6.9531 | 5.2069
[7 empty] | 3923 | 59 | 8.1556 | 6.1498
[7 empty] | 3924 | 60 | 8.7819 | 6.6409
[7 empty] | 3925 | 61 | 9.4584 | 7.1713
[7 empty] | 3926 | 62 | 9.258 | 7.0141
[7 empty] | 3927 | 63 | 9.8509 | 7.479
[7 empty] | 3928 | 64 | 10.7946 | 8.219
[7 empty] | 3929 | 65 | 11.4125 | 8.7035
[7 empty] | 3930 | 66 | 11.3123 | 8.6249
[7 empty] | 3931 | 67 | 12.0472 | 9.2011
[7 empty] | 3932 | 68 | 12.2894 | 9.391
[7 empty] | 3933 | 69 | 11.78 | 8.9916
[7 empty] | 3934 | 70 | 9.4918 | 7.1975
[7 empty] | 3935 | 71 | 4.9905 | 3.6681
[7 empty] | 3936 | 72 | 3.9097 | 2.8206
[7 empty] | 3937 | 73 | 3.1951 | 2.2603
[7 empty] | 3938 | 74 | 2.9696 | 2.0835
[7 empty] | 3939 | 75 | 2.8694 | 2.0049
[7 empty] | 3940 | 76 | 2.8109 | 1.9591
[7 empty] | 3941 | 77 | 2.9863 | 2.0966
[7 empty] | 3942 | 78 | 3.3871 | 2.4109
[7 empty] | 3943 | 79 | 4.4978 | 3.2818
[7 empty] | 3944 | 80 | 4.6732 | 3.4193
[7 empty] | 3945 | 81 | 5.8507 | 4.3426
[7 empty] | 3946 | 82 | 6.9363 | 5.1938
[7 empty] | 3947 | 83 | 7.6712 | 5.77
[7 empty] | 3948 | 84 | 8.9072 | 6.7391
[7 empty] | 3949 | 85 | 8.6066 | 6.5034
[7 empty] | 3950 | 86 | 8.0972 | 6.104
[7 empty] | 3951 | 87 | 8.5398 | 6.451
[7 empty] | 3952 | 88 | 9.1995 | 6.9683
[7 empty] | 3953 | 89 | 10.544 | 8.0225
[7 empty] | 3954 | 90 | 9.9595 | 7.5642
[7 empty] | 3955 | 91 | 10.6442 | 8.1011
[7 empty] | 3956 | 92 | 10.043 | 7.6296
[7 empty] | 3957 | 93 | 7.6378 | 5.7438
[7 empty] | 3958 | 94 | 6.7359 | 5.0366
[7 empty] | 3959 | 95 | 4.882 | 3.583
[7 empty] | 3960 | 96 | 3.8965 | 2.8103
[7 empty] | 3961 | 97 | 3.8464 | 2.7711
[7 empty] | 3962 | 98 | 3.5541 | 2.5419
[7 empty] | 3963 | 99 | 3.4957 | 2.496
[7 empty] | 3964 | 100 | 3.1449 | 2.221
[7 empty] | 3965 | 101 | 3.0865 | 2.1752
[7 empty] | 3966 | 102 | 3.3203 | 2.3585
[7 empty] | 3967 | 103 | 4.0636 | 2.9413
[7 empty] | 3968 | 104 | 4.3141 | 3.1377
[7 empty] | 3969 | 105 | 4.7985 | 3.5175
[7 empty] | 3970 | 106 | 6.2516 | 4.6569
[7 empty] | 3971 | 107 | 6.6023 | 4.9319
[7 empty] | 3972 | 108 | 8.1723 | 6.1629
[7 empty] | 3973 | 109 | 7.5126 | 5.6456
[7 empty] | 3974 | 110 | 7.0616 | 5.292
[7 empty] | 3975 | 111 | 6.9029 | 5.1676
[7 empty] | 3976 | 112 | 6.9698 | 5.22
[7 empty] | 3977 | 113 | 6.6274 | 4.9515
[7 empty] | 3978 | 114 | 6.7944 | 5.0825
[7 empty] | 3979 | 115 | 6.3434 | 4.7289
[7 empty] | 3980 | 116 | 7.0199 | 5.2593
[7 empty] | 3981 | 117 | 6.6023 | 4.9319
[7 empty] | 3982 | 118 | 5.834 | 4.3295
[7 empty] | 3983 | 119 | 4.2473 | 3.0854
[7 empty] | 3984 | 120 | 3.9311 | 2.8374
[7 empty] | 3985 | 121 | 3.2034 | 2.2669
[7 empty] | 3986 | 122 | 2.7942 | 1.946
[7 empty] | 3987 | 123 | 2.7107 | 1.8805
[7 empty] | 3988 | 124 | 2.6773 | 1.8543
[7 empty] | 3989 | 125 | 2.6355 | 1.8216
[7 empty] | 3990 | 126 | 2.7775 | 1.9329
[7 empty] | 3991 | 127 | 4.2807 | 3.1115
[7 empty] | 3992 | 128 | 5.834 | 4.3295
[7 empty] | 3993 | 129 | 6.5104 | 4.8599
[7 empty] | 3994 | 130 | 6.9447 | 5.2003
[7 empty] | 3995 | 131 | 7.1034 | 5.3248
[7 empty] | 3996 | 132 | 6.8528 | 5.1283
[7 empty] | 3997 | 133 | 7.4875 | 5.626
[7 empty] | 3998 | 134 | 7.7882 | 5.8617
[7 empty] | 3999 | 135 | 7.855 | 5.9141
[7 empty] | 4000 | 136 | 7.0449 | 5.2789
[7 empty] | 4001 | 137 | 6.9447 | 5.2003
[7 empty] | 4002 | 138 | 6.8946 | 5.1611
[7 empty] | 4003 | 139 | 6.5605 | 4.8991
[7 empty] | 4004 | 140 | 6.5689 | 4.9057
[7 empty] | 4005 | 141 | 5.9175 | 4.3949
[7 empty] | 4006 | 142 | 5.2828 | 3.8973
[7 empty] | 4007 | 143 | 4.406 | 3.2098
[7 empty] | 4008 | 144 | 3.7963 | 2.7318
[7 empty] | 4009 | 145 | 3.3287 | 2.3651
[7 empty] | 4010 | 146 | 3.1199 | 2.2014
[7 empty] | 4011 | 147 | 3.0531 | 2.149
[7 empty] | 4012 | 148 | 3.0447 | 2.1424
[7 empty] | 4013 | 149 | 3.0447 | 2.1424
[7 empty] | 4014 | 150 | 3.0531 | 2.149
[7 empty] | 4015 | 151 | 4.1304 | 2.9937
[7 empty] | 4016 | 152 | 5.6503 | 4.1854
[7 empty] | 4017 | 153 | 6.2599 | 4.6634
[7 empty] | 4018 | 154 | 6.8194 | 5.1021
[7 empty] | 4019 | 155 | 6.6691 | 4.9843
[7 empty] | 4020 | 156 | 6.8361 | 5.1152
[7 empty] | 4021 | 157 | 7.546 | 5.6718
[7 empty] | 4022 | 158 | 7.8717 | 5.9272
[7 empty] | 4023 | 159 | 8.1389 | 6.1367
[7 empty] | 4024 | 160 | 8.0136 | 6.0385
[7 empty] | 4025 | 161 | 8.7736 | 6.6343
[7 empty] | 4026 | 162 | 8.2809 | 6.248
[7 empty] | 4027 | 163 | 8.64 | 6.5296
[7 empty] | 4028 | 164 | 7.2954 | 5.4754
[7 empty] | 4029 | 165 | 10.4104 | 7.9177
[7 empty] | 4030 | 166 | 8.3727 | 6.32
[7 empty] | 4031 | 167 | 4.7818 | 3.5044
[7 empty] | 4032 | 168 | 4.1387 | 3.0002
[7 empty] | 4033 | 1 | 2.6856 | 1.8609
[7 empty] | 4034 | 2 | 2.5771 | 1.7758
[7 empty] | 4035 | 3 | 2.5687 | 1.7692
[7 empty] | 4036 | 4 | 2.7023 | 1.874
[7 empty] | 4037 | 5 | 2.719 | 1.8871
[7 empty] | 4038 | 6 | 3.1449 | 2.221
[7 empty] | 4039 | 7 | 3.8631 | 2.7841
[7 empty] | 4040 | 8 | 4.5312 | 3.308
[7 empty] | 4041 | 9 | 4.5062 | 3.2883
[7 empty] | 4042 | 10 | 6.0177 | 4.4735
[7 empty] | 4043 | 11 | 8.0888 | 6.0974
[7 empty] | 4044 | 12 | 9.0492 | 6.8504
[7 empty] | 4045 | 13 | 9.425 | 7.1451
[7 empty] | 4046 | 14 | 9.2079 | 6.9748
[7 empty] | 4047 | 15 | 9.116 | 6.9028
[7 empty] | 4048 | 16 | 10.2935 | 7.8261
[7 empty] | 4049 | 17 | 11.613 | 8.8607
[7 empty] | 4050 | 18 | 11.3708 | 8.6708
[7 empty] | 4051 | 19 | 11.8969 | 9.0833
[7 empty] | 4052 | 20 | 11.8301 | 9.0309
[7 empty] | 4053 | 21 | 12.398 | 9.4762
[7 empty] | 4054 | 22 | 8.4563 | 6.3855
[7 empty] | 4055 | 23 | 4.6983 | 3.4389
[7 empty] | 4056 | 24 | 3.0331 | 2.1333
[7 empty] | 4057 | 25 | 2.9362 | 2.0573
[7 empty] | 4058 | 26 | 2.8276 | 1.9722
[7 empty] | 4059 | 27 | 2.7274 | 1.8936
[7 empty] | 4060 | 28 | 2.8109 | 1.9591
[7 empty] | 4061 | 29 | 3.0531 | 2.149
[7 empty] | 4062 | 30 | 3.2953 | 2.3389
[7 empty] | 4063 | 31 | 4.1387 | 3.0002
[7 empty] | 4064 | 32 | 4.4895 | 3.2752
[7 empty] | 4065 | 33 | 5.1492 | 3.7925
[7 empty] | 4066 | 34 | 6.0428 | 4.4932
[7 empty] | 4067 | 35 | 8.2057 | 6.1891
[7 empty] | 4068 | 36 | 9.2329 | 6.9945
[7 empty] | 4069 | 37 | 9.3081 | 7.0534
[7 empty] | 4070 | 38 | 9.3832 | 7.1123
[7 empty] | 4071 | 39 | 9.0575 | 6.857
[7 empty] | 4072 | 40 | 10.1098 | 7.682
[7 empty] | 4073 | 41 | 10.6609 | 8.1142
[7 empty] | 4074 | 42 | 10.6776 | 8.1273
[7 empty] | 4075 | 43 | 11.0451 | 8.4154
[7 empty] | 4076 | 44 | 12.1975 | 9.319
[7 empty] | 4077 | 45 | 11.7967 | 9.0047
[7 empty] | 4078 | 46 | 9.0575 | 6.857
[7 empty] | 4079 | 47 | 5.4666 | 4.0414
[7 empty] | 4080 | 48 | 3.9717 | 2.8693
[7 empty] | 4081 | 49 | 3.312 | 2.352
[7 empty] | 4082 | 50 | 3.003 | 2.1097
[7 empty] | 4083 | 51 | 2.8944 | 2.0246
[7 empty] | 4084 | 52 | 2.9278 | 2.0508
[7 empty] | 4085 | 53 | 2.9529 | 2.0704
[7 empty] | 4086 | 54 | 3.5291 | 2.5222
[7 empty] | 4087 | 55 | 4.6648 | 3.4128
[7 empty] | 4088 | 56 | 4.907 | 3.6026
[7 empty] | 4089 | 57 | 5.8507 | 4.3426
[7 empty] | 4090 | 58 | 6.9531 | 5.2069
[7 empty] | 4091 | 59 | 8.1556 | 6.1498
[7 empty] | 4092 | 60 | 8.7819 | 6.6409
[7 empty] | 4093 | 61 | 9.4584 | 7.1713
[7 empty] | 4094 | 62 | 9.258 | 7.0141
[7 empty] | 4095 | 63 | 9.8509 | 7.479
[7 empty] | 4096 | 64 | 10.7946 | 8.219
[7 empty] | 4097 | 65 | 11.4125 | 8.7035
[7 empty] | 4098 | 66 | 11.3123 | 8.6249
[7 empty] | 4099 | 67 | 12.0472 | 9.2011
[7 empty] | 4100 | 68 | 12.2894 | 9.391
[7 empty] | 4101 | 69 | 11.78 | 8.9916
[7 empty] | 4102 | 70 | 9.4918 | 7.1975
[7 empty] | 4103 | 71 | 4.9905 | 3.6681
[7 empty] | 4104 | 72 | 3.9097 | 2.8206
[7 empty] | 4105 | 73 | 3.1951 | 2.2603
[7 empty] | 4106 | 74 | 2.9696 | 2.0835
[7 empty] | 4107 | 75 | 2.8694 | 2.0049
[7 empty] | 4108 | 76 | 2.8109 | 1.9591
[7 empty] | 4109 | 77 | 2.9863 | 2.0966
[7 empty] | 4110 | 78 | 3.3871 | 2.4109
[7 empty] | 4111 | 79 | 4.4978 | 3.2818
[7 empty] | 4112 | 80 | 4.6732 | 3.4193
[7 empty] | 4113 | 81 | 5.8507 | 4.3426
[7 empty] | 4114 | 82 | 6.9363 | 5.1938
[7 empty] | 4115 | 83 | 7.6712 | 5.77
[7 empty] | 4116 | 84 | 8.9072 | 6.7391
[7 empty] | 4117 | 85 | 8.6066 | 6.5034
[7 empty] | 4118 | 86 | 8.0972 | 6.104
[7 empty] | 4119 | 87 | 8.5398 | 6.451
[7 empty] | 4120 | 88 | 9.1995 | 6.9683
[7 empty] | 4121 | 89 | 10.544 | 8.0225
[7 empty] | 4122 | 90 | 9.9595 | 7.5642
[7 empty] | 4123 | 91 | 10.6442 | 8.1011
[7 empty] | 4124 | 92 | 10.043 | 7.6296
[7 empty] | 4125 | 93 | 7.6378 | 5.7438
[7 empty] | 4126 | 94 | 6.7359 | 5.0366
[7 empty] | 4127 | 95 | 4.882 | 3.583
[7 empty] | 4128 | 96 | 3.8965 | 2.8103
[7 empty] | 4129 | 97 | 3.8464 | 2.7711
[7 empty] | 4130 | 98 | 3.5541 | 2.5419
[7 empty] | 4131 | 99 | 3.4957 | 2.496
[7 empty] | 4132 | 100 | 3.1449 | 2.221
[7 empty] | 4133 | 101 | 3.0865 | 2.1752
[7 empty] | 4134 | 102 | 3.3203 | 2.3585
[7 empty] | 4135 | 103 | 4.0636 | 2.9413
[7 empty] | 4136 | 104 | 4.3141 | 3.1377
[7 empty] | 4137 | 105 | 4.7985 | 3.5175
[7 empty] | 4138 | 106 | 6.2516 | 4.6569
[7 empty] | 4139 | 107 | 6.6023 | 4.9319
[7 empty] | 4140 | 108 | 8.1723 | 6.1629
[7 empty] | 4141 | 109 | 7.5126 | 5.6456
[7 empty] | 4142 | 110 | 7.0616 | 5.292
[7 empty] | 4143 | 111 | 6.9029 | 5.1676
[7 empty] | 4144 | 112 | 6.9698 | 5.22
[7 empty] | 4145 | 113 | 6.6274 | 4.9515
[7 empty] | 4146 | 114 | 6.7944 | 5.0825
[7 empty] | 4147 | 115 | 6.3434 | 4.7289
[7 empty] | 4148 | 116 | 7.0199 | 5.2593
[7 empty] | 4149 | 117 | 6.6023 | 4.9319
[7 empty] | 4150 | 118 | 5.834 | 4.3295
[7 empty] | 4151 | 119 | 4.2473 | 3.0854
[7 empty] | 4152 | 120 | 3.9311 | 2.8374
[7 empty] | 4153 | 121 | 3.2034 | 2.2669
[7 empty] | 4154 | 122 | 2.7942 | 1.946
[7 empty] | 4155 | 123 | 2.7107 | 1.8805
[7 empty] | 4156 | 124 | 2.6773 | 1.8543
[7 empty] | 4157 | 125 | 2.6355 | 1.8216
[7 empty] | 4158 | 126 | 2.7775 | 1.9329
[7 empty] | 4159 | 127 | 4.2807 | 3.1115
[7 empty] | 4160 | 128 | 5.834 | 4.3295
[7 empty] | 4161 | 129 | 6.5104 | 4.8599
[7 empty] | 4162 | 130 | 6.9447 | 5.2003
[7 empty] | 4163 | 131 | 7.1034 | 5.3248
[7 empty] | 4164 | 132 | 6.8528 | 5.1283
[7 empty] | 4165 | 133 | 7.4875 | 5.626
[7 empty] | 4166 | 134 | 7.7882 | 5.8617
[7 empty] | 4167 | 135 | 7.855 | 5.9141
[7 empty] | 4168 | 136 | 7.0449 | 5.2789
[7 empty] | 4169 | 137 | 6.9447 | 5.2003
[7 empty] | 4170 | 138 | 6.8946 | 5.1611
[7 empty] | 4171 | 139 | 6.5605 | 4.8991
[7 empty] | 4172 | 140 | 6.5689 | 4.9057
[7 empty] | 4173 | 141 | 5.9175 | 4.3949
[7 empty] | 4174 | 142 | 5.2828 | 3.8973
[7 empty] | 4175 | 143 | 4.406 | 3.2098
[7 empty] | 4176 | 144 | 3.7963 | 2.7318
[7 empty] | 4177 | 145 | 3.3287 | 2.3651
[7 empty] | 4178 | 146 | 3.1199 | 2.2014
[7 empty] | 4179 | 147 | 3.0531 | 2.149
[7 empty] | 4180 | 148 | 3.0447 | 2.1424
[7 empty] | 4181 | 149 | 3.0447 | 2.1424
[7 empty] | 4182 | 150 | 3.0531 | 2.149
[7 empty] | 4183 | 151 | 4.1304 | 2.9937
[7 empty] | 4184 | 152 | 5.6503 | 4.1854
[7 empty] | 4185 | 153 | 6.2599 | 4.6634
[7 empty] | 4186 | 154 | 6.8194 | 5.1021
[7 empty] | 4187 | 155 | 6.6691 | 4.9843
[7 empty] | 4188 | 156 | 6.8361 | 5.1152
[7 empty] | 4189 | 157 | 7.546 | 5.6718
[7 empty] | 4190 | 158 | 7.8717 | 5.9272
[7 empty] | 4191 | 159 | 8.1389 | 6.1367
[7 empty] | 4192 | 160 | 8.0136 | 6.0385
[7 empty] | 4193 | 161 | 8.7736 | 6.6343
[7 empty] | 4194 | 162 | 8.2809 | 6.248
[7 empty] | 4195 | 163 | 8.64 | 6.5296
[7 empty] | 4196 | 164 | 7.2954 | 5.4754
[7 empty] | 4197 | 165 | 10.4104 | 7.9177
[7 empty] | 4198 | 166 | 8.3727 | 6.32
[7 empty] | 4199 | 167 | 4.7818 | 3.5044
[7 empty] | 4200 | 168 | 4.1387 | 3.0002
[7 empty] | 4201 | 1 | 2.6856 | 1.8609
[7 empty] | 4202 | 2 | 2.5771 | 1.7758
[7 empty] | 4203 | 3 | 2.5687 | 1.7692
[7 empty] | 4204 | 4 | 2.7023 | 1.874
[7 empty] | 4205 | 5 | 2.719 | 1.8871
[7 empty] | 4206 | 6 | 3.1449 | 2.221
[7 empty] | 4207 | 7 | 3.8631 | 2.7841
[7 empty] | 4208 | 8 | 4.5312 | 3.308
[7 empty] | 4209 | 9 | 4.5062 | 3.2883
[7 empty] | 4210 | 10 | 6.0177 | 4.4735
[7 empty] | 4211 | 11 | 8.0888 | 6.0974
[7 empty] | 4212 | 12 | 9.0492 | 6.8504
[7 empty] | 4213 | 13 | 9.425 | 7.1451
[7 empty] | 4214 | 14 | 9.2079 | 6.9748
[7 empty] | 4215 | 15 | 9.116 | 6.9028
[7 empty] | 4216 | 16 | 10.2935 | 7.8261
[7 empty] | 4217 | 17 | 11.613 | 8.8607
[7 empty] | 4218 | 18 | 11.3708 | 8.6708
[7 empty] | 4219 | 19 | 11.8969 | 9.0833
[7 empty] | 4220 | 20 | 11.8301 | 9.0309
[7 empty] | 4221 | 21 | 12.398 | 9.4762
[7 empty] | 4222 | 22 | 8.4563 | 6.3855
[7 empty] | 4223 | 23 | 4.6983 | 3.4389
[7 empty] | 4224 | 24 | 3.0331 | 2.1333
[7 empty] | 4225 | 25 | 2.9362 | 2.0573
[7 empty] | 4226 | 26 | 2.8276 | 1.9722
[7 empty] | 4227 | 27 | 2.7274 | 1.8936
[7 empty] | 4228 | 28 | 2.8109 | 1.9591
[7 empty] | 4229 | 29 | 3.0531 | 2.149
[7 empty] | 4230 | 30 | 3.2953 | 2.3389
[7 empty] | 4231 | 31 | 4.1387 | 3.0002
[7 empty] | 4232 | 32 | 4.4895 | 3.2752
[7 empty] | 4233 | 33 | 5.1492 | 3.7925
[7 empty] | 4234 | 34 | 6.0428 | 4.4932
[7 empty] | 4235 | 35 | 8.2057 | 6.1891
[7 empty] | 4236 | 36 | 9.2329 | 6.9945
[7 empty] | 4237 | 37 | 9.3081 | 7.0534
[7 empty] | 4238 | 38 | 9.3832 | 7.1123
[7 empty] | 4239 | 39 | 9.0575 | 6.857
[7 empty] | 4240 | 40 | 10.1098 | 7.682
[7 empty] | 4241 | 41 | 10.6609 | 8.1142
[7 empty] | 4242 | 42 | 10.6776 | 8.1273
[7 empty] | 4243 | 43 | 11.0451 | 8.4154
[7 empty] | 4244 | 44 | 12.1975 | 9.319
[7 empty] | 4245 | 45 | 11.7967 | 9.0047
[7 empty] | 4246 | 46 | 9.0575 | 6.857
[7 empty] | 4247 | 47 | 5.4666 | 4.0414
[7 empty] | 4248 | 48 | 3.9717 | 2.8693
[7 empty] | 4249 | 49 | 3.312 | 2.352
[7 empty] | 4250 | 50 | 3.003 | 2.1097
[7 empty] | 4251 | 51 | 2.8944 | 2.0246
[7 empty] | 4252 | 52 | 2.9278 | 2.0508
[7 empty] | 4253 | 53 | 2.9529 | 2.0704
[7 empty] | 4254 | 54 | 3.5291 | 2.5222
[7 empty] | 4255 | 55 | 4.6648 | 3.4128
[7 empty] | 4256 | 56 | 4.907 | 3.6026
[7 empty] | 4257 | 57 | 5.8507 | 4.3426
[7 empty] | 4258 | 58 | 6.9531 | 5.2069
[7 empty] | 4259 | 59 | 8.1556 | 6.1498
[7 empty] | 4260 | 60 | 8.7819 | 6.6409
[7 empty] | 4261 | 61 | 9.4584 | 7.1713
[7 empty] | 4262 | 62 | 9.258 | 7.0141
[7 empty] | 4263 | 63 | 9.8509 | 7.479
[7 empty] | 4264 | 64 | 10.7946 | 8.219
[7 empty] | 4265 | 65 | 11.4125 | 8.7035
[7 empty] | 4266 | 66 | 11.3123 | 8.6249
[7 empty] | 4267 | 67 | 12.0472 | 9.2011
[7 empty] | 4268 | 68 | 12.2894 | 9.391
[7 empty] | 4269 | 69 | 11.78 | 8.9916
[7 empty] | 4270 | 70 | 9.4918 | 7.1975
[7 empty] | 4271 | 71 | 4.9905 | 3.6681
[7 empty] | 4272 | 72 | 3.9097 | 2.8206
[7 empty] | 4273 | 73 | 3.1951 | 2.2603
[7 empty] | 4274 | 74 | 2.9696 | 2.0835
[7 empty] | 4275 | 75 | 2.8694 | 2.0049
[7 empty] | 4276 | 76 | 2.8109 | 1.9591
[7 empty] | 4277 | 77 | 2.9863 | 2.0966
[7 empty] | 4278 | 78 | 3.3871 | 2.4109
[7 empty] | 4279 | 79 | 4.4978 | 3.2818
[7 empty] | 4280 | 80 | 4.6732 | 3.4193
[7 empty] | 4281 | 81 | 5.8507 | 4.3426
[7 empty] | 4282 | 82 | 6.9363 | 5.1938
[7 empty] | 4283 | 83 | 7.6712 | 5.77
[7 empty] | 4284 | 84 | 8.9072 | 6.7391
[7 empty] | 4285 | 85 | 8.6066 | 6.5034
[7 empty] | 4286 | 86 | 8.0972 | 6.104
[7 empty] | 4287 | 87 | 8.5398 | 6.451
[7 empty] | 4288 | 88 | 9.1995 | 6.9683
[7 empty] | 4289 | 89 | 10.544 | 8.0225
[7 empty] | 4290 | 90 | 9.9595 | 7.5642
[7 empty] | 4291 | 91 | 10.6442 | 8.1011
[7 empty] | 4292 | 92 | 10.043 | 7.6296
[7 empty] | 4293 | 93 | 7.6378 | 5.7438
[7 empty] | 4294 | 94 | 6.7359 | 5.0366
[7 empty] | 4295 | 95 | 4.882 | 3.583
[7 empty] | 4296 | 96 | 3.8965 | 2.8103
[7 empty] | 4297 | 97 | 3.8464 | 2.7711
[7 empty] | 4298 | 98 | 3.5541 | 2.5419
[7 empty] | 4299 | 99 | 3.4957 | 2.496
[7 empty] | 4300 | 100 | 3.1449 | 2.221
[7 empty] | 4301 | 101 | 3.0865 | 2.1752
[7 empty] | 4302 | 102 | 3.3203 | 2.3585
[7 empty] | 4303 | 103 | 4.0636 | 2.9413
[7 empty] | 4304 | 104 | 4.3141 | 3.1377
[7 empty] | 4305 | 105 | 4.7985 | 3.5175
[7 empty] | 4306 | 106 | 6.2516 | 4.6569
[7 empty] | 4307 | 107 | 6.6023 | 4.9319
[7 empty] | 4308 | 108 | 8.1723 | 6.1629
[7 empty] | 4309 | 109 | 7.5126 | 5.6456
[7 empty] | 4310 | 110 | 7.0616 | 5.292
[7 empty] | 4311 | 111 | 6.9029 | 5.1676
[7 empty] | 4312 | 112 | 6.9698 | 5.22
[7 empty] | 4313 | 113 | 6.6274 | 4.9515
[7 empty] | 4314 | 114 | 6.7944 | 5.0825
[7 empty] | 4315 | 115 | 6.3434 | 4.7289
[7 empty] | 4316 | 116 | 7.0199 | 5.2593
[7 empty] | 4317 | 117 | 6.6023 | 4.9319
[7 empty] | 4318 | 118 | 5.834 | 4.3295
[7 empty] | 4319 | 119 | 4.2473 | 3.0854
[7 empty] | 4320 | 120 | 3.9311 | 2.8374
[7 empty] | 4321 | 121 | 3.2034 | 2.2669
[7 empty] | 4322 | 122 | 2.7942 | 1.946
[7 empty] | 4323 | 123 | 2.7107 | 1.8805
[7 empty] | 4324 | 124 | 2.6773 | 1.8543
[7 empty] | 4325 | 125 | 2.6355 | 1.8216
[7 empty] | 4326 | 126 | 2.7775 | 1.9329
[7 empty] | 4327 | 127 | 4.2807 | 3.1115
[7 empty] | 4328 | 128 | 5.834 | 4.3295
[7 empty] | 4329 | 129 | 6.5104 | 4.8599
[7 empty] | 4330 | 130 | 6.9447 | 5.2003
[7 empty] | 4331 | 131 | 7.1034 | 5.3248
[7 empty] | 4332 | 132 | 6.8528 | 5.1283
[7 empty] | 4333 | 133 | 7.4875 | 5.626
[7 empty] | 4334 | 134 | 7.7882 | 5.8617
[7 empty] | 4335 | 135 | 7.855 | 5.9141
[7 empty] | 4336 | 136 | 7.0449 | 5.2789
[7 empty] | 4337 | 137 | 6.9447 | 5.2003
[7 empty] | 4338 | 138 | 6.8946 | 5.1611
[7 empty] | 4339 | 139 | 6.5605 | 4.8991
[7 empty] | 4340 | 140 | 6.5689 | 4.9057
[7 empty] | 4341 | 141 | 5.9175 | 4.3949
[7 empty] | 4342 | 142 | 5.2828 | 3.8973
[7 empty] | 4343 | 143 | 4.406 | 3.2098
[7 empty] | 4344 | 144 | 3.7963 | 2.7318
[7 empty] | 4345 | 145 | 3.3287 | 2.3651
[7 empty] | 4346 | 146 | 3.1199 | 2.2014
[7 empty] | 4347 | 147 | 3.0531 | 2.149
[7 empty] | 4348 | 148 | 3.0447 | 2.1424
[7 empty] | 4349 | 149 | 3.0447 | 2.1424
[7 empty] | 4350 | 150 | 3.0531 | 2.149
[7 empty] | 4351 | 151 | 4.1304 | 2.9937
[7 empty] | 4352 | 152 | 5.6503 | 4.1854
[7 empty] | 4353 | 153 | 6.2599 | 4.6634
[7 empty] | 4354 | 154 | 6.8194 | 5.1021
[7 empty] | 4355 | 155 | 6.6691 | 4.9843
[7 empty] | 4356 | 156 | 6.8361 | 5.1152
[7 empty] | 4357 | 157 | 7.546 | 5.6718
[7 empty] | 4358 | 158 | 7.8717 | 5.9272
[7 empty] | 4359 | 159 | 8.1389 | 6.1367
[7 empty] | 4360 | 160 | 8.0136 | 6.0385
[7 empty] | 4361 | 161 | 8.7736 | 6.6343
[7 empty] | 4362 | 162 | 8.2809 | 6.248
[7 empty] | 4363 | 163 | 8.64 | 6.5296
[7 empty] | 4364 | 164 | 7.2954 | 5.4754
[7 empty] | 4365 | 165 | 10.4104 | 7.9177
[7 empty] | 4366 | 166 | 8.3727 | 6.32
[7 empty] | 4367 | 167 | 4.7818 | 3.5044
[7 empty] | 4368 | 168 | 4.1387 | 3.0002
[7 empty] | 4369 | 1 | 2.6856 | 1.8609
[7 empty] | 4370 | 2 | 2.5771 | 1.7758
[7 empty] | 4371 | 3 | 2.5687 | 1.7692
[7 empty] | 4372 | 4 | 2.7023 | 1.874
[7 empty] | 4373 | 5 | 2.719 | 1.8871
[7 empty] | 4374 | 6 | 3.1449 | 2.221
[7 empty] | 4375 | 7 | 3.8631 | 2.7841
[7 empty] | 4376 | 8 | 4.5312 | 3.308
[7 empty] | 4377 | 9 | 4.5062 | 3.2883
[7 empty] | 4378 | 10 | 6.0177 | 4.4735
[7 empty] | 4379 | 11 | 8.0888 | 6.0974
[7 empty] | 4380 | 12 | 9.0492 | 6.8504
[7 empty] | 4381 | 13 | 9.425 | 7.1451
[7 empty] | 4382 | 14 | 9.2079 | 6.9748
[7 empty] | 4383 | 15 | 9.116 | 6.9028
[7 empty] | 4384 | 16 | 10.2935 | 7.8261
[7 empty] | 4385 | 17 | 11.613 | 8.8607
[7 empty] | 4386 | 18 | 11.3708 | 8.6708
[7 empty] | 4387 | 19 | 11.8969 | 9.0833
[7 empty] | 4388 | 20 | 11.8301 | 9.0309
[7 empty] | 4389 | 21 | 12.398 | 9.4762
[7 empty] | 4390 | 22 | 8.4563 | 6.3855
[7 empty] | 4391 | 23 | 4.6983 | 3.4389
[7 empty] | 4392 | 24 | 3.0331 | 2.1333
[7 empty] | 4393 | 25 | 2.9362 | 2.0573
[7 empty] | 4394 | 26 | 2.8276 | 1.9722
[7 empty] | 4395 | 27 | 2.7274 | 1.8936
[7 empty] | 4396 | 28 | 2.8109 | 1.9591
[7 empty] | 4397 | 29 | 3.0531 | 2.149
[7 empty] | 4398 | 30 | 3.2953 | 2.3389
[7 empty] | 4399 | 31 | 4.1387 | 3.0002
[7 empty] | 4400 | 32 | 4.4895 | 3.2752
[7 empty] | 4401 | 33 | 5.1492 | 3.7925
[7 empty] | 4402 | 34 | 6.0428 | 4.4932
[7 empty] | 4403 | 35 | 8.2057 | 6.1891
[7 empty] | 4404 | 36 | 9.2329 | 6.9945
[7 empty] | 4405 | 37 | 9.3081 | 7.0534
[7 empty] | 4406 | 38 | 9.3832 | 7.1123
[7 empty] | 4407 | 39 | 9.0575 | 6.857
[7 empty] | 4408 | 40 | 10.1098 | 7.682
[7 empty] | 4409 | 41 | 10.6609 | 8.1142
[7 empty] | 4410 | 42 | 10.6776 | 8.1273
[7 empty] | 4411 | 43 | 11.0451 | 8.4154
[7 empty] | 4412 | 44 | 12.1975 | 9.319
[7 empty] | 4413 | 45 | 11.7967 | 9.0047
[7 empty] | 4414 | 46 | 9.0575 | 6.857
[7 empty] | 4415 | 47 | 5.4666 | 4.0414
[7 empty] | 4416 | 48 | 3.9717 | 2.8693
[7 empty] | 4417 | 49 | 3.312 | 2.352
[7 empty] | 4418 | 50 | 3.003 | 2.1097
[7 empty] | 4419 | 51 | 2.8944 | 2.0246
[7 empty] | 4420 | 52 | 2.9278 | 2.0508
[7 empty] | 4421 | 53 | 2.9529 | 2.0704
[7 empty] | 4422 | 54 | 3.5291 | 2.5222
[7 empty] | 4423 | 55 | 4.6648 | 3.4128
[7 empty] | 4424 | 56 | 4.907 | 3.6026
[7 empty] | 4425 | 57 | 5.8507 | 4.3426
[7 empty] | 4426 | 58 | 6.9531 | 5.2069
[7 empty] | 4427 | 59 | 8.1556 | 6.1498
[7 empty] | 4428 | 60 | 8.7819 | 6.6409
[7 empty] | 4429 | 61 | 9.4584 | 7.1713
[7 empty] | 4430 | 62 | 9.258 | 7.0141
[7 empty] | 4431 | 63 | 9.8509 | 7.479
[7 empty] | 4432 | 64 | 10.7946 | 8.219
[7 empty] | 4433 | 65 | 11.4125 | 8.7035
[7 empty] | 4434 | 66 | 11.3123 | 8.6249
[7 empty] | 4435 | 67 | 12.0472 | 9.2011
[7 empty] | 4436 | 68 | 12.2894 | 9.391
[7 empty] | 4437 | 69 | 11.78 | 8.9916
[7 empty] | 4438 | 70 | 9.4918 | 7.1975
[7 empty] | 4439 | 71 | 4.9905 | 3.6681
[7 empty] | 4440 | 72 | 3.9097 | 2.8206
[7 empty] | 4441 | 73 | 3.1951 | 2.2603
[7 empty] | 4442 | 74 | 2.9696 | 2.0835
[7 empty] | 4443 | 75 | 2.8694 | 2.0049
[7 empty] | 4444 | 76 | 2.8109 | 1.9591
[7 empty] | 4445 | 77 | 2.9863 | 2.0966
[7 empty] | 4446 | 78 | 3.3871 | 2.4109
[7 empty] | 4447 | 79 | 4.4978 | 3.2818
[7 empty] | 4448 | 80 | 4.6732 | 3.4193
[7 empty] | 4449 | 81 | 5.8507 | 4.3426
[7 empty] | 4450 | 82 | 6.9363 | 5.1938
[7 empty] | 4451 | 83 | 7.6712 | 5.77
[7 empty] | 4452 | 84 | 8.9072 | 6.7391
[7 empty] | 4453 | 85 | 8.6066 | 6.5034
[7 empty] | 4454 | 86 | 8.0972 | 6.104
[7 empty] | 4455 | 87 | 8.5398 | 6.451
[7 empty] | 4456 | 88 | 9.1995 | 6.9683
[7 empty] | 4457 | 89 | 10.544 | 8.0225
[7 empty] | 4458 | 90 | 9.9595 | 7.5642
[7 empty] | 4459 | 91 | 10.6442 | 8.1011
[7 empty] | 4460 | 92 | 10.043 | 7.6296
[7 empty] | 4461 | 93 | 7.6378 | 5.7438
[7 empty] | 4462 | 94 | 6.7359 | 5.0366
[7 empty] | 4463 | 95 | 4.882 | 3.583
[7 empty] | 4464 | 96 | 3.8965 | 2.8103
[7 empty] | 4465 | 97 | 3.8464 | 2.7711
[7 empty] | 4466 | 98 | 3.5541 | 2.5419
[7 empty] | 4467 | 99 | 3.4957 | 2.496
[7 empty] | 4468 | 100 | 3.1449 | 2.221
[7 empty] | 4469 | 101 | 3.0865 | 2.1752
[7 empty] | 4470 | 102 | 3.3203 | 2.3585
[7 empty] | 4471 | 103 | 4.0636 | 2.9413
[7 empty] | 4472 | 104 | 4.3141 | 3.1377
[7 empty] | 4473 | 105 | 4.7985 | 3.5175
[7 empty] | 4474 | 106 | 6.2516 | 4.6569
[7 empty] | 4475 | 107 | 6.6023 | 4.9319
[7 empty] | 4476 | 108 | 8.1723 | 6.1629
[7 empty] | 4477 | 109 | 7.5126 | 5.6456
[7 empty] | 4478 | 110 | 7.0616 | 5.292
[7 empty] | 4479 | 111 | 6.9029 | 5.1676
[7 empty] | 4480 | 112 | 6.9698 | 5.22
[7 empty] | 4481 | 113 | 6.6274 | 4.9515
[7 empty] | 4482 | 114 | 6.7944 | 5.0825
[7 empty] | 4483 | 115 | 6.3434 | 4.7289
[7 empty] | 4484 | 116 | 7.0199 | 5.2593
[7 empty] | 4485 | 117 | 6.6023 | 4.9319
[7 empty] | 4486 | 118 | 5.834 | 4.3295
[7 empty] | 4487 | 119 | 4.2473 | 3.0854
[7 empty] | 4488 | 120 | 3.9311 | 2.8374
[7 empty] | 4489 | 121 | 3.2034 | 2.2669
[7 empty] | 4490 | 122 | 2.7942 | 1.946
[7 empty] | 4491 | 123 | 2.7107 | 1.8805
[7 empty] | 4492 | 124 | 2.6773 | 1.8543
[7 empty] | 4493 | 125 | 2.6355 | 1.8216
[7 empty] | 4494 | 126 | 2.7775 | 1.9329
[7 empty] | 4495 | 127 | 4.2807 | 3.1115
[7 empty] | 4496 | 128 | 5.834 | 4.3295
[7 empty] | 4497 | 129 | 6.5104 | 4.8599
[7 empty] | 4498 | 130 | 6.9447 | 5.2003
[7 empty] | 4499 | 131 | 7.1034 | 5.3248
[7 empty] | 4500 | 132 | 6.8528 | 5.1283
[7 empty] | 4501 | 133 | 7.4875 | 5.626
[7 empty] | 4502 | 134 | 7.7882 | 5.8617
[7 empty] | 4503 | 135 | 7.855 | 5.9141
[7 empty] | 4504 | 136 | 7.0449 | 5.2789
[7 empty] | 4505 | 137 | 6.9447 | 5.2003
[7 empty] | 4506 | 138 | 6.8946 | 5.1611
[7 empty] | 4507 | 139 | 6.5605 | 4.8991
[7 empty] | 4508 | 140 | 6.5689 | 4.9057
[7 empty] | 4509 | 141 | 5.9175 | 4.3949
[7 empty] | 4510 | 142 | 5.2828 | 3.8973
[7 empty] | 4511 | 143 | 4.406 | 3.2098
[7 empty] | 4512 | 144 | 3.7963 | 2.7318
[7 empty] | 4513 | 145 | 3.3287 | 2.3651
[7 empty] | 4514 | 146 | 3.1199 | 2.2014
[7 empty] | 4515 | 147 | 3.0531 | 2.149
[7 empty] | 4516 | 148 | 3.0447 | 2.1424
[7 empty] | 4517 | 149 | 3.0447 | 2.1424
[7 empty] | 4518 | 150 | 3.0531 | 2.149
[7 empty] | 4519 | 151 | 4.1304 | 2.9937
[7 empty] | 4520 | 152 | 5.6503 | 4.1854
[7 empty] | 4521 | 153 | 6.2599 | 4.6634
[7 empty] | 4522 | 154 | 6.8194 | 5.1021
[7 empty] | 4523 | 155 | 6.6691 | 4.9843
[7 empty] | 4524 | 156 | 6.8361 | 5.1152
[7 empty] | 4525 | 157 | 7.546 | 5.6718
[7 empty] | 4526 | 158 | 7.8717 | 5.9272
[7 empty] | 4527 | 159 | 8.1389 | 6.1367
[7 empty] | 4528 | 160 | 8.0136 | 6.0385
[7 empty] | 4529 | 161 | 8.7736 | 6.6343
[7 empty] | 4530 | 162 | 8.2809 | 6.248
[7 empty] | 4531 | 163 | 8.64 | 6.5296
[7 empty] | 4532 | 164 | 7.2954 | 5.4754
[7 empty] | 4533 | 165 | 10.4104 | 7.9177
[7 empty] | 4534 | 166 | 8.3727 | 6.32
[7 empty] | 4535 | 167 | 4.7818 | 3.5044
[7 empty] | 4536 | 168 | 4.1387 | 3.0002
[7 empty] | 4537 | 1 | 2.6856 | 1.8609
[7 empty] | 4538 | 2 | 2.5771 | 1.7758
[7 empty] | 4539 | 3 | 2.5687 | 1.7692
[7 empty] | 4540 | 4 | 2.7023 | 1.874
[7 empty] | 4541 | 5 | 2.719 | 1.8871
[7 empty] | 4542 | 6 | 3.1449 | 2.221
[7 empty] | 4543 | 7 | 3.8631 | 2.7841
[7 empty] | 4544 | 8 | 4.5312 | 3.308
[7 empty] | 4545 | 9 | 4.5062 | 3.2883
[7 empty] | 4546 | 10 | 6.0177 | 4.4735
[7 empty] | 4547 | 11 | 8.0888 | 6.0974
[7 empty] | 4548 | 12 | 9.0492 | 6.8504
[7 empty] | 4549 | 13 | 9.425 | 7.1451
[7 empty] | 4550 | 14 | 9.2079 | 6.9748
[7 empty] | 4551 | 15 | 9.116 | 6.9028
[7 empty] | 4552 | 16 | 10.2935 | 7.8261
[7 empty] | 4553 | 17 | 11.613 | 8.8607
[7 empty] | 4554 | 18 | 11.3708 | 8.6708
[7 empty] | 4555 | 19 | 11.8969 | 9.0833
[7 empty] | 4556 | 20 | 11.8301 | 9.0309
[7 empty] | 4557 | 21 | 12.398 | 9.4762
[7 empty] | 4558 | 22 | 8.4563 | 6.3855
[7 empty] | 4559 | 23 | 4.6983 | 3.4389
[7 empty] | 4560 | 24 | 3.0331 | 2.1333
[7 empty] | 4561 | 25 | 2.9362 | 2.0573
[7 empty] | 4562 | 26 | 2.8276 | 1.9722
[7 empty] | 4563 | 27 | 2.7274 | 1.8936
[7 empty] | 4564 | 28 | 2.8109 | 1.9591
[7 empty] | 4565 | 29 | 3.0531 | 2.149
[7 empty] | 4566 | 30 | 3.2953 | 2.3389
[7 empty] | 4567 | 31 | 4.1387 | 3.0002
[7 empty] | 4568 | 32 | 4.4895 | 3.2752
[7 empty] | 4569 | 33 | 5.1492 | 3.7925
[7 empty] | 4570 | 34 | 6.0428 | 4.4932
[7 empty] | 4571 | 35 | 8.2057 | 6.1891
[7 empty] | 4572 | 36 | 9.2329 | 6.9945
[7 empty] | 4573 | 37 | 9.3081 | 7.0534
[7 empty] | 4574 | 38 | 9.3832 | 7.1123
[7 empty] | 4575 | 39 | 9.0575 | 6.857
[7 empty] | 4576 | 40 | 10.1098 | 7.682
[7 empty] | 4577 | 41 | 10.6609 | 8.1142
[7 empty] | 4578 | 42 | 10.6776 | 8.1273
[7 empty] | 4579 | 43 | 11.0451 | 8.4154
[7 empty] | 4580 | 44 | 12.1975 | 9.319
[7 empty] | 4581 | 45 | 11.7967 | 9.0047
[7 empty] | 4582 | 46 | 9.0575 | 6.857
[7 empty] | 4583 | 47 | 5.4666 | 4.0414
[7 empty] | 4584 | 48 | 3.9717 | 2.8693
[7 empty] | 4585 | 49 | 3.312 | 2.352
[7 empty] | 4586 | 50 | 3.003 | 2.1097
[7 empty] | 4587 | 51 | 2.8944 | 2.0246
[7 empty] | 4588 | 52 | 2.9278 | 2.0508
[7 empty] | 4589 | 53 | 2.9529 | 2.0704
[7 empty] | 4590 | 54 | 3.5291 | 2.5222
[7 empty] | 4591 | 55 | 4.6648 | 3.4128
[7 empty] | 4592 | 56 | 4.907 | 3.6026
[7 empty] | 4593 | 57 | 5.8507 | 4.3426
[7 empty] | 4594 | 58 | 6.9531 | 5.2069
[7 empty] | 4595 | 59 | 8.1556 | 6.1498
[7 empty] | 4596 | 60 | 8.7819 | 6.6409
[7 empty] | 4597 | 61 | 9.4584 | 7.1713
[7 empty] | 4598 | 62 | 9.258 | 7.0141
[7 empty] | 4599 | 63 | 9.8509 | 7.479
[7 empty] | 4600 | 64 | 10.7946 | 8.219
[7 empty] | 4601 | 65 | 11.4125 | 8.7035
[7 empty] | 4602 | 66 | 11.3123 | 8.6249
[7 empty] | 4603 | 67 | 12.0472 | 9.2011
[7 empty] | 4604 | 68 | 12.2894 | 9.391
[7 empty] | 4605 | 69 | 11.78 | 8.9916
[7 empty] | 4606 | 70 | 9.4918 | 7.1975
[7 empty] | 4607 | 71 | 4.9905 | 3.6681
[7 empty] | 4608 | 72 | 3.9097 | 2.8206
[7 empty] | 4609 | 73 | 3.1951 | 2.2603
[7 empty] | 4610 | 74 | 2.9696 | 2.0835
[7 empty] | 4611 | 75 | 2.8694 | 2.0049
[7 empty] | 4612 | 76 | 2.8109 | 1.9591
[7 empty] | 4613 | 77 | 2.9863 | 2.0966
[7 empty] | 4614 | 78 | 3.3871 | 2.4109
[7 empty] | 4615 | 79 | 4.4978 | 3.2818
[7 empty] | 4616 | 80 | 4.6732 | 3.4193
[7 empty] | 4617 | 81 | 5.8507 | 4.3426
[7 empty] | 4618 | 82 | 6.9363 | 5.1938
[7 empty] | 4619 | 83 | 7.6712 | 5.77
[7 empty] | 4620 | 84 | 8.9072 | 6.7391
[7 empty] | 4621 | 85 | 8.6066 | 6.5034
[7 empty] | 4622 | 86 | 8.0972 | 6.104
[7 empty] | 4623 | 87 | 8.5398 | 6.451
[7 empty] | 4624 | 88 | 9.1995 | 6.9683
[7 empty] | 4625 | 89 | 10.544 | 8.0225
[7 empty] | 4626 | 90 | 9.9595 | 7.5642
[7 empty] | 4627 | 91 | 10.6442 | 8.1011
[7 empty] | 4628 | 92 | 10.043 | 7.6296
[7 empty] | 4629 | 93 | 7.6378 | 5.7438
[7 empty] | 4630 | 94 | 6.7359 | 5.0366
[7 empty] | 4631 | 95 | 4.882 | 3.583
[7 empty] | 4632 | 96 | 3.8965 | 2.8103
[7 empty] | 4633 | 97 | 3.8464 | 2.7711
[7 empty] | 4634 | 98 | 3.5541 | 2.5419
[7 empty] | 4635 | 99 | 3.4957 | 2.496
[7 empty] | 4636 | 100 | 3.1449 | 2.221
[7 empty] | 4637 | 101 | 3.0865 | 2.1752
[7 empty] | 4638 | 102 | 3.3203 | 2.3585
[7 empty] | 4639 | 103 | 4.0636 | 2.9413
[7 empty] | 4640 | 104 | 4.3141 | 3.1377
[7 empty] | 4641 | 105 | 4.7985 | 3.5175
[7 empty] | 4642 | 106 | 6.2516 | 4.6569
[7 empty] | 4643 | 107 | 6.6023 | 4.9319
[7 empty] | 4644 | 108 | 8.1723 | 6.1629
[7 empty] | 4645 | 109 | 7.5126 | 5.6456
[7 empty] | 4646 | 110 | 7.0616 | 5.292
[7 empty] | 4647 | 111 | 6.9029 | 5.1676
[7 empty] | 4648 | 112 | 6.9698 | 5.22
[7 empty] | 4649 | 113 | 6.6274 | 4.9515
[7 empty] | 4650 | 114 | 6.7944 | 5.0825
[7 empty] | 4651 | 115 | 6.3434 | 4.7289
[7 empty] | 4652 | 116 | 7.0199 | 5.2593
[7 empty] | 4653 | 117 | 6.6023 | 4.9319
[7 empty] | 4654 | 118 | 5.834 | 4.3295
[7 empty] | 4655 | 119 | 4.2473 | 3.0854
[7 empty] | 4656 | 120 | 3.9311 | 2.8374
[7 empty] | 4657 | 121 | 3.2034 | 2.2669
[7 empty] | 4658 | 122 | 2.7942 | 1.946
[7 empty] | 4659 | 123 | 2.7107 | 1.8805
[7 empty] | 4660 | 124 | 2.6773 | 1.8543
[7 empty] | 4661 | 125 | 2.6355 | 1.8216
[7 empty] | 4662 | 126 | 2.7775 | 1.9329
[7 empty] | 4663 | 127 | 4.2807 | 3.1115
[7 empty] | 4664 | 128 | 5.834 | 4.3295
[7 empty] | 4665 | 129 | 6.5104 | 4.8599
[7 empty] | 4666 | 130 | 6.9447 | 5.2003
[7 empty] | 4667 | 131 | 7.1034 | 5.3248
[7 empty] | 4668 | 132 | 6.8528 | 5.1283
[7 empty] | 4669 | 133 | 7.4875 | 5.626
[7 empty] | 4670 | 134 | 7.7882 | 5.8617
[7 empty] | 4671 | 135 | 7.855 | 5.9141
[7 empty] | 4672 | 136 | 7.0449 | 5.2789
[7 empty] | 4673 | 137 | 6.9447 | 5.2003
[7 empty] | 4674 | 138 | 6.8946 | 5.1611
[7 empty] | 4675 | 139 | 6.5605 | 4.8991
[7 empty] | 4676 | 140 | 6.5689 | 4.9057
[7 empty] | 4677 | 141 | 5.9175 | 4.3949
[7 empty] | 4678 | 142 | 5.2828 | 3.8973
[7 empty] | 4679 | 143 | 4.406 | 3.2098
[7 empty] | 4680 | 144 | 3.7963 | 2.7318
[7 empty] | 4681 | 145 | 3.3287 | 2.3651
[7 empty] | 4682 | 146 | 3.1199 | 2.2014
[7 empty] | 4683 | 147 | 3.0531 | 2.149
[7 empty] | 4684 | 148 | 3.0447 | 2.1424
[7 empty] | 4685 | 149 | 3.0447 | 2.1424
[7 empty] | 4686 | 150 | 3.0531 | 2.149
[7 empty] | 4687 | 151 | 4.1304 | 2.9937
[7 empty] | 4688 | 152 | 5.6503 | 4.1854
[7 empty] | 4689 | 153 | 6.2599 | 4.6634
[7 empty] | 4690 | 154 | 6.8194 | 5.1021
[7 empty] | 4691 | 155 | 6.6691 | 4.9843
[7 empty] | 4692 | 156 | 6.8361 | 5.1152
[7 empty] | 4693 | 157 | 7.546 | 5.6718
[7 empty] | 4694 | 158 | 7.8717 | 5.9272
[7 empty] | 4695 | 159 | 8.1389 | 6.1367
[7 empty] | 4696 | 160 | 8.0136 | 6.0385
[7 empty] | 4697 | 161 | 8.7736 | 6.6343
[7 empty] | 4698 | 162 | 8.2809 | 6.248
[7 empty] | 4699 | 163 | 8.64 | 6.5296
[7 empty] | 4700 | 164 | 7.2954 | 5.4754
[7 empty] | 4701 | 165 | 10.4104 | 7.9177
[7 empty] | 4702 | 166 | 8.3727 | 6.32
[7 empty] | 4703 | 167 | 4.7818 | 3.5044
[7 empty] | 4704 | 168 | 4.1387 | 3.0002
[7 empty] | 4705 | 1 | 2.6856 | 1.8609
[7 empty] | 4706 | 2 | 2.5771 | 1.7758
[7 empty] | 4707 | 3 | 2.5687 | 1.7692
[7 empty] | 4708 | 4 | 2.7023 | 1.874
[7 empty] | 4709 | 5 | 2.719 | 1.8871
[7 empty] | 4710 | 6 | 3.1449 | 2.221
[7 empty] | 4711 | 7 | 3.8631 | 2.7841
[7 empty] | 4712 | 8 | 4.5312 | 3.308
[7 empty] | 4713 | 9 | 4.5062 | 3.2883
[7 empty] | 4714 | 10 | 6.0177 | 4.4735
[7 empty] | 4715 | 11 | 8.0888 | 6.0974
[7 empty] | 4716 | 12 | 9.0492 | 6.8504
[7 empty] | 4717 | 13 | 9.425 | 7.1451
[7 empty] | 4718 | 14 | 9.2079 | 6.9748
[7 empty] | 4719 | 15 | 9.116 | 6.9028
[7 empty] | 4720 | 16 | 10.2935 | 7.8261
[7 empty] | 4721 | 17 | 11.613 | 8.8607
[7 empty] | 4722 | 18 | 11.3708 | 8.6708
[7 empty] | 4723 | 19 | 11.8969 | 9.0833
[7 empty] | 4724 | 20 | 11.8301 | 9.0309
[7 empty] | 4725 | 21 | 12.398 | 9.4762
[7 empty] | 4726 | 22 | 8.4563 | 6.3855
[7 empty] | 4727 | 23 | 4.6983 | 3.4389
[7 empty] | 4728 | 24 | 3.0331 | 2.1333
[7 empty] | 4729 | 25 | 2.9362 | 2.0573
[7 empty] | 4730 | 26 | 2.8276 | 1.9722
[7 empty] | 4731 | 27 | 2.7274 | 1.8936
[7 empty] | 4732 | 28 | 2.8109 | 1.9591
[7 empty] | 4733 | 29 | 3.0531 | 2.149
[7 empty] | 4734 | 30 | 3.2953 | 2.3389
[7 empty] | 4735 | 31 | 4.1387 | 3.0002
[7 empty] | 4736 | 32 | 4.4895 | 3.2752
[7 empty] | 4737 | 33 | 5.1492 | 3.7925
[7 empty] | 4738 | 34 | 6.0428 | 4.4932
[7 empty] | 4739 | 35 | 8.2057 | 6.1891
[7 empty] | 4740 | 36 | 9.2329 | 6.9945
[7 empty] | 4741 | 37 | 9.3081 | 7.0534
[7 empty] | 4742 | 38 | 9.3832 | 7.1123
[7 empty] | 4743 | 39 | 9.0575 | 6.857
[7 empty] | 4744 | 40 | 10.1098 | 7.682
[7 empty] | 4745 | 41 | 10.6609 | 8.1142
[7 empty] | 4746 | 42 | 10.6776 | 8.1273
[7 empty] | 4747 | 43 | 11.0451 | 8.4154
[7 empty] | 4748 | 44 | 12.1975 | 9.319
[7 empty] | 4749 | 45 | 11.7967 | 9.0047
[7 empty] | 4750 | 46 | 9.0575 | 6.857
[7 empty] | 4751 | 47 | 5.4666 | 4.0414
[7 empty] | 4752 | 48 | 3.9717 | 2.8693
[7 empty] | 4753 | 49 | 3.312 | 2.352
[7 empty] | 4754 | 50 | 3.003 | 2.1097
[7 empty] | 4755 | 51 | 2.8944 | 2.0246
[7 empty] | 4756 | 52 | 2.9278 | 2.0508
[7 empty] | 4757 | 53 | 2.9529 | 2.0704
[7 empty] | 4758 | 54 | 3.5291 | 2.5222
[7 empty] | 4759 | 55 | 4.6648 | 3.4128
[7 empty] | 4760 | 56 | 4.907 | 3.6026
[7 empty] | 4761 | 57 | 5.8507 | 4.3426
[7 empty] | 4762 | 58 | 6.9531 | 5.2069
[7 empty] | 4763 | 59 | 8.1556 | 6.1498
[7 empty] | 4764 | 60 | 8.7819 | 6.6409
[7 empty] | 4765 | 61 | 9.4584 | 7.1713
[7 empty] | 4766 | 62 | 9.258 | 7.0141
[7 empty] | 4767 | 63 | 9.8509 | 7.479
[7 empty] | 4768 | 64 | 10.7946 | 8.219
[7 empty] | 4769 | 65 | 11.4125 | 8.7035
[7 empty] | 4770 | 66 | 11.3123 | 8.6249
[7 empty] | 4771 | 67 | 12.0472 | 9.2011
[7 empty] | 4772 | 68 | 12.2894 | 9.391
[7 empty] | 4773 | 69 | 11.78 | 8.9916
[7 empty] | 4774 | 70 | 9.4918 | 7.1975
[7 empty] | 4775 | 71 | 4.9905 | 3.6681
[7 empty] | 4776 | 72 | 3.9097 | 2.8206
[7 empty] | 4777 | 73 | 3.1951 | 2.2603
[7 empty] | 4778 | 74 | 2.9696 | 2.0835
[7 empty] | 4779 | 75 | 2.8694 | 2.0049
[7 empty] | 4780 | 76 | 2.8109 | 1.9591
[7 empty] | 4781 | 77 | 2.9863 | 2.0966
[7 empty] | 4782 | 78 | 3.3871 | 2.4109
[7 empty] | 4783 | 79 | 4.4978 | 3.2818
[7 empty] | 4784 | 80 | 4.6732 | 3.4193
[7 empty] | 4785 | 81 | 5.8507 | 4.3426
[7 empty] | 4786 | 82 | 6.9363 | 5.1938
[7 empty] | 4787 | 83 | 7.6712 | 5.77
[7 empty] | 4788 | 84 | 8.9072 | 6.7391
[7 empty] | 4789 | 85 | 8.6066 | 6.5034
[7 empty] | 4790 | 86 | 8.0972 | 6.104
[7 empty] | 4791 | 87 | 8.5398 | 6.451
[7 empty] | 4792 | 88 | 9.1995 | 6.9683
[7 empty] | 4793 | 89 | 10.544 | 8.0225
[7 empty] | 4794 | 90 | 9.9595 | 7.5642
[7 empty] | 4795 | 91 | 10.6442 | 8.1011
[7 empty] | 4796 | 92 | 10.043 | 7.6296
[7 empty] | 4797 | 93 | 7.6378 | 5.7438
[7 empty] | 4798 | 94 | 6.7359 | 5.0366
[7 empty] | 4799 | 95 | 4.882 | 3.583
[7 empty] | 4800 | 96 | 3.8965 | 2.8103
[7 empty] | 4801 | 97 | 3.8464 | 2.7711
[7 empty] | 4802 | 98 | 3.5541 | 2.5419
[7 empty] | 4803 | 99 | 3.4957 | 2.496
[7 empty] | 4804 | 100 | 3.1449 | 2.221
[7 empty] | 4805 | 101 | 3.0865 | 2.1752
[7 empty] | 4806 | 102 | 3.3203 | 2.3585
[7 empty] | 4807 | 103 | 4.0636 | 2.9413
[7 empty] | 4808 | 104 | 4.3141 | 3.1377
[7 empty] | 4809 | 105 | 4.7985 | 3.5175
[7 empty] | 4810 | 106 | 6.2516 | 4.6569
[7 empty] | 4811 | 107 | 6.6023 | 4.9319
[7 empty] | 4812 | 108 | 8.1723 | 6.1629
[7 empty] | 4813 | 109 | 7.5126 | 5.6456
[7 empty] | 4814 | 110 | 7.0616 | 5.292
[7 empty] | 4815 | 111 | 6.9029 | 5.1676
[7 empty] | 4816 | 112 | 6.9698 | 5.22
[7 empty] | 4817 | 113 | 6.6274 | 4.9515
[7 empty] | 4818 | 114 | 6.7944 | 5.0825
[7 empty] | 4819 | 115 | 6.3434 | 4.7289
[7 empty] | 4820 | 116 | 7.0199 | 5.2593
[7 empty] | 4821 | 117 | 6.6023 | 4.9319
[7 empty] | 4822 | 118 | 5.834 | 4.3295
[7 empty] | 4823 | 119 | 4.2473 | 3.0854
[7 empty] | 4824 | 120 | 3.9311 | 2.8374
[7 empty] | 4825 | 121 | 3.2034 | 2.2669
[7 empty] | 4826 | 122 | 2.7942 | 1.946
[7 empty] | 4827 | 123 | 2.7107 | 1.8805
[7 empty] | 4828 | 124 | 2.6773 | 1.8543
[7 empty] | 4829 | 125 | 2.6355 | 1.8216
[7 empty] | 4830 | 126 | 2.7775 | 1.9329
[7 empty] | 4831 | 127 | 4.2807 | 3.1115
[7 empty] | 4832 | 128 | 5.834 | 4.3295
[7 empty] | 4833 | 129 | 6.5104 | 4.8599
[7 empty] | 4834 | 130 | 6.9447 | 5.2003
[7 empty] | 4835 | 131 | 7.1034 | 5.3248
[7 empty] | 4836 | 132 | 6.8528 | 5.1283
[7 empty] | 4837 | 133 | 7.4875 | 5.626
[7 empty] | 4838 | 134 | 7.7882 | 5.8617
[7 empty] | 4839 | 135 | 7.855 | 5.9141
[7 empty] | 4840 | 136 | 7.0449 | 5.2789
[7 empty] | 4841 | 137 | 6.9447 | 5.2003
[7 empty] | 4842 | 138 | 6.8946 | 5.1611
[7 empty] | 4843 | 139 | 6.5605 | 4.8991
[7 empty] | 4844 | 140 | 6.5689 | 4.9057
[7 empty] | 4845 | 141 | 5.9175 | 4.3949
[7 empty] | 4846 | 142 | 5.2828 | 3.8973
[7 empty] | 4847 | 143 | 4.406 | 3.2098
[7 empty] | 4848 | 144 | 3.7963 | 2.7318
[7 empty] | 4849 | 145 | 3.3287 | 2.3651
[7 empty] | 4850 | 146 | 3.1199 | 2.2014
[7 empty] | 4851 | 147 | 3.0531 | 2.149
[7 empty] | 4852 | 148 | 3.0447 | 2.1424
[7 empty] | 4853 | 149 | 3.0447 | 2.1424
[7 empty] | 4854 | 150 | 3.0531 | 2.149
[7 empty] | 4855 | 151 | 4.1304 | 2.9937
[7 empty] | 4856 | 152 | 5.6503 | 4.1854
[7 empty] | 4857 | 153 | 6.2599 | 4.6634
[7 empty] | 4858 | 154 | 6.8194 | 5.1021
[7 empty] | 4859 | 155 | 6.6691 | 4.9843
[7 empty] | 4860 | 156 | 6.8361 | 5.1152
[7 empty] | 4861 | 157 | 7.546 | 5.6718
[7 empty] | 4862 | 158 | 7.8717 | 5.9272
[7 empty] | 4863 | 159 | 8.1389 | 6.1367
[7 empty] | 4864 | 160 | 8.0136 | 6.0385
[7 empty] | 4865 | 161 | 8.7736 | 6.6343
[7 empty] | 4866 | 162 | 8.2809 | 6.248
[7 empty] | 4867 | 163 | 8.64 | 6.5296
[7 empty] | 4868 | 164 | 7.2954 | 5.4754
[7 empty] | 4869 | 165 | 10.4104 | 7.9177
[7 empty] | 4870 | 166 | 8.3727 | 6.32
[7 empty] | 4871 | 167 | 4.7818 | 3.5044
[7 empty] | 4872 | 168 | 4.1387 | 3.0002
[7 empty] | 4873 | 1 | 2.6856 | 1.8609
[7 empty] | 4874 | 2 | 2.5771 | 1.7758
[7 empty] | 4875 | 3 | 2.5687 | 1.7692
[7 empty] | 4876 | 4 | 2.7023 | 1.874
[7 empty] | 4877 | 5 | 2.719 | 1.8871
[7 empty] | 4878 | 6 | 3.1449 | 2.221
[7 empty] | 4879 | 7 | 3.8631 | 2.7841
[7 empty] | 4880 | 8 | 4.5312 | 3.308
[7 empty] | 4881 | 9 | 4.5062 | 3.2883
[7 empty] | 4882 | 10 | 6.0177 | 4.4735
[7 empty] | 4883 | 11 | 8.0888 | 6.0974
[7 empty] | 4884 | 12 | 9.0492 | 6.8504
[7 empty] | 4885 | 13 | 9.425 | 7.1451
[7 empty] | 4886 | 14 | 9.2079 | 6.9748
[7 empty] | 4887 | 15 | 9.116 | 6.9028
[7 empty] | 4888 | 16 | 10.2935 | 7.8261
[7 empty] | 4889 | 17 | 11.613 | 8.8607
[7 empty] | 4890 | 18 | 11.3708 | 8.6708
[7 empty] | 4891 | 19 | 11.8969 | 9.0833
[7 empty] | 4892 | 20 | 11.8301 | 9.0309
[7 empty] | 4893 | 21 | 12.398 | 9.4762
[7 empty] | 4894 | 22 | 8.4563 | 6.3855
[7 empty] | 4895 | 23 | 4.6983 | 3.4389
[7 empty] | 4896 | 24 | 3.0331 | 2.1333
[7 empty] | 4897 | 25 | 2.9362 | 2.0573
[7 empty] | 4898 | 26 | 2.8276 | 1.9722
[7 empty] | 4899 | 27 | 2.7274 | 1.8936
[7 empty] | 4900 | 28 | 2.8109 | 1.9591
[7 empty] | 4901 | 29 | 3.0531 | 2.149
[7 empty] | 4902 | 30 | 3.2953 | 2.3389
[7 empty] | 4903 | 31 | 4.1387 | 3.0002
[7 empty] | 4904 | 32 | 4.4895 | 3.2752
[7 empty] | 4905 | 33 | 5.1492 | 3.7925
[7 empty] | 4906 | 34 | 6.0428 | 4.4932
[7 empty] | 4907 | 35 | 8.2057 | 6.1891
[7 empty] | 4908 | 36 | 9.2329 | 6.9945
[7 empty] | 4909 | 37 | 9.3081 | 7.0534
[7 empty] | 4910 | 38 | 9.3832 | 7.1123
[7 empty] | 4911 | 39 | 9.0575 | 6.857
[7 empty] | 4912 | 40 | 10.1098 | 7.682
[7 empty] | 4913 | 41 | 10.6609 | 8.1142
[7 empty] | 4914 | 42 | 10.6776 | 8.1273
[7 empty] | 4915 | 43 | 11.0451 | 8.4154
[7 empty] | 4916 | 44 | 12.1975 | 9.319
[7 empty] | 4917 | 45 | 11.7967 | 9.0047
[7 empty] | 4918 | 46 | 9.0575 | 6.857
[7 empty] | 4919 | 47 | 5.4666 | 4.0414
[7 empty] | 4920 | 48 | 3.9717 | 2.8693
[7 empty] | 4921 | 49 | 3.312 | 2.352
[7 empty] | 4922 | 50 | 3.003 | 2.1097
[7 empty] | 4923 | 51 | 2.8944 | 2.0246
[7 empty] | 4924 | 52 | 2.9278 | 2.0508
[7 empty] | 4925 | 53 | 2.9529 | 2.0704
[7 empty] | 4926 | 54 | 3.5291 | 2.5222
[7 empty] | 4927 | 55 | 4.6648 | 3.4128
[7 empty] | 4928 | 56 | 4.907 | 3.6026
[7 empty] | 4929 | 57 | 5.8507 | 4.3426
[7 empty] | 4930 | 58 | 6.9531 | 5.2069
[7 empty] | 4931 | 59 | 8.1556 | 6.1498
[7 empty] | 4932 | 60 | 8.7819 | 6.6409
[7 empty] | 4933 | 61 | 9.4584 | 7.1713
[7 empty] | 4934 | 62 | 9.258 | 7.0141
[7 empty] | 4935 | 63 | 9.8509 | 7.479
[7 empty] | 4936 | 64 | 10.7946 | 8.219
[7 empty] | 4937 | 65 | 11.4125 | 8.7035
[7 empty] | 4938 | 66 | 11.3123 | 8.6249
[7 empty] | 4939 | 67 | 12.0472 | 9.2011
[7 empty] | 4940 | 68 | 12.2894 | 9.391
[7 empty] | 4941 | 69 | 11.78 | 8.9916
[7 empty] | 4942 | 70 | 9.4918 | 7.1975
[7 empty] | 4943 | 71 | 4.9905 | 3.6681
[7 empty] | 4944 | 72 | 3.9097 | 2.8206
[7 empty] | 4945 | 73 | 3.1951 | 2.2603
[7 empty] | 4946 | 74 | 2.9696 | 2.0835
[7 empty] | 4947 | 75 | 2.8694 | 2.0049
[7 empty] | 4948 | 76 | 2.8109 | 1.9591
[7 empty] | 4949 | 77 | 2.9863 | 2.0966
[7 empty] | 4950 | 78 | 3.3871 | 2.4109
[7 empty] | 4951 | 79 | 4.4978 | 3.2818
[7 empty] | 4952 | 80 | 4.6732 | 3.4193
[7 empty] | 4953 | 81 | 5.8507 | 4.3426
[7 empty] | 4954 | 82 | 6.9363 | 5.1938
[7 empty] | 4955 | 83 | 7.6712 | 5.77
[7 empty] | 4956 | 84 | 8.9072 | 6.7391
[7 empty] | 4957 | 85 | 8.6066 | 6.5034
[7 empty] | 4958 | 86 | 8.0972 | 6.104
[7 empty] | 4959 | 87 | 8.5398 | 6.451
[7 empty] | 4960 | 88 | 9.1995 | 6.9683
[7 empty] | 4961 | 89 | 10.544 | 8.0225
[7 empty] | 4962 | 90 | 9.9595 | 7.5642
[7 empty] | 4963 | 91 | 10.6442 | 8.1011
[7 empty] | 4964 | 92 | 10.043 | 7.6296
[7 empty] | 4965 | 93 | 7.6378 | 5.7438
[7 empty] | 4966 | 94 | 6.7359 | 5.0366
[7 empty] | 4967 | 95 | 4.882 | 3.583
[7 empty] | 4968 | 96 | 3.8965 | 2.8103
[7 empty] | 4969 | 97 | 3.8464 | 2.7711
[7 empty] | 4970 | 98 | 3.5541 | 2.5419
[7 empty] | 4971 | 99 | 3.4957 | 2.496
[7 empty] | 4972 | 100 | 3.1449 | 2.221
[7 empty] | 4973 | 101 | 3.0865 | 2.1752
[7 empty] | 4974 | 102 | 3.3203 | 2.3585
[7 empty] | 4975 | 103 | 4.0636 | 2.9413
[7 empty] | 4976 | 104 | 4.3141 | 3.1377
[7 empty] | 4977 | 105 | 4.7985 | 3.5175
[7 empty] | 4978 | 106 | 6.2516 | 4.6569
[7 empty] | 4979 | 107 | 6.6023 | 4.9319
[7 empty] | 4980 | 108 | 8.1723 | 6.1629
[7 empty] | 4981 | 109 | 7.5126 | 5.6456
[7 empty] | 4982 | 110 | 7.0616 | 5.292
[7 empty] | 4983 | 111 | 6.9029 | 5.1676
[7 empty] | 4984 | 112 | 6.9698 | 5.22
[7 empty] | 4985 | 113 | 6.6274 | 4.9515
[7 empty] | 4986 | 114 | 6.7944 | 5.0825
[7 empty] | 4987 | 115 | 6.3434 | 4.7289
[7 empty] | 4988 | 116 | 7.0199 | 5.2593
[7 empty] | 4989 | 117 | 6.6023 | 4.9319
[7 empty] | 4990 | 118 | 5.834 | 4.3295
[7 empty] | 4991 | 119 | 4.2473 | 3.0854
[7 empty] | 4992 | 120 | 3.9311 | 2.8374
[7 empty] | 4993 | 121 | 3.2034 | 2.2669
[7 empty] | 4994 | 122 | 2.7942 | 1.946
[7 empty] | 4995 | 123 | 2.7107 | 1.8805
[7 empty] | 4996 | 124 | 2.6773 | 1.8543
[7 empty] | 4997 | 125 | 2.6355 | 1.8216
[7 empty] | 4998 | 126 | 2.7775 | 1.9329
[7 empty] | 4999 | 127 | 4.2807 | 3.1115
[7 empty] | 5000 | 128 | 5.834 | 4.3295
[7 empty] | 5001 | 129 | 6.5104 | 4.8599
[7 empty] | 5002 | 130 | 6.9447 | 5.2003
[7 empty] | 5003 | 131 | 7.1034 | 5.3248
[7 empty] | 5004 | 132 | 6.8528 | 5.1283
[7 empty] | 5005 | 133 | 7.4875 | 5.626
[7 empty] | 5006 | 134 | 7.7882 | 5.8617
[7 empty] | 5007 | 135 | 7.855 | 5.9141
[7 empty] | 5008 | 136 | 7.0449 | 5.2789
[7 empty] | 5009 | 137 | 6.9447 | 5.2003
[7 empty] | 5010 | 138 | 6.8946 | 5.1611
[7 empty] | 5011 | 139 | 6.5605 | 4.8991
[7 empty] | 5012 | 140 | 6.5689 | 4.9057
[7 empty] | 5013 | 141 | 5.9175 | 4.3949
[7 empty] | 5014 | 142 | 5.2828 | 3.8973
[7 empty] | 5015 | 143 | 4.406 | 3.2098
[7 empty] | 5016 | 144 | 3.7963 | 2.7318
[7 empty] | 5017 | 145 | 3.3287 | 2.3651
[7 empty] | 5018 | 146 | 3.1199 | 2.2014
[7 empty] | 5019 | 147 | 3.0531 | 2.149
[7 empty] | 5020 | 148 | 3.0447 | 2.1424
[7 empty] | 5021 | 149 | 3.0447 | 2.1424
[7 empty] | 5022 | 150 | 3.0531 | 2.149
[7 empty] | 5023 | 151 | 4.1304 | 2.9937
[7 empty] | 5024 | 152 | 5.6503 | 4.1854
[7 empty] | 5025 | 153 | 6.2599 | 4.6634
[7 empty] | 5026 | 154 | 6.8194 | 5.1021
[7 empty] | 5027 | 155 | 6.6691 | 4.9843
[7 empty] | 5028 | 156 | 6.8361 | 5.1152
[7 empty] | 5029 | 157 | 7.546 | 5.6718
[7 empty] | 5030 | 158 | 7.8717 | 5.9272
[7 empty] | 5031 | 159 | 8.1389 | 6.1367
[7 empty] | 5032 | 160 | 8.0136 | 6.0385
[7 empty] | 5033 | 161 | 8.7736 | 6.6343
[7 empty] | 5034 | 162 | 8.2809 | 6.248
[7 empty] | 5035 | 163 | 8.64 | 6.5296
[7 empty] | 5036 | 164 | 7.2954 | 5.4754
[7 empty] | 5037 | 165 | 10.4104 | 7.9177
[7 empty] | 5038 | 166 | 8.3727 | 6.32
[7 empty] | 5039 | 167 | 4.7818 | 3.5044
[7 empty] | 5040 | 168 | 4.1387 | 3.0002
[7 empty] | 5041 | 1 | 2.6856 | 1.8609
[7 empty] | 5042 | 2 | 2.5771 | 1.7758
[7 empty] | 5043 | 3 | 2.5687 | 1.7692
[7 empty] | 5044 | 4 | 2.7023 | 1.874
[7 empty] | 5045 | 5 | 2.719 | 1.8871
[7 empty] | 5046 | 6 | 3.1449 | 2.221
[7 empty] | 5047 | 7 | 3.8631 | 2.7841
[7 empty] | 5048 | 8 | 4.5312 | 3.308
[7 empty] | 5049 | 9 | 4.5062 | 3.2883
[7 empty] | 5050 | 10 | 6.0177 | 4.4735
[7 empty] | 5051 | 11 | 8.0888 | 6.0974
[7 empty] | 5052 | 12 | 9.0492 | 6.8504
[7 empty] | 5053 | 13 | 9.425 | 7.1451
[7 empty] | 5054 | 14 | 9.2079 | 6.9748
[7 empty] | 5055 | 15 | 9.116 | 6.9028
[7 empty] | 5056 | 16 | 10.2935 | 7.8261
[7 empty] | 5057 | 17 | 11.613 | 8.8607
[7 empty] | 5058 | 18 | 11.3708 | 8.6708
[7 empty] | 5059 | 19 | 11.8969 | 9.0833
[7 empty] | 5060 | 20 | 11.8301 | 9.0309
[7 empty] | 5061 | 21 | 12.398 | 9.4762
[7 empty] | 5062 | 22 | 8.4563 | 6.3855
[7 empty] | 5063 | 23 | 4.6983 | 3.4389
[7 empty] | 5064 | 24 | 3.0331 | 2.1333
[7 empty] | 5065 | 25 | 2.9362 | 2.0573
[7 empty] | 5066 | 26 | 2.8276 | 1.9722
[7 empty] | 5067 | 27 | 2.7274 | 1.8936
[7 empty] | 5068 | 28 | 2.8109 | 1.9591
[7 empty] | 5069 | 29 | 3.0531 | 2.149
[7 empty] | 5070 | 30 | 3.2953 | 2.3389
[7 empty] | 5071 | 31 | 4.1387 | 3.0002
[7 empty] | 5072 | 32 | 4.4895 | 3.2752
[7 empty] | 5073 | 33 | 5.1492 | 3.7925
[7 empty] | 5074 | 34 | 6.0428 | 4.4932
[7 empty] | 5075 | 35 | 8.2057 | 6.1891
[7 empty] | 5076 | 36 | 9.2329 | 6.9945
[7 empty] | 5077 | 37 | 9.3081 | 7.0534
[7 empty] | 5078 | 38 | 9.3832 | 7.1123
[7 empty] | 5079 | 39 | 9.0575 | 6.857
[7 empty] | 5080 | 40 | 10.1098 | 7.682
[7 empty] | 5081 | 41 | 10.6609 | 8.1142
[7 empty] | 5082 | 42 | 10.6776 | 8.1273
[7 empty] | 5083 | 43 | 11.0451 | 8.4154
[7 empty] | 5084 | 44 | 12.1975 | 9.319
[7 empty] | 5085 | 45 | 11.7967 | 9.0047
[7 empty] | 5086 | 46 | 9.0575 | 6.857
[7 empty] | 5087 | 47 | 5.4666 | 4.0414
[7 empty] | 5088 | 48 | 3.9717 | 2.8693
[7 empty] | 5089 | 49 | 3.312 | 2.352
[7 empty] | 5090 | 50 | 3.003 | 2.1097
[7 empty] | 5091 | 51 | 2.8944 | 2.0246
[7 empty] | 5092 | 52 | 2.9278 | 2.0508
[7 empty] | 5093 | 53 | 2.9529 | 2.0704
[7 empty] | 5094 | 54 | 3.5291 | 2.5222
[7 empty] | 5095 | 55 | 4.6648 | 3.4128
[7 empty] | 5096 | 56 | 4.907 | 3.6026
[7 empty] | 5097 | 57 | 5.8507 | 4.3426
[7 empty] | 5098 | 58 | 6.9531 | 5.2069
[7 empty] | 5099 | 59 | 8.1556 | 6.1498
[7 empty] | 5100 | 60 | 8.7819 | 6.6409
[7 empty] | 5101 | 61 | 9.4584 | 7.1713
[7 empty] | 5102 | 62 | 9.258 | 7.0141
[7 empty] | 5103 | 63 | 9.8509 | 7.479
[7 empty] | 5104 | 64 | 10.7946 | 8.219
[7 empty] | 5105 | 65 | 11.4125 | 8.7035
[7 empty] | 5106 | 66 | 11.3123 | 8.6249
[7 empty] | 5107 | 67 | 12.0472 | 9.2011
[7 empty] | 5108 | 68 | 12.2894 | 9.391
[7 empty] | 5109 | 69 | 11.78 | 8.9916
[7 empty] | 5110 | 70 | 9.4918 | 7.1975
[7 empty] | 5111 | 71 | 4.9905 | 3.6681
[7 empty] | 5112 | 72 | 3.9097 | 2.8206
[7 empty] | 5113 | 73 | 3.1951 | 2.2603
[7 empty] | 5114 | 74 | 2.9696 | 2.0835
[7 empty] | 5115 | 75 | 2.8694 | 2.0049
[7 empty] | 5116 | 76 | 2.8109 | 1.9591
[7 empty] | 5117 | 77 | 2.9863 | 2.0966
[7 empty] | 5118 | 78 | 3.3871 | 2.4109
[7 empty] | 5119 | 79 | 4.4978 | 3.2818
[7 empty] | 5120 | 80 | 4.6732 | 3.4193
[7 empty] | 5121 | 81 | 5.8507 | 4.3426
[7 empty] | 5122 | 82 | 6.9363 | 5.1938
[7 empty] | 5123 | 83 | 7.6712 | 5.77
[7 empty] | 5124 | 84 | 8.9072 | 6.7391
[7 empty] | 5125 | 85 | 8.6066 | 6.5034
[7 empty] | 5126 | 86 | 8.0972 | 6.104
[7 empty] | 5127 | 87 | 8.5398 | 6.451
[7 empty] | 5128 | 88 | 9.1995 | 6.9683
[7 empty] | 5129 | 89 | 10.544 | 8.0225
[7 empty] | 5130 | 90 | 9.9595 | 7.5642
[7 empty] | 5131 | 91 | 10.6442 | 8.1011
[7 empty] | 5132 | 92 | 10.043 | 7.6296
[7 empty] | 5133 | 93 | 7.6378 | 5.7438
[7 empty] | 5134 | 94 | 6.7359 | 5.0366
[7 empty] | 5135 | 95 | 4.882 | 3.583
[7 empty] | 5136 | 96 | 3.8965 | 2.8103
[7 empty] | 5137 | 97 | 3.8464 | 2.7711
[7 empty] | 5138 | 98 | 3.5541 | 2.5419
[7 empty] | 5139 | 99 | 3.4957 | 2.496
[7 empty] | 5140 | 100 | 3.1449 | 2.221
[7 empty] | 5141 | 101 | 3.0865 | 2.1752
[7 empty] | 5142 | 102 | 3.3203 | 2.3585
[7 empty] | 5143 | 103 | 4.0636 | 2.9413
[7 empty] | 5144 | 104 | 4.3141 | 3.1377
[7 empty] | 5145 | 105 | 4.7985 | 3.5175
[7 empty] | 5146 | 106 | 6.2516 | 4.6569
[7 empty] | 5147 | 107 | 6.6023 | 4.9319
[7 empty] | 5148 | 108 | 8.1723 | 6.1629
[7 empty] | 5149 | 109 | 7.5126 | 5.6456
[7 empty] | 5150 | 110 | 7.0616 | 5.292
[7 empty] | 5151 | 111 | 6.9029 | 5.1676
[7 empty] | 5152 | 112 | 6.9698 | 5.22
[7 empty] | 5153 | 113 | 6.6274 | 4.9515
[7 empty] | 5154 | 114 | 6.7944 | 5.0825
[7 empty] | 5155 | 115 | 6.3434 | 4.7289
[7 empty] | 5156 | 116 | 7.0199 | 5.2593
[7 empty] | 5157 | 117 | 6.6023 | 4.9319
[7 empty] | 5158 | 118 | 5.834 | 4.3295
[7 empty] | 5159 | 119 | 4.2473 | 3.0854
[7 empty] | 5160 | 120 | 3.9311 | 2.8374
[7 empty] | 5161 | 121 | 3.2034 | 2.2669
[7 empty] | 5162 | 122 | 2.7942 | 1.946
[7 empty] | 5163 | 123 | 2.7107 | 1.8805
[7 empty] | 5164 | 124 | 2.6773 | 1.8543
[7 empty] | 5165 | 125 | 2.6355 | 1.8216
[7 empty] | 5166 | 126 | 2.7775 | 1.9329
[7 empty] | 5167 | 127 | 4.2807 | 3.1115
[7 empty] | 5168 | 128 | 5.834 | 4.3295
[7 empty] | 5169 | 129 | 6.5104 | 4.8599
[7 empty] | 5170 | 130 | 6.9447 | 5.2003
[7 empty] | 5171 | 131 | 7.1034 | 5.3248
[7 empty] | 5172 | 132 | 6.8528 | 5.1283
[7 empty] | 5173 | 133 | 7.4875 | 5.626
[7 empty] | 5174 | 134 | 7.7882 | 5.8617
[7 empty] | 5175 | 135 | 7.855 | 5.9141
[7 empty] | 5176 | 136 | 7.0449 | 5.2789
[7 empty] | 5177 | 137 | 6.9447 | 5.2003
[7 empty] | 5178 | 138 | 6.8946 | 5.1611
[7 empty] | 5179 | 139 | 6.5605 | 4.8991
[7 empty] | 5180 | 140 | 6.5689 | 4.9057
[7 empty] | 5181 | 141 | 5.9175 | 4.3949
[7 empty] | 5182 | 142 | 5.2828 | 3.8973
[7 empty] | 5183 | 143 | 4.406 | 3.2098
[7 empty] | 5184 | 144 | 3.7963 | 2.7318
[7 empty] | 5185 | 145 | 3.3287 | 2.3651
[7 empty] | 5186 | 146 | 3.1199 | 2.2014
[7 empty] | 5187 | 147 | 3.0531 | 2.149
[7 empty] | 5188 | 148 | 3.0447 | 2.1424
[7 empty] | 5189 | 149 | 3.0447 | 2.1424
[7 empty] | 5190 | 150 | 3.0531 | 2.149
[7 empty] | 5191 | 151 | 4.1304 | 2.9937
[7 empty] | 5192 | 152 | 5.6503 | 4.1854
[7 empty] | 5193 | 153 | 6.2599 | 4.6634
[7 empty] | 5194 | 154 | 6.8194 | 5.1021
[7 empty] | 5195 | 155 | 6.6691 | 4.9843
[7 empty] | 5196 | 156 | 6.8361 | 5.1152
[7 empty] | 5197 | 157 | 7.546 | 5.6718
[7 empty] | 5198 | 158 | 7.8717 | 5.9272
[7 empty] | 5199 | 159 | 8.1389 | 6.1367
[7 empty] | 5200 | 160 | 8.0136 | 6.0385
[7 empty] | 5201 | 161 | 8.7736 | 6.6343
[7 empty] | 5202 | 162 | 8.2809 | 6.248
[7 empty] | 5203 | 163 | 8.64 | 6.5296
[7 empty] | 5204 | 164 | 7.2954 | 5.4754
[7 empty] | 5205 | 165 | 10.4104 | 7.9177
[7 empty] | 5206 | 166 | 8.3727 | 6.32
[7 empty] | 5207 | 167 | 4.7818 | 3.5044
[7 empty] | 5208 | 168 | 4.1387 | 3.0002
[7 empty] | 5209 | 1 | 2.6856 | 1.8609
[7 empty] | 5210 | 2 | 2.5771 | 1.7758
[7 empty] | 5211 | 3 | 2.5687 | 1.7692
[7 empty] | 5212 | 4 | 2.7023 | 1.874
[7 empty] | 5213 | 5 | 2.719 | 1.8871
[7 empty] | 5214 | 6 | 3.1449 | 2.221
[7 empty] | 5215 | 7 | 3.8631 | 2.7841
[7 empty] | 5216 | 8 | 4.5312 | 3.308
[7 empty] | 5217 | 9 | 4.5062 | 3.2883
[7 empty] | 5218 | 10 | 6.0177 | 4.4735
[7 empty] | 5219 | 11 | 8.0888 | 6.0974
[7 empty] | 5220 | 12 | 9.0492 | 6.8504
[7 empty] | 5221 | 13 | 9.425 | 7.1451
[7 empty] | 5222 | 14 | 9.2079 | 6.9748
[7 empty] | 5223 | 15 | 9.116 | 6.9028
[7 empty] | 5224 | 16 | 10.2935 | 7.8261
[7 empty] | 5225 | 17 | 11.613 | 8.8607
[7 empty] | 5226 | 18 | 11.3708 | 8.6708
[7 empty] | 5227 | 19 | 11.8969 | 9.0833
[7 empty] | 5228 | 20 | 11.8301 | 9.0309
[7 empty] | 5229 | 21 | 12.398 | 9.4762
[7 empty] | 5230 | 22 | 8.4563 | 6.3855
[7 empty] | 5231 | 23 | 4.6983 | 3.4389
[7 empty] | 5232 | 24 | 3.0331 | 2.1333
[7 empty] | 5233 | 25 | 2.9362 | 2.0573
[7 empty] | 5234 | 26 | 2.8276 | 1.9722
[7 empty] | 5235 | 27 | 2.7274 | 1.8936
[7 empty] | 5236 | 28 | 2.8109 | 1.9591
[7 empty] | 5237 | 29 | 3.0531 | 2.149
[7 empty] | 5238 | 30 | 3.2953 | 2.3389
[7 empty] | 5239 | 31 | 4.1387 | 3.0002
[7 empty] | 5240 | 32 | 4.4895 | 3.2752
[7 empty] | 5241 | 33 | 5.1492 | 3.7925
[7 empty] | 5242 | 34 | 6.0428 | 4.4932
[7 empty] | 5243 | 35 | 8.2057 | 6.1891
[7 empty] | 5244 | 36 | 9.2329 | 6.9945
[7 empty] | 5245 | 37 | 9.3081 | 7.0534
[7 empty] | 5246 | 38 | 9.3832 | 7.1123
[7 empty] | 5247 | 39 | 9.0575 | 6.857
[7 empty] | 5248 | 40 | 10.1098 | 7.682
[7 empty] | 5249 | 41 | 10.6609 | 8.1142
[7 empty] | 5250 | 42 | 10.6776 | 8.1273
[7 empty] | 5251 | 43 | 11.0451 | 8.4154
[7 empty] | 5252 | 44 | 12.1975 | 9.319
[7 empty] | 5253 | 45 | 11.7967 | 9.0047
[7 empty] | 5254 | 46 | 9.0575 | 6.857
[7 empty] | 5255 | 47 | 5.4666 | 4.0414
[7 empty] | 5256 | 48 | 3.9717 | 2.8693
[7 empty] | 5257 | 49 | 3.312 | 2.352
[7 empty] | 5258 | 50 | 3.003 | 2.1097
[7 empty] | 5259 | 51 | 2.8944 | 2.0246
[7 empty] | 5260 | 52 | 2.9278 | 2.0508
[7 empty] | 5261 | 53 | 2.9529 | 2.0704
[7 empty] | 5262 | 54 | 3.5291 | 2.5222
[7 empty] | 5263 | 55 | 4.6648 | 3.4128
[7 empty] | 5264 | 56 | 4.907 | 3.6026
[7 empty] | 5265 | 57 | 5.8507 | 4.3426
[7 empty] | 5266 | 58 | 6.9531 | 5.2069
[7 empty] | 5267 | 59 | 8.1556 | 6.1498
[7 empty] | 5268 | 60 | 8.7819 | 6.6409
[7 empty] | 5269 | 61 | 9.4584 | 7.1713
[7 empty] | 5270 | 62 | 9.258 | 7.0141
[7 empty] | 5271 | 63 | 9.8509 | 7.479
[7 empty] | 5272 | 64 | 10.7946 | 8.219
[7 empty] | 5273 | 65 | 11.4125 | 8.7035
[7 empty] | 5274 | 66 | 11.3123 | 8.6249
[7 empty] | 5275 | 67 | 12.0472 | 9.2011
[7 empty] | 5276 | 68 | 12.2894 | 9.391
[7 empty] | 5277 | 69 | 11.78 | 8.9916
[7 empty] | 5278 | 70 | 9.4918 | 7.1975
[7 empty] | 5279 | 71 | 4.9905 | 3.6681
[7 empty] | 5280 | 72 | 3.9097 | 2.8206
[7 empty] | 5281 | 73 | 3.1951 | 2.2603
[7 empty] | 5282 | 74 | 2.9696 | 2.0835
[7 empty] | 5283 | 75 | 2.8694 | 2.0049
[7 empty] | 5284 | 76 | 2.8109 | 1.9591
[7 empty] | 5285 | 77 | 2.9863 | 2.0966
[7 empty] | 5286 | 78 | 3.3871 | 2.4109
[7 empty] | 5287 | 79 | 4.4978 | 3.2818
[7 empty] | 5288 | 80 | 4.6732 | 3.4193
[7 empty] | 5289 | 81 | 5.8507 | 4.3426
[7 empty] | 5290 | 82 | 6.9363 | 5.1938
[7 empty] | 5291 | 83 | 7.6712 | 5.77
[7 empty] | 5292 | 84 | 8.9072 | 6.7391
[7 empty] | 5293 | 85 | 8.6066 | 6.5034
[7 empty] | 5294 | 86 | 8.0972 | 6.104
[7 empty] | 5295 | 87 | 8.5398 | 6.451
[7 empty] | 5296 | 88 | 9.1995 | 6.9683
[7 empty] | 5297 | 89 | 10.544 | 8.0225
[7 empty] | 5298 | 90 | 9.9595 | 7.5642
[7 empty] | 5299 | 91 | 10.6442 | 8.1011
[7 empty] | 5300 | 92 | 10.043 | 7.6296
[7 empty] | 5301 | 93 | 7.6378 | 5.7438
[7 empty] | 5302 | 94 | 6.7359 | 5.0366
[7 empty] | 5303 | 95 | 4.882 | 3.583
[7 empty] | 5304 | 96 | 3.8965 | 2.8103
[7 empty] | 5305 | 97 | 3.8464 | 2.7711
[7 empty] | 5306 | 98 | 3.5541 | 2.5419
[7 empty] | 5307 | 99 | 3.4957 | 2.496
[7 empty] | 5308 | 100 | 3.1449 | 2.221
[7 empty] | 5309 | 101 | 3.0865 | 2.1752
[7 empty] | 5310 | 102 | 3.3203 | 2.3585
[7 empty] | 5311 | 103 | 4.0636 | 2.9413
[7 empty] | 5312 | 104 | 4.3141 | 3.1377
[7 empty] | 5313 | 105 | 4.7985 | 3.5175
[7 empty] | 5314 | 106 | 6.2516 | 4.6569
[7 empty] | 5315 | 107 | 6.6023 | 4.9319
[7 empty] | 5316 | 108 | 8.1723 | 6.1629
[7 empty] | 5317 | 109 | 7.5126 | 5.6456
[7 empty] | 5318 | 110 | 7.0616 | 5.292
[7 empty] | 5319 | 111 | 6.9029 | 5.1676
[7 empty] | 5320 | 112 | 6.9698 | 5.22
[7 empty] | 5321 | 113 | 6.6274 | 4.9515
[7 empty] | 5322 | 114 | 6.7944 | 5.0825
[7 empty] | 5323 | 115 | 6.3434 | 4.7289
[7 empty] | 5324 | 116 | 7.0199 | 5.2593
[7 empty] | 5325 | 117 | 6.6023 | 4.9319
[7 empty] | 5326 | 118 | 5.834 | 4.3295
[7 empty] | 5327 | 119 | 4.2473 | 3.0854
[7 empty] | 5328 | 120 | 3.9311 | 2.8374
[7 empty] | 5329 | 121 | 3.2034 | 2.2669
[7 empty] | 5330 | 122 | 2.7942 | 1.946
[7 empty] | 5331 | 123 | 2.7107 | 1.8805
[7 empty] | 5332 | 124 | 2.6773 | 1.8543
[7 empty] | 5333 | 125 | 2.6355 | 1.8216
[7 empty] | 5334 | 126 | 2.7775 | 1.9329
[7 empty] | 5335 | 127 | 4.2807 | 3.1115
[7 empty] | 5336 | 128 | 5.834 | 4.3295
[7 empty] | 5337 | 129 | 6.5104 | 4.8599
[7 empty] | 5338 | 130 | 6.9447 | 5.2003
[7 empty] | 5339 | 131 | 7.1034 | 5.3248
[7 empty] | 5340 | 132 | 6.8528 | 5.1283
[7 empty] | 5341 | 133 | 7.4875 | 5.626
[7 empty] | 5342 | 134 | 7.7882 | 5.8617
[7 empty] | 5343 | 135 | 7.855 | 5.9141
[7 empty] | 5344 | 136 | 7.0449 | 5.2789
[7 empty] | 5345 | 137 | 6.9447 | 5.2003
[7 empty] | 5346 | 138 | 6.8946 | 5.1611
[7 empty] | 5347 | 139 | 6.5605 | 4.8991
[7 empty] | 5348 | 140 | 6.5689 | 4.9057
[7 empty] | 5349 | 141 | 5.9175 | 4.3949
[7 empty] | 5350 | 142 | 5.2828 | 3.8973
[7 empty] | 5351 | 143 | 4.406 | 3.2098
[7 empty] | 5352 | 144 | 3.7963 | 2.7318
[7 empty] | 5353 | 145 | 3.3287 | 2.3651
[7 empty] | 5354 | 146 | 3.1199 | 2.2014
[7 empty] | 5355 | 147 | 3.0531 | 2.149
[7 empty] | 5356 | 148 | 3.0447 | 2.1424
[7 empty] | 5357 | 149 | 3.0447 | 2.1424
[7 empty] | 5358 | 150 | 3.0531 | 2.149
[7 empty] | 5359 | 151 | 4.1304 | 2.9937
[7 empty] | 5360 | 152 | 5.6503 | 4.1854
[7 empty] | 5361 | 153 | 6.2599 | 4.6634
[7 empty] | 5362 | 154 | 6.8194 | 5.1021
[7 empty] | 5363 | 155 | 6.6691 | 4.9843
[7 empty] | 5364 | 156 | 6.8361 | 5.1152
[7 empty] | 5365 | 157 | 7.546 | 5.6718
[7 empty] | 5366 | 158 | 7.8717 | 5.9272
[7 empty] | 5367 | 159 | 8.1389 | 6.1367
[7 empty] | 5368 | 160 | 8.0136 | 6.0385
[7 empty] | 5369 | 161 | 8.7736 | 6.6343
[7 empty] | 5370 | 162 | 8.2809 | 6.248
[7 empty] | 5371 | 163 | 8.64 | 6.5296
[7 empty] | 5372 | 164 | 7.2954 | 5.4754
[7 empty] | 5373 | 165 | 10.4104 | 7.9177
[7 empty] | 5374 | 166 | 8.3727 | 6.32
[7 empty] | 5375 | 167 | 4.7818 | 3.5044
[7 empty] | 5376 | 168 | 4.1387 | 3.0002
[7 empty] | 5377 | 1 | 2.6856 | 1.8609
[7 empty] | 5378 | 2 | 2.5771 | 1.7758
[7 empty] | 5379 | 3 | 2.5687 | 1.7692
[7 empty] | 5380 | 4 | 2.7023 | 1.874
[7 empty] | 5381 | 5 | 2.719 | 1.8871
[7 empty] | 5382 | 6 | 3.1449 | 2.221
[7 empty] | 5383 | 7 | 3.8631 | 2.7841
[7 empty] | 5384 | 8 | 4.5312 | 3.308
[7 empty] | 5385 | 9 | 4.5062 | 3.2883
[7 empty] | 5386 | 10 | 6.0177 | 4.4735
[7 empty] | 5387 | 11 | 8.0888 | 6.0974
[7 empty] | 5388 | 12 | 9.0492 | 6.8504
[7 empty] | 5389 | 13 | 9.425 | 7.1451
[7 empty] | 5390 | 14 | 9.2079 | 6.9748
[7 empty] | 5391 | 15 | 9.116 | 6.9028
[7 empty] | 5392 | 16 | 10.2935 | 7.8261
[7 empty] | 5393 | 17 | 11.613 | 8.8607
[7 empty] | 5394 | 18 | 11.3708 | 8.6708
[7 empty] | 5395 | 19 | 11.8969 | 9.0833
[7 empty] | 5396 | 20 | 11.8301 | 9.0309
[7 empty] | 5397 | 21 | 12.398 | 9.4762
[7 empty] | 5398 | 22 | 8.4563 | 6.3855
[7 empty] | 5399 | 23 | 4.6983 | 3.4389
[7 empty] | 5400 | 24 | 3.0331 | 2.1333
[7 empty] | 5401 | 25 | 2.9362 | 2.0573
[7 empty] | 5402 | 26 | 2.8276 | 1.9722
[7 empty] | 5403 | 27 | 2.7274 | 1.8936
[7 empty] | 5404 | 28 | 2.8109 | 1.9591
[7 empty] | 5405 | 29 | 3.0531 | 2.149
[7 empty] | 5406 | 30 | 3.2953 | 2.3389
[7 empty] | 5407 | 31 | 4.1387 | 3.0002
[7 empty] | 5408 | 32 | 4.4895 | 3.2752
[7 empty] | 5409 | 33 | 5.1492 | 3.7925
[7 empty] | 5410 | 34 | 6.0428 | 4.4932
[7 empty] | 5411 | 35 | 8.2057 | 6.1891
[7 empty] | 5412 | 36 | 9.2329 | 6.9945
[7 empty] | 5413 | 37 | 9.3081 | 7.0534
[7 empty] | 5414 | 38 | 9.3832 | 7.1123
[7 empty] | 5415 | 39 | 9.0575 | 6.857
[7 empty] | 5416 | 40 | 10.1098 | 7.682
[7 empty] | 5417 | 41 | 10.6609 | 8.1142
[7 empty] | 5418 | 42 | 10.6776 | 8.1273
[7 empty] | 5419 | 43 | 11.0451 | 8.4154
[7 empty] | 5420 | 44 | 12.1975 | 9.319
[7 empty] | 5421 | 45 | 11.7967 | 9.0047
[7 empty] | 5422 | 46 | 9.0575 | 6.857
[7 empty] | 5423 | 47 | 5.4666 | 4.0414
[7 empty] | 5424 | 48 | 3.9717 | 2.8693
[7 empty] | 5425 | 49 | 3.312 | 2.352
[7 empty] | 5426 | 50 | 3.003 | 2.1097
[7 empty] | 5427 | 51 | 2.8944 | 2.0246
[7 empty] | 5428 | 52 | 2.9278 | 2.0508
[7 empty] | 5429 | 53 | 2.9529 | 2.0704
[7 empty] | 5430 | 54 | 3.5291 | 2.5222
[7 empty] | 5431 | 55 | 4.6648 | 3.4128
[7 empty] | 5432 | 56 | 4.907 | 3.6026
[7 empty] | 5433 | 57 | 5.8507 | 4.3426
[7 empty] | 5434 | 58 | 6.9531 | 5.2069
[7 empty] | 5435 | 59 | 8.1556 | 6.1498
[7 empty] | 5436 | 60 | 8.7819 | 6.6409
[7 empty] | 5437 | 61 | 9.4584 | 7.1713
[7 empty] | 5438 | 62 | 9.258 | 7.0141
[7 empty] | 5439 | 63 | 9.8509 | 7.479
[7 empty] | 5440 | 64 | 10.7946 | 8.219
[7 empty] | 5441 | 65 | 11.4125 | 8.7035
[7 empty] | 5442 | 66 | 11.3123 | 8.6249
[7 empty] | 5443 | 67 | 12.0472 | 9.2011
[7 empty] | 5444 | 68 | 12.2894 | 9.391
[7 empty] | 5445 | 69 | 11.78 | 8.9916
[7 empty] | 5446 | 70 | 9.4918 | 7.1975
[7 empty] | 5447 | 71 | 4.9905 | 3.6681
[7 empty] | 5448 | 72 | 3.9097 | 2.8206
[7 empty] | 5449 | 73 | 3.1951 | 2.2603
[7 empty] | 5450 | 74 | 2.9696 | 2.0835
[7 empty] | 5451 | 75 | 2.8694 | 2.0049
[7 empty] | 5452 | 76 | 2.8109 | 1.9591
[7 empty] | 5453 | 77 | 2.9863 | 2.0966
[7 empty] | 5454 | 78 | 3.3871 | 2.4109
[7 empty] | 5455 | 79 | 4.4978 | 3.2818
[7 empty] | 5456 | 80 | 4.6732 | 3.4193
[7 empty] | 5457 | 81 | 5.8507 | 4.3426
[7 empty] | 5458 | 82 | 6.9363 | 5.1938
[7 empty] | 5459 | 83 | 7.6712 | 5.77
[7 empty] | 5460 | 84 | 8.9072 | 6.7391
[7 empty] | 5461 | 85 | 8.6066 | 6.5034
[7 empty] | 5462 | 86 | 8.0972 | 6.104
[7 empty] | 5463 | 87 | 8.5398 | 6.451
[7 empty] | 5464 | 88 | 9.1995 | 6.9683
[7 empty] | 5465 | 89 | 10.544 | 8.0225
[7 empty] | 5466 | 90 | 9.9595 | 7.5642
[7 empty] | 5467 | 91 | 10.6442 | 8.1011
[7 empty] | 5468 | 92 | 10.043 | 7.6296
[7 empty] | 5469 | 93 | 7.6378 | 5.7438
[7 empty] | 5470 | 94 | 6.7359 | 5.0366
[7 empty] | 5471 | 95 | 4.882 | 3.583
[7 empty] | 5472 | 96 | 3.8965 | 2.8103
[7 empty] | 5473 | 97 | 3.8464 | 2.7711
[7 empty] | 5474 | 98 | 3.5541 | 2.5419
[7 empty] | 5475 | 99 | 3.4957 | 2.496
[7 empty] | 5476 | 100 | 3.1449 | 2.221
[7 empty] | 5477 | 101 | 3.0865 | 2.1752
[7 empty] | 5478 | 102 | 3.3203 | 2.3585
[7 empty] | 5479 | 103 | 4.0636 | 2.9413
[7 empty] | 5480 | 104 | 4.3141 | 3.1377
[7 empty] | 5481 | 105 | 4.7985 | 3.5175
[7 empty] | 5482 | 106 | 6.2516 | 4.6569
[7 empty] | 5483 | 107 | 6.6023 | 4.9319
[7 empty] | 5484 | 108 | 8.1723 | 6.1629
[7 empty] | 5485 | 109 | 7.5126 | 5.6456
[7 empty] | 5486 | 110 | 7.0616 | 5.292
[7 empty] | 5487 | 111 | 6.9029 | 5.1676
[7 empty] | 5488 | 112 | 6.9698 | 5.22
[7 empty] | 5489 | 113 | 6.6274 | 4.9515
[7 empty] | 5490 | 114 | 6.7944 | 5.0825
[7 empty] | 5491 | 115 | 6.3434 | 4.7289
[7 empty] | 5492 | 116 | 7.0199 | 5.2593
[7 empty] | 5493 | 117 | 6.6023 | 4.9319
[7 empty] | 5494 | 118 | 5.834 | 4.3295
[7 empty] | 5495 | 119 | 4.2473 | 3.0854
[7 empty] | 5496 | 120 | 3.9311 | 2.8374
[7 empty] | 5497 | 121 | 3.2034 | 2.2669
[7 empty] | 5498 | 122 | 2.7942 | 1.946
[7 empty] | 5499 | 123 | 2.7107 | 1.8805
[7 empty] | 5500 | 124 | 2.6773 | 1.8543
[7 empty] | 5501 | 125 | 2.6355 | 1.8216
[7 empty] | 5502 | 126 | 2.7775 | 1.9329
[7 empty] | 5503 | 127 | 4.2807 | 3.1115
[7 empty] | 5504 | 128 | 5.834 | 4.3295
[7 empty] | 5505 | 129 | 6.5104 | 4.8599
[7 empty] | 5506 | 130 | 6.9447 | 5.2003
[7 empty] | 5507 | 131 | 7.1034 | 5.3248
[7 empty] | 5508 | 132 | 6.8528 | 5.1283
[7 empty] | 5509 | 133 | 7.4875 | 5.626
[7 empty] | 5510 | 134 | 7.7882 | 5.8617
[7 empty] | 5511 | 135 | 7.855 | 5.9141
[7 empty] | 5512 | 136 | 7.0449 | 5.2789
[7 empty] | 5513 | 137 | 6.9447 | 5.2003
[7 empty] | 5514 | 138 | 6.8946 | 5.1611
[7 empty] | 5515 | 139 | 6.5605 | 4.8991
[7 empty] | 5516 | 140 | 6.5689 | 4.9057
[7 empty] | 5517 | 141 | 5.9175 | 4.3949
[7 empty] | 5518 | 142 | 5.2828 | 3.8973
[7 empty] | 5519 | 143 | 4.406 | 3.2098
[7 empty] | 5520 | 144 | 3.7963 | 2.7318
[7 empty] | 5521 | 145 | 3.3287 | 2.3651
[7 empty] | 5522 | 146 | 3.1199 | 2.2014
[7 empty] | 5523 | 147 | 3.0531 | 2.149
[7 empty] | 5524 | 148 | 3.0447 | 2.1424
[7 empty] | 5525 | 149 | 3.0447 | 2.1424
[7 empty] | 5526 | 150 | 3.0531 | 2.149
[7 empty] | 5527 | 151 | 4.1304 | 2.9937
[7 empty] | 5528 | 152 | 5.6503 | 4.1854
[7 empty] | 5529 | 153 | 6.2599 | 4.6634
[7 empty] | 5530 | 154 | 6.8194 | 5.1021
[7 empty] | 5531 | 155 | 6.6691 | 4.9843
[7 empty] | 5532 | 156 | 6.8361 | 5.1152
[7 empty] | 5533 | 157 | 7.546 | 5.6718
[7 empty] | 5534 | 158 | 7.8717 | 5.9272
[7 empty] | 5535 | 159 | 8.1389 | 6.1367
[7 empty] | 5536 | 160 | 8.0136 | 6.0385
[7 empty] | 5537 | 161 | 8.7736 | 6.6343
[7 empty] | 5538 | 162 | 8.2809 | 6.248
[7 empty] | 5539 | 163 | 8.64 | 6.5296
[7 empty] | 5540 | 164 | 7.2954 | 5.4754
[7 empty] | 5541 | 165 | 10.4104 | 7.9177
[7 empty] | 5542 | 166 | 8.3727 | 6.32
[7 empty] | 5543 | 167 | 4.7818 | 3.5044
[7 empty] | 5544 | 168 | 4.1387 | 3.0002
[7 empty] | 5545 | 1 | 2.6856 | 1.8609
[7 empty] | 5546 | 2 | 2.5771 | 1.7758
[7 empty] | 5547 | 3 | 2.5687 | 1.7692
[7 empty] | 5548 | 4 | 2.7023 | 1.874
[7 empty] | 5549 | 5 | 2.719 | 1.8871
[7 empty] | 5550 | 6 | 3.1449 | 2.221
[7 empty] | 5551 | 7 | 3.8631 | 2.7841
[7 empty] | 5552 | 8 | 4.5312 | 3.308
[7 empty] | 5553 | 9 | 4.5062 | 3.2883
[7 empty] | 5554 | 10 | 6.0177 | 4.4735
[7 empty] | 5555 | 11 | 8.0888 | 6.0974
[7 empty] | 5556 | 12 | 9.0492 | 6.8504
[7 empty] | 5557 | 13 | 9.425 | 7.1451
[7 empty] | 5558 | 14 | 9.2079 | 6.9748
[7 empty] | 5559 | 15 | 9.116 | 6.9028
[7 empty] | 5560 | 16 | 10.2935 | 7.8261
[7 empty] | 5561 | 17 | 11.613 | 8.8607
[7 empty] | 5562 | 18 | 11.3708 | 8.6708
[7 empty] | 5563 | 19 | 11.8969 | 9.0833
[7 empty] | 5564 | 20 | 11.8301 | 9.0309
[7 empty] | 5565 | 21 | 12.398 | 9.4762
[7 empty] | 5566 | 22 | 8.4563 | 6.3855
[7 empty] | 5567 | 23 | 4.6983 | 3.4389
[7 empty] | 5568 | 24 | 3.0331 | 2.1333
[7 empty] | 5569 | 25 | 2.9362 | 2.0573
[7 empty] | 5570 | 26 | 2.8276 | 1.9722
[7 empty] | 5571 | 27 | 2.7274 | 1.8936
[7 empty] | 5572 | 28 | 2.8109 | 1.9591
[7 empty] | 5573 | 29 | 3.0531 | 2.149
[7 empty] | 5574 | 30 | 3.2953 | 2.3389
[7 empty] | 5575 | 31 | 4.1387 | 3.0002
[7 empty] | 5576 | 32 | 4.4895 | 3.2752
[7 empty] | 5577 | 33 | 5.1492 | 3.7925
[7 empty] | 5578 | 34 | 6.0428 | 4.4932
[7 empty] | 5579 | 35 | 8.2057 | 6.1891
[7 empty] | 5580 | 36 | 9.2329 | 6.9945
[7 empty] | 5581 | 37 | 9.3081 | 7.0534
[7 empty] | 5582 | 38 | 9.3832 | 7.1123
[7 empty] | 5583 | 39 | 9.0575 | 6.857
[7 empty] | 5584 | 40 | 10.1098 | 7.682
[7 empty] | 5585 | 41 | 10.6609 | 8.1142
[7 empty] | 5586 | 42 | 10.6776 | 8.1273
[7 empty] | 5587 | 43 | 11.0451 | 8.4154
[7 empty] | 5588 | 44 | 12.1975 | 9.319
[7 empty] | 5589 | 45 | 11.7967 | 9.0047
[7 empty] | 5590 | 46 | 9.0575 | 6.857
[7 empty] | 5591 | 47 | 5.4666 | 4.0414
[7 empty] | 5592 | 48 | 3.9717 | 2.8693
[7 empty] | 5593 | 49 | 3.312 | 2.352
[7 empty] | 5594 | 50 | 3.003 | 2.1097
[7 empty] | 5595 | 51 | 2.8944 | 2.0246
[7 empty] | 5596 | 52 | 2.9278 | 2.0508
[7 empty] | 5597 | 53 | 2.9529 | 2.0704
[7 empty] | 5598 | 54 | 3.5291 | 2.5222
[7 empty] | 5599 | 55 | 4.6648 | 3.4128
[7 empty] | 5600 | 56 | 4.907 | 3.6026
[7 empty] | 5601 | 57 | 5.8507 | 4.3426
[7 empty] | 5602 | 58 | 6.9531 | 5.2069
[7 empty] | 5603 | 59 | 8.1556 | 6.1498
[7 empty] | 5604 | 60 | 8.7819 | 6.6409
[7 empty] | 5605 | 61 | 9.4584 | 7.1713
[7 empty] | 5606 | 62 | 9.258 | 7.0141
[7 empty] | 5607 | 63 | 9.8509 | 7.479
[7 empty] | 5608 | 64 | 10.7946 | 8.219
[7 empty] | 5609 | 65 | 11.4125 | 8.7035
[7 empty] | 5610 | 66 | 11.3123 | 8.6249
[7 empty] | 5611 | 67 | 12.0472 | 9.2011
[7 empty] | 5612 | 68 | 12.2894 | 9.391
[7 empty] | 5613 | 69 | 11.78 | 8.9916
[7 empty] | 5614 | 70 | 9.4918 | 7.1975
[7 empty] | 5615 | 71 | 4.9905 | 3.6681
[7 empty] | 5616 | 72 | 3.9097 | 2.8206
[7 empty] | 5617 | 73 | 3.1951 | 2.2603
[7 empty] | 5618 | 74 | 2.9696 | 2.0835
[7 empty] | 5619 | 75 | 2.8694 | 2.0049
[7 empty] | 5620 | 76 | 2.8109 | 1.9591
[7 empty] | 5621 | 77 | 2.9863 | 2.0966
[7 empty] | 5622 | 78 | 3.3871 | 2.4109
[7 empty] | 5623 | 79 | 4.4978 | 3.2818
[7 empty] | 5624 | 80 | 4.6732 | 3.4193
[7 empty] | 5625 | 81 | 5.8507 | 4.3426
[7 empty] | 5626 | 82 | 6.9363 | 5.1938
[7 empty] | 5627 | 83 | 7.6712 | 5.77
[7 empty] | 5628 | 84 | 8.9072 | 6.7391
[7 empty] | 5629 | 85 | 8.6066 | 6.5034
[7 empty] | 5630 | 86 | 8.0972 | 6.104
[7 empty] | 5631 | 87 | 8.5398 | 6.451
[7 empty] | 5632 | 88 | 9.1995 | 6.9683
[7 empty] | 5633 | 89 | 10.544 | 8.0225
[7 empty] | 5634 | 90 | 9.9595 | 7.5642
[7 empty] | 5635 | 91 | 10.6442 | 8.1011
[7 empty] | 5636 | 92 | 10.043 | 7.6296
[7 empty] | 5637 | 93 | 7.6378 | 5.7438
[7 empty] | 5638 | 94 | 6.7359 | 5.0366
[7 empty] | 5639 | 95 | 4.882 | 3.583
[7 empty] | 5640 | 96 | 3.8965 | 2.8103
[7 empty] | 5641 | 97 | 3.8464 | 2.7711
[7 empty] | 5642 | 98 | 3.5541 | 2.5419
[7 empty] | 5643 | 99 | 3.4957 | 2.496
[7 empty] | 5644 | 100 | 3.1449 | 2.221
[7 empty] | 5645 | 101 | 3.0865 | 2.1752
[7 empty] | 5646 | 102 | 3.3203 | 2.3585
[7 empty] | 5647 | 103 | 4.0636 | 2.9413
[7 empty] | 5648 | 104 | 4.3141 | 3.1377
[7 empty] | 5649 | 105 | 4.7985 | 3.5175
[7 empty] | 5650 | 106 | 6.2516 | 4.6569
[7 empty] | 5651 | 107 | 6.6023 | 4.9319
[7 empty] | 5652 | 108 | 8.1723 | 6.1629
[7 empty] | 5653 | 109 | 7.5126 | 5.6456
[7 empty] | 5654 | 110 | 7.0616 | 5.292
[7 empty] | 5655 | 111 | 6.9029 | 5.1676
[7 empty] | 5656 | 112 | 6.9698 | 5.22
[7 empty] | 5657 | 113 | 6.6274 | 4.9515
[7 empty] | 5658 | 114 | 6.7944 | 5.0825
[7 empty] | 5659 | 115 | 6.3434 | 4.7289
[7 empty] | 5660 | 116 | 7.0199 | 5.2593
[7 empty] | 5661 | 117 | 6.6023 | 4.9319
[7 empty] | 5662 | 118 | 5.834 | 4.3295
[7 empty] | 5663 | 119 | 4.2473 | 3.0854
[7 empty] | 5664 | 120 | 3.9311 | 2.8374
[7 empty] | 5665 | 121 | 3.2034 | 2.2669
[7 empty] | 5666 | 122 | 2.7942 | 1.946
[7 empty] | 5667 | 123 | 2.7107 | 1.8805
[7 empty] | 5668 | 124 | 2.6773 | 1.8543
[7 empty] | 5669 | 125 | 2.6355 | 1.8216
[7 empty] | 5670 | 126 | 2.7775 | 1.9329
[7 empty] | 5671 | 127 | 4.2807 | 3.1115
[7 empty] | 5672 | 128 | 5.834 | 4.3295
[7 empty] | 5673 | 129 | 6.5104 | 4.8599
[7 empty] | 5674 | 130 | 6.9447 | 5.2003
[7 empty] | 5675 | 131 | 7.1034 | 5.3248
[7 empty] | 5676 | 132 | 6.8528 | 5.1283
[7 empty] | 5677 | 133 | 7.4875 | 5.626
[7 empty] | 5678 | 134 | 7.7882 | 5.8617
[7 empty] | 5679 | 135 | 7.855 | 5.9141
[7 empty] | 5680 | 136 | 7.0449 | 5.2789
[7 empty] | 5681 | 137 | 6.9447 | 5.2003
[7 empty] | 5682 | 138 | 6.8946 | 5.1611
[7 empty] | 5683 | 139 | 6.5605 | 4.8991
[7 empty] | 5684 | 140 | 6.5689 | 4.9057
[7 empty] | 5685 | 141 | 5.9175 | 4.3949
[7 empty] | 5686 | 142 | 5.2828 | 3.8973
[7 empty] | 5687 | 143 | 4.406 | 3.2098
[7 empty] | 5688 | 144 | 3.7963 | 2.7318
[7 empty] | 5689 | 145 | 3.3287 | 2.3651
[7 empty] | 5690 | 146 | 3.1199 | 2.2014
[7 empty] | 5691 | 147 | 3.0531 | 2.149
[7 empty] | 5692 | 148 | 3.0447 | 2.1424
[7 empty] | 5693 | 149 | 3.0447 | 2.1424
[7 empty] | 5694 | 150 | 3.0531 | 2.149
[7 empty] | 5695 | 151 | 4.1304 | 2.9937
[7 empty] | 5696 | 152 | 5.6503 | 4.1854
[7 empty] | 5697 | 153 | 6.2599 | 4.6634
[7 empty] | 5698 | 154 | 6.8194 | 5.1021
[7 empty] | 5699 | 155 | 6.6691 | 4.9843
[7 empty] | 5700 | 156 | 6.8361 | 5.1152
[7 empty] | 5701 | 157 | 7.546 | 5.6718
[7 empty] | 5702 | 158 | 7.8717 | 5.9272
[7 empty] | 5703 | 159 | 8.1389 | 6.1367
[7 empty] | 5704 | 160 | 8.0136 | 6.0385
[7 empty] | 5705 | 161 | 8.7736 | 6.6343
[7 empty] | 5706 | 162 | 8.2809 | 6.248
[7 empty] | 5707 | 163 | 8.64 | 6.5296
[7 empty] | 5708 | 164 | 7.2954 | 5.4754
[7 empty] | 5709 | 165 | 10.4104 | 7.9177
[7 empty] | 5710 | 166 | 8.3727 | 6.32
[7 empty] | 5711 | 167 | 4.7818 | 3.5044
[7 empty] | 5712 | 168 | 4.1387 | 3.0002
[7 empty] | 5713 | 1 | 2.6856 | 1.8609
[7 empty] | 5714 | 2 | 2.5771 | 1.7758
[7 empty] | 5715 | 3 | 2.5687 | 1.7692
[7 empty] | 5716 | 4 | 2.7023 | 1.874
[7 empty] | 5717 | 5 | 2.719 | 1.8871
[7 empty] | 5718 | 6 | 3.1449 | 2.221
[7 empty] | 5719 | 7 | 3.8631 | 2.7841
[7 empty] | 5720 | 8 | 4.5312 | 3.308
[7 empty] | 5721 | 9 | 4.5062 | 3.2883
[7 empty] | 5722 | 10 | 6.0177 | 4.4735
[7 empty] | 5723 | 11 | 8.0888 | 6.0974
[7 empty] | 5724 | 12 | 9.0492 | 6.8504
[7 empty] | 5725 | 13 | 9.425 | 7.1451
[7 empty] | 5726 | 14 | 9.2079 | 6.9748
[7 empty] | 5727 | 15 | 9.116 | 6.9028
[7 empty] | 5728 | 16 | 10.2935 | 7.8261
[7 empty] | 5729 | 17 | 11.613 | 8.8607
[7 empty] | 5730 | 18 | 11.3708 | 8.6708
[7 empty] | 5731 | 19 | 11.8969 | 9.0833
[7 empty] | 5732 | 20 | 11.8301 | 9.0309
[7 empty] | 5733 | 21 | 12.398 | 9.4762
[7 empty] | 5734 | 22 | 8.4563 | 6.3855
[7 empty] | 5735 | 23 | 4.6983 | 3.4389
[7 empty] | 5736 | 24 | 3.0331 | 2.1333
[7 empty] | 5737 | 25 | 2.9362 | 2.0573
[7 empty] | 5738 | 26 | 2.8276 | 1.9722
[7 empty] | 5739 | 27 | 2.7274 | 1.8936
[7 empty] | 5740 | 28 | 2.8109 | 1.9591
[7 empty] | 5741 | 29 | 3.0531 | 2.149
[7 empty] | 5742 | 30 | 3.2953 | 2.3389
[7 empty] | 5743 | 31 | 4.1387 | 3.0002
[7 empty] | 5744 | 32 | 4.4895 | 3.2752
[7 empty] | 5745 | 33 | 5.1492 | 3.7925
[7 empty] | 5746 | 34 | 6.0428 | 4.4932
[7 empty] | 5747 | 35 | 8.2057 | 6.1891
[7 empty] | 5748 | 36 | 9.2329 | 6.9945
[7 empty] | 5749 | 37 | 9.3081 | 7.0534
[7 empty] | 5750 | 38 | 9.3832 | 7.1123
[7 empty] | 5751 | 39 | 9.0575 | 6.857
[7 empty] | 5752 | 40 | 10.1098 | 7.682
[7 empty] | 5753 | 41 | 10.6609 | 8.1142
[7 empty] | 5754 | 42 | 10.6776 | 8.1273
[7 empty] | 5755 | 43 | 11.0451 | 8.4154
[7 empty] | 5756 | 44 | 12.1975 | 9.319
[7 empty] | 5757 | 45 | 11.7967 | 9.0047
[7 empty] | 5758 | 46 | 9.0575 | 6.857
[7 empty] | 5759 | 47 | 5.4666 | 4.0414
[7 empty] | 5760 | 48 | 3.9717 | 2.8693
[7 empty] | 5761 | 49 | 3.312 | 2.352
[7 empty] | 5762 | 50 | 3.003 | 2.1097
[7 empty] | 5763 | 51 | 2.8944 | 2.0246
[7 empty] | 5764 | 52 | 2.9278 | 2.0508
[7 empty] | 5765 | 53 | 2.9529 | 2.0704
[7 empty] | 5766 | 54 | 3.5291 | 2.5222
[7 empty] | 5767 | 55 | 4.6648 | 3.4128
[7 empty] | 5768 | 56 | 4.907 | 3.6026
[7 empty] | 5769 | 57 | 5.8507 | 4.3426
[7 empty] | 5770 | 58 | 6.9531 | 5.2069
[7 empty] | 5771 | 59 | 8.1556 | 6.1498
[7 empty] | 5772 | 60 | 8.7819 | 6.6409
[7 empty] | 5773 | 61 | 9.4584 | 7.1713
[7 empty] | 5774 | 62 | 9.258 | 7.0141
[7 empty] | 5775 | 63 | 9.8509 | 7.479
[7 empty] | 5776 | 64 | 10.7946 | 8.219
[7 empty] | 5777 | 65 | 11.4125 | 8.7035
[7 empty] | 5778 | 66 | 11.3123 | 8.6249
[7 empty] | 5779 | 67 | 12.0472 | 9.2011
[7 empty] | 5780 | 68 | 12.2894 | 9.391
[7 empty] | 5781 | 69 | 11.78 | 8.9916
[7 empty] | 5782 | 70 | 9.4918 | 7.1975
[7 empty] | 5783 | 71 | 4.9905 | 3.6681
[7 empty] | 5784 | 72 | 3.9097 | 2.8206
[7 empty] | 5785 | 73 | 3.1951 | 2.2603
[7 empty] | 5786 | 74 | 2.9696 | 2.0835
[7 empty] | 5787 | 75 | 2.8694 | 2.0049
[7 empty] | 5788 | 76 | 2.8109 | 1.9591
[7 empty] | 5789 | 77 | 2.9863 | 2.0966
[7 empty] | 5790 | 78 | 3.3871 | 2.4109
[7 empty] | 5791 | 79 | 4.4978 | 3.2818
[7 empty] | 5792 | 80 | 4.6732 | 3.4193
[7 empty] | 5793 | 81 | 5.8507 | 4.3426
[7 empty] | 5794 | 82 | 6.9363 | 5.1938
[7 empty] | 5795 | 83 | 7.6712 | 5.77
[7 empty] | 5796 | 84 | 8.9072 | 6.7391
[7 empty] | 5797 | 85 | 8.6066 | 6.5034
[7 empty] | 5798 | 86 | 8.0972 | 6.104
[7 empty] | 5799 | 87 | 8.5398 | 6.451
[7 empty] | 5800 | 88 | 9.1995 | 6.9683
[7 empty] | 5801 | 89 | 10.544 | 8.0225
[7 empty] | 5802 | 90 | 9.9595 | 7.5642
[7 empty] | 5803 | 91 | 10.6442 | 8.1011
[7 empty] | 5804 | 92 | 10.043 | 7.6296
[7 empty] | 5805 | 93 | 7.6378 | 5.7438
[7 empty] | 5806 | 94 | 6.7359 | 5.0366
[7 empty] | 5807 | 95 | 4.882 | 3.583
[7 empty] | 5808 | 96 | 3.8965 | 2.8103
[7 empty] | 5809 | 97 | 3.8464 | 2.7711
[7 empty] | 5810 | 98 | 3.5541 | 2.5419
[7 empty] | 5811 | 99 | 3.4957 | 2.496
[7 empty] | 5812 | 100 | 3.1449 | 2.221
[7 empty] | 5813 | 101 | 3.0865 | 2.1752
[7 empty] | 5814 | 102 | 3.3203 | 2.3585
[7 empty] | 5815 | 103 | 4.0636 | 2.9413
[7 empty] | 5816 | 104 | 4.3141 | 3.1377
[7 empty] | 5817 | 105 | 4.7985 | 3.5175
[7 empty] | 5818 | 106 | 6.2516 | 4.6569
[7 empty] | 5819 | 107 | 6.6023 | 4.9319
[7 empty] | 5820 | 108 | 8.1723 | 6.1629
[7 empty] | 5821 | 109 | 7.5126 | 5.6456
[7 empty] | 5822 | 110 | 7.0616 | 5.292
[7 empty] | 5823 | 111 | 6.9029 | 5.1676
[7 empty] | 5824 | 112 | 6.9698 | 5.22
[7 empty] | 5825 | 113 | 6.6274 | 4.9515
[7 empty] | 5826 | 114 | 6.7944 | 5.0825
[7 empty] | 5827 | 115 | 6.3434 | 4.7289
[7 empty] | 5828 | 116 | 7.0199 | 5.2593
[7 empty] | 5829 | 117 | 6.6023 | 4.9319
[7 empty] | 5830 | 118 | 5.834 | 4.3295
[7 empty] | 5831 | 119 | 4.2473 | 3.0854
[7 empty] | 5832 | 120 | 3.9311 | 2.8374
[7 empty] | 5833 | 121 | 3.2034 | 2.2669
[7 empty] | 5834 | 122 | 2.7942 | 1.946
[7 empty] | 5835 | 123 | 2.7107 | 1.8805
[7 empty] | 5836 | 124 | 2.6773 | 1.8543
[7 empty] | 5837 | 125 | 2.6355 | 1.8216
[7 empty] | 5838 | 126 | 2.7775 | 1.9329
[7 empty] | 5839 | 127 | 4.2807 | 3.1115
[7 empty] | 5840 | 128 | 5.834 | 4.3295
[7 empty] | 5841 | 129 | 6.5104 | 4.8599
[7 empty] | 5842 | 130 | 6.9447 | 5.2003
[7 empty] | 5843 | 131 | 7.1034 | 5.3248
[7 empty] | 5844 | 132 | 6.8528 | 5.1283
[7 empty] | 5845 | 133 | 7.4875 | 5.626
[7 empty] | 5846 | 134 | 7.7882 | 5.8617
[7 empty] | 5847 | 135 | 7.855 | 5.9141
[7 empty] | 5848 | 136 | 7.0449 | 5.2789
[7 empty] | 5849 | 137 | 6.9447 | 5.2003
[7 empty] | 5850 | 138 | 6.8946 | 5.1611
[7 empty] | 5851 | 139 | 6.5605 | 4.8991
[7 empty] | 5852 | 140 | 6.5689 | 4.9057
[7 empty] | 5853 | 141 | 5.9175 | 4.3949
[7 empty] | 5854 | 142 | 5.2828 | 3.8973
[7 empty] | 5855 | 143 | 4.406 | 3.2098
[7 empty] | 5856 | 144 | 3.7963 | 2.7318
[7 empty] | 5857 | 145 | 3.3287 | 2.3651
[7 empty] | 5858 | 146 | 3.1199 | 2.2014
[7 empty] | 5859 | 147 | 3.0531 | 2.149
[7 empty] | 5860 | 148 | 3.0447 | 2.1424
[7 empty] | 5861 | 149 | 3.0447 | 2.1424
[7 empty] | 5862 | 150 | 3.0531 | 2.149
[7 empty] | 5863 | 151 | 4.1304 | 2.9937
[7 empty] | 5864 | 152 | 5.6503 | 4.1854
[7 empty] | 5865 | 153 | 6.2599 | 4.6634
[7 empty] | 5866 | 154 | 6.8194 | 5.1021
[7 empty] | 5867 | 155 | 6.6691 | 4.9843
[7 empty] | 5868 | 156 | 6.8361 | 5.1152
[7 empty] | 5869 | 157 | 7.546 | 5.6718
[7 empty] | 5870 | 158 | 7.8717 | 5.9272
[7 empty] | 5871 | 159 | 8.1389 | 6.1367
[7 empty] | 5872 | 160 | 8.0136 | 6.0385
[7 empty] | 5873 | 161 | 8.7736 | 6.6343
[7 empty] | 5874 | 162 | 8.2809 | 6.248
[7 empty] | 5875 | 163 | 8.64 | 6.5296
[7 empty] | 5876 | 164 | 7.2954 | 5.4754
[7 empty] | 5877 | 165 | 10.4104 | 7.9177
[7 empty] | 5878 | 166 | 8.3727 | 6.32
[7 empty] | 5879 | 167 | 4.7818 | 3.5044
[7 empty] | 5880 | 168 | 4.1387 | 3.0002
[7 empty] | 5881 | 1 | 2.6856 | 1.8609
[7 empty] | 5882 | 2 | 2.5771 | 1.7758
[7 empty] | 5883 | 3 | 2.5687 | 1.7692
[7 empty] | 5884 | 4 | 2.7023 | 1.874
[7 empty] | 5885 | 5 | 2.719 | 1.8871
[7 empty] | 5886 | 6 | 3.1449 | 2.221
[7 empty] | 5887 | 7 | 3.8631 | 2.7841
[7 empty] | 5888 | 8 | 4.5312 | 3.308
[7 empty] | 5889 | 9 | 4.5062 | 3.2883
[7 empty] | 5890 | 10 | 6.0177 | 4.4735
[7 empty] | 5891 | 11 | 8.0888 | 6.0974
[7 empty] | 5892 | 12 | 9.0492 | 6.8504
[7 empty] | 5893 | 13 | 9.425 | 7.1451
[7 empty] | 5894 | 14 | 9.2079 | 6.9748
[7 empty] | 5895 | 15 | 9.116 | 6.9028
[7 empty] | 5896 | 16 | 10.2935 | 7.8261
[7 empty] | 5897 | 17 | 11.613 | 8.8607
[7 empty] | 5898 | 18 | 11.3708 | 8.6708
[7 empty] | 5899 | 19 | 11.8969 | 9.0833
[7 empty] | 5900 | 20 | 11.8301 | 9.0309
[7 empty] | 5901 | 21 | 12.398 | 9.4762
[7 empty] | 5902 | 22 | 8.4563 | 6.3855
[7 empty] | 5903 | 23 | 4.6983 | 3.4389
[7 empty] | 5904 | 24 | 3.0331 | 2.1333
[7 empty] | 5905 | 25 | 2.9362 | 2.0573
[7 empty] | 5906 | 26 | 2.8276 | 1.9722
[7 empty] | 5907 | 27 | 2.7274 | 1.8936
[7 empty] | 5908 | 28 | 2.8109 | 1.9591
[7 empty] | 5909 | 29 | 3.0531 | 2.149
[7 empty] | 5910 | 30 | 3.2953 | 2.3389
[7 empty] | 5911 | 31 | 4.1387 | 3.0002
[7 empty] | 5912 | 32 | 4.4895 | 3.2752
[7 empty] | 5913 | 33 | 5.1492 | 3.7925
[7 empty] | 5914 | 34 | 6.0428 | 4.4932
[7 empty] | 5915 | 35 | 8.2057 | 6.1891
[7 empty] | 5916 | 36 | 9.2329 | 6.9945
[7 empty] | 5917 | 37 | 9.3081 | 7.0534
[7 empty] | 5918 | 38 | 9.3832 | 7.1123
[7 empty] | 5919 | 39 | 9.0575 | 6.857
[7 empty] | 5920 | 40 | 10.1098 | 7.682
[7 empty] | 5921 | 41 | 10.6609 | 8.1142
[7 empty] | 5922 | 42 | 10.6776 | 8.1273
[7 empty] | 5923 | 43 | 11.0451 | 8.4154
[7 empty] | 5924 | 44 | 12.1975 | 9.319
[7 empty] | 5925 | 45 | 11.7967 | 9.0047
[7 empty] | 5926 | 46 | 9.0575 | 6.857
[7 empty] | 5927 | 47 | 5.4666 | 4.0414
[7 empty] | 5928 | 48 | 3.9717 | 2.8693
[7 empty] | 5929 | 49 | 3.312 | 2.352
[7 empty] | 5930 | 50 | 3.003 | 2.1097
[7 empty] | 5931 | 51 | 2.8944 | 2.0246
[7 empty] | 5932 | 52 | 2.9278 | 2.0508
[7 empty] | 5933 | 53 | 2.9529 | 2.0704
[7 empty] | 5934 | 54 | 3.5291 | 2.5222
[7 empty] | 5935 | 55 | 4.6648 | 3.4128
[7 empty] | 5936 | 56 | 4.907 | 3.6026
[7 empty] | 5937 | 57 | 5.8507 | 4.3426
[7 empty] | 5938 | 58 | 6.9531 | 5.2069
[7 empty] | 5939 | 59 | 8.1556 | 6.1498
[7 empty] | 5940 | 60 | 8.7819 | 6.6409
[7 empty] | 5941 | 61 | 9.4584 | 7.1713
[7 empty] | 5942 | 62 | 9.258 | 7.0141
[7 empty] | 5943 | 63 | 9.8509 | 7.479
[7 empty] | 5944 | 64 | 10.7946 | 8.219
[7 empty] | 5945 | 65 | 11.4125 | 8.7035
[7 empty] | 5946 | 66 | 11.3123 | 8.6249
[7 empty] | 5947 | 67 | 12.0472 | 9.2011
[7 empty] | 5948 | 68 | 12.2894 | 9.391
[7 empty] | 5949 | 69 | 11.78 | 8.9916
[7 empty] | 5950 | 70 | 9.4918 | 7.1975
[7 empty] | 5951 | 71 | 4.9905 | 3.6681
[7 empty] | 5952 | 72 | 3.9097 | 2.8206
[7 empty] | 5953 | 73 | 3.1951 | 2.2603
[7 empty] | 5954 | 74 | 2.9696 | 2.0835
[7 empty] | 5955 | 75 | 2.8694 | 2.0049
[7 empty] | 5956 | 76 | 2.8109 | 1.9591
[7 empty] | 5957 | 77 | 2.9863 | 2.0966
[7 empty] | 5958 | 78 | 3.3871 | 2.4109
[7 empty] | 5959 | 79 | 4.4978 | 3.2818
[7 empty] | 5960 | 80 | 4.6732 | 3.4193
[7 empty] | 5961 | 81 | 5.8507 | 4.3426
[7 empty] | 5962 | 82 | 6.9363 | 5.1938
[7 empty] | 5963 | 83 | 7.6712 | 5.77
[7 empty] | 5964 | 84 | 8.9072 | 6.7391
[7 empty] | 5965 | 85 | 8.6066 | 6.5034
[7 empty] | 5966 | 86 | 8.0972 | 6.104
[7 empty] | 5967 | 87 | 8.5398 | 6.451
[7 empty] | 5968 | 88 | 9.1995 | 6.9683
[7 empty] | 5969 | 89 | 10.544 | 8.0225
[7 empty] | 5970 | 90 | 9.9595 | 7.5642
[7 empty] | 5971 | 91 | 10.6442 | 8.1011
[7 empty] | 5972 | 92 | 10.043 | 7.6296
[7 empty] | 5973 | 93 | 7.6378 | 5.7438
[7 empty] | 5974 | 94 | 6.7359 | 5.0366
[7 empty] | 5975 | 95 | 4.882 | 3.583
[7 empty] | 5976 | 96 | 3.8965 | 2.8103
[7 empty] | 5977 | 97 | 3.8464 | 2.7711
[7 empty] | 5978 | 98 | 3.5541 | 2.5419
[7 empty] | 5979 | 99 | 3.4957 | 2.496
[7 empty] | 5980 | 100 | 3.1449 | 2.221
[7 empty] | 5981 | 101 | 3.0865 | 2.1752
[7 empty] | 5982 | 102 | 3.3203 | 2.3585
[7 empty] | 5983 | 103 | 4.0636 | 2.9413
[7 empty] | 5984 | 104 | 4.3141 | 3.1377
[7 empty] | 5985 | 105 | 4.7985 | 3.5175
[7 empty] | 5986 | 106 | 6.2516 | 4.6569
[7 empty] | 5987 | 107 | 6.6023 | 4.9319
[7 empty] | 5988 | 108 | 8.1723 | 6.1629
[7 empty] | 5989 | 109 | 7.5126 | 5.6456
[7 empty] | 5990 | 110 | 7.0616 | 5.292
[7 empty] | 5991 | 111 | 6.9029 | 5.1676
[7 empty] | 5992 | 112 | 6.9698 | 5.22
[7 empty] | 5993 | 113 | 6.6274 | 4.9515
[7 empty] | 5994 | 114 | 6.7944 | 5.0825
[7 empty] | 5995 | 115 | 6.3434 | 4.7289
[7 empty] | 5996 | 116 | 7.0199 | 5.2593
[7 empty] | 5997 | 117 | 6.6023 | 4.9319
[7 empty] | 5998 | 118 | 5.834 | 4.3295
[7 empty] | 5999 | 119 | 4.2473 | 3.0854
[7 empty] | 6000 | 120 | 3.9311 | 2.8374
[7 empty] | 6001 | 121 | 3.2034 | 2.2669
[7 empty] | 6002 | 122 | 2.7942 | 1.946
[7 empty] | 6003 | 123 | 2.7107 | 1.8805
[7 empty] | 6004 | 124 | 2.6773 | 1.8543
[7 empty] | 6005 | 125 | 2.6355 | 1.8216
[7 empty] | 6006 | 126 | 2.7775 | 1.9329
[7 empty] | 6007 | 127 | 4.2807 | 3.1115
[7 empty] | 6008 | 128 | 5.834 | 4.3295
[7 empty] | 6009 | 129 | 6.5104 | 4.8599
[7 empty] | 6010 | 130 | 6.9447 | 5.2003
[7 empty] | 6011 | 131 | 7.1034 | 5.3248
[7 empty] | 6012 | 132 | 6.8528 | 5.1283
[7 empty] | 6013 | 133 | 7.4875 | 5.626
[7 empty] | 6014 | 134 | 7.7882 | 5.8617
[7 empty] | 6015 | 135 | 7.855 | 5.9141
[7 empty] | 6016 | 136 | 7.0449 | 5.2789
[7 empty] | 6017 | 137 | 6.9447 | 5.2003
[7 empty] | 6018 | 138 | 6.8946 | 5.1611
[7 empty] | 6019 | 139 | 6.5605 | 4.8991
[7 empty] | 6020 | 140 | 6.5689 | 4.9057
[7 empty] | 6021 | 141 | 5.9175 | 4.3949
[7 empty] | 6022 | 142 | 5.2828 | 3.8973
[7 empty] | 6023 | 143 | 4.406 | 3.2098
[7 empty] | 6024 | 144 | 3.7963 | 2.7318
[7 empty] | 6025 | 145 | 3.3287 | 2.3651
[7 empty] | 6026 | 146 | 3.1199 | 2.2014
[7 empty] | 6027 | 147 | 3.0531 | 2.149
[7 empty] | 6028 | 148 | 3.0447 | 2.1424
[7 empty] | 6029 | 149 | 3.0447 | 2.1424
[7 empty] | 6030 | 150 | 3.0531 | 2.149
[7 empty] | 6031 | 151 | 4.1304 | 2.9937
[7 empty] | 6032 | 152 | 5.6503 | 4.1854
[7 empty] | 6033 | 153 | 6.2599 | 4.6634
[7 empty] | 6034 | 154 | 6.8194 | 5.1021
[7 empty] | 6035 | 155 | 6.6691 | 4.9843
[7 empty] | 6036 | 156 | 6.8361 | 5.1152
[7 empty] | 6037 | 157 | 7.546 | 5.6718
[7 empty] | 6038 | 158 | 7.8717 | 5.9272
[7 empty] | 6039 | 159 | 8.1389 | 6.1367
[7 empty] | 6040 | 160 | 8.0136 | 6.0385
[7 empty] | 6041 | 161 | 8.7736 | 6.6343
[7 empty] | 6042 | 162 | 8.2809 | 6.248
[7 empty] | 6043 | 163 | 8.64 | 6.5296
[7 empty] | 6044 | 164 | 7.2954 | 5.4754
[7 empty] | 6045 | 165 | 10.4104 | 7.9177
[7 empty] | 6046 | 166 | 8.3727 | 6.32
[7 empty] | 6047 | 167 | 4.7818 | 3.5044
[7 empty] | 6048 | 168 | 4.1387 | 3.0002
[7 empty] | 6049 | 1 | 2.6856 | 1.8609
[7 empty] | 6050 | 2 | 2.5771 | 1.7758
[7 empty] | 6051 | 3 | 2.5687 | 1.7692
[7 empty] | 6052 | 4 | 2.7023 | 1.874
[7 empty] | 6053 | 5 | 2.719 | 1.8871
[7 empty] | 6054 | 6 | 3.1449 | 2.221
[7 empty] | 6055 | 7 | 3.8631 | 2.7841
[7 empty] | 6056 | 8 | 4.5312 | 3.308
[7 empty] | 6057 | 9 | 4.5062 | 3.2883
[7 empty] | 6058 | 10 | 6.0177 | 4.4735
[7 empty] | 6059 | 11 | 8.0888 | 6.0974
[7 empty] | 6060 | 12 | 9.0492 | 6.8504
[7 empty] | 6061 | 13 | 9.425 | 7.1451
[7 empty] | 6062 | 14 | 9.2079 | 6.9748
[7 empty] | 6063 | 15 | 9.116 | 6.9028
[7 empty] | 6064 | 16 | 10.2935 | 7.8261
[7 empty] | 6065 | 17 | 11.613 | 8.8607
[7 empty] | 6066 | 18 | 11.3708 | 8.6708
[7 empty] | 6067 | 19 | 11.8969 | 9.0833
[7 empty] | 6068 | 20 | 11.8301 | 9.0309
[7 empty] | 6069 | 21 | 12.398 | 9.4762
[7 empty] | 6070 | 22 | 8.4563 | 6.3855
[7 empty] | 6071 | 23 | 4.6983 | 3.4389
[7 empty] | 6072 | 24 | 3.0331 | 2.1333
[7 empty] | 6073 | 25 | 2.9362 | 2.0573
[7 empty] | 6074 | 26 | 2.8276 | 1.9722
[7 empty] | 6075 | 27 | 2.7274 | 1.8936
[7 empty] | 6076 | 28 | 2.8109 | 1.9591
[7 empty] | 6077 | 29 | 3.0531 | 2.149
[7 empty] | 6078 | 30 | 3.2953 | 2.3389
[7 empty] | 6079 | 31 | 4.1387 | 3.0002
[7 empty] | 6080 | 32 | 4.4895 | 3.2752
[7 empty] | 6081 | 33 | 5.1492 | 3.7925
[7 empty] | 6082 | 34 | 6.0428 | 4.4932
[7 empty] | 6083 | 35 | 8.2057 | 6.1891
[7 empty] | 6084 | 36 | 9.2329 | 6.9945
[7 empty] | 6085 | 37 | 9.3081 | 7.0534
[7 empty] | 6086 | 38 | 9.3832 | 7.1123
[7 empty] | 6087 | 39 | 9.0575 | 6.857
[7 empty] | 6088 | 40 | 10.1098 | 7.682
[7 empty] | 6089 | 41 | 10.6609 | 8.1142
[7 empty] | 6090 | 42 | 10.6776 | 8.1273
[7 empty] | 6091 | 43 | 11.0451 | 8.4154
[7 empty] | 6092 | 44 | 12.1975 | 9.319
[7 empty] | 6093 | 45 | 11.7967 | 9.0047
[7 empty] | 6094 | 46 | 9.0575 | 6.857
[7 empty] | 6095 | 47 | 5.4666 | 4.0414
[7 empty] | 6096 | 48 | 3.9717 | 2.8693
[7 empty] | 6097 | 49 | 3.312 | 2.352
[7 empty] | 6098 | 50 | 3.003 | 2.1097
[7 empty] | 6099 | 51 | 2.8944 | 2.0246
[7 empty] | 6100 | 52 | 2.9278 | 2.0508
[7 empty] | 6101 | 53 | 2.9529 | 2.0704
[7 empty] | 6102 | 54 | 3.5291 | 2.5222
[7 empty] | 6103 | 55 | 4.6648 | 3.4128
[7 empty] | 6104 | 56 | 4.907 | 3.6026
[7 empty] | 6105 | 57 | 5.8507 | 4.3426
[7 empty] | 6106 | 58 | 6.9531 | 5.2069
[7 empty] | 6107 | 59 | 8.1556 | 6.1498
[7 empty] | 6108 | 60 | 8.7819 | 6.6409
[7 empty] | 6109 | 61 | 9.4584 | 7.1713
[7 empty] | 6110 | 62 | 9.258 | 7.0141
[7 empty] | 6111 | 63 | 9.8509 | 7.479
[7 empty] | 6112 | 64 | 10.7946 | 8.219
[7 empty] | 6113 | 65 | 11.4125 | 8.7035
[7 empty] | 6114 | 66 | 11.3123 | 8.6249
[7 empty] | 6115 | 67 | 12.0472 | 9.2011
[7 empty] | 6116 | 68 | 12.2894 | 9.391
[7 empty] | 6117 | 69 | 11.78 | 8.9916
[7 empty] | 6118 | 70 | 9.4918 | 7.1975
[7 empty] | 6119 | 71 | 4.9905 | 3.6681
[7 empty] | 6120 | 72 | 3.9097 | 2.8206
[7 empty] | 6121 | 73 | 3.1951 | 2.2603
[7 empty] | 6122 | 74 | 2.9696 | 2.0835
[7 empty] | 6123 | 75 | 2.8694 | 2.0049
[7 empty] | 6124 | 76 | 2.8109 | 1.9591
[7 empty] | 6125 | 77 | 2.9863 | 2.0966
[7 empty] | 6126 | 78 | 3.3871 | 2.4109
[7 empty] | 6127 | 79 | 4.4978 | 3.2818
[7 empty] | 6128 | 80 | 4.6732 | 3.4193
[7 empty] | 6129 | 81 | 5.8507 | 4.3426
[7 empty] | 6130 | 82 | 6.9363 | 5.1938
[7 empty] | 6131 | 83 | 7.6712 | 5.77
[7 empty] | 6132 | 84 | 8.9072 | 6.7391
[7 empty] | 6133 | 85 | 8.6066 | 6.5034
[7 empty] | 6134 | 86 | 8.0972 | 6.104
[7 empty] | 6135 | 87 | 8.5398 | 6.451
[7 empty] | 6136 | 88 | 9.1995 | 6.9683
[7 empty] | 6137 | 89 | 10.544 | 8.0225
[7 empty] | 6138 | 90 | 9.9595 | 7.5642
[7 empty] | 6139 | 91 | 10.6442 | 8.1011
[7 empty] | 6140 | 92 | 10.043 | 7.6296
[7 empty] | 6141 | 93 | 7.6378 | 5.7438
[7 empty] | 6142 | 94 | 6.7359 | 5.0366
[7 empty] | 6143 | 95 | 4.882 | 3.583
[7 empty] | 6144 | 96 | 3.8965 | 2.8103
[7 empty] | 6145 | 97 | 3.8464 | 2.7711
[7 empty] | 6146 | 98 | 3.5541 | 2.5419
[7 empty] | 6147 | 99 | 3.4957 | 2.496
[7 empty] | 6148 | 100 | 3.1449 | 2.221
[7 empty] | 6149 | 101 | 3.0865 | 2.1752
[7 empty] | 6150 | 102 | 3.3203 | 2.3585
[7 empty] | 6151 | 103 | 4.0636 | 2.9413
[7 empty] | 6152 | 104 | 4.3141 | 3.1377
[7 empty] | 6153 | 105 | 4.7985 | 3.5175
[7 empty] | 6154 | 106 | 6.2516 | 4.6569
[7 empty] | 6155 | 107 | 6.6023 | 4.9319
[7 empty] | 6156 | 108 | 8.1723 | 6.1629
[7 empty] | 6157 | 109 | 7.5126 | 5.6456
[7 empty] | 6158 | 110 | 7.0616 | 5.292
[7 empty] | 6159 | 111 | 6.9029 | 5.1676
[7 empty] | 6160 | 112 | 6.9698 | 5.22
[7 empty] | 6161 | 113 | 6.6274 | 4.9515
[7 empty] | 6162 | 114 | 6.7944 | 5.0825
[7 empty] | 6163 | 115 | 6.3434 | 4.7289
[7 empty] | 6164 | 116 | 7.0199 | 5.2593
[7 empty] | 6165 | 117 | 6.6023 | 4.9319
[7 empty] | 6166 | 118 | 5.834 | 4.3295
[7 empty] | 6167 | 119 | 4.2473 | 3.0854
[7 empty] | 6168 | 120 | 3.9311 | 2.8374
[7 empty] | 6169 | 121 | 3.2034 | 2.2669
[7 empty] | 6170 | 122 | 2.7942 | 1.946
[7 empty] | 6171 | 123 | 2.7107 | 1.8805
[7 empty] | 6172 | 124 | 2.6773 | 1.8543
[7 empty] | 6173 | 125 | 2.6355 | 1.8216
[7 empty] | 6174 | 126 | 2.7775 | 1.9329
[7 empty] | 6175 | 127 | 4.2807 | 3.1115
[7 empty] | 6176 | 128 | 5.834 | 4.3295
[7 empty] | 6177 | 129 | 6.5104 | 4.8599
[7 empty] | 6178 | 130 | 6.9447 | 5.2003
[7 empty] | 6179 | 131 | 7.1034 | 5.3248
[7 empty] | 6180 | 132 | 6.8528 | 5.1283
[7 empty] | 6181 | 133 | 7.4875 | 5.626
[7 empty] | 6182 | 134 | 7.7882 | 5.8617
[7 empty] | 6183 | 135 | 7.855 | 5.9141
[7 empty] | 6184 | 136 | 7.0449 | 5.2789
[7 empty] | 6185 | 137 | 6.9447 | 5.2003
[7 empty] | 6186 | 138 | 6.8946 | 5.1611
[7 empty] | 6187 | 139 | 6.5605 | 4.8991
[7 empty] | 6188 | 140 | 6.5689 | 4.9057
[7 empty] | 6189 | 141 | 5.9175 | 4.3949
[7 empty] | 6190 | 142 | 5.2828 | 3.8973
[7 empty] | 6191 | 143 | 4.406 | 3.2098
[7 empty] | 6192 | 144 | 3.7963 | 2.7318
[7 empty] | 6193 | 145 | 3.3287 | 2.3651
[7 empty] | 6194 | 146 | 3.1199 | 2.2014
[7 empty] | 6195 | 147 | 3.0531 | 2.149
[7 empty] | 6196 | 148 | 3.0447 | 2.1424
[7 empty] | 6197 | 149 | 3.0447 | 2.1424
[7 empty] | 6198 | 150 | 3.0531 | 2.149
[7 empty] | 6199 | 151 | 4.1304 | 2.9937
[7 empty] | 6200 | 152 | 5.6503 | 4.1854
[7 empty] | 6201 | 153 | 6.2599 | 4.6634
[7 empty] | 6202 | 154 | 6.8194 | 5.1021
[7 empty] | 6203 | 155 | 6.6691 | 4.9843
[7 empty] | 6204 | 156 | 6.8361 | 5.1152
[7 empty] | 6205 | 157 | 7.546 | 5.6718
[7 empty] | 6206 | 158 | 7.8717 | 5.9272
[7 empty] | 6207 | 159 | 8.1389 | 6.1367
[7 empty] | 6208 | 160 | 8.0136 | 6.0385
[7 empty] | 6209 | 161 | 8.7736 | 6.6343
[7 empty] | 6210 | 162 | 8.2809 | 6.248
[7 empty] | 6211 | 163 | 8.64 | 6.5296
[7 empty] | 6212 | 164 | 7.2954 | 5.4754
[7 empty] | 6213 | 165 | 10.4104 | 7.9177
[7 empty] | 6214 | 166 | 8.3727 | 6.32
[7 empty] | 6215 | 167 | 4.7818 | 3.5044
[7 empty] | 6216 | 168 | 4.1387 | 3.0002
[7 empty] | 6217 | 1 | 2.6856 | 1.8609
[7 empty] | 6218 | 2 | 2.5771 | 1.7758
[7 empty] | 6219 | 3 | 2.5687 | 1.7692
[7 empty] | 6220 | 4 | 2.7023 | 1.874
[7 empty] | 6221 | 5 | 2.719 | 1.8871
[7 empty] | 6222 | 6 | 3.1449 | 2.221
[7 empty] | 6223 | 7 | 3.8631 | 2.7841
[7 empty] | 6224 | 8 | 4.5312 | 3.308
[7 empty] | 6225 | 9 | 4.5062 | 3.2883
[7 empty] | 6226 | 10 | 6.0177 | 4.4735
[7 empty] | 6227 | 11 | 8.0888 | 6.0974
[7 empty] | 6228 | 12 | 9.0492 | 6.8504
[7 empty] | 6229 | 13 | 9.425 | 7.1451
[7 empty] | 6230 | 14 | 9.2079 | 6.9748
[7 empty] | 6231 | 15 | 9.116 | 6.9028
[7 empty] | 6232 | 16 | 10.2935 | 7.8261
[7 empty] | 6233 | 17 | 11.613 | 8.8607
[7 empty] | 6234 | 18 | 11.3708 | 8.6708
[7 empty] | 6235 | 19 | 11.8969 | 9.0833
[7 empty] | 6236 | 20 | 11.8301 | 9.0309
[7 empty] | 6237 | 21 | 12.398 | 9.4762
[7 empty] | 6238 | 22 | 8.4563 | 6.3855
[7 empty] | 6239 | 23 | 4.6983 | 3.4389
[7 empty] | 6240 | 24 | 3.0331 | 2.1333
[7 empty] | 6241 | 25 | 2.9362 | 2.0573
[7 empty] | 6242 | 26 | 2.8276 | 1.9722
[7 empty] | 6243 | 27 | 2.7274 | 1.8936
[7 empty] | 6244 | 28 | 2.8109 | 1.9591
[7 empty] | 6245 | 29 | 3.0531 | 2.149
[7 empty] | 6246 | 30 | 3.2953 | 2.3389
[7 empty] | 6247 | 31 | 4.1387 | 3.0002
[7 empty] | 6248 | 32 | 4.4895 | 3.2752
[7 empty] | 6249 | 33 | 5.1492 | 3.7925
[7 empty] | 6250 | 34 | 6.0428 | 4.4932
[7 empty] | 6251 | 35 | 8.2057 | 6.1891
[7 empty] | 6252 | 36 | 9.2329 | 6.9945
[7 empty] | 6253 | 37 | 9.3081 | 7.0534
[7 empty] | 6254 | 38 | 9.3832 | 7.1123
[7 empty] | 6255 | 39 | 9.0575 | 6.857
[7 empty] | 6256 | 40 | 10.1098 | 7.682
[7 empty] | 6257 | 41 | 10.6609 | 8.1142
[7 empty] | 6258 | 42 | 10.6776 | 8.1273
[7 empty] | 6259 | 43 | 11.0451 | 8.4154
[7 empty] | 6260 | 44 | 12.1975 | 9.319
[7 empty] | 6261 | 45 | 11.7967 | 9.0047
[7 empty] | 6262 | 46 | 9.0575 | 6.857
[7 empty] | 6263 | 47 | 5.4666 | 4.0414
[7 empty] | 6264 | 48 | 3.9717 | 2.8693
[7 empty] | 6265 | 49 | 3.312 | 2.352
[7 empty] | 6266 | 50 | 3.003 | 2.1097
[7 empty] | 6267 | 51 | 2.8944 | 2.0246
[7 empty] | 6268 | 52 | 2.9278 | 2.0508
[7 empty] | 6269 | 53 | 2.9529 | 2.0704
[7 empty] | 6270 | 54 | 3.5291 | 2.5222
[7 empty] | 6271 | 55 | 4.6648 | 3.4128
[7 empty] | 6272 | 56 | 4.907 | 3.6026
[7 empty] | 6273 | 57 | 5.8507 | 4.3426
[7 empty] | 6274 | 58 | 6.9531 | 5.2069
[7 empty] | 6275 | 59 | 8.1556 | 6.1498
[7 empty] | 6276 | 60 | 8.7819 | 6.6409
[7 empty] | 6277 | 61 | 9.4584 | 7.1713
[7 empty] | 6278 | 62 | 9.258 | 7.0141
[7 empty] | 6279 | 63 | 9.8509 | 7.479
[7 empty] | 6280 | 64 | 10.7946 | 8.219
[7 empty] | 6281 | 65 | 11.4125 | 8.7035
[7 empty] | 6282 | 66 | 11.3123 | 8.6249
[7 empty] | 6283 | 67 | 12.0472 | 9.2011
[7 empty] | 6284 | 68 | 12.2894 | 9.391
[7 empty] | 6285 | 69 | 11.78 | 8.9916
[7 empty] | 6286 | 70 | 9.4918 | 7.1975
[7 empty] | 6287 | 71 | 4.9905 | 3.6681
[7 empty] | 6288 | 72 | 3.9097 | 2.8206
[7 empty] | 6289 | 73 | 3.1951 | 2.2603
[7 empty] | 6290 | 74 | 2.9696 | 2.0835
[7 empty] | 6291 | 75 | 2.8694 | 2.0049
[7 empty] | 6292 | 76 | 2.8109 | 1.9591
[7 empty] | 6293 | 77 | 2.9863 | 2.0966
[7 empty] | 6294 | 78 | 3.3871 | 2.4109
[7 empty] | 6295 | 79 | 4.4978 | 3.2818
[7 empty] | 6296 | 80 | 4.6732 | 3.4193
[7 empty] | 6297 | 81 | 5.8507 | 4.3426
[7 empty] | 6298 | 82 | 6.9363 | 5.1938
[7 empty] | 6299 | 83 | 7.6712 | 5.77
[7 empty] | 6300 | 84 | 8.9072 | 6.7391
[7 empty] | 6301 | 85 | 8.6066 | 6.5034
[7 empty] | 6302 | 86 | 8.0972 | 6.104
[7 empty] | 6303 | 87 | 8.5398 | 6.451
[7 empty] | 6304 | 88 | 9.1995 | 6.9683
[7 empty] | 6305 | 89 | 10.544 | 8.0225
[7 empty] | 6306 | 90 | 9.9595 | 7.5642
[7 empty] | 6307 | 91 | 10.6442 | 8.1011
[7 empty] | 6308 | 92 | 10.043 | 7.6296
[7 empty] | 6309 | 93 | 7.6378 | 5.7438
[7 empty] | 6310 | 94 | 6.7359 | 5.0366
[7 empty] | 6311 | 95 | 4.882 | 3.583
[7 empty] | 6312 | 96 | 3.8965 | 2.8103
[7 empty] | 6313 | 97 | 3.8464 | 2.7711
[7 empty] | 6314 | 98 | 3.5541 | 2.5419
[7 empty] | 6315 | 99 | 3.4957 | 2.496
[7 empty] | 6316 | 100 | 3.1449 | 2.221
[7 empty] | 6317 | 101 | 3.0865 | 2.1752
[7 empty] | 6318 | 102 | 3.3203 | 2.3585
[7 empty] | 6319 | 103 | 4.0636 | 2.9413
[7 empty] | 6320 | 104 | 4.3141 | 3.1377
[7 empty] | 6321 | 105 | 4.7985 | 3.5175
[7 empty] | 6322 | 106 | 6.2516 | 4.6569
[7 empty] | 6323 | 107 | 6.6023 | 4.9319
[7 empty] | 6324 | 108 | 8.1723 | 6.1629
[7 empty] | 6325 | 109 | 7.5126 | 5.6456
[7 empty] | 6326 | 110 | 7.0616 | 5.292
[7 empty] | 6327 | 111 | 6.9029 | 5.1676
[7 empty] | 6328 | 112 | 6.9698 | 5.22
[7 empty] | 6329 | 113 | 6.6274 | 4.9515
[7 empty] | 6330 | 114 | 6.7944 | 5.0825
[7 empty] | 6331 | 115 | 6.3434 | 4.7289
[7 empty] | 6332 | 116 | 7.0199 | 5.2593
[7 empty] | 6333 | 117 | 6.6023 | 4.9319
[7 empty] | 6334 | 118 | 5.834 | 4.3295
[7 empty] | 6335 | 119 | 4.2473 | 3.0854
[7 empty] | 6336 | 120 | 3.9311 | 2.8374
[7 empty] | 6337 | 121 | 3.2034 | 2.2669
[7 empty] | 6338 | 122 | 2.7942 | 1.946
[7 empty] | 6339 | 123 | 2.7107 | 1.8805
[7 empty] | 6340 | 124 | 2.6773 | 1.8543
[7 empty] | 6341 | 125 | 2.6355 | 1.8216
[7 empty] | 6342 | 126 | 2.7775 | 1.9329
[7 empty] | 6343 | 127 | 4.2807 | 3.1115
[7 empty] | 6344 | 128 | 5.834 | 4.3295
[7 empty] | 6345 | 129 | 6.5104 | 4.8599
[7 empty] | 6346 | 130 | 6.9447 | 5.2003
[7 empty] | 6347 | 131 | 7.1034 | 5.3248
[7 empty] | 6348 | 132 | 6.8528 | 5.1283
[7 empty] | 6349 | 133 | 7.4875 | 5.626
[7 empty] | 6350 | 134 | 7.7882 | 5.8617
[7 empty] | 6351 | 135 | 7.855 | 5.9141
[7 empty] | 6352 | 136 | 7.0449 | 5.2789
[7 empty] | 6353 | 137 | 6.9447 | 5.2003
[7 empty] | 6354 | 138 | 6.8946 | 5.1611
[7 empty] | 6355 | 139 | 6.5605 | 4.8991
[7 empty] | 6356 | 140 | 6.5689 | 4.9057
[7 empty] | 6357 | 141 | 5.9175 | 4.3949
[7 empty] | 6358 | 142 | 5.2828 | 3.8973
[7 empty] | 6359 | 143 | 4.406 | 3.2098
[7 empty] | 6360 | 144 | 3.7963 | 2.7318
[7 empty] | 6361 | 145 | 3.3287 | 2.3651
[7 empty] | 6362 | 146 | 3.1199 | 2.2014
[7 empty] | 6363 | 147 | 3.0531 | 2.149
[7 empty] | 6364 | 148 | 3.0447 | 2.1424
[7 empty] | 6365 | 149 | 3.0447 | 2.1424
[7 empty] | 6366 | 150 | 3.0531 | 2.149
[7 empty] | 6367 | 151 | 4.1304 | 2.9937
[7 empty] | 6368 | 152 | 5.6503 | 4.1854
[7 empty] | 6369 | 153 | 6.2599 | 4.6634
[7 empty] | 6370 | 154 | 6.8194 | 5.1021
[7 empty] | 6371 | 155 | 6.6691 | 4.9843
[7 empty] | 6372 | 156 | 6.8361 | 5.1152
[7 empty] | 6373 | 157 | 7.546 | 5.6718
[7 empty] | 6374 | 158 | 7.8717 | 5.9272
[7 empty] | 6375 | 159 | 8.1389 | 6.1367
[7 empty] | 6376 | 160 | 8.0136 | 6.0385
[7 empty] | 6377 | 161 | 8.7736 | 6.6343
[7 empty] | 6378 | 162 | 8.2809 | 6.248
[7 empty] | 6379 | 163 | 8.64 | 6.5296
[7 empty] | 6380 | 164 | 7.2954 | 5.4754
[7 empty] | 6381 | 165 | 10.4104 | 7.9177
[7 empty] | 6382 | 166 | 8.3727 | 6.32
[7 empty] | 6383 | 167 | 4.7818 | 3.5044
[7 empty] | 6384 | 168 | 4.1387 | 3.0002
[7 empty] | 6385 | 1 | 2.6856 | 1.8609
[7 empty] | 6386 | 2 | 2.5771 | 1.7758
[7 empty] | 6387 | 3 | 2.5687 | 1.7692
[7 empty] | 6388 | 4 | 2.7023 | 1.874
[7 empty] | 6389 | 5 | 2.719 | 1.8871
[7 empty] | 6390 | 6 | 3.1449 | 2.221
[7 empty] | 6391 | 7 | 3.8631 | 2.7841
[7 empty] | 6392 | 8 | 4.5312 | 3.308
[7 empty] | 6393 | 9 | 4.5062 | 3.2883
[7 empty] | 6394 | 10 | 6.0177 | 4.4735
[7 empty] | 6395 | 11 | 8.0888 | 6.0974
[7 empty] | 6396 | 12 | 9.0492 | 6.8504
[7 empty] | 6397 | 13 | 9.425 | 7.1451
[7 empty] | 6398 | 14 | 9.2079 | 6.9748
[7 empty] | 6399 | 15 | 9.116 | 6.9028
[7 empty] | 6400 | 16 | 10.2935 | 7.8261
[7 empty] | 6401 | 17 | 11.613 | 8.8607
[7 empty] | 6402 | 18 | 11.3708 | 8.6708
[7 empty] | 6403 | 19 | 11.8969 | 9.0833
[7 empty] | 6404 | 20 | 11.8301 | 9.0309
[7 empty] | 6405 | 21 | 12.398 | 9.4762
[7 empty] | 6406 | 22 | 8.4563 | 6.3855
[7 empty] | 6407 | 23 | 4.6983 | 3.4389
[7 empty] | 6408 | 24 | 3.0331 | 2.1333
[7 empty] | 6409 | 25 | 2.9362 | 2.0573
[7 empty] | 6410 | 26 | 2.8276 | 1.9722
[7 empty] | 6411 | 27 | 2.7274 | 1.8936
[7 empty] | 6412 | 28 | 2.8109 | 1.9591
[7 empty] | 6413 | 29 | 3.0531 | 2.149
[7 empty] | 6414 | 30 | 3.2953 | 2.3389
[7 empty] | 6415 | 31 | 4.1387 | 3.0002
[7 empty] | 6416 | 32 | 4.4895 | 3.2752
[7 empty] | 6417 | 33 | 5.1492 | 3.7925
[7 empty] | 6418 | 34 | 6.0428 | 4.4932
[7 empty] | 6419 | 35 | 8.2057 | 6.1891
[7 empty] | 6420 | 36 | 9.2329 | 6.9945
[7 empty] | 6421 | 37 | 9.3081 | 7.0534
[7 empty] | 6422 | 38 | 9.3832 | 7.1123
[7 empty] | 6423 | 39 | 9.0575 | 6.857
[7 empty] | 6424 | 40 | 10.1098 | 7.682
[7 empty] | 6425 | 41 | 10.6609 | 8.1142
[7 empty] | 6426 | 42 | 10.6776 | 8.1273
[7 empty] | 6427 | 43 | 11.0451 | 8.4154
[7 empty] | 6428 | 44 | 12.1975 | 9.319
[7 empty] | 6429 | 45 | 11.7967 | 9.0047
[7 empty] | 6430 | 46 | 9.0575 | 6.857
[7 empty] | 6431 | 47 | 5.4666 | 4.0414
[7 empty] | 6432 | 48 | 3.9717 | 2.8693
[7 empty] | 6433 | 49 | 3.312 | 2.352
[7 empty] | 6434 | 50 | 3.003 | 2.1097
[7 empty] | 6435 | 51 | 2.8944 | 2.0246
[7 empty] | 6436 | 52 | 2.9278 | 2.0508
[7 empty] | 6437 | 53 | 2.9529 | 2.0704
[7 empty] | 6438 | 54 | 3.5291 | 2.5222
[7 empty] | 6439 | 55 | 4.6648 | 3.4128
[7 empty] | 6440 | 56 | 4.907 | 3.6026
[7 empty] | 6441 | 57 | 5.8507 | 4.3426
[7 empty] | 6442 | 58 | 6.9531 | 5.2069
[7 empty] | 6443 | 59 | 8.1556 | 6.1498
[7 empty] | 6444 | 60 | 8.7819 | 6.6409
[7 empty] | 6445 | 61 | 9.4584 | 7.1713
[7 empty] | 6446 | 62 | 9.258 | 7.0141
[7 empty] | 6447 | 63 | 9.8509 | 7.479
[7 empty] | 6448 | 64 | 10.7946 | 8.219
[7 empty] | 6449 | 65 | 11.4125 | 8.7035
[7 empty] | 6450 | 66 | 11.3123 | 8.6249
[7 empty] | 6451 | 67 | 12.0472 | 9.2011
[7 empty] | 6452 | 68 | 12.2894 | 9.391
[7 empty] | 6453 | 69 | 11.78 | 8.9916
[7 empty] | 6454 | 70 | 9.4918 | 7.1975
[7 empty] | 6455 | 71 | 4.9905 | 3.6681
[7 empty] | 6456 | 72 | 3.9097 | 2.8206
[7 empty] | 6457 | 73 | 3.1951 | 2.2603
[7 empty] | 6458 | 74 | 2.9696 | 2.0835
[7 empty] | 6459 | 75 | 2.8694 | 2.0049
[7 empty] | 6460 | 76 | 2.8109 | 1.9591
[7 empty] | 6461 | 77 | 2.9863 | 2.0966
[7 empty] | 6462 | 78 | 3.3871 | 2.4109
[7 empty] | 6463 | 79 | 4.4978 | 3.2818
[7 empty] | 6464 | 80 | 4.6732 | 3.4193
[7 empty] | 6465 | 81 | 5.8507 | 4.3426
[7 empty] | 6466 | 82 | 6.9363 | 5.1938
[7 empty] | 6467 | 83 | 7.6712 | 5.77
[7 empty] | 6468 | 84 | 8.9072 | 6.7391
[7 empty] | 6469 | 85 | 8.6066 | 6.5034
[7 empty] | 6470 | 86 | 8.0972 | 6.104
[7 empty] | 6471 | 87 | 8.5398 | 6.451
[7 empty] | 6472 | 88 | 9.1995 | 6.9683
[7 empty] | 6473 | 89 | 10.544 | 8.0225
[7 empty] | 6474 | 90 | 9.9595 | 7.5642
[7 empty] | 6475 | 91 | 10.6442 | 8.1011
[7 empty] | 6476 | 92 | 10.043 | 7.6296
[7 empty] | 6477 | 93 | 7.6378 | 5.7438
[7 empty] | 6478 | 94 | 6.7359 | 5.0366
[7 empty] | 6479 | 95 | 4.882 | 3.583
[7 empty] | 6480 | 96 | 3.8965 | 2.8103
[7 empty] | 6481 | 97 | 3.8464 | 2.7711
[7 empty] | 6482 | 98 | 3.5541 | 2.5419
[7 empty] | 6483 | 99 | 3.4957 | 2.496
[7 empty] | 6484 | 100 | 3.1449 | 2.221
[7 empty] | 6485 | 101 | 3.0865 | 2.1752
[7 empty] | 6486 | 102 | 3.3203 | 2.3585
[7 empty] | 6487 | 103 | 4.0636 | 2.9413
[7 empty] | 6488 | 104 | 4.3141 | 3.1377
[7 empty] | 6489 | 105 | 4.7985 | 3.5175
[7 empty] | 6490 | 106 | 6.2516 | 4.6569
[7 empty] | 6491 | 107 | 6.6023 | 4.9319
[7 empty] | 6492 | 108 | 8.1723 | 6.1629
[7 empty] | 6493 | 109 | 7.5126 | 5.6456
[7 empty] | 6494 | 110 | 7.0616 | 5.292
[7 empty] | 6495 | 111 | 6.9029 | 5.1676
[7 empty] | 6496 | 112 | 6.9698 | 5.22
[7 empty] | 6497 | 113 | 6.6274 | 4.9515
[7 empty] | 6498 | 114 | 6.7944 | 5.0825
[7 empty] | 6499 | 115 | 6.3434 | 4.7289
[7 empty] | 6500 | 116 | 7.0199 | 5.2593
[7 empty] | 6501 | 117 | 6.6023 | 4.9319
[7 empty] | 6502 | 118 | 5.834 | 4.3295
[7 empty] | 6503 | 119 | 4.2473 | 3.0854
[7 empty] | 6504 | 120 | 3.9311 | 2.8374
[7 empty] | 6505 | 121 | 3.2034 | 2.2669
[7 empty] | 6506 | 122 | 2.7942 | 1.946
[7 empty] | 6507 | 123 | 2.7107 | 1.8805
[7 empty] | 6508 | 124 | 2.6773 | 1.8543
[7 empty] | 6509 | 125 | 2.6355 | 1.8216
[7 empty] | 6510 | 126 | 2.7775 | 1.9329
[7 empty] | 6511 | 127 | 4.2807 | 3.1115
[7 empty] | 6512 | 128 | 5.834 | 4.3295
[7 empty] | 6513 | 129 | 6.5104 | 4.8599
[7 empty] | 6514 | 130 | 6.9447 | 5.2003
[7 empty] | 6515 | 131 | 7.1034 | 5.3248
[7 empty] | 6516 | 132 | 6.8528 | 5.1283
[7 empty] | 6517 | 133 | 7.4875 | 5.626
[7 empty] | 6518 | 134 | 7.7882 | 5.8617
[7 empty] | 6519 | 135 | 7.855 | 5.9141
[7 empty] | 6520 | 136 | 7.0449 | 5.2789
[7 empty] | 6521 | 137 | 6.9447 | 5.2003
[7 empty] | 6522 | 138 | 6.8946 | 5.1611
[7 empty] | 6523 | 139 | 6.5605 | 4.8991
[7 empty] | 6524 | 140 | 6.5689 | 4.9057
[7 empty] | 6525 | 141 | 5.9175 | 4.3949
[7 empty] | 6526 | 142 | 5.2828 | 3.8973
[7 empty] | 6527 | 143 | 4.406 | 3.2098
[7 empty] | 6528 | 144 | 3.7963 | 2.7318
[7 empty] | 6529 | 145 | 3.3287 | 2.3651
[7 empty] | 6530 | 146 | 3.1199 | 2.2014
[7 empty] | 6531 | 147 | 3.0531 | 2.149
[7 empty] | 6532 | 148 | 3.0447 | 2.1424
[7 empty] | 6533 | 149 | 3.0447 | 2.1424
[7 empty] | 6534 | 150 | 3.0531 | 2.149
[7 empty] | 6535 | 151 | 4.1304 | 2.9937
[7 empty] | 6536 | 152 | 5.6503 | 4.1854
[7 empty] | 6537 | 153 | 6.2599 | 4.6634
[7 empty] | 6538 | 154 | 6.8194 | 5.1021
[7 empty] | 6539 | 155 | 6.6691 | 4.9843
[7 empty] | 6540 | 156 | 6.8361 | 5.1152
[7 empty] | 6541 | 157 | 7.546 | 5.6718
[7 empty] | 6542 | 158 | 7.8717 | 5.9272
[7 empty] | 6543 | 159 | 8.1389 | 6.1367
[7 empty] | 6544 | 160 | 8.0136 | 6.0385
[7 empty] | 6545 | 161 | 8.7736 | 6.6343
[7 empty] | 6546 | 162 | 8.2809 | 6.248
[7 empty] | 6547 | 163 | 8.64 | 6.5296
[7 empty] | 6548 | 164 | 7.2954 | 5.4754
[7 empty] | 6549 | 165 | 10.4104 | 7.9177
[7 empty] | 6550 | 166 | 8.3727 | 6.32
[7 empty] | 6551 | 167 | 4.7818 | 3.5044
[7 empty] | 6552 | 168 | 4.1387 | 3.0002
[7 empty] | 6553 | 1 | 2.6856 | 1.8609
[7 empty] | 6554 | 2 | 2.5771 | 1.7758
[7 empty] | 6555 | 3 | 2.5687 | 1.7692
[7 empty] | 6556 | 4 | 2.7023 | 1.874
[7 empty] | 6557 | 5 | 2.719 | 1.8871
[7 empty] | 6558 | 6 | 3.1449 | 2.221
[7 empty] | 6559 | 7 | 3.8631 | 2.7841
[7 empty] | 6560 | 8 | 4.5312 | 3.308
[7 empty] | 6561 | 9 | 4.5062 | 3.2883
[7 empty] | 6562 | 10 | 6.0177 | 4.4735
[7 empty] | 6563 | 11 | 8.0888 | 6.0974
[7 empty] | 6564 | 12 | 9.0492 | 6.8504
[7 empty] | 6565 | 13 | 9.425 | 7.1451
[7 empty] | 6566 | 14 | 9.2079 | 6.9748
[7 empty] | 6567 | 15 | 9.116 | 6.9028
[7 empty] | 6568 | 16 | 10.2935 | 7.8261
[7 empty] | 6569 | 17 | 11.613 | 8.8607
[7 empty] | 6570 | 18 | 11.3708 | 8.6708
[7 empty] | 6571 | 19 | 11.8969 | 9.0833
[7 empty] | 6572 | 20 | 11.8301 | 9.0309
[7 empty] | 6573 | 21 | 12.398 | 9.4762
[7 empty] | 6574 | 22 | 8.4563 | 6.3855
[7 empty] | 6575 | 23 | 4.6983 | 3.4389
[7 empty] | 6576 | 24 | 3.0331 | 2.1333
[7 empty] | 6577 | 25 | 2.9362 | 2.0573
[7 empty] | 6578 | 26 | 2.8276 | 1.9722
[7 empty] | 6579 | 27 | 2.7274 | 1.8936
[7 empty] | 6580 | 28 | 2.8109 | 1.9591
[7 empty] | 6581 | 29 | 3.0531 | 2.149
[7 empty] | 6582 | 30 | 3.2953 | 2.3389
[7 empty] | 6583 | 31 | 4.1387 | 3.0002
[7 empty] | 6584 | 32 | 4.4895 | 3.2752
[7 empty] | 6585 | 33 | 5.1492 | 3.7925
[7 empty] | 6586 | 34 | 6.0428 | 4.4932
[7 empty] | 6587 | 35 | 8.2057 | 6.1891
[7 empty] | 6588 | 36 | 9.2329 | 6.9945
[7 empty] | 6589 | 37 | 9.3081 | 7.0534
[7 empty] | 6590 | 38 | 9.3832 | 7.1123
[7 empty] | 6591 | 39 | 9.0575 | 6.857
[7 empty] | 6592 | 40 | 10.1098 | 7.682
[7 empty] | 6593 | 41 | 10.6609 | 8.1142
[7 empty] | 6594 | 42 | 10.6776 | 8.1273
[7 empty] | 6595 | 43 | 11.0451 | 8.4154
[7 empty] | 6596 | 44 | 12.1975 | 9.319
[7 empty] | 6597 | 45 | 11.7967 | 9.0047
[7 empty] | 6598 | 46 | 9.0575 | 6.857
[7 empty] | 6599 | 47 | 5.4666 | 4.0414
[7 empty] | 6600 | 48 | 3.9717 | 2.8693
[7 empty] | 6601 | 49 | 3.312 | 2.352
[7 empty] | 6602 | 50 | 3.003 | 2.1097
[7 empty] | 6603 | 51 | 2.8944 | 2.0246
[7 empty] | 6604 | 52 | 2.9278 | 2.0508
[7 empty] | 6605 | 53 | 2.9529 | 2.0704
[7 empty] | 6606 | 54 | 3.5291 | 2.5222
[7 empty] | 6607 | 55 | 4.6648 | 3.4128
[7 empty] | 6608 | 56 | 4.907 | 3.6026
[7 empty] | 6609 | 57 | 5.8507 | 4.3426
[7 empty] | 6610 | 58 | 6.9531 | 5.2069
[7 empty] | 6611 | 59 | 8.1556 | 6.1498
[7 empty] | 6612 | 60 | 8.7819 | 6.6409
[7 empty] | 6613 | 61 | 9.4584 | 7.1713
[7 empty] | 6614 | 62 | 9.258 | 7.0141
[7 empty] | 6615 | 63 | 9.8509 | 7.479
[7 empty] | 6616 | 64 | 10.7946 | 8.219
[7 empty] | 6617 | 65 | 11.4125 | 8.7035
[7 empty] | 6618 | 66 | 11.3123 | 8.6249
[7 empty] | 6619 | 67 | 12.0472 | 9.2011
[7 empty] | 6620 | 68 | 12.2894 | 9.391
[7 empty] | 6621 | 69 | 11.78 | 8.9916
[7 empty] | 6622 | 70 | 9.4918 | 7.1975
[7 empty] | 6623 | 71 | 4.9905 | 3.6681
[7 empty] | 6624 | 72 | 3.9097 | 2.8206
[7 empty] | 6625 | 73 | 3.1951 | 2.2603
[7 empty] | 6626 | 74 | 2.9696 | 2.0835
[7 empty] | 6627 | 75 | 2.8694 | 2.0049
[7 empty] | 6628 | 76 | 2.8109 | 1.9591
[7 empty] | 6629 | 77 | 2.9863 | 2.0966
[7 empty] | 6630 | 78 | 3.3871 | 2.4109
[7 empty] | 6631 | 79 | 4.4978 | 3.2818
[7 empty] | 6632 | 80 | 4.6732 | 3.4193
[7 empty] | 6633 | 81 | 5.8507 | 4.3426
[7 empty] | 6634 | 82 | 6.9363 | 5.1938
[7 empty] | 6635 | 83 | 7.6712 | 5.77
[7 empty] | 6636 | 84 | 8.9072 | 6.7391
[7 empty] | 6637 | 85 | 8.6066 | 6.5034
[7 empty] | 6638 | 86 | 8.0972 | 6.104
[7 empty] | 6639 | 87 | 8.5398 | 6.451
[7 empty] | 6640 | 88 | 9.1995 | 6.9683
[7 empty] | 6641 | 89 | 10.544 | 8.0225
[7 empty] | 6642 | 90 | 9.9595 | 7.5642
[7 empty] | 6643 | 91 | 10.6442 | 8.1011
[7 empty] | 6644 | 92 | 10.043 | 7.6296
[7 empty] | 6645 | 93 | 7.6378 | 5.7438
[7 empty] | 6646 | 94 | 6.7359 | 5.0366
[7 empty] | 6647 | 95 | 4.882 | 3.583
[7 empty] | 6648 | 96 | 3.8965 | 2.8103
[7 empty] | 6649 | 97 | 3.8464 | 2.7711
[7 empty] | 6650 | 98 | 3.5541 | 2.5419
[7 empty] | 6651 | 99 | 3.4957 | 2.496
[7 empty] | 6652 | 100 | 3.1449 | 2.221
[7 empty] | 6653 | 101 | 3.0865 | 2.1752
[7 empty] | 6654 | 102 | 3.3203 | 2.3585
[7 empty] | 6655 | 103 | 4.0636 | 2.9413
[7 empty] | 6656 | 104 | 4.3141 | 3.1377
[7 empty] | 6657 | 105 | 4.7985 | 3.5175
[7 empty] | 6658 | 106 | 6.2516 | 4.6569
[7 empty] | 6659 | 107 | 6.6023 | 4.9319
[7 empty] | 6660 | 108 | 8.1723 | 6.1629
[7 empty] | 6661 | 109 | 7.5126 | 5.6456
[7 empty] | 6662 | 110 | 7.0616 | 5.292
[7 empty] | 6663 | 111 | 6.9029 | 5.1676
[7 empty] | 6664 | 112 | 6.9698 | 5.22
[7 empty] | 6665 | 113 | 6.6274 | 4.9515
[7 empty] | 6666 | 114 | 6.7944 | 5.0825
[7 empty] | 6667 | 115 | 6.3434 | 4.7289
[7 empty] | 6668 | 116 | 7.0199 | 5.2593
[7 empty] | 6669 | 117 | 6.6023 | 4.9319
[7 empty] | 6670 | 118 | 5.834 | 4.3295
[7 empty] | 6671 | 119 | 4.2473 | 3.0854
[7 empty] | 6672 | 120 | 3.9311 | 2.8374
[7 empty] | 6673 | 121 | 3.2034 | 2.2669
[7 empty] | 6674 | 122 | 2.7942 | 1.946
[7 empty] | 6675 | 123 | 2.7107 | 1.8805
[7 empty] | 6676 | 124 | 2.6773 | 1.8543
[7 empty] | 6677 | 125 | 2.6355 | 1.8216
[7 empty] | 6678 | 126 | 2.7775 | 1.9329
[7 empty] | 6679 | 127 | 4.2807 | 3.1115
[7 empty] | 6680 | 128 | 5.834 | 4.3295
[7 empty] | 6681 | 129 | 6.5104 | 4.8599
[7 empty] | 6682 | 130 | 6.9447 | 5.2003
[7 empty] | 6683 | 131 | 7.1034 | 5.3248
[7 empty] | 6684 | 132 | 6.8528 | 5.1283
[7 empty] | 6685 | 133 | 7.4875 | 5.626
[7 empty] | 6686 | 134 | 7.7882 | 5.8617
[7 empty] | 6687 | 135 | 7.855 | 5.9141
[7 empty] | 6688 | 136 | 7.0449 | 5.2789
[7 empty] | 6689 | 137 | 6.9447 | 5.2003
[7 empty] | 6690 | 138 | 6.8946 | 5.1611
[7 empty] | 6691 | 139 | 6.5605 | 4.8991
[7 empty] | 6692 | 140 | 6.5689 | 4.9057
[7 empty] | 6693 | 141 | 5.9175 | 4.3949
[7 empty] | 6694 | 142 | 5.2828 | 3.8973
[7 empty] | 6695 | 143 | 4.406 | 3.2098
[7 empty] | 6696 | 144 | 3.7963 | 2.7318
[7 empty] | 6697 | 145 | 3.3287 | 2.3651
[7 empty] | 6698 | 146 | 3.1199 | 2.2014
[7 empty] | 6699 | 147 | 3.0531 | 2.149
[7 empty] | 6700 | 148 | 3.0447 | 2.1424
[7 empty] | 6701 | 149 | 3.0447 | 2.1424
[7 empty] | 6702 | 150 | 3.0531 | 2.149
[7 empty] | 6703 | 151 | 4.1304 | 2.9937
[7 empty] | 6704 | 152 | 5.6503 | 4.1854
[7 empty] | 6705 | 153 | 6.2599 | 4.6634
[7 empty] | 6706 | 154 | 6.8194 | 5.1021
[7 empty] | 6707 | 155 | 6.6691 | 4.9843
[7 empty] | 6708 | 156 | 6.8361 | 5.1152
[7 empty] | 6709 | 157 | 7.546 | 5.6718
[7 empty] | 6710 | 158 | 7.8717 | 5.9272
[7 empty] | 6711 | 159 | 8.1389 | 6.1367
[7 empty] | 6712 | 160 | 8.0136 | 6.0385
[7 empty] | 6713 | 161 | 8.7736 | 6.6343
[7 empty] | 6714 | 162 | 8.2809 | 6.248
[7 empty] | 6715 | 163 | 8.64 | 6.5296
[7 empty] | 6716 | 164 | 7.2954 | 5.4754
[7 empty] | 6717 | 165 | 10.4104 | 7.9177
[7 empty] | 6718 | 166 | 8.3727 | 6.32
[7 empty] | 6719 | 167 | 4.7818 | 3.5044
[7 empty] | 6720 | 168 | 4.1387 | 3.0002
[7 empty] | 6721 | 1 | 2.6856 | 1.8609
[7 empty] | 6722 | 2 | 2.5771 | 1.7758
[7 empty] | 6723 | 3 | 2.5687 | 1.7692
[7 empty] | 6724 | 4 | 2.7023 | 1.874
[7 empty] | 6725 | 5 | 2.719 | 1.8871
[7 empty] | 6726 | 6 | 3.1449 | 2.221
[7 empty] | 6727 | 7 | 3.8631 | 2.7841
[7 empty] | 6728 | 8 | 4.5312 | 3.308
[7 empty] | 6729 | 9 | 4.5062 | 3.2883
[7 empty] | 6730 | 10 | 6.0177 | 4.4735
[7 empty] | 6731 | 11 | 8.0888 | 6.0974
[7 empty] | 6732 | 12 | 9.0492 | 6.8504
[7 empty] | 6733 | 13 | 9.425 | 7.1451
[7 empty] | 6734 | 14 | 9.2079 | 6.9748
[7 empty] | 6735 | 15 | 9.116 | 6.9028
[7 empty] | 6736 | 16 | 10.2935 | 7.8261
[7 empty] | 6737 | 17 | 11.613 | 8.8607
[7 empty] | 6738 | 18 | 11.3708 | 8.6708
[7 empty] | 6739 | 19 | 11.8969 | 9.0833
[7 empty] | 6740 | 20 | 11.8301 | 9.0309
[7 empty] | 6741 | 21 | 12.398 | 9.4762
[7 empty] | 6742 | 22 | 8.4563 | 6.3855
[7 empty] | 6743 | 23 | 4.6983 | 3.4389
[7 empty] | 6744 | 24 | 3.0331 | 2.1333
[7 empty] | 6745 | 25 | 2.9362 | 2.0573
[7 empty] | 6746 | 26 | 2.8276 | 1.9722
[7 empty] | 6747 | 27 | 2.7274 | 1.8936
[7 empty] | 6748 | 28 | 2.8109 | 1.9591
[7 empty] | 6749 | 29 | 3.0531 | 2.149
[7 empty] | 6750 | 30 | 3.2953 | 2.3389
[7 empty] | 6751 | 31 | 4.1387 | 3.0002
[7 empty] | 6752 | 32 | 4.4895 | 3.2752
[7 empty] | 6753 | 33 | 5.1492 | 3.7925
[7 empty] | 6754 | 34 | 6.0428 | 4.4932
[7 empty] | 6755 | 35 | 8.2057 | 6.1891
[7 empty] | 6756 | 36 | 9.2329 | 6.9945
[7 empty] | 6757 | 37 | 9.3081 | 7.0534
[7 empty] | 6758 | 38 | 9.3832 | 7.1123
[7 empty] | 6759 | 39 | 9.0575 | 6.857
[7 empty] | 6760 | 40 | 10.1098 | 7.682
[7 empty] | 6761 | 41 | 10.6609 | 8.1142
[7 empty] | 6762 | 42 | 10.6776 | 8.1273
[7 empty] | 6763 | 43 | 11.0451 | 8.4154
[7 empty] | 6764 | 44 | 12.1975 | 9.319
[7 empty] | 6765 | 45 | 11.7967 | 9.0047
[7 empty] | 6766 | 46 | 9.0575 | 6.857
[7 empty] | 6767 | 47 | 5.4666 | 4.0414
[7 empty] | 6768 | 48 | 3.9717 | 2.8693
[7 empty] | 6769 | 49 | 3.312 | 2.352
[7 empty] | 6770 | 50 | 3.003 | 2.1097
[7 empty] | 6771 | 51 | 2.8944 | 2.0246
[7 empty] | 6772 | 52 | 2.9278 | 2.0508
[7 empty] | 6773 | 53 | 2.9529 | 2.0704
[7 empty] | 6774 | 54 | 3.5291 | 2.5222
[7 empty] | 6775 | 55 | 4.6648 | 3.4128
[7 empty] | 6776 | 56 | 4.907 | 3.6026
[7 empty] | 6777 | 57 | 5.8507 | 4.3426
[7 empty] | 6778 | 58 | 6.9531 | 5.2069
[7 empty] | 6779 | 59 | 8.1556 | 6.1498
[7 empty] | 6780 | 60 | 8.7819 | 6.6409
[7 empty] | 6781 | 61 | 9.4584 | 7.1713
[7 empty] | 6782 | 62 | 9.258 | 7.0141
[7 empty] | 6783 | 63 | 9.8509 | 7.479
[7 empty] | 6784 | 64 | 10.7946 | 8.219
[7 empty] | 6785 | 65 | 11.4125 | 8.7035
[7 empty] | 6786 | 66 | 11.3123 | 8.6249
[7 empty] | 6787 | 67 | 12.0472 | 9.2011
[7 empty] | 6788 | 68 | 12.2894 | 9.391
[7 empty] | 6789 | 69 | 11.78 | 8.9916
[7 empty] | 6790 | 70 | 9.4918 | 7.1975
[7 empty] | 6791 | 71 | 4.9905 | 3.6681
[7 empty] | 6792 | 72 | 3.9097 | 2.8206
[7 empty] | 6793 | 73 | 3.1951 | 2.2603
[7 empty] | 6794 | 74 | 2.9696 | 2.0835
[7 empty] | 6795 | 75 | 2.8694 | 2.0049
[7 empty] | 6796 | 76 | 2.8109 | 1.9591
[7 empty] | 6797 | 77 | 2.9863 | 2.0966
[7 empty] | 6798 | 78 | 3.3871 | 2.4109
[7 empty] | 6799 | 79 | 4.4978 | 3.2818
[7 empty] | 6800 | 80 | 4.6732 | 3.4193
[7 empty] | 6801 | 81 | 5.8507 | 4.3426
[7 empty] | 6802 | 82 | 6.9363 | 5.1938
[7 empty] | 6803 | 83 | 7.6712 | 5.77
[7 empty] | 6804 | 84 | 8.9072 | 6.7391
[7 empty] | 6805 | 85 | 8.6066 | 6.5034
[7 empty] | 6806 | 86 | 8.0972 | 6.104
[7 empty] | 6807 | 87 | 8.5398 | 6.451
[7 empty] | 6808 | 88 | 9.1995 | 6.9683
[7 empty] | 6809 | 89 | 10.544 | 8.0225
[7 empty] | 6810 | 90 | 9.9595 | 7.5642
[7 empty] | 6811 | 91 | 10.6442 | 8.1011
[7 empty] | 6812 | 92 | 10.043 | 7.6296
[7 empty] | 6813 | 93 | 7.6378 | 5.7438
[7 empty] | 6814 | 94 | 6.7359 | 5.0366
[7 empty] | 6815 | 95 | 4.882 | 3.583
[7 empty] | 6816 | 96 | 3.8965 | 2.8103
[7 empty] | 6817 | 97 | 3.8464 | 2.7711
[7 empty] | 6818 | 98 | 3.5541 | 2.5419
[7 empty] | 6819 | 99 | 3.4957 | 2.496
[7 empty] | 6820 | 100 | 3.1449 | 2.221
[7 empty] | 6821 | 101 | 3.0865 | 2.1752
[7 empty] | 6822 | 102 | 3.3203 | 2.3585
[7 empty] | 6823 | 103 | 4.0636 | 2.9413
[7 empty] | 6824 | 104 | 4.3141 | 3.1377
[7 empty] | 6825 | 105 | 4.7985 | 3.5175
[7 empty] | 6826 | 106 | 6.2516 | 4.6569
[7 empty] | 6827 | 107 | 6.6023 | 4.9319
[7 empty] | 6828 | 108 | 8.1723 | 6.1629
[7 empty] | 6829 | 109 | 7.5126 | 5.6456
[7 empty] | 6830 | 110 | 7.0616 | 5.292
[7 empty] | 6831 | 111 | 6.9029 | 5.1676
[7 empty] | 6832 | 112 | 6.9698 | 5.22
[7 empty] | 6833 | 113 | 6.6274 | 4.9515
[7 empty] | 6834 | 114 | 6.7944 | 5.0825
[7 empty] | 6835 | 115 | 6.3434 | 4.7289
[7 empty] | 6836 | 116 | 7.0199 | 5.2593
[7 empty] | 6837 | 117 | 6.6023 | 4.9319
[7 empty] | 6838 | 118 | 5.834 | 4.3295
[7 empty] | 6839 | 119 | 4.2473 | 3.0854
[7 empty] | 6840 | 120 | 3.9311 | 2.8374
[7 empty] | 6841 | 121 | 3.2034 | 2.2669
[7 empty] | 6842 | 122 | 2.7942 | 1.946
[7 empty] | 6843 | 123 | 2.7107 | 1.8805
[7 empty] | 6844 | 124 | 2.6773 | 1.8543
[7 empty] | 6845 | 125 | 2.6355 | 1.8216
[7 empty] | 6846 | 126 | 2.7775 | 1.9329
[7 empty] | 6847 | 127 | 4.2807 | 3.1115
[7 empty] | 6848 | 128 | 5.834 | 4.3295
[7 empty] | 6849 | 129 | 6.5104 | 4.8599
[7 empty] | 6850 | 130 | 6.9447 | 5.2003
[7 empty] | 6851 | 131 | 7.1034 | 5.3248
[7 empty] | 6852 | 132 | 6.8528 | 5.1283
[7 empty] | 6853 | 133 | 7.4875 | 5.626
[7 empty] | 6854 | 134 | 7.7882 | 5.8617
[7 empty] | 6855 | 135 | 7.855 | 5.9141
[7 empty] | 6856 | 136 | 7.0449 | 5.2789
[7 empty] | 6857 | 137 | 6.9447 | 5.2003
[7 empty] | 6858 | 138 | 6.8946 | 5.1611
[7 empty] | 6859 | 139 | 6.5605 | 4.8991
[7 empty] | 6860 | 140 | 6.5689 | 4.9057
[7 empty] | 6861 | 141 | 5.9175 | 4.3949
[7 empty] | 6862 | 142 | 5.2828 | 3.8973
[7 empty] | 6863 | 143 | 4.406 | 3.2098
[7 empty] | 6864 | 144 | 3.7963 | 2.7318
[7 empty] | 6865 | 145 | 3.3287 | 2.3651
[7 empty] | 6866 | 146 | 3.1199 | 2.2014
[7 empty] | 6867 | 147 | 3.0531 | 2.149
[7 empty] | 6868 | 148 | 3.0447 | 2.1424
[7 empty] | 6869 | 149 | 3.0447 | 2.1424
[7 empty] | 6870 | 150 | 3.0531 | 2.149
[7 empty] | 6871 | 151 | 4.1304 | 2.9937
[7 empty] | 6872 | 152 | 5.6503 | 4.1854
[7 empty] | 6873 | 153 | 6.2599 | 4.6634
[7 empty] | 6874 | 154 | 6.8194 | 5.1021
[7 empty] | 6875 | 155 | 6.6691 | 4.9843
[7 empty] | 6876 | 156 | 6.8361 | 5.1152
[7 empty] | 6877 | 157 | 7.546 | 5.6718
[7 empty] | 6878 | 158 | 7.8717 | 5.9272
[7 empty] | 6879 | 159 | 8.1389 | 6.1367
[7 empty] | 6880 | 160 | 8.0136 | 6.0385
[7 empty] | 6881 | 161 | 8.7736 | 6.6343
[7 empty] | 6882 | 162 | 8.2809 | 6.248
[7 empty] | 6883 | 163 | 8.64 | 6.5296
[7 empty] | 6884 | 164 | 7.2954 | 5.4754
[7 empty] | 6885 | 165 | 10.4104 | 7.9177
[7 empty] | 6886 | 166 | 8.3727 | 6.32
[7 empty] | 6887 | 167 | 4.7818 | 3.5044
[7 empty] | 6888 | 168 | 4.1387 | 3.0002
[7 empty] | 6889 | 1 | 2.6856 | 1.8609
[7 empty] | 6890 | 2 | 2.5771 | 1.7758
[7 empty] | 6891 | 3 | 2.5687 | 1.7692
[7 empty] | 6892 | 4 | 2.7023 | 1.874
[7 empty] | 6893 | 5 | 2.719 | 1.8871
[7 empty] | 6894 | 6 | 3.1449 | 2.221
[7 empty] | 6895 | 7 | 3.8631 | 2.7841
[7 empty] | 6896 | 8 | 4.5312 | 3.308
[7 empty] | 6897 | 9 | 4.5062 | 3.2883
[7 empty] | 6898 | 10 | 6.0177 | 4.4735
[7 empty] | 6899 | 11 | 8.0888 | 6.0974
[7 empty] | 6900 | 12 | 9.0492 | 6.8504
[7 empty] | 6901 | 13 | 9.425 | 7.1451
[7 empty] | 6902 | 14 | 9.2079 | 6.9748
[7 empty] | 6903 | 15 | 9.116 | 6.9028
[7 empty] | 6904 | 16 | 10.2935 | 7.8261
[7 empty] | 6905 | 17 | 11.613 | 8.8607
[7 empty] | 6906 | 18 | 11.3708 | 8.6708
[7 empty] | 6907 | 19 | 11.8969 | 9.0833
[7 empty] | 6908 | 20 | 11.8301 | 9.0309
[7 empty] | 6909 | 21 | 12.398 | 9.4762
[7 empty] | 6910 | 22 | 8.4563 | 6.3855
[7 empty] | 6911 | 23 | 4.6983 | 3.4389
[7 empty] | 6912 | 24 | 3.0331 | 2.1333
[7 empty] | 6913 | 25 | 2.9362 | 2.0573
[7 empty] | 6914 | 26 | 2.8276 | 1.9722
[7 empty] | 6915 | 27 | 2.7274 | 1.8936
[7 empty] | 6916 | 28 | 2.8109 | 1.9591
[7 empty] | 6917 | 29 | 3.0531 | 2.149
[7 empty] | 6918 | 30 | 3.2953 | 2.3389
[7 empty] | 6919 | 31 | 4.1387 | 3.0002
[7 empty] | 6920 | 32 | 4.4895 | 3.2752
[7 empty] | 6921 | 33 | 5.1492 | 3.7925
[7 empty] | 6922 | 34 | 6.0428 | 4.4932
[7 empty] | 6923 | 35 | 8.2057 | 6.1891
[7 empty] | 6924 | 36 | 9.2329 | 6.9945
[7 empty] | 6925 | 37 | 9.3081 | 7.0534
[7 empty] | 6926 | 38 | 9.3832 | 7.1123
[7 empty] | 6927 | 39 | 9.0575 | 6.857
[7 empty] | 6928 | 40 | 10.1098 | 7.682
[7 empty] | 6929 | 41 | 10.6609 | 8.1142
[7 empty] | 6930 | 42 | 10.6776 | 8.1273
[7 empty] | 6931 | 43 | 11.0451 | 8.4154
[7 empty] | 6932 | 44 | 12.1975 | 9.319
[7 empty] | 6933 | 45 | 11.7967 | 9.0047
[7 empty] | 6934 | 46 | 9.0575 | 6.857
[7 empty] | 6935 | 47 | 5.4666 | 4.0414
[7 empty] | 6936 | 48 | 3.9717 | 2.8693
[7 empty] | 6937 | 49 | 3.312 | 2.352
[7 empty] | 6938 | 50 | 3.003 | 2.1097
[7 empty] | 6939 | 51 | 2.8944 | 2.0246
[7 empty] | 6940 | 52 | 2.9278 | 2.0508
[7 empty] | 6941 | 53 | 2.9529 | 2.0704
[7 empty] | 6942 | 54 | 3.5291 | 2.5222
[7 empty] | 6943 | 55 | 4.6648 | 3.4128
[7 empty] | 6944 | 56 | 4.907 | 3.6026
[7 empty] | 6945 | 57 | 5.8507 | 4.3426
[7 empty] | 6946 | 58 | 6.9531 | 5.2069
[7 empty] | 6947 | 59 | 8.1556 | 6.1498
[7 empty] | 6948 | 60 | 8.7819 | 6.6409
[7 empty] | 6949 | 61 | 9.4584 | 7.1713
[7 empty] | 6950 | 62 | 9.258 | 7.0141
[7 empty] | 6951 | 63 | 9.8509 | 7.479
[7 empty] | 6952 | 64 | 10.7946 | 8.219
[7 empty] | 6953 | 65 | 11.4125 | 8.7035
[7 empty] | 6954 | 66 | 11.3123 | 8.6249
[7 empty] | 6955 | 67 | 12.0472 | 9.2011
[7 empty] | 6956 | 68 | 12.2894 | 9.391
[7 empty] | 6957 | 69 | 11.78 | 8.9916
[7 empty] | 6958 | 70 | 9.4918 | 7.1975
[7 empty] | 6959 | 71 | 4.9905 | 3.6681
[7 empty] | 6960 | 72 | 3.9097 | 2.8206
[7 empty] | 6961 | 73 | 3.1951 | 2.2603
[7 empty] | 6962 | 74 | 2.9696 | 2.0835
[7 empty] | 6963 | 75 | 2.8694 | 2.0049
[7 empty] | 6964 | 76 | 2.8109 | 1.9591
[7 empty] | 6965 | 77 | 2.9863 | 2.0966
[7 empty] | 6966 | 78 | 3.3871 | 2.4109
[7 empty] | 6967 | 79 | 4.4978 | 3.2818
[7 empty] | 6968 | 80 | 4.6732 | 3.4193
[7 empty] | 6969 | 81 | 5.8507 | 4.3426
[7 empty] | 6970 | 82 | 6.9363 | 5.1938
[7 empty] | 6971 | 83 | 7.6712 | 5.77
[7 empty] | 6972 | 84 | 8.9072 | 6.7391
[7 empty] | 6973 | 85 | 8.6066 | 6.5034
[7 empty] | 6974 | 86 | 8.0972 | 6.104
[7 empty] | 6975 | 87 | 8.5398 | 6.451
[7 empty] | 6976 | 88 | 9.1995 | 6.9683
[7 empty] | 6977 | 89 | 10.544 | 8.0225
[7 empty] | 6978 | 90 | 9.9595 | 7.5642
[7 empty] | 6979 | 91 | 10.6442 | 8.1011
[7 empty] | 6980 | 92 | 10.043 | 7.6296
[7 empty] | 6981 | 93 | 7.6378 | 5.7438
[7 empty] | 6982 | 94 | 6.7359 | 5.0366
[7 empty] | 6983 | 95 | 4.882 | 3.583
[7 empty] | 6984 | 96 | 3.8965 | 2.8103
[7 empty] | 6985 | 97 | 3.8464 | 2.7711
[7 empty] | 6986 | 98 | 3.5541 | 2.5419
[7 empty] | 6987 | 99 | 3.4957 | 2.496
[7 empty] | 6988 | 100 | 3.1449 | 2.221
[7 empty] | 6989 | 101 | 3.0865 | 2.1752
[7 empty] | 6990 | 102 | 3.3203 | 2.3585
[7 empty] | 6991 | 103 | 4.0636 | 2.9413
[7 empty] | 6992 | 104 | 4.3141 | 3.1377
[7 empty] | 6993 | 105 | 4.7985 | 3.5175
[7 empty] | 6994 | 106 | 6.2516 | 4.6569
[7 empty] | 6995 | 107 | 6.6023 | 4.9319
[7 empty] | 6996 | 108 | 8.1723 | 6.1629
[7 empty] | 6997 | 109 | 7.5126 | 5.6456
[7 empty] | 6998 | 110 | 7.0616 | 5.292
[7 empty] | 6999 | 111 | 6.9029 | 5.1676
[7 empty] | 7000 | 112 | 6.9698 | 5.22
[7 empty] | 7001 | 113 | 6.6274 | 4.9515
[7 empty] | 7002 | 114 | 6.7944 | 5.0825
[7 empty] | 7003 | 115 | 6.3434 | 4.7289
[7 empty] | 7004 | 116 | 7.0199 | 5.2593
[7 empty] | 7005 | 117 | 6.6023 | 4.9319
[7 empty] | 7006 | 118 | 5.834 | 4.3295
[7 empty] | 7007 | 119 | 4.2473 | 3.0854
[7 empty] | 7008 | 120 | 3.9311 | 2.8374
[7 empty] | 7009 | 121 | 3.2034 | 2.2669
[7 empty] | 7010 | 122 | 2.7942 | 1.946
[7 empty] | 7011 | 123 | 2.7107 | 1.8805
[7 empty] | 7012 | 124 | 2.6773 | 1.8543
[7 empty] | 7013 | 125 | 2.6355 | 1.8216
[7 empty] | 7014 | 126 | 2.7775 | 1.9329
[7 empty] | 7015 | 127 | 4.2807 | 3.1115
[7 empty] | 7016 | 128 | 5.834 | 4.3295
[7 empty] | 7017 | 129 | 6.5104 | 4.8599
[7 empty] | 7018 | 130 | 6.9447 | 5.2003
[7 empty] | 7019 | 131 | 7.1034 | 5.3248
[7 empty] | 7020 | 132 | 6.8528 | 5.1283
[7 empty] | 7021 | 133 | 7.4875 | 5.626
[7 empty] | 7022 | 134 | 7.7882 | 5.8617
[7 empty] | 7023 | 135 | 7.855 | 5.9141
[7 empty] | 7024 | 136 | 7.0449 | 5.2789
[7 empty] | 7025 | 137 | 6.9447 | 5.2003
[7 empty] | 7026 | 138 | 6.8946 | 5.1611
[7 empty] | 7027 | 139 | 6.5605 | 4.8991
[7 empty] | 7028 | 140 | 6.5689 | 4.9057
[7 empty] | 7029 | 141 | 5.9175 | 4.3949
[7 empty] | 7030 | 142 | 5.2828 | 3.8973
[7 empty] | 7031 | 143 | 4.406 | 3.2098
[7 empty] | 7032 | 144 | 3.7963 | 2.7318
[7 empty] | 7033 | 145 | 3.3287 | 2.3651
[7 empty] | 7034 | 146 | 3.1199 | 2.2014
[7 empty] | 7035 | 147 | 3.0531 | 2.149
[7 empty] | 7036 | 148 | 3.0447 | 2.1424
[7 empty] | 7037 | 149 | 3.0447 | 2.1424
[7 empty] | 7038 | 150 | 3.0531 | 2.149
[7 empty] | 7039 | 151 | 4.1304 | 2.9937
[7 empty] | 7040 | 152 | 5.6503 | 4.1854
[7 empty] | 7041 | 153 | 6.2599 | 4.6634
[7 empty] | 7042 | 154 | 6.8194 | 5.1021
[7 empty] | 7043 | 155 | 6.6691 | 4.9843
[7 empty] | 7044 | 156 | 6.8361 | 5.1152
[7 empty] | 7045 | 157 | 7.546 | 5.6718
[7 empty] | 7046 | 158 | 7.8717 | 5.9272
[7 empty] | 7047 | 159 | 8.1389 | 6.1367
[7 empty] | 7048 | 160 | 8.0136 | 6.0385
[7 empty] | 7049 | 161 | 8.7736 | 6.6343
[7 empty] | 7050 | 162 | 8.2809 | 6.248
[7 empty] | 7051 | 163 | 8.64 | 6.5296
[7 empty] | 7052 | 164 | 7.2954 | 5.4754
[7 empty] | 7053 | 165 | 10.4104 | 7.9177
[7 empty] | 7054 | 166 | 8.3727 | 6.32
[7 empty] | 7055 | 167 | 4.7818 | 3.5044
[7 empty] | 7056 | 168 | 4.1387 | 3.0002
[7 empty] | 7057 | 1 | 2.6856 | 1.8609
[7 empty] | 7058 | 2 | 2.5771 | 1.7758
[7 empty] | 7059 | 3 | 2.5687 | 1.7692
[7 empty] | 7060 | 4 | 2.7023 | 1.874
[7 empty] | 7061 | 5 | 2.719 | 1.8871
[7 empty] | 7062 | 6 | 3.1449 | 2.221
[7 empty] | 7063 | 7 | 3.8631 | 2.7841
[7 empty] | 7064 | 8 | 4.5312 | 3.308
[7 empty] | 7065 | 9 | 4.5062 | 3.2883
[7 empty] | 7066 | 10 | 6.0177 | 4.4735
[7 empty] | 7067 | 11 | 8.0888 | 6.0974
[7 empty] | 7068 | 12 | 9.0492 | 6.8504
[7 empty] | 7069 | 13 | 9.425 | 7.1451
[7 empty] | 7070 | 14 | 9.2079 | 6.9748
[7 empty] | 7071 | 15 | 9.116 | 6.9028
[7 empty] | 7072 | 16 | 10.2935 | 7.8261
[7 empty] | 7073 | 17 | 11.613 | 8.8607
[7 empty] | 7074 | 18 | 11.3708 | 8.6708
[7 empty] | 7075 | 19 | 11.8969 | 9.0833
[7 empty] | 7076 | 20 | 11.8301 | 9.0309
[7 empty] | 7077 | 21 | 12.398 | 9.4762
[7 empty] | 7078 | 22 | 8.4563 | 6.3855
[7 empty] | 7079 | 23 | 4.6983 | 3.4389
[7 empty] | 7080 | 24 | 3.0331 | 2.1333
[7 empty] | 7081 | 25 | 2.9362 | 2.0573
[7 empty] | 7082 | 26 | 2.8276 | 1.9722
[7 empty] | 7083 | 27 | 2.7274 | 1.8936
[7 empty] | 7084 | 28 | 2.8109 | 1.9591
[7 empty] | 7085 | 29 | 3.0531 | 2.149
[7 empty] | 7086 | 30 | 3.2953 | 2.3389
[7 empty] | 7087 | 31 | 4.1387 | 3.0002
[7 empty] | 7088 | 32 | 4.4895 | 3.2752
[7 empty] | 7089 | 33 | 5.1492 | 3.7925
[7 empty] | 7090 | 34 | 6.0428 | 4.4932
[7 empty] | 7091 | 35 | 8.2057 | 6.1891
[7 empty] | 7092 | 36 | 9.2329 | 6.9945
[7 empty] | 7093 | 37 | 9.3081 | 7.0534
[7 empty] | 7094 | 38 | 9.3832 | 7.1123
[7 empty] | 7095 | 39 | 9.0575 | 6.857
[7 empty] | 7096 | 40 | 10.1098 | 7.682
[7 empty] | 7097 | 41 | 10.6609 | 8.1142
[7 empty] | 7098 | 42 | 10.6776 | 8.1273
[7 empty] | 7099 | 43 | 11.0451 | 8.4154
[7 empty] | 7100 | 44 | 12.1975 | 9.319
[7 empty] | 7101 | 45 | 11.7967 | 9.0047
[7 empty] | 7102 | 46 | 9.0575 | 6.857
[7 empty] | 7103 | 47 | 5.4666 | 4.0414
[7 empty] | 7104 | 48 | 3.9717 | 2.8693
[7 empty] | 7105 | 49 | 3.312 | 2.352
[7 empty] | 7106 | 50 | 3.003 | 2.1097
[7 empty] | 7107 | 51 | 2.8944 | 2.0246
[7 empty] | 7108 | 52 | 2.9278 | 2.0508
[7 empty] | 7109 | 53 | 2.9529 | 2.0704
[7 empty] | 7110 | 54 | 3.5291 | 2.5222
[7 empty] | 7111 | 55 | 4.6648 | 3.4128
[7 empty] | 7112 | 56 | 4.907 | 3.6026
[7 empty] | 7113 | 57 | 5.8507 | 4.3426
[7 empty] | 7114 | 58 | 6.9531 | 5.2069
[7 empty] | 7115 | 59 | 8.1556 | 6.1498
[7 empty] | 7116 | 60 | 8.7819 | 6.6409
[7 empty] | 7117 | 61 | 9.4584 | 7.1713
[7 empty] | 7118 | 62 | 9.258 | 7.0141
[7 empty] | 7119 | 63 | 9.8509 | 7.479
[7 empty] | 7120 | 64 | 10.7946 | 8.219
[7 empty] | 7121 | 65 | 11.4125 | 8.7035
[7 empty] | 7122 | 66 | 11.3123 | 8.6249
[7 empty] | 7123 | 67 | 12.0472 | 9.2011
[7 empty] | 7124 | 68 | 12.2894 | 9.391
[7 empty] | 7125 | 69 | 11.78 | 8.9916
[7 empty] | 7126 | 70 | 9.4918 | 7.1975
[7 empty] | 7127 | 71 | 4.9905 | 3.6681
[7 empty] | 7128 | 72 | 3.9097 | 2.8206
[7 empty] | 7129 | 73 | 3.1951 | 2.2603
[7 empty] | 7130 | 74 | 2.9696 | 2.0835
[7 empty] | 7131 | 75 | 2.8694 | 2.0049
[7 empty] | 7132 | 76 | 2.8109 | 1.9591
[7 empty] | 7133 | 77 | 2.9863 | 2.0966
[7 empty] | 7134 | 78 | 3.3871 | 2.4109
[7 empty] | 7135 | 79 | 4.4978 | 3.2818
[7 empty] | 7136 | 80 | 4.6732 | 3.4193
[7 empty] | 7137 | 81 | 5.8507 | 4.3426
[7 empty] | 7138 | 82 | 6.9363 | 5.1938
[7 empty] | 7139 | 83 | 7.6712 | 5.77
[7 empty] | 7140 | 84 | 8.9072 | 6.7391
[7 empty] | 7141 | 85 | 8.6066 | 6.5034
[7 empty] | 7142 | 86 | 8.0972 | 6.104
[7 empty] | 7143 | 87 | 8.5398 | 6.451
[7 empty] | 7144 | 88 | 9.1995 | 6.9683
[7 empty] | 7145 | 89 | 10.544 | 8.0225
[7 empty] | 7146 | 90 | 9.9595 | 7.5642
[7 empty] | 7147 | 91 | 10.6442 | 8.1011
[7 empty] | 7148 | 92 | 10.043 | 7.6296
[7 empty] | 7149 | 93 | 7.6378 | 5.7438
[7 empty] | 7150 | 94 | 6.7359 | 5.0366
[7 empty] | 7151 | 95 | 4.882 | 3.583
[7 empty] | 7152 | 96 | 3.8965 | 2.8103
[7 empty] | 7153 | 97 | 3.8464 | 2.7711
[7 empty] | 7154 | 98 | 3.5541 | 2.5419
[7 empty] | 7155 | 99 | 3.4957 | 2.496
[7 empty] | 7156 | 100 | 3.1449 | 2.221
[7 empty] | 7157 | 101 | 3.0865 | 2.1752
[7 empty] | 7158 | 102 | 3.3203 | 2.3585
[7 empty] | 7159 | 103 | 4.0636 | 2.9413
[7 empty] | 7160 | 104 | 4.3141 | 3.1377
[7 empty] | 7161 | 105 | 4.7985 | 3.5175
[7 empty] | 7162 | 106 | 6.2516 | 4.6569
[7 empty] | 7163 | 107 | 6.6023 | 4.9319
[7 empty] | 7164 | 108 | 8.1723 | 6.1629
[7 empty] | 7165 | 109 | 7.5126 | 5.6456
[7 empty] | 7166 | 110 | 7.0616 | 5.292
[7 empty] | 7167 | 111 | 6.9029 | 5.1676
[7 empty] | 7168 | 112 | 6.9698 | 5.22
[7 empty] | 7169 | 113 | 6.6274 | 4.9515
[7 empty] | 7170 | 114 | 6.7944 | 5.0825
[7 empty] | 7171 | 115 | 6.3434 | 4.7289
[7 empty] | 7172 | 116 | 7.0199 | 5.2593
[7 empty] | 7173 | 117 | 6.6023 | 4.9319
[7 empty] | 7174 | 118 | 5.834 | 4.3295
[7 empty] | 7175 | 119 | 4.2473 | 3.0854
[7 empty] | 7176 | 120 | 3.9311 | 2.8374
[7 empty] | 7177 | 121 | 3.2034 | 2.2669
[7 empty] | 7178 | 122 | 2.7942 | 1.946
[7 empty] | 7179 | 123 | 2.7107 | 1.8805
[7 empty] | 7180 | 124 | 2.6773 | 1.8543
[7 empty] | 7181 | 125 | 2.6355 | 1.8216
[7 empty] | 7182 | 126 | 2.7775 | 1.9329
[7 empty] | 7183 | 127 | 4.2807 | 3.1115
[7 empty] | 7184 | 128 | 5.834 | 4.3295
[7 empty] | 7185 | 129 | 6.5104 | 4.8599
[7 empty] | 7186 | 130 | 6.9447 | 5.2003
[7 empty] | 7187 | 131 | 7.1034 | 5.3248
[7 empty] | 7188 | 132 | 6.8528 | 5.1283
[7 empty] | 7189 | 133 | 7.4875 | 5.626
[7 empty] | 7190 | 134 | 7.7882 | 5.8617
[7 empty] | 7191 | 135 | 7.855 | 5.9141
[7 empty] | 7192 | 136 | 7.0449 | 5.2789
[7 empty] | 7193 | 137 | 6.9447 | 5.2003
[7 empty] | 7194 | 138 | 6.8946 | 5.1611
[7 empty] | 7195 | 139 | 6.5605 | 4.8991
[7 empty] | 7196 | 140 | 6.5689 | 4.9057
[7 empty] | 7197 | 141 | 5.9175 | 4.3949
[7 empty] | 7198 | 142 | 5.2828 | 3.8973
[7 empty] | 7199 | 143 | 4.406 | 3.2098
[7 empty] | 7200 | 144 | 3.7963 | 2.7318
[7 empty] | 7201 | 145 | 3.3287 | 2.3651
[7 empty] | 7202 | 146 | 3.1199 | 2.2014
[7 empty] | 7203 | 147 | 3.0531 | 2.149
[7 empty] | 7204 | 148 | 3.0447 | 2.1424
[7 empty] | 7205 | 149 | 3.0447 | 2.1424
[7 empty] | 7206 | 150 | 3.0531 | 2.149
[7 empty] | 7207 | 151 | 4.1304 | 2.9937
[7 empty] | 7208 | 152 | 5.6503 | 4.1854
[7 empty] | 7209 | 153 | 6.2599 | 4.6634
[7 empty] | 7210 | 154 | 6.8194 | 5.1021
[7 empty] | 7211 | 155 | 6.6691 | 4.9843
[7 empty] | 7212 | 156 | 6.8361 | 5.1152
[7 empty] | 7213 | 157 | 7.546 | 5.6718
[7 empty] | 7214 | 158 | 7.8717 | 5.9272
[7 empty] | 7215 | 159 | 8.1389 | 6.1367
[7 empty] | 7216 | 160 | 8.0136 | 6.0385
[7 empty] | 7217 | 161 | 8.7736 | 6.6343
[7 empty] | 7218 | 162 | 8.2809 | 6.248
[7 empty] | 7219 | 163 | 8.64 | 6.5296
[7 empty] | 7220 | 164 | 7.2954 | 5.4754
[7 empty] | 7221 | 165 | 10.4104 | 7.9177
[7 empty] | 7222 | 166 | 8.3727 | 6.32
[7 empty] | 7223 | 167 | 4.7818 | 3.5044
[7 empty] | 7224 | 168 | 4.1387 | 3.0002
[7 empty] | 7225 | 1 | 2.6856 | 1.8609
[7 empty] | 7226 | 2 | 2.5771 | 1.7758
[7 empty] | 7227 | 3 | 2.5687 | 1.7692
[7 empty] | 7228 | 4 | 2.7023 | 1.874
[7 empty] | 7229 | 5 | 2.719 | 1.8871
[7 empty] | 7230 | 6 | 3.1449 | 2.221
[7 empty] | 7231 | 7 | 3.8631 | 2.7841
[7 empty] | 7232 | 8 | 4.5312 | 3.308
[7 empty] | 7233 | 9 | 4.5062 | 3.2883
[7 empty] | 7234 | 10 | 6.0177 | 4.4735
[7 empty] | 7235 | 11 | 8.0888 | 6.0974
[7 empty] | 7236 | 12 | 9.0492 | 6.8504
[7 empty] | 7237 | 13 | 9.425 | 7.1451
[7 empty] | 7238 | 14 | 9.2079 | 6.9748
[7 empty] | 7239 | 15 | 9.116 | 6.9028
[7 empty] | 7240 | 16 | 10.2935 | 7.8261
[7 empty] | 7241 | 17 | 11.613 | 8.8607
[7 empty] | 7242 | 18 | 11.3708 | 8.6708
[7 empty] | 7243 | 19 | 11.8969 | 9.0833
[7 empty] | 7244 | 20 | 11.8301 | 9.0309
[7 empty] | 7245 | 21 | 12.398 | 9.4762
[7 empty] | 7246 | 22 | 8.4563 | 6.3855
[7 empty] | 7247 | 23 | 4.6983 | 3.4389
[7 empty] | 7248 | 24 | 3.0331 | 2.1333
[7 empty] | 7249 | 25 | 2.9362 | 2.0573
[7 empty] | 7250 | 26 | 2.8276 | 1.9722
[7 empty] | 7251 | 27 | 2.7274 | 1.8936
[7 empty] | 7252 | 28 | 2.8109 | 1.9591
[7 empty] | 7253 | 29 | 3.0531 | 2.149
[7 empty] | 7254 | 30 | 3.2953 | 2.3389
[7 empty] | 7255 | 31 | 4.1387 | 3.0002
[7 empty] | 7256 | 32 | 4.4895 | 3.2752
[7 empty] | 7257 | 33 | 5.1492 | 3.7925
[7 empty] | 7258 | 34 | 6.0428 | 4.4932
[7 empty] | 7259 | 35 | 8.2057 | 6.1891
[7 empty] | 7260 | 36 | 9.2329 | 6.9945
[7 empty] | 7261 | 37 | 9.3081 | 7.0534
[7 empty] | 7262 | 38 | 9.3832 | 7.1123
[7 empty] | 7263 | 39 | 9.0575 | 6.857
[7 empty] | 7264 | 40 | 10.1098 | 7.682
[7 empty] | 7265 | 41 | 10.6609 | 8.1142
[7 empty] | 7266 | 42 | 10.6776 | 8.1273
[7 empty] | 7267 | 43 | 11.0451 | 8.4154
[7 empty] | 7268 | 44 | 12.1975 | 9.319
[7 empty] | 7269 | 45 | 11.7967 | 9.0047
[7 empty] | 7270 | 46 | 9.0575 | 6.857
[7 empty] | 7271 | 47 | 5.4666 | 4.0414
[7 empty] | 7272 | 48 | 3.9717 | 2.8693
[7 empty] | 7273 | 49 | 3.312 | 2.352
[7 empty] | 7274 | 50 | 3.003 | 2.1097
[7 empty] | 7275 | 51 | 2.8944 | 2.0246
[7 empty] | 7276 | 52 | 2.9278 | 2.0508
[7 empty] | 7277 | 53 | 2.9529 | 2.0704
[7 empty] | 7278 | 54 | 3.5291 | 2.5222
[7 empty] | 7279 | 55 | 4.6648 | 3.4128
[7 empty] | 7280 | 56 | 4.907 | 3.6026
[7 empty] | 7281 | 57 | 5.8507 | 4.3426
[7 empty] | 7282 | 58 | 6.9531 | 5.2069
[7 empty] | 7283 | 59 | 8.1556 | 6.1498
[7 empty] | 7284 | 60 | 8.7819 | 6.6409
[7 empty] | 7285 | 61 | 9.4584 | 7.1713
[7 empty] | 7286 | 62 | 9.258 | 7.0141
[7 empty] | 7287 | 63 | 9.8509 | 7.479
[7 empty] | 7288 | 64 | 10.7946 | 8.219
[7 empty] | 7289 | 65 | 11.4125 | 8.7035
[7 empty] | 7290 | 66 | 11.3123 | 8.6249
[7 empty] | 7291 | 67 | 12.0472 | 9.2011
[7 empty] | 7292 | 68 | 12.2894 | 9.391
[7 empty] | 7293 | 69 | 11.78 | 8.9916
[7 empty] | 7294 | 70 | 9.4918 | 7.1975
[7 empty] | 7295 | 71 | 4.9905 | 3.6681
[7 empty] | 7296 | 72 | 3.9097 | 2.8206
[7 empty] | 7297 | 73 | 3.1951 | 2.2603
[7 empty] | 7298 | 74 | 2.9696 | 2.0835
[7 empty] | 7299 | 75 | 2.8694 | 2.0049
[7 empty] | 7300 | 76 | 2.8109 | 1.9591
[7 empty] | 7301 | 77 | 2.9863 | 2.0966
[7 empty] | 7302 | 78 | 3.3871 | 2.4109
[7 empty] | 7303 | 79 | 4.4978 | 3.2818
[7 empty] | 7304 | 80 | 4.6732 | 3.4193
[7 empty] | 7305 | 81 | 5.8507 | 4.3426
[7 empty] | 7306 | 82 | 6.9363 | 5.1938
[7 empty] | 7307 | 83 | 7.6712 | 5.77
[7 empty] | 7308 | 84 | 8.9072 | 6.7391
[7 empty] | 7309 | 85 | 8.6066 | 6.5034
[7 empty] | 7310 | 86 | 8.0972 | 6.104
[7 empty] | 7311 | 87 | 8.5398 | 6.451
[7 empty] | 7312 | 88 | 9.1995 | 6.9683
[7 empty] | 7313 | 89 | 10.544 | 8.0225
[7 empty] | 7314 | 90 | 9.9595 | 7.5642
[7 empty] | 7315 | 91 | 10.6442 | 8.1011
[7 empty] | 7316 | 92 | 10.043 | 7.6296
[7 empty] | 7317 | 93 | 7.6378 | 5.7438
[7 empty] | 7318 | 94 | 6.7359 | 5.0366
[7 empty] | 7319 | 95 | 4.882 | 3.583
[7 empty] | 7320 | 96 | 3.8965 | 2.8103
[7 empty] | 7321 | 97 | 3.8464 | 2.7711
[7 empty] | 7322 | 98 | 3.5541 | 2.5419
[7 empty] | 7323 | 99 | 3.4957 | 2.496
[7 empty] | 7324 | 100 | 3.1449 | 2.221
[7 empty] | 7325 | 101 | 3.0865 | 2.1752
[7 empty] | 7326 | 102 | 3.3203 | 2.3585
[7 empty] | 7327 | 103 | 4.0636 | 2.9413
[7 empty] | 7328 | 104 | 4.3141 | 3.1377
[7 empty] | 7329 | 105 | 4.7985 | 3.5175
[7 empty] | 7330 | 106 | 6.2516 | 4.6569
[7 empty] | 7331 | 107 | 6.6023 | 4.9319
[7 empty] | 7332 | 108 | 8.1723 | 6.1629
[7 empty] | 7333 | 109 | 7.5126 | 5.6456
[7 empty] | 7334 | 110 | 7.0616 | 5.292
[7 empty] | 7335 | 111 | 6.9029 | 5.1676
[7 empty] | 7336 | 112 | 6.9698 | 5.22
[7 empty] | 7337 | 113 | 6.6274 | 4.9515
[7 empty] | 7338 | 114 | 6.7944 | 5.0825
[7 empty] | 7339 | 115 | 6.3434 | 4.7289
[7 empty] | 7340 | 116 | 7.0199 | 5.2593
[7 empty] | 7341 | 117 | 6.6023 | 4.9319
[7 empty] | 7342 | 118 | 5.834 | 4.3295
[7 empty] | 7343 | 119 | 4.2473 | 3.0854
[7 empty] | 7344 | 120 | 3.9311 | 2.8374
[7 empty] | 7345 | 121 | 3.2034 | 2.2669
[7 empty] | 7346 | 122 | 2.7942 | 1.946
[7 empty] | 7347 | 123 | 2.7107 | 1.8805
[7 empty] | 7348 | 124 | 2.6773 | 1.8543
[7 empty] | 7349 | 125 | 2.6355 | 1.8216
[7 empty] | 7350 | 126 | 2.7775 | 1.9329
[7 empty] | 7351 | 127 | 4.2807 | 3.1115
[7 empty] | 7352 | 128 | 5.834 | 4.3295
[7 empty] | 7353 | 129 | 6.5104 | 4.8599
[7 empty] | 7354 | 130 | 6.9447 | 5.2003
[7 empty] | 7355 | 131 | 7.1034 | 5.3248
[7 empty] | 7356 | 132 | 6.8528 | 5.1283
[7 empty] | 7357 | 133 | 7.4875 | 5.626
[7 empty] | 7358 | 134 | 7.7882 | 5.8617
[7 empty] | 7359 | 135 | 7.855 | 5.9141
[7 empty] | 7360 | 136 | 7.0449 | 5.2789
[7 empty] | 7361 | 137 | 6.9447 | 5.2003
[7 empty] | 7362 | 138 | 6.8946 | 5.1611
[7 empty] | 7363 | 139 | 6.5605 | 4.8991
[7 empty] | 7364 | 140 | 6.5689 | 4.9057
[7 empty] | 7365 | 141 | 5.9175 | 4.3949
[7 empty] | 7366 | 142 | 5.2828 | 3.8973
[7 empty] | 7367 | 143 | 4.406 | 3.2098
[7 empty] | 7368 | 144 | 3.7963 | 2.7318
[7 empty] | 7369 | 145 | 3.3287 | 2.3651
[7 empty] | 7370 | 146 | 3.1199 | 2.2014
[7 empty] | 7371 | 147 | 3.0531 | 2.149
[7 empty] | 7372 | 148 | 3.0447 | 2.1424
[7 empty] | 7373 | 149 | 3.0447 | 2.1424
[7 empty] | 7374 | 150 | 3.0531 | 2.149
[7 empty] | 7375 | 151 | 4.1304 | 2.9937
[7 empty] | 7376 | 152 | 5.6503 | 4.1854
[7 empty] | 7377 | 153 | 6.2599 | 4.6634
[7 empty] | 7378 | 154 | 6.8194 | 5.1021
[7 empty] | 7379 | 155 | 6.6691 | 4.9843
[7 empty] | 7380 | 156 | 6.8361 | 5.1152
[7 empty] | 7381 | 157 | 7.546 | 5.6718
[7 empty] | 7382 | 158 | 7.8717 | 5.9272
[7 empty] | 7383 | 159 | 8.1389 | 6.1367
[7 empty] | 7384 | 160 | 8.0136 | 6.0385
[7 empty] | 7385 | 161 | 8.7736 | 6.6343
[7 empty] | 7386 | 162 | 8.2809 | 6.248
[7 empty] | 7387 | 163 | 8.64 | 6.5296
[7 empty] | 7388 | 164 | 7.2954 | 5.4754
[7 empty] | 7389 | 165 | 10.4104 | 7.9177
[7 empty] | 7390 | 166 | 8.3727 | 6.32
[7 empty] | 7391 | 167 | 4.7818 | 3.5044
[7 empty] | 7392 | 168 | 4.1387 | 3.0002
[7 empty] | 7393 | 1 | 2.6856 | 1.8609
[7 empty] | 7394 | 2 | 2.5771 | 1.7758
[7 empty] | 7395 | 3 | 2.5687 | 1.7692
[7 empty] | 7396 | 4 | 2.7023 | 1.874
[7 empty] | 7397 | 5 | 2.719 | 1.8871
[7 empty] | 7398 | 6 | 3.1449 | 2.221
[7 empty] | 7399 | 7 | 3.8631 | 2.7841
[7 empty] | 7400 | 8 | 4.5312 | 3.308
[7 empty] | 7401 | 9 | 4.5062 | 3.2883
[7 empty] | 7402 | 10 | 6.0177 | 4.4735
[7 empty] | 7403 | 11 | 8.0888 | 6.0974
[7 empty] | 7404 | 12 | 9.0492 | 6.8504
[7 empty] | 7405 | 13 | 9.425 | 7.1451
[7 empty] | 7406 | 14 | 9.2079 | 6.9748
[7 empty] | 7407 | 15 | 9.116 | 6.9028
[7 empty] | 7408 | 16 | 10.2935 | 7.8261
[7 empty] | 7409 | 17 | 11.613 | 8.8607
[7 empty] | 7410 | 18 | 11.3708 | 8.6708
[7 empty] | 7411 | 19 | 11.8969 | 9.0833
[7 empty] | 7412 | 20 | 11.8301 | 9.0309
[7 empty] | 7413 | 21 | 12.398 | 9.4762
[7 empty] | 7414 | 22 | 8.4563 | 6.3855
[7 empty] | 7415 | 23 | 4.6983 | 3.4389
[7 empty] | 7416 | 24 | 3.0331 | 2.1333
[7 empty] | 7417 | 25 | 2.9362 | 2.0573
[7 empty] | 7418 | 26 | 2.8276 | 1.9722
[7 empty] | 7419 | 27 | 2.7274 | 1.8936
[7 empty] | 7420 | 28 | 2.8109 | 1.9591
[7 empty] | 7421 | 29 | 3.0531 | 2.149
[7 empty] | 7422 | 30 | 3.2953 | 2.3389
[7 empty] | 7423 | 31 | 4.1387 | 3.0002
[7 empty] | 7424 | 32 | 4.4895 | 3.2752
[7 empty] | 7425 | 33 | 5.1492 | 3.7925
[7 empty] | 7426 | 34 | 6.0428 | 4.4932
[7 empty] | 7427 | 35 | 8.2057 | 6.1891
[7 empty] | 7428 | 36 | 9.2329 | 6.9945
[7 empty] | 7429 | 37 | 9.3081 | 7.0534
[7 empty] | 7430 | 38 | 9.3832 | 7.1123
[7 empty] | 7431 | 39 | 9.0575 | 6.857
[7 empty] | 7432 | 40 | 10.1098 | 7.682
[7 empty] | 7433 | 41 | 10.6609 | 8.1142
[7 empty] | 7434 | 42 | 10.6776 | 8.1273
[7 empty] | 7435 | 43 | 11.0451 | 8.4154
[7 empty] | 7436 | 44 | 12.1975 | 9.319
[7 empty] | 7437 | 45 | 11.7967 | 9.0047
[7 empty] | 7438 | 46 | 9.0575 | 6.857
[7 empty] | 7439 | 47 | 5.4666 | 4.0414
[7 empty] | 7440 | 48 | 3.9717 | 2.8693
[7 empty] | 7441 | 49 | 3.312 | 2.352
[7 empty] | 7442 | 50 | 3.003 | 2.1097
[7 empty] | 7443 | 51 | 2.8944 | 2.0246
[7 empty] | 7444 | 52 | 2.9278 | 2.0508
[7 empty] | 7445 | 53 | 2.9529 | 2.0704
[7 empty] | 7446 | 54 | 3.5291 | 2.5222
[7 empty] | 7447 | 55 | 4.6648 | 3.4128
[7 empty] | 7448 | 56 | 4.907 | 3.6026
[7 empty] | 7449 | 57 | 5.8507 | 4.3426
[7 empty] | 7450 | 58 | 6.9531 | 5.2069
[7 empty] | 7451 | 59 | 8.1556 | 6.1498
[7 empty] | 7452 | 60 | 8.7819 | 6.6409
[7 empty] | 7453 | 61 | 9.4584 | 7.1713
[7 empty] | 7454 | 62 | 9.258 | 7.0141
[7 empty] | 7455 | 63 | 9.8509 | 7.479
[7 empty] | 7456 | 64 | 10.7946 | 8.219
[7 empty] | 7457 | 65 | 11.4125 | 8.7035
[7 empty] | 7458 | 66 | 11.3123 | 8.6249
[7 empty] | 7459 | 67 | 12.0472 | 9.2011
[7 empty] | 7460 | 68 | 12.2894 | 9.391
[7 empty] | 7461 | 69 | 11.78 | 8.9916
[7 empty] | 7462 | 70 | 9.4918 | 7.1975
[7 empty] | 7463 | 71 | 4.9905 | 3.6681
[7 empty] | 7464 | 72 | 3.9097 | 2.8206
[7 empty] | 7465 | 73 | 3.1951 | 2.2603
[7 empty] | 7466 | 74 | 2.9696 | 2.0835
[7 empty] | 7467 | 75 | 2.8694 | 2.0049
[7 empty] | 7468 | 76 | 2.8109 | 1.9591
[7 empty] | 7469 | 77 | 2.9863 | 2.0966
[7 empty] | 7470 | 78 | 3.3871 | 2.4109
[7 empty] | 7471 | 79 | 4.4978 | 3.2818
[7 empty] | 7472 | 80 | 4.6732 | 3.4193
[7 empty] | 7473 | 81 | 5.8507 | 4.3426
[7 empty] | 7474 | 82 | 6.9363 | 5.1938
[7 empty] | 7475 | 83 | 7.6712 | 5.77
[7 empty] | 7476 | 84 | 8.9072 | 6.7391
[7 empty] | 7477 | 85 | 8.6066 | 6.5034
[7 empty] | 7478 | 86 | 8.0972 | 6.104
[7 empty] | 7479 | 87 | 8.5398 | 6.451
[7 empty] | 7480 | 88 | 9.1995 | 6.9683
[7 empty] | 7481 | 89 | 10.544 | 8.0225
[7 empty] | 7482 | 90 | 9.9595 | 7.5642
[7 empty] | 7483 | 91 | 10.6442 | 8.1011
[7 empty] | 7484 | 92 | 10.043 | 7.6296
[7 empty] | 7485 | 93 | 7.6378 | 5.7438
[7 empty] | 7486 | 94 | 6.7359 | 5.0366
[7 empty] | 7487 | 95 | 4.882 | 3.583
[7 empty] | 7488 | 96 | 3.8965 | 2.8103
[7 empty] | 7489 | 97 | 3.8464 | 2.7711
[7 empty] | 7490 | 98 | 3.5541 | 2.5419
[7 empty] | 7491 | 99 | 3.4957 | 2.496
[7 empty] | 7492 | 100 | 3.1449 | 2.221
[7 empty] | 7493 | 101 | 3.0865 | 2.1752
[7 empty] | 7494 | 102 | 3.3203 | 2.3585
[7 empty] | 7495 | 103 | 4.0636 | 2.9413
[7 empty] | 7496 | 104 | 4.3141 | 3.1377
[7 empty] | 7497 | 105 | 4.7985 | 3.5175
[7 empty] | 7498 | 106 | 6.2516 | 4.6569
[7 empty] | 7499 | 107 | 6.6023 | 4.9319
[7 empty] | 7500 | 108 | 8.1723 | 6.1629
[7 empty] | 7501 | 109 | 7.5126 | 5.6456
[7 empty] | 7502 | 110 | 7.0616 | 5.292
[7 empty] | 7503 | 111 | 6.9029 | 5.1676
[7 empty] | 7504 | 112 | 6.9698 | 5.22
[7 empty] | 7505 | 113 | 6.6274 | 4.9515
[7 empty] | 7506 | 114 | 6.7944 | 5.0825
[7 empty] | 7507 | 115 | 6.3434 | 4.7289
[7 empty] | 7508 | 116 | 7.0199 | 5.2593
[7 empty] | 7509 | 117 | 6.6023 | 4.9319
[7 empty] | 7510 | 118 | 5.834 | 4.3295
[7 empty] | 7511 | 119 | 4.2473 | 3.0854
[7 empty] | 7512 | 120 | 3.9311 | 2.8374
[7 empty] | 7513 | 121 | 3.2034 | 2.2669
[7 empty] | 7514 | 122 | 2.7942 | 1.946
[7 empty] | 7515 | 123 | 2.7107 | 1.8805
[7 empty] | 7516 | 124 | 2.6773 | 1.8543
[7 empty] | 7517 | 125 | 2.6355 | 1.8216
[7 empty] | 7518 | 126 | 2.7775 | 1.9329
[7 empty] | 7519 | 127 | 4.2807 | 3.1115
[7 empty] | 7520 | 128 | 5.834 | 4.3295
[7 empty] | 7521 | 129 | 6.5104 | 4.8599
[7 empty] | 7522 | 130 | 6.9447 | 5.2003
[7 empty] | 7523 | 131 | 7.1034 | 5.3248
[7 empty] | 7524 | 132 | 6.8528 | 5.1283
[7 empty] | 7525 | 133 | 7.4875 | 5.626
[7 empty] | 7526 | 134 | 7.7882 | 5.8617
[7 empty] | 7527 | 135 | 7.855 | 5.9141
[7 empty] | 7528 | 136 | 7.0449 | 5.2789
[7 empty] | 7529 | 137 | 6.9447 | 5.2003
[7 empty] | 7530 | 138 | 6.8946 | 5.1611
[7 empty] | 7531 | 139 | 6.5605 | 4.8991
[7 empty] | 7532 | 140 | 6.5689 | 4.9057
[7 empty] | 7533 | 141 | 5.9175 | 4.3949
[7 empty] | 7534 | 142 | 5.2828 | 3.8973
[7 empty] | 7535 | 143 | 4.406 | 3.2098
[7 empty] | 7536 | 144 | 3.7963 | 2.7318
[7 empty] | 7537 | 145 | 3.3287 | 2.3651
[7 empty] | 7538 | 146 | 3.1199 | 2.2014
[7 empty] | 7539 | 147 | 3.0531 | 2.149
[7 empty] | 7540 | 148 | 3.0447 | 2.1424
[7 empty] | 7541 | 149 | 3.0447 | 2.1424
[7 empty] | 7542 | 150 | 3.0531 | 2.149
[7 empty] | 7543 | 151 | 4.1304 | 2.9937
[7 empty] | 7544 | 152 | 5.6503 | 4.1854
[7 empty] | 7545 | 153 | 6.2599 | 4.6634
[7 empty] | 7546 | 154 | 6.8194 | 5.1021
[7 empty] | 7547 | 155 | 6.6691 | 4.9843
[7 empty] | 7548 | 156 | 6.8361 | 5.1152
[7 empty] | 7549 | 157 | 7.546 | 5.6718
[7 empty] | 7550 | 158 | 7.8717 | 5.9272
[7 empty] | 7551 | 159 | 8.1389 | 6.1367
[7 empty] | 7552 | 160 | 8.0136 | 6.0385
[7 empty] | 7553 | 161 | 8.7736 | 6.6343
[7 empty] | 7554 | 162 | 8.2809 | 6.248
[7 empty] | 7555 | 163 | 8.64 | 6.5296
[7 empty] | 7556 | 164 | 7.2954 | 5.4754
[7 empty] | 7557 | 165 | 10.4104 | 7.9177
[7 empty] | 7558 | 166 | 8.3727 | 6.32
[7 empty] | 7559 | 167 | 4.7818 | 3.5044
[7 empty] | 7560 | 168 | 4.1387 | 3.0002
[7 empty] | 7561 | 1 | 2.6856 | 1.8609
[7 empty] | 7562 | 2 | 2.5771 | 1.7758
[7 empty] | 7563 | 3 | 2.5687 | 1.7692
[7 empty] | 7564 | 4 | 2.7023 | 1.874
[7 empty] | 7565 | 5 | 2.719 | 1.8871
[7 empty] | 7566 | 6 | 3.1449 | 2.221
[7 empty] | 7567 | 7 | 3.8631 | 2.7841
[7 empty] | 7568 | 8 | 4.5312 | 3.308
[7 empty] | 7569 | 9 | 4.5062 | 3.2883
[7 empty] | 7570 | 10 | 6.0177 | 4.4735
[7 empty] | 7571 | 11 | 8.0888 | 6.0974
[7 empty] | 7572 | 12 | 9.0492 | 6.8504
[7 empty] | 7573 | 13 | 9.425 | 7.1451
[7 empty] | 7574 | 14 | 9.2079 | 6.9748
[7 empty] | 7575 | 15 | 9.116 | 6.9028
[7 empty] | 7576 | 16 | 10.2935 | 7.8261
[7 empty] | 7577 | 17 | 11.613 | 8.8607
[7 empty] | 7578 | 18 | 11.3708 | 8.6708
[7 empty] | 7579 | 19 | 11.8969 | 9.0833
[7 empty] | 7580 | 20 | 11.8301 | 9.0309
[7 empty] | 7581 | 21 | 12.398 | 9.4762
[7 empty] | 7582 | 22 | 8.4563 | 6.3855
[7 empty] | 7583 | 23 | 4.6983 | 3.4389
[7 empty] | 7584 | 24 | 3.0331 | 2.1333
[7 empty] | 7585 | 25 | 2.9362 | 2.0573
[7 empty] | 7586 | 26 | 2.8276 | 1.9722
[7 empty] | 7587 | 27 | 2.7274 | 1.8936
[7 empty] | 7588 | 28 | 2.8109 | 1.9591
[7 empty] | 7589 | 29 | 3.0531 | 2.149
[7 empty] | 7590 | 30 | 3.2953 | 2.3389
[7 empty] | 7591 | 31 | 4.1387 | 3.0002
[7 empty] | 7592 | 32 | 4.4895 | 3.2752
[7 empty] | 7593 | 33 | 5.1492 | 3.7925
[7 empty] | 7594 | 34 | 6.0428 | 4.4932
[7 empty] | 7595 | 35 | 8.2057 | 6.1891
[7 empty] | 7596 | 36 | 9.2329 | 6.9945
[7 empty] | 7597 | 37 | 9.3081 | 7.0534
[7 empty] | 7598 | 38 | 9.3832 | 7.1123
[7 empty] | 7599 | 39 | 9.0575 | 6.857
[7 empty] | 7600 | 40 | 10.1098 | 7.682
[7 empty] | 7601 | 41 | 10.6609 | 8.1142
[7 empty] | 7602 | 42 | 10.6776 | 8.1273
[7 empty] | 7603 | 43 | 11.0451 | 8.4154
[7 empty] | 7604 | 44 | 12.1975 | 9.319
[7 empty] | 7605 | 45 | 11.7967 | 9.0047
[7 empty] | 7606 | 46 | 9.0575 | 6.857
[7 empty] | 7607 | 47 | 5.4666 | 4.0414
[7 empty] | 7608 | 48 | 3.9717 | 2.8693
[7 empty] | 7609 | 49 | 3.312 | 2.352
[7 empty] | 7610 | 50 | 3.003 | 2.1097
[7 empty] | 7611 | 51 | 2.8944 | 2.0246
[7 empty] | 7612 | 52 | 2.9278 | 2.0508
[7 empty] | 7613 | 53 | 2.9529 | 2.0704
[7 empty] | 7614 | 54 | 3.5291 | 2.5222
[7 empty] | 7615 | 55 | 4.6648 | 3.4128
[7 empty] | 7616 | 56 | 4.907 | 3.6026
[7 empty] | 7617 | 57 | 5.8507 | 4.3426
[7 empty] | 7618 | 58 | 6.9531 | 5.2069
[7 empty] | 7619 | 59 | 8.1556 | 6.1498
[7 empty] | 7620 | 60 | 8.7819 | 6.6409
[7 empty] | 7621 | 61 | 9.4584 | 7.1713
[7 empty] | 7622 | 62 | 9.258 | 7.0141
[7 empty] | 7623 | 63 | 9.8509 | 7.479
[7 empty] | 7624 | 64 | 10.7946 | 8.219
[7 empty] | 7625 | 65 | 11.4125 | 8.7035
[7 empty] | 7626 | 66 | 11.3123 | 8.6249
[7 empty] | 7627 | 67 | 12.0472 | 9.2011
[7 empty] | 7628 | 68 | 12.2894 | 9.391
[7 empty] | 7629 | 69 | 11.78 | 8.9916
[7 empty] | 7630 | 70 | 9.4918 | 7.1975
[7 empty] | 7631 | 71 | 4.9905 | 3.6681
[7 empty] | 7632 | 72 | 3.9097 | 2.8206
[7 empty] | 7633 | 73 | 3.1951 | 2.2603
[7 empty] | 7634 | 74 | 2.9696 | 2.0835
[7 empty] | 7635 | 75 | 2.8694 | 2.0049
[7 empty] | 7636 | 76 | 2.8109 | 1.9591
[7 empty] | 7637 | 77 | 2.9863 | 2.0966
[7 empty] | 7638 | 78 | 3.3871 | 2.4109
[7 empty] | 7639 | 79 | 4.4978 | 3.2818
[7 empty] | 7640 | 80 | 4.6732 | 3.4193
[7 empty] | 7641 | 81 | 5.8507 | 4.3426
[7 empty] | 7642 | 82 | 6.9363 | 5.1938
[7 empty] | 7643 | 83 | 7.6712 | 5.77
[7 empty] | 7644 | 84 | 8.9072 | 6.7391
[7 empty] | 7645 | 85 | 8.6066 | 6.5034
[7 empty] | 7646 | 86 | 8.0972 | 6.104
[7 empty] | 7647 | 87 | 8.5398 | 6.451
[7 empty] | 7648 | 88 | 9.1995 | 6.9683
[7 empty] | 7649 | 89 | 10.544 | 8.0225
[7 empty] | 7650 | 90 | 9.9595 | 7.5642
[7 empty] | 7651 | 91 | 10.6442 | 8.1011
[7 empty] | 7652 | 92 | 10.043 | 7.6296
[7 empty] | 7653 | 93 | 7.6378 | 5.7438
[7 empty] | 7654 | 94 | 6.7359 | 5.0366
[7 empty] | 7655 | 95 | 4.882 | 3.583
[7 empty] | 7656 | 96 | 3.8965 | 2.8103
[7 empty] | 7657 | 97 | 3.8464 | 2.7711
[7 empty] | 7658 | 98 | 3.5541 | 2.5419
[7 empty] | 7659 | 99 | 3.4957 | 2.496
[7 empty] | 7660 | 100 | 3.1449 | 2.221
[7 empty] | 7661 | 101 | 3.0865 | 2.1752
[7 empty] | 7662 | 102 | 3.3203 | 2.3585
[7 empty] | 7663 | 103 | 4.0636 | 2.9413
[7 empty] | 7664 | 104 | 4.3141 | 3.1377
[7 empty] | 7665 | 105 | 4.7985 | 3.5175
[7 empty] | 7666 | 106 | 6.2516 | 4.6569
[7 empty] | 7667 | 107 | 6.6023 | 4.9319
[7 empty] | 7668 | 108 | 8.1723 | 6.1629
[7 empty] | 7669 | 109 | 7.5126 | 5.6456
[7 empty] | 7670 | 110 | 7.0616 | 5.292
[7 empty] | 7671 | 111 | 6.9029 | 5.1676
[7 empty] | 7672 | 112 | 6.9698 | 5.22
[7 empty] | 7673 | 113 | 6.6274 | 4.9515
[7 empty] | 7674 | 114 | 6.7944 | 5.0825
[7 empty] | 7675 | 115 | 6.3434 | 4.7289
[7 empty] | 7676 | 116 | 7.0199 | 5.2593
[7 empty] | 7677 | 117 | 6.6023 | 4.9319
[7 empty] | 7678 | 118 | 5.834 | 4.3295
[7 empty] | 7679 | 119 | 4.2473 | 3.0854
[7 empty] | 7680 | 120 | 3.9311 | 2.8374
[7 empty] | 7681 | 121 | 3.2034 | 2.2669
[7 empty] | 7682 | 122 | 2.7942 | 1.946
[7 empty] | 7683 | 123 | 2.7107 | 1.8805
[7 empty] | 7684 | 124 | 2.6773 | 1.8543
[7 empty] | 7685 | 125 | 2.6355 | 1.8216
[7 empty] | 7686 | 126 | 2.7775 | 1.9329
[7 empty] | 7687 | 127 | 4.2807 | 3.1115
[7 empty] | 7688 | 128 | 5.834 | 4.3295
[7 empty] | 7689 | 129 | 6.5104 | 4.8599
[7 empty] | 7690 | 130 | 6.9447 | 5.2003
[7 empty] | 7691 | 131 | 7.1034 | 5.3248
[7 empty] | 7692 | 132 | 6.8528 | 5.1283
[7 empty] | 7693 | 133 | 7.4875 | 5.626
[7 empty] | 7694 | 134 | 7.7882 | 5.8617
[7 empty] | 7695 | 135 | 7.855 | 5.9141
[7 empty] | 7696 | 136 | 7.0449 | 5.2789
[7 empty] | 7697 | 137 | 6.9447 | 5.2003
[7 empty] | 7698 | 138 | 6.8946 | 5.1611
[7 empty] | 7699 | 139 | 6.5605 | 4.8991
[7 empty] | 7700 | 140 | 6.5689 | 4.9057
[7 empty] | 7701 | 141 | 5.9175 | 4.3949
[7 empty] | 7702 | 142 | 5.2828 | 3.8973
[7 empty] | 7703 | 143 | 4.406 | 3.2098
[7 empty] | 7704 | 144 | 3.7963 | 2.7318
[7 empty] | 7705 | 145 | 3.3287 | 2.3651
[7 empty] | 7706 | 146 | 3.1199 | 2.2014
[7 empty] | 7707 | 147 | 3.0531 | 2.149
[7 empty] | 7708 | 148 | 3.0447 | 2.1424
[7 empty] | 7709 | 149 | 3.0447 | 2.1424
[7 empty] | 7710 | 150 | 3.0531 | 2.149
[7 empty] | 7711 | 151 | 4.1304 | 2.9937
[7 empty] | 7712 | 152 | 5.6503 | 4.1854
[7 empty] | 7713 | 153 | 6.2599 | 4.6634
[7 empty] | 7714 | 154 | 6.8194 | 5.1021
[7 empty] | 7715 | 155 | 6.6691 | 4.9843
[7 empty] | 7716 | 156 | 6.8361 | 5.1152
[7 empty] | 7717 | 157 | 7.546 | 5.6718
[7 empty] | 7718 | 158 | 7.8717 | 5.9272
[7 empty] | 7719 | 159 | 8.1389 | 6.1367
[7 empty] | 7720 | 160 | 8.0136 | 6.0385
[7 empty] | 7721 | 161 | 8.7736 | 6.6343
[7 empty] | 7722 | 162 | 8.2809 | 6.248
[7 empty] | 7723 | 163 | 8.64 | 6.5296
[7 empty] | 7724 | 164 | 7.2954 | 5.4754
[7 empty] | 7725 | 165 | 10.4104 | 7.9177
[7 empty] | 7726 | 166 | 8.3727 | 6.32
[7 empty] | 7727 | 167 | 4.7818 | 3.5044
[7 empty] | 7728 | 168 | 4.1387 | 3.0002
[7 empty] | 7729 | 1 | 2.6856 | 1.8609
[7 empty] | 7730 | 2 | 2.5771 | 1.7758
[7 empty] | 7731 | 3 | 2.5687 | 1.7692
[7 empty] | 7732 | 4 | 2.7023 | 1.874
[7 empty] | 7733 | 5 | 2.719 | 1.8871
[7 empty] | 7734 | 6 | 3.1449 | 2.221
[7 empty] | 7735 | 7 | 3.8631 | 2.7841
[7 empty] | 7736 | 8 | 4.5312 | 3.308
[7 empty] | 7737 | 9 | 4.5062 | 3.2883
[7 empty] | 7738 | 10 | 6.0177 | 4.4735
[7 empty] | 7739 | 11 | 8.0888 | 6.0974
[7 empty] | 7740 | 12 | 9.0492 | 6.8504
[7 empty] | 7741 | 13 | 9.425 | 7.1451
[7 empty] | 7742 | 14 | 9.2079 | 6.9748
[7 empty] | 7743 | 15 | 9.116 | 6.9028
[7 empty] | 7744 | 16 | 10.2935 | 7.8261
[7 empty] | 7745 | 17 | 11.613 | 8.8607
[7 empty] | 7746 | 18 | 11.3708 | 8.6708
[7 empty] | 7747 | 19 | 11.8969 | 9.0833
[7 empty] | 7748 | 20 | 11.8301 | 9.0309
[7 empty] | 7749 | 21 | 12.398 | 9.4762
[7 empty] | 7750 | 22 | 8.4563 | 6.3855
[7 empty] | 7751 | 23 | 4.6983 | 3.4389
[7 empty] | 7752 | 24 | 3.0331 | 2.1333
[7 empty] | 7753 | 25 | 2.9362 | 2.0573
[7 empty] | 7754 | 26 | 2.8276 | 1.9722
[7 empty] | 7755 | 27 | 2.7274 | 1.8936
[7 empty] | 7756 | 28 | 2.8109 | 1.9591
[7 empty] | 7757 | 29 | 3.0531 | 2.149
[7 empty] | 7758 | 30 | 3.2953 | 2.3389
[7 empty] | 7759 | 31 | 4.1387 | 3.0002
[7 empty] | 7760 | 32 | 4.4895 | 3.2752
[7 empty] | 7761 | 33 | 5.1492 | 3.7925
[7 empty] | 7762 | 34 | 6.0428 | 4.4932
[7 empty] | 7763 | 35 | 8.2057 | 6.1891
[7 empty] | 7764 | 36 | 9.2329 | 6.9945
[7 empty] | 7765 | 37 | 9.3081 | 7.0534
[7 empty] | 7766 | 38 | 9.3832 | 7.1123
[7 empty] | 7767 | 39 | 9.0575 | 6.857
[7 empty] | 7768 | 40 | 10.1098 | 7.682
[7 empty] | 7769 | 41 | 10.6609 | 8.1142
[7 empty] | 7770 | 42 | 10.6776 | 8.1273
[7 empty] | 7771 | 43 | 11.0451 | 8.4154
[7 empty] | 7772 | 44 | 12.1975 | 9.319
[7 empty] | 7773 | 45 | 11.7967 | 9.0047
[7 empty] | 7774 | 46 | 9.0575 | 6.857
[7 empty] | 7775 | 47 | 5.4666 | 4.0414
[7 empty] | 7776 | 48 | 3.9717 | 2.8693
[7 empty] | 7777 | 49 | 3.312 | 2.352
[7 empty] | 7778 | 50 | 3.003 | 2.1097
[7 empty] | 7779 | 51 | 2.8944 | 2.0246
[7 empty] | 7780 | 52 | 2.9278 | 2.0508
[7 empty] | 7781 | 53 | 2.9529 | 2.0704
[7 empty] | 7782 | 54 | 3.5291 | 2.5222
[7 empty] | 7783 | 55 | 4.6648 | 3.4128
[7 empty] | 7784 | 56 | 4.907 | 3.6026
[7 empty] | 7785 | 57 | 5.8507 | 4.3426
[7 empty] | 7786 | 58 | 6.9531 | 5.2069
[7 empty] | 7787 | 59 | 8.1556 | 6.1498
[7 empty] | 7788 | 60 | 8.7819 | 6.6409
[7 empty] | 7789 | 61 | 9.4584 | 7.1713
[7 empty] | 7790 | 62 | 9.258 | 7.0141
[7 empty] | 7791 | 63 | 9.8509 | 7.479
[7 empty] | 7792 | 64 | 10.7946 | 8.219
[7 empty] | 7793 | 65 | 11.4125 | 8.7035
[7 empty] | 7794 | 66 | 11.3123 | 8.6249
[7 empty] | 7795 | 67 | 12.0472 | 9.2011
[7 empty] | 7796 | 68 | 12.2894 | 9.391
[7 empty] | 7797 | 69 | 11.78 | 8.9916
[7 empty] | 7798 | 70 | 9.4918 | 7.1975
[7 empty] | 7799 | 71 | 4.9905 | 3.6681
[7 empty] | 7800 | 72 | 3.9097 | 2.8206
[7 empty] | 7801 | 73 | 3.1951 | 2.2603
[7 empty] | 7802 | 74 | 2.9696 | 2.0835
[7 empty] | 7803 | 75 | 2.8694 | 2.0049
[7 empty] | 7804 | 76 | 2.8109 | 1.9591
[7 empty] | 7805 | 77 | 2.9863 | 2.0966
[7 empty] | 7806 | 78 | 3.3871 | 2.4109
[7 empty] | 7807 | 79 | 4.4978 | 3.2818
[7 empty] | 7808 | 80 | 4.6732 | 3.4193
[7 empty] | 7809 | 81 | 5.8507 | 4.3426
[7 empty] | 7810 | 82 | 6.9363 | 5.1938
[7 empty] | 7811 | 83 | 7.6712 | 5.77
[7 empty] | 7812 | 84 | 8.9072 | 6.7391
[7 empty] | 7813 | 85 | 8.6066 | 6.5034
[7 empty] | 7814 | 86 | 8.0972 | 6.104
[7 empty] | 7815 | 87 | 8.5398 | 6.451
[7 empty] | 7816 | 88 | 9.1995 | 6.9683
[7 empty] | 7817 | 89 | 10.544 | 8.0225
[7 empty] | 7818 | 90 | 9.9595 | 7.5642
[7 empty] | 7819 | 91 | 10.6442 | 8.1011
[7 empty] | 7820 | 92 | 10.043 | 7.6296
[7 empty] | 7821 | 93 | 7.6378 | 5.7438
[7 empty] | 7822 | 94 | 6.7359 | 5.0366
[7 empty] | 7823 | 95 | 4.882 | 3.583
[7 empty] | 7824 | 96 | 3.8965 | 2.8103
[7 empty] | 7825 | 97 | 3.8464 | 2.7711
[7 empty] | 7826 | 98 | 3.5541 | 2.5419
[7 empty] | 7827 | 99 | 3.4957 | 2.496
[7 empty] | 7828 | 100 | 3.1449 | 2.221
[7 empty] | 7829 | 101 | 3.0865 | 2.1752
[7 empty] | 7830 | 102 | 3.3203 | 2.3585
[7 empty] | 7831 | 103 | 4.0636 | 2.9413
[7 empty] | 7832 | 104 | 4.3141 | 3.1377
[7 empty] | 7833 | 105 | 4.7985 | 3.5175
[7 empty] | 7834 | 106 | 6.2516 | 4.6569
[7 empty] | 7835 | 107 | 6.6023 | 4.9319
[7 empty] | 7836 | 108 | 8.1723 | 6.1629
[7 empty] | 7837 | 109 | 7.5126 | 5.6456
[7 empty] | 7838 | 110 | 7.0616 | 5.292
[7 empty] | 7839 | 111 | 6.9029 | 5.1676
[7 empty] | 7840 | 112 | 6.9698 | 5.22
[7 empty] | 7841 | 113 | 6.6274 | 4.9515
[7 empty] | 7842 | 114 | 6.7944 | 5.0825
[7 empty] | 7843 | 115 | 6.3434 | 4.7289
[7 empty] | 7844 | 116 | 7.0199 | 5.2593
[7 empty] | 7845 | 117 | 6.6023 | 4.9319
[7 empty] | 7846 | 118 | 5.834 | 4.3295
[7 empty] | 7847 | 119 | 4.2473 | 3.0854
[7 empty] | 7848 | 120 | 3.9311 | 2.8374
[7 empty] | 7849 | 121 | 3.2034 | 2.2669
[7 empty] | 7850 | 122 | 2.7942 | 1.946
[7 empty] | 7851 | 123 | 2.7107 | 1.8805
[7 empty] | 7852 | 124 | 2.6773 | 1.8543
[7 empty] | 7853 | 125 | 2.6355 | 1.8216
[7 empty] | 7854 | 126 | 2.7775 | 1.9329
[7 empty] | 7855 | 127 | 4.2807 | 3.1115
[7 empty] | 7856 | 128 | 5.834 | 4.3295
[7 empty] | 7857 | 129 | 6.5104 | 4.8599
[7 empty] | 7858 | 130 | 6.9447 | 5.2003
[7 empty] | 7859 | 131 | 7.1034 | 5.3248
[7 empty] | 7860 | 132 | 6.8528 | 5.1283
[7 empty] | 7861 | 133 | 7.4875 | 5.626
[7 empty] | 7862 | 134 | 7.7882 | 5.8617
[7 empty] | 7863 | 135 | 7.855 | 5.9141
[7 empty] | 7864 | 136 | 7.0449 | 5.2789
[7 empty] | 7865 | 137 | 6.9447 | 5.2003
[7 empty] | 7866 | 138 | 6.8946 | 5.1611
[7 empty] | 7867 | 139 | 6.5605 | 4.8991
[7 empty] | 7868 | 140 | 6.5689 | 4.9057
[7 empty] | 7869 | 141 | 5.9175 | 4.3949
[7 empty] | 7870 | 142 | 5.2828 | 3.8973
[7 empty] | 7871 | 143 | 4.406 | 3.2098
[7 empty] | 7872 | 144 | 3.7963 | 2.7318
[7 empty] | 7873 | 145 | 3.3287 | 2.3651
[7 empty] | 7874 | 146 | 3.1199 | 2.2014
[7 empty] | 7875 | 147 | 3.0531 | 2.149
[7 empty] | 7876 | 148 | 3.0447 | 2.1424
[7 empty] | 7877 | 149 | 3.0447 | 2.1424
[7 empty] | 7878 | 150 | 3.0531 | 2.149
[7 empty] | 7879 | 151 | 4.1304 | 2.9937
[7 empty] | 7880 | 152 | 5.6503 | 4.1854
[7 empty] | 7881 | 153 | 6.2599 | 4.6634
[7 empty] | 7882 | 154 | 6.8194 | 5.1021
[7 empty] | 7883 | 155 | 6.6691 | 4.9843
[7 empty] | 7884 | 156 | 6.8361 | 5.1152
[7 empty] | 7885 | 157 | 7.546 | 5.6718
[7 empty] | 7886 | 158 | 7.8717 | 5.9272
[7 empty] | 7887 | 159 | 8.1389 | 6.1367
[7 empty] | 7888 | 160 | 8.0136 | 6.0385
[7 empty] | 7889 | 161 | 8.7736 | 6.6343
[7 empty] | 7890 | 162 | 8.2809 | 6.248
[7 empty] | 7891 | 163 | 8.64 | 6.5296
[7 empty] | 7892 | 164 | 7.2954 | 5.4754
[7 empty] | 7893 | 165 | 10.4104 | 7.9177
[7 empty] | 7894 | 166 | 8.3727 | 6.32
[7 empty] | 7895 | 167 | 4.7818 | 3.5044
[7 empty] | 7896 | 168 | 4.1387 | 3.0002
[7 empty] | 7897 | 1 | 2.6856 | 1.8609
[7 empty] | 7898 | 2 | 2.5771 | 1.7758
[7 empty] | 7899 | 3 | 2.5687 | 1.7692
[7 empty] | 7900 | 4 | 2.7023 | 1.874
[7 empty] | 7901 | 5 | 2.719 | 1.8871
[7 empty] | 7902 | 6 | 3.1449 | 2.221
[7 empty] | 7903 | 7 | 3.8631 | 2.7841
[7 empty] | 7904 | 8 | 4.5312 | 3.308
[7 empty] | 7905 | 9 | 4.5062 | 3.2883
[7 empty] | 7906 | 10 | 6.0177 | 4.4735
[7 empty] | 7907 | 11 | 8.0888 | 6.0974
[7 empty] | 7908 | 12 | 9.0492 | 6.8504
[7 empty] | 7909 | 13 | 9.425 | 7.1451
[7 empty] | 7910 | 14 | 9.2079 | 6.9748
[7 empty] | 7911 | 15 | 9.116 | 6.9028
[7 empty] | 7912 | 16 | 10.2935 | 7.8261
[7 empty] | 7913 | 17 | 11.613 | 8.8607
[7 empty] | 7914 | 18 | 11.3708 | 8.6708
[7 empty] | 7915 | 19 | 11.8969 | 9.0833
[7 empty] | 7916 | 20 | 11.8301 | 9.0309
[7 empty] | 7917 | 21 | 12.398 | 9.4762
[7 empty] | 7918 | 22 | 8.4563 | 6.3855
[7 empty] | 7919 | 23 | 4.6983 | 3.4389
[7 empty] | 7920 | 24 | 3.0331 | 2.1333
[7 empty] | 7921 | 25 | 2.9362 | 2.0573
[7 empty] | 7922 | 26 | 2.8276 | 1.9722
[7 empty] | 7923 | 27 | 2.7274 | 1.8936
[7 empty] | 7924 | 28 | 2.8109 | 1.9591
[7 empty] | 7925 | 29 | 3.0531 | 2.149
[7 empty] | 7926 | 30 | 3.2953 | 2.3389
[7 empty] | 7927 | 31 | 4.1387 | 3.0002
[7 empty] | 7928 | 32 | 4.4895 | 3.2752
[7 empty] | 7929 | 33 | 5.1492 | 3.7925
[7 empty] | 7930 | 34 | 6.0428 | 4.4932
[7 empty] | 7931 | 35 | 8.2057 | 6.1891
[7 empty] | 7932 | 36 | 9.2329 | 6.9945
[7 empty] | 7933 | 37 | 9.3081 | 7.0534
[7 empty] | 7934 | 38 | 9.3832 | 7.1123
[7 empty] | 7935 | 39 | 9.0575 | 6.857
[7 empty] | 7936 | 40 | 10.1098 | 7.682
[7 empty] | 7937 | 41 | 10.6609 | 8.1142
[7 empty] | 7938 | 42 | 10.6776 | 8.1273
[7 empty] | 7939 | 43 | 11.0451 | 8.4154
[7 empty] | 7940 | 44 | 12.1975 | 9.319
[7 empty] | 7941 | 45 | 11.7967 | 9.0047
[7 empty] | 7942 | 46 | 9.0575 | 6.857
[7 empty] | 7943 | 47 | 5.4666 | 4.0414
[7 empty] | 7944 | 48 | 3.9717 | 2.8693
[7 empty] | 7945 | 49 | 3.312 | 2.352
[7 empty] | 7946 | 50 | 3.003 | 2.1097
[7 empty] | 7947 | 51 | 2.8944 | 2.0246
[7 empty] | 7948 | 52 | 2.9278 | 2.0508
[7 empty] | 7949 | 53 | 2.9529 | 2.0704
[7 empty] | 7950 | 54 | 3.5291 | 2.5222
[7 empty] | 7951 | 55 | 4.6648 | 3.4128
[7 empty] | 7952 | 56 | 4.907 | 3.6026
[7 empty] | 7953 | 57 | 5.8507 | 4.3426
[7 empty] | 7954 | 58 | 6.9531 | 5.2069
[7 empty] | 7955 | 59 | 8.1556 | 6.1498
[7 empty] | 7956 | 60 | 8.7819 | 6.6409
[7 empty] | 7957 | 61 | 9.4584 | 7.1713
[7 empty] | 7958 | 62 | 9.258 | 7.0141
[7 empty] | 7959 | 63 | 9.8509 | 7.479
[7 empty] | 7960 | 64 | 10.7946 | 8.219
[7 empty] | 7961 | 65 | 11.4125 | 8.7035
[7 empty] | 7962 | 66 | 11.3123 | 8.6249
[7 empty] | 7963 | 67 | 12.0472 | 9.2011
[7 empty] | 7964 | 68 | 12.2894 | 9.391
[7 empty] | 7965 | 69 | 11.78 | 8.9916
[7 empty] | 7966 | 70 | 9.4918 | 7.1975
[7 empty] | 7967 | 71 | 4.9905 | 3.6681
[7 empty] | 7968 | 72 | 3.9097 | 2.8206
[7 empty] | 7969 | 73 | 3.1951 | 2.2603
[7 empty] | 7970 | 74 | 2.9696 | 2.0835
[7 empty] | 7971 | 75 | 2.8694 | 2.0049
[7 empty] | 7972 | 76 | 2.8109 | 1.9591
[7 empty] | 7973 | 77 | 2.9863 | 2.0966
[7 empty] | 7974 | 78 | 3.3871 | 2.4109
[7 empty] | 7975 | 79 | 4.4978 | 3.2818
[7 empty] | 7976 | 80 | 4.6732 | 3.4193
[7 empty] | 7977 | 81 | 5.8507 | 4.3426
[7 empty] | 7978 | 82 | 6.9363 | 5.1938
[7 empty] | 7979 | 83 | 7.6712 | 5.77
[7 empty] | 7980 | 84 | 8.9072 | 6.7391
[7 empty] | 7981 | 85 | 8.6066 | 6.5034
[7 empty] | 7982 | 86 | 8.0972 | 6.104
[7 empty] | 7983 | 87 | 8.5398 | 6.451
[7 empty] | 7984 | 88 | 9.1995 | 6.9683
[7 empty] | 7985 | 89 | 10.544 | 8.0225
[7 empty] | 7986 | 90 | 9.9595 | 7.5642
[7 empty] | 7987 | 91 | 10.6442 | 8.1011
[7 empty] | 7988 | 92 | 10.043 | 7.6296
[7 empty] | 7989 | 93 | 7.6378 | 5.7438
[7 empty] | 7990 | 94 | 6.7359 | 5.0366
[7 empty] | 7991 | 95 | 4.882 | 3.583
[7 empty] | 7992 | 96 | 3.8965 | 2.8103
[7 empty] | 7993 | 97 | 3.8464 | 2.7711
[7 empty] | 7994 | 98 | 3.5541 | 2.5419
[7 empty] | 7995 | 99 | 3.4957 | 2.496
[7 empty] | 7996 | 100 | 3.1449 | 2.221
[7 empty] | 7997 | 101 | 3.0865 | 2.1752
[7 empty] | 7998 | 102 | 3.3203 | 2.3585
[7 empty] | 7999 | 103 | 4.0636 | 2.9413
[7 empty] | 8000 | 104 | 4.3141 | 3.1377
[7 empty] | 8001 | 105 | 4.7985 | 3.5175
[7 empty] | 8002 | 106 | 6.2516 | 4.6569
[7 empty] | 8003 | 107 | 6.6023 | 4.9319
[7 empty] | 8004 | 108 | 8.1723 | 6.1629
[7 empty] | 8005 | 109 | 7.5126 | 5.6456
[7 empty] | 8006 | 110 | 7.0616 | 5.292
[7 empty] | 8007 | 111 | 6.9029 | 5.1676
[7 empty] | 8008 | 112 | 6.9698 | 5.22
[7 empty] | 8009 | 113 | 6.6274 | 4.9515
[7 empty] | 8010 | 114 | 6.7944 | 5.0825
[7 empty] | 8011 | 115 | 6.3434 | 4.7289
[7 empty] | 8012 | 116 | 7.0199 | 5.2593
[7 empty] | 8013 | 117 | 6.6023 | 4.9319
[7 empty] | 8014 | 118 | 5.834 | 4.3295
[7 empty] | 8015 | 119 | 4.2473 | 3.0854
[7 empty] | 8016 | 120 | 3.9311 | 2.8374
[7 empty] | 8017 | 121 | 3.2034 | 2.2669
[7 empty] | 8018 | 122 | 2.7942 | 1.946
[7 empty] | 8019 | 123 | 2.7107 | 1.8805
[7 empty] | 8020 | 124 | 2.6773 | 1.8543
[7 empty] | 8021 | 125 | 2.6355 | 1.8216
[7 empty] | 8022 | 126 | 2.7775 | 1.9329
[7 empty] | 8023 | 127 | 4.2807 | 3.1115
[7 empty] | 8024 | 128 | 5.834 | 4.3295
[7 empty] | 8025 | 129 | 6.5104 | 4.8599
[7 empty] | 8026 | 130 | 6.9447 | 5.2003
[7 empty] | 8027 | 131 | 7.1034 | 5.3248
[7 empty] | 8028 | 132 | 6.8528 | 5.1283
[7 empty] | 8029 | 133 | 7.4875 | 5.626
[7 empty] | 8030 | 134 | 7.7882 | 5.8617
[7 empty] | 8031 | 135 | 7.855 | 5.9141
[7 empty] | 8032 | 136 | 7.0449 | 5.2789
[7 empty] | 8033 | 137 | 6.9447 | 5.2003
[7 empty] | 8034 | 138 | 6.8946 | 5.1611
[7 empty] | 8035 | 139 | 6.5605 | 4.8991
[7 empty] | 8036 | 140 | 6.5689 | 4.9057
[7 empty] | 8037 | 141 | 5.9175 | 4.3949
[7 empty] | 8038 | 142 | 5.2828 | 3.8973
[7 empty] | 8039 | 143 | 4.406 | 3.2098
[7 empty] | 8040 | 144 | 3.7963 | 2.7318
[7 empty] | 8041 | 145 | 3.3287 | 2.3651
[7 empty] | 8042 | 146 | 3.1199 | 2.2014
[7 empty] | 8043 | 147 | 3.0531 | 2.149
[7 empty] | 8044 | 148 | 3.0447 | 2.1424
[7 empty] | 8045 | 149 | 3.0447 | 2.1424
[7 empty] | 8046 | 150 | 3.0531 | 2.149
[7 empty] | 8047 | 151 | 4.1304 | 2.9937
[7 empty] | 8048 | 152 | 5.6503 | 4.1854
[7 empty] | 8049 | 153 | 6.2599 | 4.6634
[7 empty] | 8050 | 154 | 6.8194 | 5.1021
[7 empty] | 8051 | 155 | 6.6691 | 4.9843
[7 empty] | 8052 | 156 | 6.8361 | 5.1152
[7 empty] | 8053 | 157 | 7.546 | 5.6718
[7 empty] | 8054 | 158 | 7.8717 | 5.9272
[7 empty] | 8055 | 159 | 8.1389 | 6.1367
[7 empty] | 8056 | 160 | 8.0136 | 6.0385
[7 empty] | 8057 | 161 | 8.7736 | 6.6343
[7 empty] | 8058 | 162 | 8.2809 | 6.248
[7 empty] | 8059 | 163 | 8.64 | 6.5296
[7 empty] | 8060 | 164 | 7.2954 | 5.4754
[7 empty] | 8061 | 165 | 10.4104 | 7.9177
[7 empty] | 8062 | 166 | 8.3727 | 6.32
[7 empty] | 8063 | 167 | 4.7818 | 3.5044
[7 empty] | 8064 | 168 | 4.1387 | 3.0002
[7 empty] | 8065 | 1 | 2.6856 | 1.8609
[7 empty] | 8066 | 2 | 2.5771 | 1.7758
[7 empty] | 8067 | 3 | 2.5687 | 1.7692
[7 empty] | 8068 | 4 | 2.7023 | 1.874
[7 empty] | 8069 | 5 | 2.719 | 1.8871
[7 empty] | 8070 | 6 | 3.1449 | 2.221
[7 empty] | 8071 | 7 | 3.8631 | 2.7841
[7 empty] | 8072 | 8 | 4.5312 | 3.308
[7 empty] | 8073 | 9 | 4.5062 | 3.2883
[7 empty] | 8074 | 10 | 6.0177 | 4.4735
[7 empty] | 8075 | 11 | 8.0888 | 6.0974
[7 empty] | 8076 | 12 | 9.0492 | 6.8504
[7 empty] | 8077 | 13 | 9.425 | 7.1451
[7 empty] | 8078 | 14 | 9.2079 | 6.9748
[7 empty] | 8079 | 15 | 9.116 | 6.9028
[7 empty] | 8080 | 16 | 10.2935 | 7.8261
[7 empty] | 8081 | 17 | 11.613 | 8.8607
[7 empty] | 8082 | 18 | 11.3708 | 8.6708
[7 empty] | 8083 | 19 | 11.8969 | 9.0833
[7 empty] | 8084 | 20 | 11.8301 | 9.0309
[7 empty] | 8085 | 21 | 12.398 | 9.4762
[7 empty] | 8086 | 22 | 8.4563 | 6.3855
[7 empty] | 8087 | 23 | 4.6983 | 3.4389
[7 empty] | 8088 | 24 | 3.0331 | 2.1333
[7 empty] | 8089 | 25 | 2.9362 | 2.0573
[7 empty] | 8090 | 26 | 2.8276 | 1.9722
[7 empty] | 8091 | 27 | 2.7274 | 1.8936
[7 empty] | 8092 | 28 | 2.8109 | 1.9591
[7 empty] | 8093 | 29 | 3.0531 | 2.149
[7 empty] | 8094 | 30 | 3.2953 | 2.3389
[7 empty] | 8095 | 31 | 4.1387 | 3.0002
[7 empty] | 8096 | 32 | 4.4895 | 3.2752
[7 empty] | 8097 | 33 | 5.1492 | 3.7925
[7 empty] | 8098 | 34 | 6.0428 | 4.4932
[7 empty] | 8099 | 35 | 8.2057 | 6.1891
[7 empty] | 8100 | 36 | 9.2329 | 6.9945
[7 empty] | 8101 | 37 | 9.3081 | 7.0534
[7 empty] | 8102 | 38 | 9.3832 | 7.1123
[7 empty] | 8103 | 39 | 9.0575 | 6.857
[7 empty] | 8104 | 40 | 10.1098 | 7.682
[7 empty] | 8105 | 41 | 10.6609 | 8.1142
[7 empty] | 8106 | 42 | 10.6776 | 8.1273
[7 empty] | 8107 | 43 | 11.0451 | 8.4154
[7 empty] | 8108 | 44 | 12.1975 | 9.319
[7 empty] | 8109 | 45 | 11.7967 | 9.0047
[7 empty] | 8110 | 46 | 9.0575 | 6.857
[7 empty] | 8111 | 47 | 5.4666 | 4.0414
[7 empty] | 8112 | 48 | 3.9717 | 2.8693
[7 empty] | 8113 | 49 | 3.312 | 2.352
[7 empty] | 8114 | 50 | 3.003 | 2.1097
[7 empty] | 8115 | 51 | 2.8944 | 2.0246
[7 empty] | 8116 | 52 | 2.9278 | 2.0508
[7 empty] | 8117 | 53 | 2.9529 | 2.0704
[7 empty] | 8118 | 54 | 3.5291 | 2.5222
[7 empty] | 8119 | 55 | 4.6648 | 3.4128
[7 empty] | 8120 | 56 | 4.907 | 3.6026
[7 empty] | 8121 | 57 | 5.8507 | 4.3426
[7 empty] | 8122 | 58 | 6.9531 | 5.2069
[7 empty] | 8123 | 59 | 8.1556 | 6.1498
[7 empty] | 8124 | 60 | 8.7819 | 6.6409
[7 empty] | 8125 | 61 | 9.4584 | 7.1713
[7 empty] | 8126 | 62 | 9.258 | 7.0141
[7 empty] | 8127 | 63 | 9.8509 | 7.479
[7 empty] | 8128 | 64 | 10.7946 | 8.219
[7 empty] | 8129 | 65 | 11.4125 | 8.7035
[7 empty] | 8130 | 66 | 11.3123 | 8.6249
[7 empty] | 8131 | 67 | 12.0472 | 9.2011
[7 empty] | 8132 | 68 | 12.2894 | 9.391
[7 empty] | 8133 | 69 | 11.78 | 8.9916
[7 empty] | 8134 | 70 | 9.4918 | 7.1975
[7 empty] | 8135 | 71 | 4.9905 | 3.6681
[7 empty] | 8136 | 72 | 3.9097 | 2.8206
[7 empty] | 8137 | 73 | 3.1951 | 2.2603
[7 empty] | 8138 | 74 | 2.9696 | 2.0835
[7 empty] | 8139 | 75 | 2.8694 | 2.0049
[7 empty] | 8140 | 76 | 2.8109 | 1.9591
[7 empty] | 8141 | 77 | 2.9863 | 2.0966
[7 empty] | 8142 | 78 | 3.3871 | 2.4109
[7 empty] | 8143 | 79 | 4.4978 | 3.2818
[7 empty] | 8144 | 80 | 4.6732 | 3.4193
[7 empty] | 8145 | 81 | 5.8507 | 4.3426
[7 empty] | 8146 | 82 | 6.9363 | 5.1938
[7 empty] | 8147 | 83 | 7.6712 | 5.77
[7 empty] | 8148 | 84 | 8.9072 | 6.7391
[7 empty] | 8149 | 85 | 8.6066 | 6.5034
[7 empty] | 8150 | 86 | 8.0972 | 6.104
[7 empty] | 8151 | 87 | 8.5398 | 6.451
[7 empty] | 8152 | 88 | 9.1995 | 6.9683
[7 empty] | 8153 | 89 | 10.544 | 8.0225
[7 empty] | 8154 | 90 | 9.9595 | 7.5642
[7 empty] | 8155 | 91 | 10.6442 | 8.1011
[7 empty] | 8156 | 92 | 10.043 | 7.6296
[7 empty] | 8157 | 93 | 7.6378 | 5.7438
[7 empty] | 8158 | 94 | 6.7359 | 5.0366
[7 empty] | 8159 | 95 | 4.882 | 3.583
[7 empty] | 8160 | 96 | 3.8965 | 2.8103
[7 empty] | 8161 | 97 | 3.8464 | 2.7711
[7 empty] | 8162 | 98 | 3.5541 | 2.5419
[7 empty] | 8163 | 99 | 3.4957 | 2.496
[7 empty] | 8164 | 100 | 3.1449 | 2.221
[7 empty] | 8165 | 101 | 3.0865 | 2.1752
[7 empty] | 8166 | 102 | 3.3203 | 2.3585
[7 empty] | 8167 | 103 | 4.0636 | 2.9413
[7 empty] | 8168 | 104 | 4.3141 | 3.1377
[7 empty] | 8169 | 105 | 4.7985 | 3.5175
[7 empty] | 8170 | 106 | 6.2516 | 4.6569
[7 empty] | 8171 | 107 | 6.6023 | 4.9319
[7 empty] | 8172 | 108 | 8.1723 | 6.1629
[7 empty] | 8173 | 109 | 7.5126 | 5.6456
[7 empty] | 8174 | 110 | 7.0616 | 5.292
[7 empty] | 8175 | 111 | 6.9029 | 5.1676
[7 empty] | 8176 | 112 | 6.9698 | 5.22
[7 empty] | 8177 | 113 | 6.6274 | 4.9515
[7 empty] | 8178 | 114 | 6.7944 | 5.0825
[7 empty] | 8179 | 115 | 6.3434 | 4.7289
[7 empty] | 8180 | 116 | 7.0199 | 5.2593
[7 empty] | 8181 | 117 | 6.6023 | 4.9319
[7 empty] | 8182 | 118 | 5.834 | 4.3295
[7 empty] | 8183 | 119 | 4.2473 | 3.0854
[7 empty] | 8184 | 120 | 3.9311 | 2.8374
[7 empty] | 8185 | 121 | 3.2034 | 2.2669
[7 empty] | 8186 | 122 | 2.7942 | 1.946
[7 empty] | 8187 | 123 | 2.7107 | 1.8805
[7 empty] | 8188 | 124 | 2.6773 | 1.8543
[7 empty] | 8189 | 125 | 2.6355 | 1.8216
[7 empty] | 8190 | 126 | 2.7775 | 1.9329
[7 empty] | 8191 | 127 | 4.2807 | 3.1115
[7 empty] | 8192 | 128 | 5.834 | 4.3295
[7 empty] | 8193 | 129 | 6.5104 | 4.8599
[7 empty] | 8194 | 130 | 6.9447 | 5.2003
[7 empty] | 8195 | 131 | 7.1034 | 5.3248
[7 empty] | 8196 | 132 | 6.8528 | 5.1283
[7 empty] | 8197 | 133 | 7.4875 | 5.626
[7 empty] | 8198 | 134 | 7.7882 | 5.8617
[7 empty] | 8199 | 135 | 7.855 | 5.9141
[7 empty] | 8200 | 136 | 7.0449 | 5.2789
[7 empty] | 8201 | 137 | 6.9447 | 5.2003
[7 empty] | 8202 | 138 | 6.8946 | 5.1611
[7 empty] | 8203 | 139 | 6.5605 | 4.8991
[7 empty] | 8204 | 140 | 6.5689 | 4.9057
[7 empty] | 8205 | 141 | 5.9175 | 4.3949
[7 empty] | 8206 | 142 | 5.2828 | 3.8973
[7 empty] | 8207 | 143 | 4.406 | 3.2098
[7 empty] | 8208 | 144 | 3.7963 | 2.7318
[7 empty] | 8209 | 145 | 3.3287 | 2.3651
[7 empty] | 8210 | 146 | 3.1199 | 2.2014
[7 empty] | 8211 | 147 | 3.0531 | 2.149
[7 empty] | 8212 | 148 | 3.0447 | 2.1424
[7 empty] | 8213 | 149 | 3.0447 | 2.1424
[7 empty] | 8214 | 150 | 3.0531 | 2.149
[7 empty] | 8215 | 151 | 4.1304 | 2.9937
[7 empty] | 8216 | 152 | 5.6503 | 4.1854
[7 empty] | 8217 | 153 | 6.2599 | 4.6634
[7 empty] | 8218 | 154 | 6.8194 | 5.1021
[7 empty] | 8219 | 155 | 6.6691 | 4.9843
[7 empty] | 8220 | 156 | 6.8361 | 5.1152
[7 empty] | 8221 | 157 | 7.546 | 5.6718
[7 empty] | 8222 | 158 | 7.8717 | 5.9272
[7 empty] | 8223 | 159 | 8.1389 | 6.1367
[7 empty] | 8224 | 160 | 8.0136 | 6.0385
[7 empty] | 8225 | 161 | 8.7736 | 6.6343
[7 empty] | 8226 | 162 | 8.2809 | 6.248
[7 empty] | 8227 | 163 | 8.64 | 6.5296
[7 empty] | 8228 | 164 | 7.2954 | 5.4754
[7 empty] | 8229 | 165 | 10.4104 | 7.9177
[7 empty] | 8230 | 166 | 8.3727 | 6.32
[7 empty] | 8231 | 167 | 4.7818 | 3.5044
[7 empty] | 8232 | 168 | 4.1387 | 3.0002
[7 empty] | 8233 | 1 | 2.6856 | 1.8609
[7 empty] | 8234 | 2 | 2.5771 | 1.7758
[7 empty] | 8235 | 3 | 2.5687 | 1.7692
[7 empty] | 8236 | 4 | 2.7023 | 1.874
[7 empty] | 8237 | 5 | 2.719 | 1.8871
[7 empty] | 8238 | 6 | 3.1449 | 2.221
[7 empty] | 8239 | 7 | 3.8631 | 2.7841
[7 empty] | 8240 | 8 | 4.5312 | 3.308
[7 empty] | 8241 | 9 | 4.5062 | 3.2883
[7 empty] | 8242 | 10 | 6.0177 | 4.4735
[7 empty] | 8243 | 11 | 8.0888 | 6.0974
[7 empty] | 8244 | 12 | 9.0492 | 6.8504
[7 empty] | 8245 | 13 | 9.425 | 7.1451
[7 empty] | 8246 | 14 | 9.2079 | 6.9748
[7 empty] | 8247 | 15 | 9.116 | 6.9028
[7 empty] | 8248 | 16 | 10.2935 | 7.8261
[7 empty] | 8249 | 17 | 11.613 | 8.8607
[7 empty] | 8250 | 18 | 11.3708 | 8.6708
[7 empty] | 8251 | 19 | 11.8969 | 9.0833
[7 empty] | 8252 | 20 | 11.8301 | 9.0309
[7 empty] | 8253 | 21 | 12.398 | 9.4762
[7 empty] | 8254 | 22 | 8.4563 | 6.3855
[7 empty] | 8255 | 23 | 4.6983 | 3.4389
[7 empty] | 8256 | 24 | 3.0331 | 2.1333
[7 empty] | 8257 | 25 | 2.9362 | 2.0573
[7 empty] | 8258 | 26 | 2.8276 | 1.9722
[7 empty] | 8259 | 27 | 2.7274 | 1.8936
[7 empty] | 8260 | 28 | 2.8109 | 1.9591
[7 empty] | 8261 | 29 | 3.0531 | 2.149
[7 empty] | 8262 | 30 | 3.2953 | 2.3389
[7 empty] | 8263 | 31 | 4.1387 | 3.0002
[7 empty] | 8264 | 32 | 4.4895 | 3.2752
[7 empty] | 8265 | 33 | 5.1492 | 3.7925
[7 empty] | 8266 | 34 | 6.0428 | 4.4932
[7 empty] | 8267 | 35 | 8.2057 | 6.1891
[7 empty] | 8268 | 36 | 9.2329 | 6.9945
[7 empty] | 8269 | 37 | 9.3081 | 7.0534
[7 empty] | 8270 | 38 | 9.3832 | 7.1123
[7 empty] | 8271 | 39 | 9.0575 | 6.857
[7 empty] | 8272 | 40 | 10.1098 | 7.682
[7 empty] | 8273 | 41 | 10.6609 | 8.1142
[7 empty] | 8274 | 42 | 10.6776 | 8.1273
[7 empty] | 8275 | 43 | 11.0451 | 8.4154
[7 empty] | 8276 | 44 | 12.1975 | 9.319
[7 empty] | 8277 | 45 | 11.7967 | 9.0047
[7 empty] | 8278 | 46 | 9.0575 | 6.857
[7 empty] | 8279 | 47 | 5.4666 | 4.0414
[7 empty] | 8280 | 48 | 3.9717 | 2.8693
[7 empty] | 8281 | 49 | 3.312 | 2.352
[7 empty] | 8282 | 50 | 3.003 | 2.1097
[7 empty] | 8283 | 51 | 2.8944 | 2.0246
[7 empty] | 8284 | 52 | 2.9278 | 2.0508
[7 empty] | 8285 | 53 | 2.9529 | 2.0704
[7 empty] | 8286 | 54 | 3.5291 | 2.5222
[7 empty] | 8287 | 55 | 4.6648 | 3.4128
[7 empty] | 8288 | 56 | 4.907 | 3.6026
[7 empty] | 8289 | 57 | 5.8507 | 4.3426
[7 empty] | 8290 | 58 | 6.9531 | 5.2069
[7 empty] | 8291 | 59 | 8.1556 | 6.1498
[7 empty] | 8292 | 60 | 8.7819 | 6.6409
[7 empty] | 8293 | 61 | 9.4584 | 7.1713
[7 empty] | 8294 | 62 | 9.258 | 7.0141
[7 empty] | 8295 | 63 | 9.8509 | 7.479
[7 empty] | 8296 | 64 | 10.7946 | 8.219
[7 empty] | 8297 | 65 | 11.4125 | 8.7035
[7 empty] | 8298 | 66 | 11.3123 | 8.6249
[7 empty] | 8299 | 67 | 12.0472 | 9.2011
[7 empty] | 8300 | 68 | 12.2894 | 9.391
[7 empty] | 8301 | 69 | 11.78 | 8.9916
[7 empty] | 8302 | 70 | 9.4918 | 7.1975
[7 empty] | 8303 | 71 | 4.9905 | 3.6681
[7 empty] | 8304 | 72 | 3.9097 | 2.8206
[7 empty] | 8305 | 73 | 3.1951 | 2.2603
[7 empty] | 8306 | 74 | 2.9696 | 2.0835
[7 empty] | 8307 | 75 | 2.8694 | 2.0049
[7 empty] | 8308 | 76 | 2.8109 | 1.9591
[7 empty] | 8309 | 77 | 2.9863 | 2.0966
[7 empty] | 8310 | 78 | 3.3871 | 2.4109
[7 empty] | 8311 | 79 | 4.4978 | 3.2818
[7 empty] | 8312 | 80 | 4.6732 | 3.4193
[7 empty] | 8313 | 81 | 5.8507 | 4.3426
[7 empty] | 8314 | 82 | 6.9363 | 5.1938
[7 empty] | 8315 | 83 | 7.6712 | 5.77
[7 empty] | 8316 | 84 | 8.9072 | 6.7391
[7 empty] | 8317 | 85 | 8.6066 | 6.5034
[7 empty] | 8318 | 86 | 8.0972 | 6.104
[7 empty] | 8319 | 87 | 8.5398 | 6.451
[7 empty] | 8320 | 88 | 9.1995 | 6.9683
[7 empty] | 8321 | 89 | 10.544 | 8.0225
[7 empty] | 8322 | 90 | 9.9595 | 7.5642
[7 empty] | 8323 | 91 | 10.6442 | 8.1011
[7 empty] | 8324 | 92 | 10.043 | 7.6296
[7 empty] | 8325 | 93 | 7.6378 | 5.7438
[7 empty] | 8326 | 94 | 6.7359 | 5.0366
[7 empty] | 8327 | 95 | 4.882 | 3.583
[7 empty] | 8328 | 96 | 3.8965 | 2.8103
[7 empty] | 8329 | 97 | 3.8464 | 2.7711
[7 empty] | 8330 | 98 | 3.5541 | 2.5419
[7 empty] | 8331 | 99 | 3.4957 | 2.496
[7 empty] | 8332 | 100 | 3.1449 | 2.221
[7 empty] | 8333 | 101 | 3.0865 | 2.1752
[7 empty] | 8334 | 102 | 3.3203 | 2.3585
[7 empty] | 8335 | 103 | 4.0636 | 2.9413
[7 empty] | 8336 | 104 | 4.3141 | 3.1377
[7 empty] | 8337 | 105 | 4.7985 | 3.5175
[7 empty] | 8338 | 106 | 6.2516 | 4.6569
[7 empty] | 8339 | 107 | 6.6023 | 4.9319
[7 empty] | 8340 | 108 | 8.1723 | 6.1629
[7 empty] | 8341 | 109 | 7.5126 | 5.6456
[7 empty] | 8342 | 110 | 7.0616 | 5.292
[7 empty] | 8343 | 111 | 6.9029 | 5.1676
[7 empty] | 8344 | 112 | 6.9698 | 5.22
[7 empty] | 8345 | 113 | 6.6274 | 4.9515
[7 empty] | 8346 | 114 | 6.7944 | 5.0825
[7 empty] | 8347 | 115 | 6.3434 | 4.7289
[7 empty] | 8348 | 116 | 7.0199 | 5.2593
[7 empty] | 8349 | 117 | 6.6023 | 4.9319
[7 empty] | 8350 | 118 | 5.834 | 4.3295
[7 empty] | 8351 | 119 | 4.2473 | 3.0854
[7 empty] | 8352 | 120 | 3.9311 | 2.8374
[7 empty] | 8353 | 121 | 3.2034 | 2.2669
[7 empty] | 8354 | 122 | 2.7942 | 1.946
[7 empty] | 8355 | 123 | 2.7107 | 1.8805
[7 empty] | 8356 | 124 | 2.6773 | 1.8543
[7 empty] | 8357 | 125 | 2.6355 | 1.8216
[7 empty] | 8358 | 126 | 2.7775 | 1.9329
[7 empty] | 8359 | 127 | 4.2807 | 3.1115
[7 empty] | 8360 | 128 | 5.834 | 4.3295
[7 empty] | 8361 | 129 | 6.5104 | 4.8599
[7 empty] | 8362 | 130 | 6.9447 | 5.2003
[7 empty] | 8363 | 131 | 7.1034 | 5.3248
[7 empty] | 8364 | 132 | 6.8528 | 5.1283
[7 empty] | 8365 | 133 | 7.4875 | 5.626
[7 empty] | 8366 | 134 | 7.7882 | 5.8617
[7 empty] | 8367 | 135 | 7.855 | 5.9141
[7 empty] | 8368 | 136 | 7.0449 | 5.2789
[7 empty] | 8369 | 137 | 6.9447 | 5.2003
[7 empty] | 8370 | 138 | 6.8946 | 5.1611
[7 empty] | 8371 | 139 | 6.5605 | 4.8991
[7 empty] | 8372 | 140 | 6.5689 | 4.9057
[7 empty] | 8373 | 141 | 5.9175 | 4.3949
[7 empty] | 8374 | 142 | 5.2828 | 3.8973
[7 empty] | 8375 | 143 | 4.406 | 3.2098
[7 empty] | 8376 | 144 | 3.7963 | 2.7318
[7 empty] | 8377 | 145 | 3.3287 | 2.3651
[7 empty] | 8378 | 146 | 3.1199 | 2.2014
[7 empty] | 8379 | 147 | 3.0531 | 2.149
[7 empty] | 8380 | 148 | 3.0447 | 2.1424
[7 empty] | 8381 | 149 | 3.0447 | 2.1424
[7 empty] | 8382 | 150 | 3.0531 | 2.149
[7 empty] | 8383 | 151 | 4.1304 | 2.9937
[7 empty] | 8384 | 152 | 5.6503 | 4.1854
[7 empty] | 8385 | 153 | 6.2599 | 4.6634
[7 empty] | 8386 | 154 | 6.8194 | 5.1021
[7 empty] | 8387 | 155 | 6.6691 | 4.9843
[7 empty] | 8388 | 156 | 6.8361 | 5.1152
[7 empty] | 8389 | 157 | 7.546 | 5.6718
[7 empty] | 8390 | 158 | 7.8717 | 5.9272
[7 empty] | 8391 | 159 | 8.1389 | 6.1367
[7 empty] | 8392 | 160 | 8.0136 | 6.0385
[7 empty] | 8393 | 161 | 8.7736 | 6.6343
[7 empty] | 8394 | 162 | 8.2809 | 6.248
[7 empty] | 8395 | 163 | 8.64 | 6.5296
[7 empty] | 8396 | 164 | 7.2954 | 5.4754
[7 empty] | 8397 | 165 | 10.4104 | 7.9177
[7 empty] | 8398 | 166 | 8.3727 | 6.32
[7 empty] | 8399 | 167 | 4.7818 | 3.5044
[7 empty] | 8400 | 168 | 4.1387 | 3.0002
[7 empty] | 8401 | 1 | 2.6856 | 1.8609
[7 empty] | 8402 | 2 | 2.5771 | 1.7758
[7 empty] | 8403 | 3 | 2.5687 | 1.7692
[7 empty] | 8404 | 4 | 2.7023 | 1.874
[7 empty] | 8405 | 5 | 2.719 | 1.8871
[7 empty] | 8406 | 6 | 3.1449 | 2.221
[7 empty] | 8407 | 7 | 3.8631 | 2.7841
[7 empty] | 8408 | 8 | 4.5312 | 3.308
[7 empty] | 8409 | 9 | 4.5062 | 3.2883
[7 empty] | 8410 | 10 | 6.0177 | 4.4735
[7 empty] | 8411 | 11 | 8.0888 | 6.0974
[7 empty] | 8412 | 12 | 9.0492 | 6.8504
[7 empty] | 8413 | 13 | 9.425 | 7.1451
[7 empty] | 8414 | 14 | 9.2079 | 6.9748
[7 empty] | 8415 | 15 | 9.116 | 6.9028
[7 empty] | 8416 | 16 | 10.2935 | 7.8261
[7 empty] | 8417 | 17 | 11.613 | 8.8607
[7 empty] | 8418 | 18 | 11.3708 | 8.6708
[7 empty] | 8419 | 19 | 11.8969 | 9.0833
[7 empty] | 8420 | 20 | 11.8301 | 9.0309
[7 empty] | 8421 | 21 | 12.398 | 9.4762
[7 empty] | 8422 | 22 | 8.4563 | 6.3855
[7 empty] | 8423 | 23 | 4.6983 | 3.4389
[7 empty] | 8424 | 24 | 3.0331 | 2.1333
[7 empty] | 8425 | 25 | 2.9362 | 2.0573
[7 empty] | 8426 | 26 | 2.8276 | 1.9722
[7 empty] | 8427 | 27 | 2.7274 | 1.8936
[7 empty] | 8428 | 28 | 2.8109 | 1.9591
[7 empty] | 8429 | 29 | 3.0531 | 2.149
[7 empty] | 8430 | 30 | 3.2953 | 2.3389
[7 empty] | 8431 | 31 | 4.1387 | 3.0002
[7 empty] | 8432 | 32 | 4.4895 | 3.2752
[7 empty] | 8433 | 33 | 5.1492 | 3.7925
[7 empty] | 8434 | 34 | 6.0428 | 4.4932
[7 empty] | 8435 | 35 | 8.2057 | 6.1891
[7 empty] | 8436 | 36 | 9.2329 | 6.9945
[7 empty] | 8437 | 37 | 9.3081 | 7.0534
[7 empty] | 8438 | 38 | 9.3832 | 7.1123
[7 empty] | 8439 | 39 | 9.0575 | 6.857
[7 empty] | 8440 | 40 | 10.1098 | 7.682
[7 empty] | 8441 | 41 | 10.6609 | 8.1142
[7 empty] | 8442 | 42 | 10.6776 | 8.1273
[7 empty] | 8443 | 43 | 11.0451 | 8.4154
[7 empty] | 8444 | 44 | 12.1975 | 9.319
[7 empty] | 8445 | 45 | 11.7967 | 9.0047
[7 empty] | 8446 | 46 | 9.0575 | 6.857
[7 empty] | 8447 | 47 | 5.4666 | 4.0414
[7 empty] | 8448 | 48 | 3.9717 | 2.8693
[7 empty] | 8449 | 49 | 3.312 | 2.352
[7 empty] | 8450 | 50 | 3.003 | 2.1097
[7 empty] | 8451 | 51 | 2.8944 | 2.0246
[7 empty] | 8452 | 52 | 2.9278 | 2.0508
[7 empty] | 8453 | 53 | 2.9529 | 2.0704
[7 empty] | 8454 | 54 | 3.5291 | 2.5222
[7 empty] | 8455 | 55 | 4.6648 | 3.4128
[7 empty] | 8456 | 56 | 4.907 | 3.6026
[7 empty] | 8457 | 57 | 5.8507 | 4.3426
[7 empty] | 8458 | 58 | 6.9531 | 5.2069
[7 empty] | 8459 | 59 | 8.1556 | 6.1498
[7 empty] | 8460 | 60 | 8.7819 | 6.6409
[7 empty] | 8461 | 61 | 9.4584 | 7.1713
[7 empty] | 8462 | 62 | 9.258 | 7.0141
[7 empty] | 8463 | 63 | 9.8509 | 7.479
[7 empty] | 8464 | 64 | 10.7946 | 8.219
[7 empty] | 8465 | 65 | 11.4125 | 8.7035
[7 empty] | 8466 | 66 | 11.3123 | 8.6249
[7 empty] | 8467 | 67 | 12.0472 | 9.2011
[7 empty] | 8468 | 68 | 12.2894 | 9.391
[7 empty] | 8469 | 69 | 11.78 | 8.9916
[7 empty] | 8470 | 70 | 9.4918 | 7.1975
[7 empty] | 8471 | 71 | 4.9905 | 3.6681
[7 empty] | 8472 | 72 | 3.9097 | 2.8206
[7 empty] | 8473 | 73 | 3.1951 | 2.2603
[7 empty] | 8474 | 74 | 2.9696 | 2.0835
[7 empty] | 8475 | 75 | 2.8694 | 2.0049
[7 empty] | 8476 | 76 | 2.8109 | 1.9591
[7 empty] | 8477 | 77 | 2.9863 | 2.0966
[7 empty] | 8478 | 78 | 3.3871 | 2.4109
[7 empty] | 8479 | 79 | 4.4978 | 3.2818
[7 empty] | 8480 | 80 | 4.6732 | 3.4193
[7 empty] | 8481 | 81 | 5.8507 | 4.3426
[7 empty] | 8482 | 82 | 6.9363 | 5.1938
[7 empty] | 8483 | 83 | 7.6712 | 5.77
[7 empty] | 8484 | 84 | 8.9072 | 6.7391
[7 empty] | 8485 | 85 | 8.6066 | 6.5034
[7 empty] | 8486 | 86 | 8.0972 | 6.104
[7 empty] | 8487 | 87 | 8.5398 | 6.451
[7 empty] | 8488 | 88 | 9.1995 | 6.9683
[7 empty] | 8489 | 89 | 10.544 | 8.0225
[7 empty] | 8490 | 90 | 9.9595 | 7.5642
[7 empty] | 8491 | 91 | 10.6442 | 8.1011
[7 empty] | 8492 | 92 | 10.043 | 7.6296
[7 empty] | 8493 | 93 | 7.6378 | 5.7438
[7 empty] | 8494 | 94 | 6.7359 | 5.0366
[7 empty] | 8495 | 95 | 4.882 | 3.583
[7 empty] | 8496 | 96 | 3.8965 | 2.8103
[7 empty] | 8497 | 97 | 3.8464 | 2.7711
[7 empty] | 8498 | 98 | 3.5541 | 2.5419
[7 empty] | 8499 | 99 | 3.4957 | 2.496
[7 empty] | 8500 | 100 | 3.1449 | 2.221
[7 empty] | 8501 | 101 | 3.0865 | 2.1752
[7 empty] | 8502 | 102 | 3.3203 | 2.3585
[7 empty] | 8503 | 103 | 4.0636 | 2.9413
[7 empty] | 8504 | 104 | 4.3141 | 3.1377
[7 empty] | 8505 | 105 | 4.7985 | 3.5175
[7 empty] | 8506 | 106 | 6.2516 | 4.6569
[7 empty] | 8507 | 107 | 6.6023 | 4.9319
[7 empty] | 8508 | 108 | 8.1723 | 6.1629
[7 empty] | 8509 | 109 | 7.5126 | 5.6456
[7 empty] | 8510 | 110 | 7.0616 | 5.292
[7 empty] | 8511 | 111 | 6.9029 | 5.1676
[7 empty] | 8512 | 112 | 6.9698 | 5.22
[7 empty] | 8513 | 113 | 6.6274 | 4.9515
[7 empty] | 8514 | 114 | 6.7944 | 5.0825
[7 empty] | 8515 | 115 | 6.3434 | 4.7289
[7 empty] | 8516 | 116 | 7.0199 | 5.2593
[7 empty] | 8517 | 117 | 6.6023 | 4.9319
[7 empty] | 8518 | 118 | 5.834 | 4.3295
[7 empty] | 8519 | 119 | 4.2473 | 3.0854
[7 empty] | 8520 | 120 | 3.9311 | 2.8374
[7 empty] | 8521 | 121 | 3.2034 | 2.2669
[7 empty] | 8522 | 122 | 2.7942 | 1.946
[7 empty] | 8523 | 123 | 2.7107 | 1.8805
[7 empty] | 8524 | 124 | 2.6773 | 1.8543
[7 empty] | 8525 | 125 | 2.6355 | 1.8216
[7 empty] | 8526 | 126 | 2.7775 | 1.9329
[7 empty] | 8527 | 127 | 4.2807 | 3.1115
[7 empty] | 8528 | 128 | 5.834 | 4.3295
[7 empty] | 8529 | 129 | 6.5104 | 4.8599
[7 empty] | 8530 | 130 | 6.9447 | 5.2003
[7 empty] | 8531 | 131 | 7.1034 | 5.3248
[7 empty] | 8532 | 132 | 6.8528 | 5.1283
[7 empty] | 8533 | 133 | 7.4875 | 5.626
[7 empty] | 8534 | 134 | 7.7882 | 5.8617
[7 empty] | 8535 | 135 | 7.855 | 5.9141
[7 empty] | 8536 | 136 | 7.0449 | 5.2789
[7 empty] | 8537 | 137 | 6.9447 | 5.2003
[7 empty] | 8538 | 138 | 6.8946 | 5.1611
[7 empty] | 8539 | 139 | 6.5605 | 4.8991
[7 empty] | 8540 | 140 | 6.5689 | 4.9057
[7 empty] | 8541 | 141 | 5.9175 | 4.3949
[7 empty] | 8542 | 142 | 5.2828 | 3.8973
[7 empty] | 8543 | 143 | 4.406 | 3.2098
[7 empty] | 8544 | 144 | 3.7963 | 2.7318
[7 empty] | 8545 | 145 | 3.3287 | 2.3651
[7 empty] | 8546 | 146 | 3.1199 | 2.2014
[7 empty] | 8547 | 147 | 3.0531 | 2.149
[7 empty] | 8548 | 148 | 3.0447 | 2.1424
[7 empty] | 8549 | 149 | 3.0447 | 2.1424
[7 empty] | 8550 | 150 | 3.0531 | 2.149
[7 empty] | 8551 | 151 | 4.1304 | 2.9937
[7 empty] | 8552 | 152 | 5.6503 | 4.1854
[7 empty] | 8553 | 153 | 6.2599 | 4.6634
[7 empty] | 8554 | 154 | 6.8194 | 5.1021
[7 empty] | 8555 | 155 | 6.6691 | 4.9843
[7 empty] | 8556 | 156 | 6.8361 | 5.1152
[7 empty] | 8557 | 157 | 7.546 | 5.6718
[7 empty] | 8558 | 158 | 7.8717 | 5.9272
[7 empty] | 8559 | 159 | 8.1389 | 6.1367
[7 empty] | 8560 | 160 | 8.0136 | 6.0385
[7 empty] | 8561 | 161 | 8.7736 | 6.6343
[7 empty] | 8562 | 162 | 8.2809 | 6.248
[7 empty] | 8563 | 163 | 8.64 | 6.5296
[7 empty] | 8564 | 164 | 7.2954 | 5.4754
[7 empty] | 8565 | 165 | 10.4104 | 7.9177
[7 empty] | 8566 | 166 | 8.3727 | 6.32
[7 empty] | 8567 | 167 | 4.7818 | 3.5044
[7 empty] | 8568 | 168 | 4.1387 | 3.0002
[7 empty] | 8569 | 1 | 2.6856 | 1.8609
[7 empty] | 8570 | 2 | 2.5771 | 1.7758
[7 empty] | 8571 | 3 | 2.5687 | 1.7692
[7 empty] | 8572 | 4 | 2.7023 | 1.874
[7 empty] | 8573 | 5 | 2.719 | 1.8871
[7 empty] | 8574 | 6 | 3.1449 | 2.221
[7 empty] | 8575 | 7 | 3.8631 | 2.7841
[7 empty] | 8576 | 8 | 4.5312 | 3.308
[7 empty] | 8577 | 9 | 4.5062 | 3.2883
[7 empty] | 8578 | 10 | 6.0177 | 4.4735
[7 empty] | 8579 | 11 | 8.0888 | 6.0974
[7 empty] | 8580 | 12 | 9.0492 | 6.8504
[7 empty] | 8581 | 13 | 9.425 | 7.1451
[7 empty] | 8582 | 14 | 9.2079 | 6.9748
[7 empty] | 8583 | 15 | 9.116 | 6.9028
[7 empty] | 8584 | 16 | 10.2935 | 7.8261
[7 empty] | 8585 | 17 | 11.613 | 8.8607
[7 empty] | 8586 | 18 | 11.3708 | 8.6708
[7 empty] | 8587 | 19 | 11.8969 | 9.0833
[7 empty] | 8588 | 20 | 11.8301 | 9.0309
[7 empty] | 8589 | 21 | 12.398 | 9.4762
[7 empty] | 8590 | 22 | 8.4563 | 6.3855
[7 empty] | 8591 | 23 | 4.6983 | 3.4389
[7 empty] | 8592 | 24 | 3.0331 | 2.1333
[7 empty] | 8593 | 25 | 2.9362 | 2.0573
[7 empty] | 8594 | 26 | 2.8276 | 1.9722
[7 empty] | 8595 | 27 | 2.7274 | 1.8936
[7 empty] | 8596 | 28 | 2.8109 | 1.9591
[7 empty] | 8597 | 29 | 3.0531 | 2.149
[7 empty] | 8598 | 30 | 3.2953 | 2.3389
[7 empty] | 8599 | 31 | 4.1387 | 3.0002
[7 empty] | 8600 | 32 | 4.4895 | 3.2752
[7 empty] | 8601 | 33 | 5.1492 | 3.7925
[7 empty] | 8602 | 34 | 6.0428 | 4.4932
[7 empty] | 8603 | 35 | 8.2057 | 6.1891
[7 empty] | 8604 | 36 | 9.2329 | 6.9945
[7 empty] | 8605 | 37 | 9.3081 | 7.0534
[7 empty] | 8606 | 38 | 9.3832 | 7.1123
[7 empty] | 8607 | 39 | 9.0575 | 6.857
[7 empty] | 8608 | 40 | 10.1098 | 7.682
[7 empty] | 8609 | 41 | 10.6609 | 8.1142
[7 empty] | 8610 | 42 | 10.6776 | 8.1273
[7 empty] | 8611 | 43 | 11.0451 | 8.4154
[7 empty] | 8612 | 44 | 12.1975 | 9.319
[7 empty] | 8613 | 45 | 11.7967 | 9.0047
[7 empty] | 8614 | 46 | 9.0575 | 6.857
[7 empty] | 8615 | 47 | 5.4666 | 4.0414
[7 empty] | 8616 | 48 | 3.9717 | 2.8693
[7 empty] | 8617 | 49 | 3.312 | 2.352
[7 empty] | 8618 | 50 | 3.003 | 2.1097
[7 empty] | 8619 | 51 | 2.8944 | 2.0246
[7 empty] | 8620 | 52 | 2.9278 | 2.0508
[7 empty] | 8621 | 53 | 2.9529 | 2.0704
[7 empty] | 8622 | 54 | 3.5291 | 2.5222
[7 empty] | 8623 | 55 | 4.6648 | 3.4128
[7 empty] | 8624 | 56 | 4.907 | 3.6026
[7 empty] | 8625 | 57 | 5.8507 | 4.3426
[7 empty] | 8626 | 58 | 6.9531 | 5.2069
[7 empty] | 8627 | 59 | 8.1556 | 6.1498
[7 empty] | 8628 | 60 | 8.7819 | 6.6409
[7 empty] | 8629 | 61 | 9.4584 | 7.1713
[7 empty] | 8630 | 62 | 9.258 | 7.0141
[7 empty] | 8631 | 63 | 9.8509 | 7.479
[7 empty] | 8632 | 64 | 10.7946 | 8.219
[7 empty] | 8633 | 65 | 11.4125 | 8.7035
[7 empty] | 8634 | 66 | 11.3123 | 8.6249
[7 empty] | 8635 | 67 | 12.0472 | 9.2011
[7 empty] | 8636 | 68 | 12.2894 | 9.391
[7 empty] | 8637 | 69 | 11.78 | 8.9916
[7 empty] | 8638 | 70 | 9.4918 | 7.1975
[7 empty] | 8639 | 71 | 4.9905 | 3.6681
[7 empty] | 8640 | 72 | 3.9097 | 2.8206
[7 empty] | 8641 | 73 | 3.1951 | 2.2603
[7 empty] | 8642 | 74 | 2.9696 | 2.0835
[7 empty] | 8643 | 75 | 2.8694 | 2.0049
[7 empty] | 8644 | 76 | 2.8109 | 1.9591
[7 empty] | 8645 | 77 | 2.9863 | 2.0966
[7 empty] | 8646 | 78 | 3.3871 | 2.4109
[7 empty] | 8647 | 79 | 4.4978 | 3.2818
[7 empty] | 8648 | 80 | 4.6732 | 3.4193
[7 empty] | 8649 | 81 | 5.8507 | 4.3426
[7 empty] | 8650 | 82 | 6.9363 | 5.1938
[7 empty] | 8651 | 83 | 7.6712 | 5.77
[7 empty] | 8652 | 84 | 8.9072 | 6.7391
[7 empty] | 8653 | 85 | 8.6066 | 6.5034
[7 empty] | 8654 | 86 | 8.0972 | 6.104
[7 empty] | 8655 | 87 | 8.5398 | 6.451
[7 empty] | 8656 | 88 | 9.1995 | 6.9683
[7 empty] | 8657 | 89 | 10.544 | 8.0225
[7 empty] | 8658 | 90 | 9.9595 | 7.5642
[7 empty] | 8659 | 91 | 10.6442 | 8.1011
[7 empty] | 8660 | 92 | 10.043 | 7.6296
[7 empty] | 8661 | 93 | 7.6378 | 5.7438
[7 empty] | 8662 | 94 | 6.7359 | 5.0366
[7 empty] | 8663 | 95 | 4.882 | 3.583
[7 empty] | 8664 | 96 | 3.8965 | 2.8103
[7 empty] | 8665 | 97 | 3.8464 | 2.7711
[7 empty] | 8666 | 98 | 3.5541 | 2.5419
[7 empty] | 8667 | 99 | 3.4957 | 2.496
[7 empty] | 8668 | 100 | 3.1449 | 2.221
[7 empty] | 8669 | 101 | 3.0865 | 2.1752
[7 empty] | 8670 | 102 | 3.3203 | 2.3585
[7 empty] | 8671 | 103 | 4.0636 | 2.9413
[7 empty] | 8672 | 104 | 4.3141 | 3.1377
[7 empty] | 8673 | 105 | 4.7985 | 3.5175
[7 empty] | 8674 | 106 | 6.2516 | 4.6569
[7 empty] | 8675 | 107 | 6.6023 | 4.9319
[7 empty] | 8676 | 108 | 8.1723 | 6.1629
[7 empty] | 8677 | 109 | 7.5126 | 5.6456
[7 empty] | 8678 | 110 | 7.0616 | 5.292
[7 empty] | 8679 | 111 | 6.9029 | 5.1676
[7 empty] | 8680 | 112 | 6.9698 | 5.22
[7 empty] | 8681 | 113 | 6.6274 | 4.9515
[7 empty] | 8682 | 114 | 6.7944 | 5.0825
[7 empty] | 8683 | 115 | 6.3434 | 4.7289
[7 empty] | 8684 | 116 | 7.0199 | 5.2593
[7 empty] | 8685 | 117 | 6.6023 | 4.9319
[7 empty] | 8686 | 118 | 5.834 | 4.3295
[7 empty] | 8687 | 119 | 4.2473 | 3.0854
[7 empty] | 8688 | 120 | 3.9311 | 2.8374
[7 empty] | 8689 | 121 | 3.2034 | 2.2669
[7 empty] | 8690 | 122 | 2.7942 | 1.946
[7 empty] | 8691 | 123 | 2.7107 | 1.8805
[7 empty] | 8692 | 124 | 2.6773 | 1.8543
[7 empty] | 8693 | 125 | 2.6355 | 1.8216
[7 empty] | 8694 | 126 | 2.7775 | 1.9329
[7 empty] | 8695 | 127 | 4.2807 | 3.1115
[7 empty] | 8696 | 128 | 5.834 | 4.3295
[7 empty] | 8697 | 129 | 6.5104 | 4.8599
[7 empty] | 8698 | 130 | 6.9447 | 5.2003
[7 empty] | 8699 | 131 | 7.1034 | 5.3248
[7 empty] | 8700 | 132 | 6.8528 | 5.1283
[7 empty] | 8701 | 133 | 7.4875 | 5.626
[7 empty] | 8702 | 134 | 7.7882 | 5.8617
[7 empty] | 8703 | 135 | 7.855 | 5.9141
[7 empty] | 8704 | 136 | 7.0449 | 5.2789
[7 empty] | 8705 | 137 | 6.9447 | 5.2003
[7 empty] | 8706 | 138 | 6.8946 | 5.1611
[7 empty] | 8707 | 139 | 6.5605 | 4.8991
[7 empty] | 8708 | 140 | 6.5689 | 4.9057
[7 empty] | 8709 | 141 | 5.9175 | 4.3949
[7 empty] | 8710 | 142 | 5.2828 | 3.8973
[7 empty] | 8711 | 143 | 4.406 | 3.2098
[7 empty] | 8712 | 144 | 3.7963 | 2.7318
[7 empty] | 8713 | 145 | 3.3287 | 2.3651
[7 empty] | 8714 | 146 | 3.1199 | 2.2014
[7 empty] | 8715 | 147 | 3.0531 | 2.149
[7 empty] | 8716 | 148 | 3.0447 | 2.1424
[7 empty] | 8717 | 149 | 3.0447 | 2.1424
[7 empty] | 8718 | 150 | 3.0531 | 2.149
[7 empty] | 8719 | 151 | 4.1304 | 2.9937
[7 empty] | 8720 | 152 | 5.6503 | 4.1854
[7 empty] | 8721 | 153 | 6.2599 | 4.6634
[7 empty] | 8722 | 154 | 6.8194 | 5.1021
[7 empty] | 8723 | 155 | 6.6691 | 4.9843
[7 empty] | 8724 | 156 | 6.8361 | 5.1152
[7 empty] | 8725 | 157 | 7.546 | 5.6718
[7 empty] | 8726 | 158 | 7.8717 | 5.9272
[7 empty] | 8727 | 159 | 8.1389 | 6.1367
[7 empty] | 8728 | 160 | 8.0136 | 6.0385
[7 empty] | 8729 | 161 | 8.7736 | 6.6343
[7 empty] | 8730 | 162 | 8.2809 | 6.248
[7 empty] | 8731 | 163 | 8.64 | 6.5296
[7 empty] | 8732 | 164 | 7.2954 | 5.4754
[7 empty] | 8733 | 165 | 10.4104 | 7.9177
[7 empty] | 8734 | 166 | 8.3727 | 6.32
[7 empty] | 8735 | 167 | 4.7818 | 3.5044
[7 empty] | 8736 | 168 | 4.1387 | 3.0002
[7 empty] | 8737 | 1 | 2.6856 | 1.8609
[7 empty] | 8738 | 2 | 2.5771 | 1.7758
[7 empty] | 8739 | 3 | 2.5687 | 1.7692
[7 empty] | 8740 | 4 | 2.7023 | 1.874
[7 empty] | 8741 | 5 | 2.719 | 1.8871
[7 empty] | 8742 | 6 | 3.1449 | 2.221
[7 empty] | 8743 | 7 | 3.8631 | 2.7841
[7 empty] | 8744 | 8 | 4.5312 | 3.308
[7 empty] | 8745 | 9 | 4.5062 | 3.2883
[7 empty] | 8746 | 10 | 6.0177 | 4.4735
[7 empty] | 8747 | 11 | 8.0888 | 6.0974
[7 empty] | 8748 | 12 | 9.0492 | 6.8504
[7 empty] | 8749 | 13 | 9.425 | 7.1451
[7 empty] | 8750 | 14 | 9.2079 | 6.9748
[7 empty] | 8751 | 15 | 9.116 | 6.9028
[7 empty] | 8752 | 16 | 10.2935 | 7.8261
[7 empty] | 8753 | 17 | 11.613 | 8.8607
[7 empty] | 8754 | 18 | 11.3708 | 8.6708
[7 empty] | 8755 | 19 | 11.8969 | 9.0833
[7 empty] | 8756 | 20 | 11.8301 | 9.0309
[7 empty] | 8757 | 21 | 12.398 | 9.4762
[7 empty] | 8758 | 22 | 8.4563 | 6.3855
[7 empty] | 8759 | 23 | 4.6983 | 3.4389
[7 empty] | 8760 | 24 | 3.0331 | 2.1333

## DC_2019
Hour | Server | Non-server | Total | Unit: MW | PUE | PUE-Max | Hour-year | Hour-week | Total (MWh) | Server (MWh)
1 | 1.6738 | 0.70721 | 2.381 |  | 1.3 | 1.2647 | 1 | 1 | 2.381 | 1.6738
2 | 1.5867 | 0.68711 | 2.2738 |  |  |  | 2 | 2 | 2.2738 | 1.5867
3 | 1.58 | 0.68557 | 2.2656 |  | Server-Max | Total-Max | 3 | 3 | 2.2656 | 1.58
4 | 1.6872 | 0.71031 | 2.3975 |  | 9.4641 | 11.9696 | 4 | 4 | 2.3975 | 1.6872
5 | 1.7006 | 0.7134 | 2.414 |  |  |  | 5 | 5 | 2.414 | 1.7006
6 | 2.0422 | 0.79225 | 2.8345 |  | Assumed max utilization rate (UR) |  | 6 | 6 | 2.8345 | 2.0422
7 | 2.6183 | 0.92523 | 3.5435 |  | 65% |  | 7 | 7 | 3.5435 | 2.6183
8 | 3.1541 | 1.0489 | 4.2031 |  |  |  | 8 | 8 | 4.2031 | 3.1541
9 | 3.134 | 1.0443 | 4.1783 |  | Servers energy at max UR | Total energy at max UR | 9 | 9 | 4.1783 | 3.134
10 | 4.3465 | 1.3241 | 5.6706 |  | 6.885 | 8.7951 | 10 | 10 | 5.6706 | 4.3465
11 | 6.0077 | 1.7076 | 7.7153 |  |  |  | 11 | 11 | 7.7153 | 6.0077
12 | 6.778 | 1.8854 | 8.6634 |  | Non-server power linear model scaling factor |  | 12 | 12 | 8.6634 | 6.778
13 | 7.0795 | 1.955 | 9.0344 |  | 0.22547 |  | 13 | 13 | 9.0344 | 7.0795
14 | 6.9053 | 1.9148 | 8.8201 |  |  |  | 14 | 14 | 8.8201 | 6.9053
15 | 6.8316 | 1.8978 | 8.7294 |  |  |  | 15 | 15 | 8.7294 | 6.8316
16 | 7.7761 | 2.1158 | 9.8919 |  |  |  | 16 | 16 | 9.8919 | 7.7761
17 | 8.8345 | 2.3601 | 11.1946 |  |  |  | 17 | 17 | 11.1946 | 8.8345
18 | 8.6402 | 2.3153 | 10.9555 |  |  |  | 18 | 18 | 10.9555 | 8.6402
19 | 9.0622 | 2.4127 | 11.4749 |  |  |  | 19 | 19 | 11.4749 | 9.0622
20 | 9.0086 | 2.4003 | 11.4089 |  |  |  | 20 | 20 | 11.4089 | 9.0086
21 | 9.4641 | 2.5054 | 11.9696 |  |  |  | 21 | 21 | 11.9696 | 9.4641
22 | 6.3024 | 1.7756 | 8.0781 |  |  |  | 22 | 22 | 8.0781 | 6.3024
23 | 3.2881 | 1.0798 | 4.368 |  |  |  | 23 | 23 | 4.368 | 3.2881
24 | 1.9525 | 0.77155 | 2.724 |  |  |  | 24 | 24 | 2.724 | 1.9525
25 | 1.8747 | 0.7536 | 2.6283 |  |  |  | 25 | 25 | 2.6283 | 1.8747
26 | 1.7877 | 0.7335 | 2.5212 |  |  |  | 26 | 26 | 2.5212 | 1.7877
27 | 1.7073 | 0.71495 | 2.4222 |  |  |  | 27 | 27 | 2.4222 | 1.7073
28 | 1.7743 | 0.73041 | 2.5047 |  |  |  | 28 | 28 | 2.5047 | 1.7743
29 | 1.9685 | 0.77525 | 2.7438 |  |  |  | 29 | 29 | 2.7438 | 1.9685
30 | 2.1628 | 0.82009 | 2.9829 |  |  |  | 30 | 30 | 2.9829 | 2.1628
31 | 2.8393 | 0.97625 | 3.8156 |  |  |  | 31 | 31 | 3.8156 | 2.8393
32 | 3.1207 | 1.0412 | 4.1618 |  |  |  | 32 | 32 | 4.1618 | 3.1207
33 | 3.6498 | 1.1633 | 4.8132 |  |  |  | 33 | 33 | 4.8132 | 3.6498
34 | 4.3666 | 1.3288 | 5.6954 |  |  |  | 34 | 34 | 5.6954 | 4.3666
35 | 6.1015 | 1.7292 | 7.8307 |  |  |  | 35 | 35 | 7.8307 | 6.1015
36 | 6.9254 | 1.9194 | 8.8448 |  |  |  | 36 | 36 | 8.8448 | 6.9254
37 | 6.9857 | 1.9333 | 8.919 |  |  |  | 37 | 37 | 8.919 | 6.9857
38 | 7.046 | 1.9473 | 8.9932 |  |  |  | 38 | 38 | 8.9932 | 7.046
39 | 6.7847 | 1.887 | 8.6717 |  |  |  | 39 | 39 | 8.6717 | 6.7847
40 | 7.6287 | 2.0818 | 9.7105 |  |  |  | 40 | 40 | 9.7105 | 7.6287
41 | 8.0708 | 2.1838 | 10.2547 |  |  |  | 41 | 41 | 10.2547 | 8.0708
42 | 8.0842 | 2.1869 | 10.2711 |  |  |  | 42 | 42 | 10.2711 | 8.0842
43 | 8.379 | 2.2549 | 10.6339 |  |  |  | 43 | 43 | 10.6339 | 8.379
44 | 9.3034 | 2.4683 | 11.7717 |  |  |  | 44 | 44 | 11.7717 | 9.3034
45 | 8.9818 | 2.3941 | 11.3759 |  |  |  | 45 | 45 | 11.3759 | 8.9818
46 | 6.7847 | 1.887 | 8.6717 |  |  |  | 46 | 46 | 8.6717 | 6.7847
47 | 3.9044 | 1.2221 | 5.1265 |  |  |  | 47 | 47 | 5.1265 | 3.9044
48 | 2.7053 | 0.94533 | 3.6507 |  |  |  | 48 | 48 | 3.6507 | 2.7053
49 | 2.1762 | 0.82318 | 2.9993 |  |  |  | 49 | 49 | 2.9993 | 2.1762
50 | 1.9283 | 0.76597 | 2.6943 |  |  |  | 50 | 50 | 2.6943 | 1.9283
51 | 1.8412 | 0.74587 | 2.5871 |  |  |  | 51 | 51 | 2.5871 | 1.8412
52 | 1.868 | 0.75205 | 2.6201 |  |  |  | 52 | 52 | 2.6201 | 1.868
53 | 1.8881 | 0.75669 | 2.6448 |  |  |  | 53 | 53 | 2.6448 | 1.8881
54 | 2.3503 | 0.86338 | 3.2137 |  |  |  | 54 | 54 | 3.2137 | 2.3503
55 | 3.2613 | 1.0737 | 4.335 |  |  |  | 55 | 55 | 4.335 | 3.2613
56 | 3.4556 | 1.1185 | 4.5741 |  |  |  | 56 | 56 | 4.5741 | 3.4556
57 | 4.2125 | 1.2932 | 5.5057 |  |  |  | 57 | 57 | 5.5057 | 4.2125
58 | 5.0967 | 1.4973 | 6.594 |  |  |  | 58 | 58 | 6.594 | 5.0967
59 | 6.0613 | 1.72 | 7.7813 |  |  |  | 59 | 59 | 7.7813 | 6.0613
60 | 6.5637 | 1.8359 | 8.3996 |  |  |  | 60 | 60 | 8.3996 | 6.5637
61 | 7.1063 | 1.9612 | 9.0674 |  |  |  | 61 | 61 | 9.0674 | 7.1063
62 | 6.9455 | 1.9241 | 8.8696 |  |  |  | 62 | 62 | 8.8696 | 6.9455
63 | 7.4211 | 2.0338 | 9.4549 |  |  |  | 63 | 63 | 9.4549 | 7.4211
64 | 8.178 | 2.2086 | 10.3866 |  |  |  | 64 | 64 | 10.3866 | 8.178
65 | 8.6737 | 2.323 | 10.9967 |  |  |  | 65 | 65 | 10.9967 | 8.6737
66 | 8.5933 | 2.3044 | 10.8977 |  |  |  | 66 | 66 | 10.8977 | 8.5933
67 | 9.1828 | 2.4405 | 11.6233 |  |  |  | 67 | 67 | 11.6233 | 9.1828
68 | 9.377 | 2.4853 | 11.8624 |  |  |  | 68 | 68 | 11.8624 | 9.377
69 | 8.9684 | 2.391 | 11.3594 |  |  |  | 69 | 69 | 11.3594 | 8.9684
70 | 7.133 | 1.9674 | 9.1004 |  |  |  | 70 | 70 | 9.1004 | 7.133
71 | 3.5226 | 1.134 | 4.6565 |  |  |  | 71 | 71 | 4.6565 | 3.5226
72 | 2.6556 | 0.93384 | 3.5894 |  |  |  | 72 | 72 | 3.5894 | 2.6556
73 | 2.0824 | 0.80153 | 2.8839 |  |  |  | 73 | 73 | 2.8839 | 2.0824
74 | 1.9015 | 0.75978 | 2.6613 |  |  |  | 74 | 74 | 2.6613 | 1.9015
75 | 1.8211 | 0.74123 | 2.5624 |  |  |  | 75 | 75 | 2.5624 | 1.8211
76 | 1.7743 | 0.73041 | 2.5047 |  |  |  | 76 | 76 | 2.5047 | 1.7743
77 | 1.9149 | 0.76288 | 2.6778 |  |  |  | 77 | 77 | 2.6778 | 1.9149
78 | 2.2365 | 0.83709 | 3.0735 |  |  |  | 78 | 78 | 3.0735 | 2.2365
79 | 3.1274 | 1.0427 | 4.1701 |  |  |  | 79 | 79 | 4.1701 | 3.1274
80 | 3.268 | 1.0752 | 4.3432 |  |  |  | 80 | 80 | 4.3432 | 3.268
81 | 4.2125 | 1.2932 | 5.5057 |  |  |  | 81 | 81 | 5.5057 | 4.2125
82 | 5.0833 | 1.4942 | 6.5775 |  |  |  | 82 | 82 | 6.5775 | 5.0833
83 | 5.6728 | 1.6303 | 7.3031 |  |  |  | 83 | 83 | 7.3031 | 5.6728
84 | 6.6642 | 1.8591 | 8.5233 |  |  |  | 84 | 84 | 8.5233 | 6.6642
85 | 6.423 | 1.8035 | 8.2265 |  |  |  | 85 | 85 | 8.2265 | 6.423
86 | 6.0144 | 1.7091 | 7.7235 |  |  |  | 86 | 86 | 7.7235 | 6.0144
87 | 6.3694 | 1.7911 | 8.1605 |  |  |  | 87 | 87 | 8.1605 | 6.3694
88 | 6.8986 | 1.9132 | 8.8118 |  |  |  | 88 | 88 | 8.8118 | 6.8986
89 | 7.9771 | 2.1622 | 10.1392 |  |  |  | 89 | 89 | 10.1392 | 7.9771
90 | 7.5082 | 2.0539 | 9.5621 |  |  |  | 90 | 90 | 9.5621 | 7.5082
91 | 8.0574 | 2.1807 | 10.2382 |  |  |  | 91 | 91 | 10.2382 | 8.0574
92 | 7.5751 | 2.0694 | 9.6446 |  |  |  | 92 | 92 | 9.6446 | 7.5751
93 | 5.646 | 1.6241 | 7.2701 |  |  |  | 93 | 93 | 7.2701 | 5.646
94 | 4.9225 | 1.4571 | 6.3797 |  |  |  | 94 | 94 | 6.3797 | 4.9225
95 | 3.4355 | 1.1139 | 4.5493 |  |  |  | 95 | 95 | 4.5493 | 3.4355
96 | 2.6451 | 0.93141 | 3.5765 |  |  |  | 96 | 96 | 3.5765 | 2.6451
97 | 2.6049 | 0.92213 | 3.527 |  |  |  | 97 | 97 | 3.527 | 2.6049
98 | 2.3704 | 0.86802 | 3.2384 |  |  |  | 98 | 98 | 3.2384 | 2.3704
99 | 2.3235 | 0.85719 | 3.1807 |  |  |  | 99 | 99 | 3.1807 | 2.3235
100 | 2.0422 | 0.79225 | 2.8345 |  |  |  | 100 | 100 | 2.8345 | 2.0422
101 | 1.9953 | 0.78143 | 2.7767 |  |  |  | 101 | 101 | 2.7767 | 1.9953
102 | 2.1829 | 0.82472 | 3.0076 |  |  |  | 102 | 102 | 3.0076 | 2.1829
103 | 2.779 | 0.96234 | 3.7414 |  |  |  | 103 | 103 | 3.7414 | 2.779
104 | 2.98 | 1.0087 | 3.9887 |  |  |  | 104 | 104 | 3.9887 | 2.98
105 | 3.3685 | 1.0984 | 4.4669 |  |  |  | 105 | 105 | 4.4669 | 3.3685
106 | 4.534 | 1.3674 | 5.9015 |  |  |  | 106 | 106 | 5.9015 | 4.534
107 | 4.8154 | 1.4324 | 6.2477 |  |  |  | 107 | 107 | 6.2477 | 4.8154
108 | 6.0747 | 1.7231 | 7.7977 |  |  |  | 108 | 108 | 7.7977 | 6.0747
109 | 5.5455 | 1.6009 | 7.1464 |  |  |  | 109 | 109 | 7.1464 | 5.5455
110 | 5.1838 | 1.5174 | 6.7012 |  |  |  | 110 | 110 | 6.7012 | 5.1838
111 | 5.0565 | 1.488 | 6.5446 |  |  |  | 111 | 111 | 6.5446 | 5.0565
112 | 5.1101 | 1.5004 | 6.6105 |  |  |  | 112 | 112 | 6.6105 | 5.1101
113 | 4.8355 | 1.437 | 6.2725 |  |  |  | 113 | 113 | 6.2725 | 4.8355
114 | 4.9694 | 1.4679 | 6.4374 |  |  |  | 114 | 114 | 6.4374 | 4.9694
115 | 4.6077 | 1.3844 | 5.9922 |  |  |  | 115 | 115 | 5.9922 | 4.6077
116 | 5.1503 | 1.5097 | 6.66 |  |  |  | 116 | 116 | 6.66 | 5.1503
117 | 4.8154 | 1.4324 | 6.2477 |  |  |  | 117 | 117 | 6.2477 | 4.8154
118 | 4.1991 | 1.2901 | 5.4892 |  |  |  | 118 | 118 | 5.4892 | 4.1991
119 | 2.9264 | 0.99635 | 3.9227 |  |  |  | 119 | 119 | 3.9227 | 2.9264
120 | 2.6728 | 0.9378 | 3.6106 |  |  |  | 120 | 120 | 3.6106 | 2.6728
121 | 2.0891 | 0.80308 | 2.8922 |  |  |  | 121 | 121 | 2.8922 | 2.0891
122 | 1.7609 | 0.72731 | 2.4882 |  |  |  | 122 | 122 | 2.4882 | 1.7609
123 | 1.6939 | 0.71185 | 2.4057 |  |  |  | 123 | 123 | 2.4057 | 1.6939
124 | 1.6671 | 0.70567 | 2.3727 |  |  |  | 124 | 124 | 2.3727 | 1.6671
125 | 1.6336 | 0.69794 | 2.3315 |  |  |  | 125 | 125 | 2.3315 | 1.6336
126 | 1.7475 | 0.72422 | 2.4717 |  |  |  | 126 | 126 | 2.4717 | 1.7475
127 | 2.9532 | 1.0025 | 3.9557 |  |  |  | 127 | 127 | 3.9557 | 2.9532
128 | 4.1991 | 1.2901 | 5.4892 |  |  |  | 128 | 128 | 5.4892 | 4.1991
129 | 4.7417 | 1.4154 | 6.1571 |  |  |  | 129 | 129 | 6.1571 | 4.7417
130 | 5.09 | 1.4958 | 6.5858 |  |  |  | 130 | 130 | 6.5858 | 5.09
131 | 5.2173 | 1.5251 | 6.7424 |  |  |  | 131 | 131 | 6.7424 | 5.2173
132 | 5.0163 | 1.4788 | 6.4951 |  |  |  | 132 | 132 | 6.4951 | 5.0163
133 | 5.5254 | 1.5963 | 7.1217 |  |  |  | 133 | 133 | 7.1217 | 5.5254
134 | 5.7666 | 1.6519 | 7.4185 |  |  |  | 134 | 134 | 7.4185 | 5.7666
135 | 5.8201 | 1.6643 | 7.4844 |  |  |  | 135 | 135 | 7.4844 | 5.8201
136 | 5.1704 | 1.5143 | 6.6847 |  |  |  | 136 | 136 | 6.6847 | 5.1704
137 | 5.09 | 1.4958 | 6.5858 |  |  |  | 137 | 137 | 6.5858 | 5.09
138 | 5.0498 | 1.4865 | 6.5363 |  |  |  | 138 | 138 | 6.5363 | 5.0498
139 | 4.7819 | 1.4246 | 6.2065 |  |  |  | 139 | 139 | 6.2065 | 4.7819
140 | 4.7886 | 1.4262 | 6.2148 |  |  |  | 140 | 140 | 6.2148 | 4.7886
141 | 4.2661 | 1.3056 | 5.5717 |  |  |  | 141 | 141 | 5.5717 | 4.2661
142 | 3.757 | 1.1881 | 4.9451 |  |  |  | 142 | 142 | 4.9451 | 3.757
143 | 3.0537 | 1.0257 | 4.0794 |  |  |  | 143 | 143 | 4.0794 | 3.0537
144 | 2.5647 | 0.91286 | 3.4775 |  |  |  | 144 | 144 | 3.4775 | 2.5647
145 | 2.1896 | 0.82627 | 3.0158 |  |  |  | 145 | 145 | 3.0158 | 2.1896
146 | 2.0221 | 0.78762 | 2.8097 |  |  |  | 146 | 146 | 2.8097 | 2.0221
147 | 1.9685 | 0.77525 | 2.7438 |  |  |  | 147 | 147 | 2.7438 | 1.9685
148 | 1.9618 | 0.7737 | 2.7355 |  |  |  | 148 | 148 | 2.7355 | 1.9618
149 | 1.9618 | 0.7737 | 2.7355 |  |  |  | 149 | 149 | 2.7355 | 1.9618
150 | 1.9685 | 0.77525 | 2.7438 |  |  |  | 150 | 150 | 2.7438 | 1.9685
151 | 2.8326 | 0.97471 | 3.8073 |  |  |  | 151 | 151 | 3.8073 | 2.8326
152 | 4.0517 | 1.2561 | 5.3079 |  |  |  | 152 | 152 | 5.3079 | 4.0517
153 | 4.5407 | 1.369 | 5.9097 |  |  |  | 153 | 153 | 5.9097 | 4.5407
154 | 4.9895 | 1.4726 | 6.4621 |  |  |  | 154 | 154 | 6.4621 | 4.9895
155 | 4.869 | 1.4447 | 6.3137 |  |  |  | 155 | 155 | 6.3137 | 4.869
156 | 5.0029 | 1.4757 | 6.4786 |  |  |  | 156 | 156 | 6.4786 | 5.0029
157 | 5.5723 | 1.6071 | 7.1794 |  |  |  | 157 | 157 | 7.1794 | 5.5723
158 | 5.8335 | 1.6674 | 7.5009 |  |  |  | 158 | 158 | 7.5009 | 5.8335
159 | 6.0479 | 1.7169 | 7.7648 |  |  |  | 159 | 159 | 7.7648 | 6.0479
160 | 5.9474 | 1.6937 | 7.6411 |  |  |  | 160 | 160 | 7.6411 | 5.9474
161 | 6.557 | 1.8344 | 8.3914 |  |  |  | 161 | 161 | 8.3914 | 6.557
162 | 6.1618 | 1.7432 | 7.9049 |  |  |  | 162 | 162 | 7.9049 | 6.1618
163 | 6.4498 | 1.8096 | 8.2594 |  |  |  | 163 | 163 | 8.2594 | 6.4498
164 | 5.3713 | 1.5607 | 6.9321 |  |  |  | 164 | 164 | 6.9321 | 5.3713
165 | 7.8699 | 2.1374 | 10.0073 |  |  |  | 165 | 165 | 10.0073 | 7.8699
166 | 6.2354 | 1.7602 | 7.9956 |  |  |  | 166 | 166 | 7.9956 | 6.2354
167 | 3.3551 | 1.0953 | 4.4504 |  |  |  | 167 | 167 | 4.4504 | 3.3551
168 | 2.8393 | 0.97625 | 3.8156 |  |  |  | 168 | 168 | 3.8156 | 2.8393
[7 empty] | 169 | 1 | 2.381 | 1.6738
[7 empty] | 170 | 2 | 2.2738 | 1.5867
[7 empty] | 171 | 3 | 2.2656 | 1.58
[7 empty] | 172 | 4 | 2.3975 | 1.6872
[7 empty] | 173 | 5 | 2.414 | 1.7006
[7 empty] | 174 | 6 | 2.8345 | 2.0422
[7 empty] | 175 | 7 | 3.5435 | 2.6183
[7 empty] | 176 | 8 | 4.2031 | 3.1541
[7 empty] | 177 | 9 | 4.1783 | 3.134
[7 empty] | 178 | 10 | 5.6706 | 4.3465
[7 empty] | 179 | 11 | 7.7153 | 6.0077
[7 empty] | 180 | 12 | 8.6634 | 6.778
[7 empty] | 181 | 13 | 9.0344 | 7.0795
[7 empty] | 182 | 14 | 8.8201 | 6.9053
[7 empty] | 183 | 15 | 8.7294 | 6.8316
[7 empty] | 184 | 16 | 9.8919 | 7.7761
[7 empty] | 185 | 17 | 11.1946 | 8.8345
[7 empty] | 186 | 18 | 10.9555 | 8.6402
[7 empty] | 187 | 19 | 11.4749 | 9.0622
[7 empty] | 188 | 20 | 11.4089 | 9.0086
[7 empty] | 189 | 21 | 11.9696 | 9.4641
[7 empty] | 190 | 22 | 8.0781 | 6.3024
[7 empty] | 191 | 23 | 4.368 | 3.2881
[7 empty] | 192 | 24 | 2.724 | 1.9525
[7 empty] | 193 | 25 | 2.6283 | 1.8747
[7 empty] | 194 | 26 | 2.5212 | 1.7877
[7 empty] | 195 | 27 | 2.4222 | 1.7073
[7 empty] | 196 | 28 | 2.5047 | 1.7743
[7 empty] | 197 | 29 | 2.7438 | 1.9685
[7 empty] | 198 | 30 | 2.9829 | 2.1628
[7 empty] | 199 | 31 | 3.8156 | 2.8393
[7 empty] | 200 | 32 | 4.1618 | 3.1207
[7 empty] | 201 | 33 | 4.8132 | 3.6498
[7 empty] | 202 | 34 | 5.6954 | 4.3666
[7 empty] | 203 | 35 | 7.8307 | 6.1015
[7 empty] | 204 | 36 | 8.8448 | 6.9254
[7 empty] | 205 | 37 | 8.919 | 6.9857
[7 empty] | 206 | 38 | 8.9932 | 7.046
[7 empty] | 207 | 39 | 8.6717 | 6.7847
[7 empty] | 208 | 40 | 9.7105 | 7.6287
[7 empty] | 209 | 41 | 10.2547 | 8.0708
[7 empty] | 210 | 42 | 10.2711 | 8.0842
[7 empty] | 211 | 43 | 10.6339 | 8.379
[7 empty] | 212 | 44 | 11.7717 | 9.3034
[7 empty] | 213 | 45 | 11.3759 | 8.9818
[7 empty] | 214 | 46 | 8.6717 | 6.7847
[7 empty] | 215 | 47 | 5.1265 | 3.9044
[7 empty] | 216 | 48 | 3.6507 | 2.7053
[7 empty] | 217 | 49 | 2.9993 | 2.1762
[7 empty] | 218 | 50 | 2.6943 | 1.9283
[7 empty] | 219 | 51 | 2.5871 | 1.8412
[7 empty] | 220 | 52 | 2.6201 | 1.868
[7 empty] | 221 | 53 | 2.6448 | 1.8881
[7 empty] | 222 | 54 | 3.2137 | 2.3503
[7 empty] | 223 | 55 | 4.335 | 3.2613
[7 empty] | 224 | 56 | 4.5741 | 3.4556
[7 empty] | 225 | 57 | 5.5057 | 4.2125
[7 empty] | 226 | 58 | 6.594 | 5.0967
[7 empty] | 227 | 59 | 7.7813 | 6.0613
[7 empty] | 228 | 60 | 8.3996 | 6.5637
[7 empty] | 229 | 61 | 9.0674 | 7.1063
[7 empty] | 230 | 62 | 8.8696 | 6.9455
[7 empty] | 231 | 63 | 9.4549 | 7.4211
[7 empty] | 232 | 64 | 10.3866 | 8.178
[7 empty] | 233 | 65 | 10.9967 | 8.6737
[7 empty] | 234 | 66 | 10.8977 | 8.5933
[7 empty] | 235 | 67 | 11.6233 | 9.1828
[7 empty] | 236 | 68 | 11.8624 | 9.377
[7 empty] | 237 | 69 | 11.3594 | 8.9684
[7 empty] | 238 | 70 | 9.1004 | 7.133
[7 empty] | 239 | 71 | 4.6565 | 3.5226
[7 empty] | 240 | 72 | 3.5894 | 2.6556
[7 empty] | 241 | 73 | 2.8839 | 2.0824
[7 empty] | 242 | 74 | 2.6613 | 1.9015
[7 empty] | 243 | 75 | 2.5624 | 1.8211
[7 empty] | 244 | 76 | 2.5047 | 1.7743
[7 empty] | 245 | 77 | 2.6778 | 1.9149
[7 empty] | 246 | 78 | 3.0735 | 2.2365
[7 empty] | 247 | 79 | 4.1701 | 3.1274
[7 empty] | 248 | 80 | 4.3432 | 3.268
[7 empty] | 249 | 81 | 5.5057 | 4.2125
[7 empty] | 250 | 82 | 6.5775 | 5.0833
[7 empty] | 251 | 83 | 7.3031 | 5.6728
[7 empty] | 252 | 84 | 8.5233 | 6.6642
[7 empty] | 253 | 85 | 8.2265 | 6.423
[7 empty] | 254 | 86 | 7.7235 | 6.0144
[7 empty] | 255 | 87 | 8.1605 | 6.3694
[7 empty] | 256 | 88 | 8.8118 | 6.8986
[7 empty] | 257 | 89 | 10.1392 | 7.9771
[7 empty] | 258 | 90 | 9.5621 | 7.5082
[7 empty] | 259 | 91 | 10.2382 | 8.0574
[7 empty] | 260 | 92 | 9.6446 | 7.5751
[7 empty] | 261 | 93 | 7.2701 | 5.646
[7 empty] | 262 | 94 | 6.3797 | 4.9225
[7 empty] | 263 | 95 | 4.5493 | 3.4355
[7 empty] | 264 | 96 | 3.5765 | 2.6451
[7 empty] | 265 | 97 | 3.527 | 2.6049
[7 empty] | 266 | 98 | 3.2384 | 2.3704
[7 empty] | 267 | 99 | 3.1807 | 2.3235
[7 empty] | 268 | 100 | 2.8345 | 2.0422
[7 empty] | 269 | 101 | 2.7767 | 1.9953
[7 empty] | 270 | 102 | 3.0076 | 2.1829
[7 empty] | 271 | 103 | 3.7414 | 2.779
[7 empty] | 272 | 104 | 3.9887 | 2.98
[7 empty] | 273 | 105 | 4.4669 | 3.3685
[7 empty] | 274 | 106 | 5.9015 | 4.534
[7 empty] | 275 | 107 | 6.2477 | 4.8154
[7 empty] | 276 | 108 | 7.7977 | 6.0747
[7 empty] | 277 | 109 | 7.1464 | 5.5455
[7 empty] | 278 | 110 | 6.7012 | 5.1838
[7 empty] | 279 | 111 | 6.5446 | 5.0565
[7 empty] | 280 | 112 | 6.6105 | 5.1101
[7 empty] | 281 | 113 | 6.2725 | 4.8355
[7 empty] | 282 | 114 | 6.4374 | 4.9694
[7 empty] | 283 | 115 | 5.9922 | 4.6077
[7 empty] | 284 | 116 | 6.66 | 5.1503
[7 empty] | 285 | 117 | 6.2477 | 4.8154
[7 empty] | 286 | 118 | 5.4892 | 4.1991
[7 empty] | 287 | 119 | 3.9227 | 2.9264
[7 empty] | 288 | 120 | 3.6106 | 2.6728
[7 empty] | 289 | 121 | 2.8922 | 2.0891
[7 empty] | 290 | 122 | 2.4882 | 1.7609
[7 empty] | 291 | 123 | 2.4057 | 1.6939
[7 empty] | 292 | 124 | 2.3727 | 1.6671
[7 empty] | 293 | 125 | 2.3315 | 1.6336
[7 empty] | 294 | 126 | 2.4717 | 1.7475
[7 empty] | 295 | 127 | 3.9557 | 2.9532
[7 empty] | 296 | 128 | 5.4892 | 4.1991
[7 empty] | 297 | 129 | 6.1571 | 4.7417
[7 empty] | 298 | 130 | 6.5858 | 5.09
[7 empty] | 299 | 131 | 6.7424 | 5.2173
[7 empty] | 300 | 132 | 6.4951 | 5.0163
[7 empty] | 301 | 133 | 7.1217 | 5.5254
[7 empty] | 302 | 134 | 7.4185 | 5.7666
[7 empty] | 303 | 135 | 7.4844 | 5.8201
[7 empty] | 304 | 136 | 6.6847 | 5.1704
[7 empty] | 305 | 137 | 6.5858 | 5.09
[7 empty] | 306 | 138 | 6.5363 | 5.0498
[7 empty] | 307 | 139 | 6.2065 | 4.7819
[7 empty] | 308 | 140 | 6.2148 | 4.7886
[7 empty] | 309 | 141 | 5.5717 | 4.2661
[7 empty] | 310 | 142 | 4.9451 | 3.757
[7 empty] | 311 | 143 | 4.0794 | 3.0537
[7 empty] | 312 | 144 | 3.4775 | 2.5647
[7 empty] | 313 | 145 | 3.0158 | 2.1896
[7 empty] | 314 | 146 | 2.8097 | 2.0221
[7 empty] | 315 | 147 | 2.7438 | 1.9685
[7 empty] | 316 | 148 | 2.7355 | 1.9618
[7 empty] | 317 | 149 | 2.7355 | 1.9618
[7 empty] | 318 | 150 | 2.7438 | 1.9685
[7 empty] | 319 | 151 | 3.8073 | 2.8326
[7 empty] | 320 | 152 | 5.3079 | 4.0517
[7 empty] | 321 | 153 | 5.9097 | 4.5407
[7 empty] | 322 | 154 | 6.4621 | 4.9895
[7 empty] | 323 | 155 | 6.3137 | 4.869
[7 empty] | 324 | 156 | 6.4786 | 5.0029
[7 empty] | 325 | 157 | 7.1794 | 5.5723
[7 empty] | 326 | 158 | 7.5009 | 5.8335
[7 empty] | 327 | 159 | 7.7648 | 6.0479
[7 empty] | 328 | 160 | 7.6411 | 5.9474
[7 empty] | 329 | 161 | 8.3914 | 6.557
[7 empty] | 330 | 162 | 7.9049 | 6.1618
[7 empty] | 331 | 163 | 8.2594 | 6.4498
[7 empty] | 332 | 164 | 6.9321 | 5.3713
[7 empty] | 333 | 165 | 10.0073 | 7.8699
[7 empty] | 334 | 166 | 7.9956 | 6.2354
[7 empty] | 335 | 167 | 4.4504 | 3.3551
[7 empty] | 336 | 168 | 3.8156 | 2.8393
[7 empty] | 337 | 1 | 2.381 | 1.6738
[7 empty] | 338 | 2 | 2.2738 | 1.5867
[7 empty] | 339 | 3 | 2.2656 | 1.58
[7 empty] | 340 | 4 | 2.3975 | 1.6872
[7 empty] | 341 | 5 | 2.414 | 1.7006
[7 empty] | 342 | 6 | 2.8345 | 2.0422
[7 empty] | 343 | 7 | 3.5435 | 2.6183
[7 empty] | 344 | 8 | 4.2031 | 3.1541
[7 empty] | 345 | 9 | 4.1783 | 3.134
[7 empty] | 346 | 10 | 5.6706 | 4.3465
[7 empty] | 347 | 11 | 7.7153 | 6.0077
[7 empty] | 348 | 12 | 8.6634 | 6.778
[7 empty] | 349 | 13 | 9.0344 | 7.0795
[7 empty] | 350 | 14 | 8.8201 | 6.9053
[7 empty] | 351 | 15 | 8.7294 | 6.8316
[7 empty] | 352 | 16 | 9.8919 | 7.7761
[7 empty] | 353 | 17 | 11.1946 | 8.8345
[7 empty] | 354 | 18 | 10.9555 | 8.6402
[7 empty] | 355 | 19 | 11.4749 | 9.0622
[7 empty] | 356 | 20 | 11.4089 | 9.0086
[7 empty] | 357 | 21 | 11.9696 | 9.4641
[7 empty] | 358 | 22 | 8.0781 | 6.3024
[7 empty] | 359 | 23 | 4.368 | 3.2881
[7 empty] | 360 | 24 | 2.724 | 1.9525
[7 empty] | 361 | 25 | 2.6283 | 1.8747
[7 empty] | 362 | 26 | 2.5212 | 1.7877
[7 empty] | 363 | 27 | 2.4222 | 1.7073
[7 empty] | 364 | 28 | 2.5047 | 1.7743
[7 empty] | 365 | 29 | 2.7438 | 1.9685
[7 empty] | 366 | 30 | 2.9829 | 2.1628
[7 empty] | 367 | 31 | 3.8156 | 2.8393
[7 empty] | 368 | 32 | 4.1618 | 3.1207
[7 empty] | 369 | 33 | 4.8132 | 3.6498
[7 empty] | 370 | 34 | 5.6954 | 4.3666
[7 empty] | 371 | 35 | 7.8307 | 6.1015
[7 empty] | 372 | 36 | 8.8448 | 6.9254
[7 empty] | 373 | 37 | 8.919 | 6.9857
[7 empty] | 374 | 38 | 8.9932 | 7.046
[7 empty] | 375 | 39 | 8.6717 | 6.7847
[7 empty] | 376 | 40 | 9.7105 | 7.6287
[7 empty] | 377 | 41 | 10.2547 | 8.0708
[7 empty] | 378 | 42 | 10.2711 | 8.0842
[7 empty] | 379 | 43 | 10.6339 | 8.379
[7 empty] | 380 | 44 | 11.7717 | 9.3034
[7 empty] | 381 | 45 | 11.3759 | 8.9818
[7 empty] | 382 | 46 | 8.6717 | 6.7847
[7 empty] | 383 | 47 | 5.1265 | 3.9044
[7 empty] | 384 | 48 | 3.6507 | 2.7053
[7 empty] | 385 | 49 | 2.9993 | 2.1762
[7 empty] | 386 | 50 | 2.6943 | 1.9283
[7 empty] | 387 | 51 | 2.5871 | 1.8412
[7 empty] | 388 | 52 | 2.6201 | 1.868
[7 empty] | 389 | 53 | 2.6448 | 1.8881
[7 empty] | 390 | 54 | 3.2137 | 2.3503
[7 empty] | 391 | 55 | 4.335 | 3.2613
[7 empty] | 392 | 56 | 4.5741 | 3.4556
[7 empty] | 393 | 57 | 5.5057 | 4.2125
[7 empty] | 394 | 58 | 6.594 | 5.0967
[7 empty] | 395 | 59 | 7.7813 | 6.0613
[7 empty] | 396 | 60 | 8.3996 | 6.5637
[7 empty] | 397 | 61 | 9.0674 | 7.1063
[7 empty] | 398 | 62 | 8.8696 | 6.9455
[7 empty] | 399 | 63 | 9.4549 | 7.4211
[7 empty] | 400 | 64 | 10.3866 | 8.178
[7 empty] | 401 | 65 | 10.9967 | 8.6737
[7 empty] | 402 | 66 | 10.8977 | 8.5933
[7 empty] | 403 | 67 | 11.6233 | 9.1828
[7 empty] | 404 | 68 | 11.8624 | 9.377
[7 empty] | 405 | 69 | 11.3594 | 8.9684
[7 empty] | 406 | 70 | 9.1004 | 7.133
[7 empty] | 407 | 71 | 4.6565 | 3.5226
[7 empty] | 408 | 72 | 3.5894 | 2.6556
[7 empty] | 409 | 73 | 2.8839 | 2.0824
[7 empty] | 410 | 74 | 2.6613 | 1.9015
[7 empty] | 411 | 75 | 2.5624 | 1.8211
[7 empty] | 412 | 76 | 2.5047 | 1.7743
[7 empty] | 413 | 77 | 2.6778 | 1.9149
[7 empty] | 414 | 78 | 3.0735 | 2.2365
[7 empty] | 415 | 79 | 4.1701 | 3.1274
[7 empty] | 416 | 80 | 4.3432 | 3.268
[7 empty] | 417 | 81 | 5.5057 | 4.2125
[7 empty] | 418 | 82 | 6.5775 | 5.0833
[7 empty] | 419 | 83 | 7.3031 | 5.6728
[7 empty] | 420 | 84 | 8.5233 | 6.6642
[7 empty] | 421 | 85 | 8.2265 | 6.423
[7 empty] | 422 | 86 | 7.7235 | 6.0144
[7 empty] | 423 | 87 | 8.1605 | 6.3694
[7 empty] | 424 | 88 | 8.8118 | 6.8986
[7 empty] | 425 | 89 | 10.1392 | 7.9771
[7 empty] | 426 | 90 | 9.5621 | 7.5082
[7 empty] | 427 | 91 | 10.2382 | 8.0574
[7 empty] | 428 | 92 | 9.6446 | 7.5751
[7 empty] | 429 | 93 | 7.2701 | 5.646
[7 empty] | 430 | 94 | 6.3797 | 4.9225
[7 empty] | 431 | 95 | 4.5493 | 3.4355
[7 empty] | 432 | 96 | 3.5765 | 2.6451
[7 empty] | 433 | 97 | 3.527 | 2.6049
[7 empty] | 434 | 98 | 3.2384 | 2.3704
[7 empty] | 435 | 99 | 3.1807 | 2.3235
[7 empty] | 436 | 100 | 2.8345 | 2.0422
[7 empty] | 437 | 101 | 2.7767 | 1.9953
[7 empty] | 438 | 102 | 3.0076 | 2.1829
[7 empty] | 439 | 103 | 3.7414 | 2.779
[7 empty] | 440 | 104 | 3.9887 | 2.98
[7 empty] | 441 | 105 | 4.4669 | 3.3685
[7 empty] | 442 | 106 | 5.9015 | 4.534
[7 empty] | 443 | 107 | 6.2477 | 4.8154
[7 empty] | 444 | 108 | 7.7977 | 6.0747
[7 empty] | 445 | 109 | 7.1464 | 5.5455
[7 empty] | 446 | 110 | 6.7012 | 5.1838
[7 empty] | 447 | 111 | 6.5446 | 5.0565
[7 empty] | 448 | 112 | 6.6105 | 5.1101
[7 empty] | 449 | 113 | 6.2725 | 4.8355
[7 empty] | 450 | 114 | 6.4374 | 4.9694
[7 empty] | 451 | 115 | 5.9922 | 4.6077
[7 empty] | 452 | 116 | 6.66 | 5.1503
[7 empty] | 453 | 117 | 6.2477 | 4.8154
[7 empty] | 454 | 118 | 5.4892 | 4.1991
[7 empty] | 455 | 119 | 3.9227 | 2.9264
[7 empty] | 456 | 120 | 3.6106 | 2.6728
[7 empty] | 457 | 121 | 2.8922 | 2.0891
[7 empty] | 458 | 122 | 2.4882 | 1.7609
[7 empty] | 459 | 123 | 2.4057 | 1.6939
[7 empty] | 460 | 124 | 2.3727 | 1.6671
[7 empty] | 461 | 125 | 2.3315 | 1.6336
[7 empty] | 462 | 126 | 2.4717 | 1.7475
[7 empty] | 463 | 127 | 3.9557 | 2.9532
[7 empty] | 464 | 128 | 5.4892 | 4.1991
[7 empty] | 465 | 129 | 6.1571 | 4.7417
[7 empty] | 466 | 130 | 6.5858 | 5.09
[7 empty] | 467 | 131 | 6.7424 | 5.2173
[7 empty] | 468 | 132 | 6.4951 | 5.0163
[7 empty] | 469 | 133 | 7.1217 | 5.5254
[7 empty] | 470 | 134 | 7.4185 | 5.7666
[7 empty] | 471 | 135 | 7.4844 | 5.8201
[7 empty] | 472 | 136 | 6.6847 | 5.1704
[7 empty] | 473 | 137 | 6.5858 | 5.09
[7 empty] | 474 | 138 | 6.5363 | 5.0498
[7 empty] | 475 | 139 | 6.2065 | 4.7819
[7 empty] | 476 | 140 | 6.2148 | 4.7886
[7 empty] | 477 | 141 | 5.5717 | 4.2661
[7 empty] | 478 | 142 | 4.9451 | 3.757
[7 empty] | 479 | 143 | 4.0794 | 3.0537
[7 empty] | 480 | 144 | 3.4775 | 2.5647
[7 empty] | 481 | 145 | 3.0158 | 2.1896
[7 empty] | 482 | 146 | 2.8097 | 2.0221
[7 empty] | 483 | 147 | 2.7438 | 1.9685
[7 empty] | 484 | 148 | 2.7355 | 1.9618
[7 empty] | 485 | 149 | 2.7355 | 1.9618
[7 empty] | 486 | 150 | 2.7438 | 1.9685
[7 empty] | 487 | 151 | 3.8073 | 2.8326
[7 empty] | 488 | 152 | 5.3079 | 4.0517
[7 empty] | 489 | 153 | 5.9097 | 4.5407
[7 empty] | 490 | 154 | 6.4621 | 4.9895
[7 empty] | 491 | 155 | 6.3137 | 4.869
[7 empty] | 492 | 156 | 6.4786 | 5.0029
[7 empty] | 493 | 157 | 7.1794 | 5.5723
[7 empty] | 494 | 158 | 7.5009 | 5.8335
[7 empty] | 495 | 159 | 7.7648 | 6.0479
[7 empty] | 496 | 160 | 7.6411 | 5.9474
[7 empty] | 497 | 161 | 8.3914 | 6.557
[7 empty] | 498 | 162 | 7.9049 | 6.1618
[7 empty] | 499 | 163 | 8.2594 | 6.4498
[7 empty] | 500 | 164 | 6.9321 | 5.3713
[7 empty] | 501 | 165 | 10.0073 | 7.8699
[7 empty] | 502 | 166 | 7.9956 | 6.2354
[7 empty] | 503 | 167 | 4.4504 | 3.3551
[7 empty] | 504 | 168 | 3.8156 | 2.8393
[7 empty] | 505 | 1 | 2.381 | 1.6738
[7 empty] | 506 | 2 | 2.2738 | 1.5867
[7 empty] | 507 | 3 | 2.2656 | 1.58
[7 empty] | 508 | 4 | 2.3975 | 1.6872
[7 empty] | 509 | 5 | 2.414 | 1.7006
[7 empty] | 510 | 6 | 2.8345 | 2.0422
[7 empty] | 511 | 7 | 3.5435 | 2.6183
[7 empty] | 512 | 8 | 4.2031 | 3.1541
[7 empty] | 513 | 9 | 4.1783 | 3.134
[7 empty] | 514 | 10 | 5.6706 | 4.3465
[7 empty] | 515 | 11 | 7.7153 | 6.0077
[7 empty] | 516 | 12 | 8.6634 | 6.778
[7 empty] | 517 | 13 | 9.0344 | 7.0795
[7 empty] | 518 | 14 | 8.8201 | 6.9053
[7 empty] | 519 | 15 | 8.7294 | 6.8316
[7 empty] | 520 | 16 | 9.8919 | 7.7761
[7 empty] | 521 | 17 | 11.1946 | 8.8345
[7 empty] | 522 | 18 | 10.9555 | 8.6402
[7 empty] | 523 | 19 | 11.4749 | 9.0622
[7 empty] | 524 | 20 | 11.4089 | 9.0086
[7 empty] | 525 | 21 | 11.9696 | 9.4641
[7 empty] | 526 | 22 | 8.0781 | 6.3024
[7 empty] | 527 | 23 | 4.368 | 3.2881
[7 empty] | 528 | 24 | 2.724 | 1.9525
[7 empty] | 529 | 25 | 2.6283 | 1.8747
[7 empty] | 530 | 26 | 2.5212 | 1.7877
[7 empty] | 531 | 27 | 2.4222 | 1.7073
[7 empty] | 532 | 28 | 2.5047 | 1.7743
[7 empty] | 533 | 29 | 2.7438 | 1.9685
[7 empty] | 534 | 30 | 2.9829 | 2.1628
[7 empty] | 535 | 31 | 3.8156 | 2.8393
[7 empty] | 536 | 32 | 4.1618 | 3.1207
[7 empty] | 537 | 33 | 4.8132 | 3.6498
[7 empty] | 538 | 34 | 5.6954 | 4.3666
[7 empty] | 539 | 35 | 7.8307 | 6.1015
[7 empty] | 540 | 36 | 8.8448 | 6.9254
[7 empty] | 541 | 37 | 8.919 | 6.9857
[7 empty] | 542 | 38 | 8.9932 | 7.046
[7 empty] | 543 | 39 | 8.6717 | 6.7847
[7 empty] | 544 | 40 | 9.7105 | 7.6287
[7 empty] | 545 | 41 | 10.2547 | 8.0708
[7 empty] | 546 | 42 | 10.2711 | 8.0842
[7 empty] | 547 | 43 | 10.6339 | 8.379
[7 empty] | 548 | 44 | 11.7717 | 9.3034
[7 empty] | 549 | 45 | 11.3759 | 8.9818
[7 empty] | 550 | 46 | 8.6717 | 6.7847
[7 empty] | 551 | 47 | 5.1265 | 3.9044
[7 empty] | 552 | 48 | 3.6507 | 2.7053
[7 empty] | 553 | 49 | 2.9993 | 2.1762
[7 empty] | 554 | 50 | 2.6943 | 1.9283
[7 empty] | 555 | 51 | 2.5871 | 1.8412
[7 empty] | 556 | 52 | 2.6201 | 1.868
[7 empty] | 557 | 53 | 2.6448 | 1.8881
[7 empty] | 558 | 54 | 3.2137 | 2.3503
[7 empty] | 559 | 55 | 4.335 | 3.2613
[7 empty] | 560 | 56 | 4.5741 | 3.4556
[7 empty] | 561 | 57 | 5.5057 | 4.2125
[7 empty] | 562 | 58 | 6.594 | 5.0967
[7 empty] | 563 | 59 | 7.7813 | 6.0613
[7 empty] | 564 | 60 | 8.3996 | 6.5637
[7 empty] | 565 | 61 | 9.0674 | 7.1063
[7 empty] | 566 | 62 | 8.8696 | 6.9455
[7 empty] | 567 | 63 | 9.4549 | 7.4211
[7 empty] | 568 | 64 | 10.3866 | 8.178
[7 empty] | 569 | 65 | 10.9967 | 8.6737
[7 empty] | 570 | 66 | 10.8977 | 8.5933
[7 empty] | 571 | 67 | 11.6233 | 9.1828
[7 empty] | 572 | 68 | 11.8624 | 9.377
[7 empty] | 573 | 69 | 11.3594 | 8.9684
[7 empty] | 574 | 70 | 9.1004 | 7.133
[7 empty] | 575 | 71 | 4.6565 | 3.5226
[7 empty] | 576 | 72 | 3.5894 | 2.6556
[7 empty] | 577 | 73 | 2.8839 | 2.0824
[7 empty] | 578 | 74 | 2.6613 | 1.9015
[7 empty] | 579 | 75 | 2.5624 | 1.8211
[7 empty] | 580 | 76 | 2.5047 | 1.7743
[7 empty] | 581 | 77 | 2.6778 | 1.9149
[7 empty] | 582 | 78 | 3.0735 | 2.2365
[7 empty] | 583 | 79 | 4.1701 | 3.1274
[7 empty] | 584 | 80 | 4.3432 | 3.268
[7 empty] | 585 | 81 | 5.5057 | 4.2125
[7 empty] | 586 | 82 | 6.5775 | 5.0833
[7 empty] | 587 | 83 | 7.3031 | 5.6728
[7 empty] | 588 | 84 | 8.5233 | 6.6642
[7 empty] | 589 | 85 | 8.2265 | 6.423
[7 empty] | 590 | 86 | 7.7235 | 6.0144
[7 empty] | 591 | 87 | 8.1605 | 6.3694
[7 empty] | 592 | 88 | 8.8118 | 6.8986
[7 empty] | 593 | 89 | 10.1392 | 7.9771
[7 empty] | 594 | 90 | 9.5621 | 7.5082
[7 empty] | 595 | 91 | 10.2382 | 8.0574
[7 empty] | 596 | 92 | 9.6446 | 7.5751
[7 empty] | 597 | 93 | 7.2701 | 5.646
[7 empty] | 598 | 94 | 6.3797 | 4.9225
[7 empty] | 599 | 95 | 4.5493 | 3.4355
[7 empty] | 600 | 96 | 3.5765 | 2.6451
[7 empty] | 601 | 97 | 3.527 | 2.6049
[7 empty] | 602 | 98 | 3.2384 | 2.3704
[7 empty] | 603 | 99 | 3.1807 | 2.3235
[7 empty] | 604 | 100 | 2.8345 | 2.0422
[7 empty] | 605 | 101 | 2.7767 | 1.9953
[7 empty] | 606 | 102 | 3.0076 | 2.1829
[7 empty] | 607 | 103 | 3.7414 | 2.779
[7 empty] | 608 | 104 | 3.9887 | 2.98
[7 empty] | 609 | 105 | 4.4669 | 3.3685
[7 empty] | 610 | 106 | 5.9015 | 4.534
[7 empty] | 611 | 107 | 6.2477 | 4.8154
[7 empty] | 612 | 108 | 7.7977 | 6.0747
[7 empty] | 613 | 109 | 7.1464 | 5.5455
[7 empty] | 614 | 110 | 6.7012 | 5.1838
[7 empty] | 615 | 111 | 6.5446 | 5.0565
[7 empty] | 616 | 112 | 6.6105 | 5.1101
[7 empty] | 617 | 113 | 6.2725 | 4.8355
[7 empty] | 618 | 114 | 6.4374 | 4.9694
[7 empty] | 619 | 115 | 5.9922 | 4.6077
[7 empty] | 620 | 116 | 6.66 | 5.1503
[7 empty] | 621 | 117 | 6.2477 | 4.8154
[7 empty] | 622 | 118 | 5.4892 | 4.1991
[7 empty] | 623 | 119 | 3.9227 | 2.9264
[7 empty] | 624 | 120 | 3.6106 | 2.6728
[7 empty] | 625 | 121 | 2.8922 | 2.0891
[7 empty] | 626 | 122 | 2.4882 | 1.7609
[7 empty] | 627 | 123 | 2.4057 | 1.6939
[7 empty] | 628 | 124 | 2.3727 | 1.6671
[7 empty] | 629 | 125 | 2.3315 | 1.6336
[7 empty] | 630 | 126 | 2.4717 | 1.7475
[7 empty] | 631 | 127 | 3.9557 | 2.9532
[7 empty] | 632 | 128 | 5.4892 | 4.1991
[7 empty] | 633 | 129 | 6.1571 | 4.7417
[7 empty] | 634 | 130 | 6.5858 | 5.09
[7 empty] | 635 | 131 | 6.7424 | 5.2173
[7 empty] | 636 | 132 | 6.4951 | 5.0163
[7 empty] | 637 | 133 | 7.1217 | 5.5254
[7 empty] | 638 | 134 | 7.4185 | 5.7666
[7 empty] | 639 | 135 | 7.4844 | 5.8201
[7 empty] | 640 | 136 | 6.6847 | 5.1704
[7 empty] | 641 | 137 | 6.5858 | 5.09
[7 empty] | 642 | 138 | 6.5363 | 5.0498
[7 empty] | 643 | 139 | 6.2065 | 4.7819
[7 empty] | 644 | 140 | 6.2148 | 4.7886
[7 empty] | 645 | 141 | 5.5717 | 4.2661
[7 empty] | 646 | 142 | 4.9451 | 3.757
[7 empty] | 647 | 143 | 4.0794 | 3.0537
[7 empty] | 648 | 144 | 3.4775 | 2.5647
[7 empty] | 649 | 145 | 3.0158 | 2.1896
[7 empty] | 650 | 146 | 2.8097 | 2.0221
[7 empty] | 651 | 147 | 2.7438 | 1.9685
[7 empty] | 652 | 148 | 2.7355 | 1.9618
[7 empty] | 653 | 149 | 2.7355 | 1.9618
[7 empty] | 654 | 150 | 2.7438 | 1.9685
[7 empty] | 655 | 151 | 3.8073 | 2.8326
[7 empty] | 656 | 152 | 5.3079 | 4.0517
[7 empty] | 657 | 153 | 5.9097 | 4.5407
[7 empty] | 658 | 154 | 6.4621 | 4.9895
[7 empty] | 659 | 155 | 6.3137 | 4.869
[7 empty] | 660 | 156 | 6.4786 | 5.0029
[7 empty] | 661 | 157 | 7.1794 | 5.5723
[7 empty] | 662 | 158 | 7.5009 | 5.8335
[7 empty] | 663 | 159 | 7.7648 | 6.0479
[7 empty] | 664 | 160 | 7.6411 | 5.9474
[7 empty] | 665 | 161 | 8.3914 | 6.557
[7 empty] | 666 | 162 | 7.9049 | 6.1618
[7 empty] | 667 | 163 | 8.2594 | 6.4498
[7 empty] | 668 | 164 | 6.9321 | 5.3713
[7 empty] | 669 | 165 | 10.0073 | 7.8699
[7 empty] | 670 | 166 | 7.9956 | 6.2354
[7 empty] | 671 | 167 | 4.4504 | 3.3551
[7 empty] | 672 | 168 | 3.8156 | 2.8393
[7 empty] | 673 | 1 | 2.381 | 1.6738
[7 empty] | 674 | 2 | 2.2738 | 1.5867
[7 empty] | 675 | 3 | 2.2656 | 1.58
[7 empty] | 676 | 4 | 2.3975 | 1.6872
[7 empty] | 677 | 5 | 2.414 | 1.7006
[7 empty] | 678 | 6 | 2.8345 | 2.0422
[7 empty] | 679 | 7 | 3.5435 | 2.6183
[7 empty] | 680 | 8 | 4.2031 | 3.1541
[7 empty] | 681 | 9 | 4.1783 | 3.134
[7 empty] | 682 | 10 | 5.6706 | 4.3465
[7 empty] | 683 | 11 | 7.7153 | 6.0077
[7 empty] | 684 | 12 | 8.6634 | 6.778
[7 empty] | 685 | 13 | 9.0344 | 7.0795
[7 empty] | 686 | 14 | 8.8201 | 6.9053
[7 empty] | 687 | 15 | 8.7294 | 6.8316
[7 empty] | 688 | 16 | 9.8919 | 7.7761
[7 empty] | 689 | 17 | 11.1946 | 8.8345
[7 empty] | 690 | 18 | 10.9555 | 8.6402
[7 empty] | 691 | 19 | 11.4749 | 9.0622
[7 empty] | 692 | 20 | 11.4089 | 9.0086
[7 empty] | 693 | 21 | 11.9696 | 9.4641
[7 empty] | 694 | 22 | 8.0781 | 6.3024
[7 empty] | 695 | 23 | 4.368 | 3.2881
[7 empty] | 696 | 24 | 2.724 | 1.9525
[7 empty] | 697 | 25 | 2.6283 | 1.8747
[7 empty] | 698 | 26 | 2.5212 | 1.7877
[7 empty] | 699 | 27 | 2.4222 | 1.7073
[7 empty] | 700 | 28 | 2.5047 | 1.7743
[7 empty] | 701 | 29 | 2.7438 | 1.9685
[7 empty] | 702 | 30 | 2.9829 | 2.1628
[7 empty] | 703 | 31 | 3.8156 | 2.8393
[7 empty] | 704 | 32 | 4.1618 | 3.1207
[7 empty] | 705 | 33 | 4.8132 | 3.6498
[7 empty] | 706 | 34 | 5.6954 | 4.3666
[7 empty] | 707 | 35 | 7.8307 | 6.1015
[7 empty] | 708 | 36 | 8.8448 | 6.9254
[7 empty] | 709 | 37 | 8.919 | 6.9857
[7 empty] | 710 | 38 | 8.9932 | 7.046
[7 empty] | 711 | 39 | 8.6717 | 6.7847
[7 empty] | 712 | 40 | 9.7105 | 7.6287
[7 empty] | 713 | 41 | 10.2547 | 8.0708
[7 empty] | 714 | 42 | 10.2711 | 8.0842
[7 empty] | 715 | 43 | 10.6339 | 8.379
[7 empty] | 716 | 44 | 11.7717 | 9.3034
[7 empty] | 717 | 45 | 11.3759 | 8.9818
[7 empty] | 718 | 46 | 8.6717 | 6.7847
[7 empty] | 719 | 47 | 5.1265 | 3.9044
[7 empty] | 720 | 48 | 3.6507 | 2.7053
[7 empty] | 721 | 49 | 2.9993 | 2.1762
[7 empty] | 722 | 50 | 2.6943 | 1.9283
[7 empty] | 723 | 51 | 2.5871 | 1.8412
[7 empty] | 724 | 52 | 2.6201 | 1.868
[7 empty] | 725 | 53 | 2.6448 | 1.8881
[7 empty] | 726 | 54 | 3.2137 | 2.3503
[7 empty] | 727 | 55 | 4.335 | 3.2613
[7 empty] | 728 | 56 | 4.5741 | 3.4556
[7 empty] | 729 | 57 | 5.5057 | 4.2125
[7 empty] | 730 | 58 | 6.594 | 5.0967
[7 empty] | 731 | 59 | 7.7813 | 6.0613
[7 empty] | 732 | 60 | 8.3996 | 6.5637
[7 empty] | 733 | 61 | 9.0674 | 7.1063
[7 empty] | 734 | 62 | 8.8696 | 6.9455
[7 empty] | 735 | 63 | 9.4549 | 7.4211
[7 empty] | 736 | 64 | 10.3866 | 8.178
[7 empty] | 737 | 65 | 10.9967 | 8.6737
[7 empty] | 738 | 66 | 10.8977 | 8.5933
[7 empty] | 739 | 67 | 11.6233 | 9.1828
[7 empty] | 740 | 68 | 11.8624 | 9.377
[7 empty] | 741 | 69 | 11.3594 | 8.9684
[7 empty] | 742 | 70 | 9.1004 | 7.133
[7 empty] | 743 | 71 | 4.6565 | 3.5226
[7 empty] | 744 | 72 | 3.5894 | 2.6556
[7 empty] | 745 | 73 | 2.8839 | 2.0824
[7 empty] | 746 | 74 | 2.6613 | 1.9015
[7 empty] | 747 | 75 | 2.5624 | 1.8211
[7 empty] | 748 | 76 | 2.5047 | 1.7743
[7 empty] | 749 | 77 | 2.6778 | 1.9149
[7 empty] | 750 | 78 | 3.0735 | 2.2365
[7 empty] | 751 | 79 | 4.1701 | 3.1274
[7 empty] | 752 | 80 | 4.3432 | 3.268
[7 empty] | 753 | 81 | 5.5057 | 4.2125
[7 empty] | 754 | 82 | 6.5775 | 5.0833
[7 empty] | 755 | 83 | 7.3031 | 5.6728
[7 empty] | 756 | 84 | 8.5233 | 6.6642
[7 empty] | 757 | 85 | 8.2265 | 6.423
[7 empty] | 758 | 86 | 7.7235 | 6.0144
[7 empty] | 759 | 87 | 8.1605 | 6.3694
[7 empty] | 760 | 88 | 8.8118 | 6.8986
[7 empty] | 761 | 89 | 10.1392 | 7.9771
[7 empty] | 762 | 90 | 9.5621 | 7.5082
[7 empty] | 763 | 91 | 10.2382 | 8.0574
[7 empty] | 764 | 92 | 9.6446 | 7.5751
[7 empty] | 765 | 93 | 7.2701 | 5.646
[7 empty] | 766 | 94 | 6.3797 | 4.9225
[7 empty] | 767 | 95 | 4.5493 | 3.4355
[7 empty] | 768 | 96 | 3.5765 | 2.6451
[7 empty] | 769 | 97 | 3.527 | 2.6049
[7 empty] | 770 | 98 | 3.2384 | 2.3704
[7 empty] | 771 | 99 | 3.1807 | 2.3235
[7 empty] | 772 | 100 | 2.8345 | 2.0422
[7 empty] | 773 | 101 | 2.7767 | 1.9953
[7 empty] | 774 | 102 | 3.0076 | 2.1829
[7 empty] | 775 | 103 | 3.7414 | 2.779
[7 empty] | 776 | 104 | 3.9887 | 2.98
[7 empty] | 777 | 105 | 4.4669 | 3.3685
[7 empty] | 778 | 106 | 5.9015 | 4.534
[7 empty] | 779 | 107 | 6.2477 | 4.8154
[7 empty] | 780 | 108 | 7.7977 | 6.0747
[7 empty] | 781 | 109 | 7.1464 | 5.5455
[7 empty] | 782 | 110 | 6.7012 | 5.1838
[7 empty] | 783 | 111 | 6.5446 | 5.0565
[7 empty] | 784 | 112 | 6.6105 | 5.1101
[7 empty] | 785 | 113 | 6.2725 | 4.8355
[7 empty] | 786 | 114 | 6.4374 | 4.9694
[7 empty] | 787 | 115 | 5.9922 | 4.6077
[7 empty] | 788 | 116 | 6.66 | 5.1503
[7 empty] | 789 | 117 | 6.2477 | 4.8154
[7 empty] | 790 | 118 | 5.4892 | 4.1991
[7 empty] | 791 | 119 | 3.9227 | 2.9264
[7 empty] | 792 | 120 | 3.6106 | 2.6728
[7 empty] | 793 | 121 | 2.8922 | 2.0891
[7 empty] | 794 | 122 | 2.4882 | 1.7609
[7 empty] | 795 | 123 | 2.4057 | 1.6939
[7 empty] | 796 | 124 | 2.3727 | 1.6671
[7 empty] | 797 | 125 | 2.3315 | 1.6336
[7 empty] | 798 | 126 | 2.4717 | 1.7475
[7 empty] | 799 | 127 | 3.9557 | 2.9532
[7 empty] | 800 | 128 | 5.4892 | 4.1991
[7 empty] | 801 | 129 | 6.1571 | 4.7417
[7 empty] | 802 | 130 | 6.5858 | 5.09
[7 empty] | 803 | 131 | 6.7424 | 5.2173
[7 empty] | 804 | 132 | 6.4951 | 5.0163
[7 empty] | 805 | 133 | 7.1217 | 5.5254
[7 empty] | 806 | 134 | 7.4185 | 5.7666
[7 empty] | 807 | 135 | 7.4844 | 5.8201
[7 empty] | 808 | 136 | 6.6847 | 5.1704
[7 empty] | 809 | 137 | 6.5858 | 5.09
[7 empty] | 810 | 138 | 6.5363 | 5.0498
[7 empty] | 811 | 139 | 6.2065 | 4.7819
[7 empty] | 812 | 140 | 6.2148 | 4.7886
[7 empty] | 813 | 141 | 5.5717 | 4.2661
[7 empty] | 814 | 142 | 4.9451 | 3.757
[7 empty] | 815 | 143 | 4.0794 | 3.0537
[7 empty] | 816 | 144 | 3.4775 | 2.5647
[7 empty] | 817 | 145 | 3.0158 | 2.1896
[7 empty] | 818 | 146 | 2.8097 | 2.0221
[7 empty] | 819 | 147 | 2.7438 | 1.9685
[7 empty] | 820 | 148 | 2.7355 | 1.9618
[7 empty] | 821 | 149 | 2.7355 | 1.9618
[7 empty] | 822 | 150 | 2.7438 | 1.9685
[7 empty] | 823 | 151 | 3.8073 | 2.8326
[7 empty] | 824 | 152 | 5.3079 | 4.0517
[7 empty] | 825 | 153 | 5.9097 | 4.5407
[7 empty] | 826 | 154 | 6.4621 | 4.9895
[7 empty] | 827 | 155 | 6.3137 | 4.869
[7 empty] | 828 | 156 | 6.4786 | 5.0029
[7 empty] | 829 | 157 | 7.1794 | 5.5723
[7 empty] | 830 | 158 | 7.5009 | 5.8335
[7 empty] | 831 | 159 | 7.7648 | 6.0479
[7 empty] | 832 | 160 | 7.6411 | 5.9474
[7 empty] | 833 | 161 | 8.3914 | 6.557
[7 empty] | 834 | 162 | 7.9049 | 6.1618
[7 empty] | 835 | 163 | 8.2594 | 6.4498
[7 empty] | 836 | 164 | 6.9321 | 5.3713
[7 empty] | 837 | 165 | 10.0073 | 7.8699
[7 empty] | 838 | 166 | 7.9956 | 6.2354
[7 empty] | 839 | 167 | 4.4504 | 3.3551
[7 empty] | 840 | 168 | 3.8156 | 2.8393
[7 empty] | 841 | 1 | 2.381 | 1.6738
[7 empty] | 842 | 2 | 2.2738 | 1.5867
[7 empty] | 843 | 3 | 2.2656 | 1.58
[7 empty] | 844 | 4 | 2.3975 | 1.6872
[7 empty] | 845 | 5 | 2.414 | 1.7006
[7 empty] | 846 | 6 | 2.8345 | 2.0422
[7 empty] | 847 | 7 | 3.5435 | 2.6183
[7 empty] | 848 | 8 | 4.2031 | 3.1541
[7 empty] | 849 | 9 | 4.1783 | 3.134
[7 empty] | 850 | 10 | 5.6706 | 4.3465
[7 empty] | 851 | 11 | 7.7153 | 6.0077
[7 empty] | 852 | 12 | 8.6634 | 6.778
[7 empty] | 853 | 13 | 9.0344 | 7.0795
[7 empty] | 854 | 14 | 8.8201 | 6.9053
[7 empty] | 855 | 15 | 8.7294 | 6.8316
[7 empty] | 856 | 16 | 9.8919 | 7.7761
[7 empty] | 857 | 17 | 11.1946 | 8.8345
[7 empty] | 858 | 18 | 10.9555 | 8.6402
[7 empty] | 859 | 19 | 11.4749 | 9.0622
[7 empty] | 860 | 20 | 11.4089 | 9.0086
[7 empty] | 861 | 21 | 11.9696 | 9.4641
[7 empty] | 862 | 22 | 8.0781 | 6.3024
[7 empty] | 863 | 23 | 4.368 | 3.2881
[7 empty] | 864 | 24 | 2.724 | 1.9525
[7 empty] | 865 | 25 | 2.6283 | 1.8747
[7 empty] | 866 | 26 | 2.5212 | 1.7877
[7 empty] | 867 | 27 | 2.4222 | 1.7073
[7 empty] | 868 | 28 | 2.5047 | 1.7743
[7 empty] | 869 | 29 | 2.7438 | 1.9685
[7 empty] | 870 | 30 | 2.9829 | 2.1628
[7 empty] | 871 | 31 | 3.8156 | 2.8393
[7 empty] | 872 | 32 | 4.1618 | 3.1207
[7 empty] | 873 | 33 | 4.8132 | 3.6498
[7 empty] | 874 | 34 | 5.6954 | 4.3666
[7 empty] | 875 | 35 | 7.8307 | 6.1015
[7 empty] | 876 | 36 | 8.8448 | 6.9254
[7 empty] | 877 | 37 | 8.919 | 6.9857
[7 empty] | 878 | 38 | 8.9932 | 7.046
[7 empty] | 879 | 39 | 8.6717 | 6.7847
[7 empty] | 880 | 40 | 9.7105 | 7.6287
[7 empty] | 881 | 41 | 10.2547 | 8.0708
[7 empty] | 882 | 42 | 10.2711 | 8.0842
[7 empty] | 883 | 43 | 10.6339 | 8.379
[7 empty] | 884 | 44 | 11.7717 | 9.3034
[7 empty] | 885 | 45 | 11.3759 | 8.9818
[7 empty] | 886 | 46 | 8.6717 | 6.7847
[7 empty] | 887 | 47 | 5.1265 | 3.9044
[7 empty] | 888 | 48 | 3.6507 | 2.7053
[7 empty] | 889 | 49 | 2.9993 | 2.1762
[7 empty] | 890 | 50 | 2.6943 | 1.9283
[7 empty] | 891 | 51 | 2.5871 | 1.8412
[7 empty] | 892 | 52 | 2.6201 | 1.868
[7 empty] | 893 | 53 | 2.6448 | 1.8881
[7 empty] | 894 | 54 | 3.2137 | 2.3503
[7 empty] | 895 | 55 | 4.335 | 3.2613
[7 empty] | 896 | 56 | 4.5741 | 3.4556
[7 empty] | 897 | 57 | 5.5057 | 4.2125
[7 empty] | 898 | 58 | 6.594 | 5.0967
[7 empty] | 899 | 59 | 7.7813 | 6.0613
[7 empty] | 900 | 60 | 8.3996 | 6.5637
[7 empty] | 901 | 61 | 9.0674 | 7.1063
[7 empty] | 902 | 62 | 8.8696 | 6.9455
[7 empty] | 903 | 63 | 9.4549 | 7.4211
[7 empty] | 904 | 64 | 10.3866 | 8.178
[7 empty] | 905 | 65 | 10.9967 | 8.6737
[7 empty] | 906 | 66 | 10.8977 | 8.5933
[7 empty] | 907 | 67 | 11.6233 | 9.1828
[7 empty] | 908 | 68 | 11.8624 | 9.377
[7 empty] | 909 | 69 | 11.3594 | 8.9684
[7 empty] | 910 | 70 | 9.1004 | 7.133
[7 empty] | 911 | 71 | 4.6565 | 3.5226
[7 empty] | 912 | 72 | 3.5894 | 2.6556
[7 empty] | 913 | 73 | 2.8839 | 2.0824
[7 empty] | 914 | 74 | 2.6613 | 1.9015
[7 empty] | 915 | 75 | 2.5624 | 1.8211
[7 empty] | 916 | 76 | 2.5047 | 1.7743
[7 empty] | 917 | 77 | 2.6778 | 1.9149
[7 empty] | 918 | 78 | 3.0735 | 2.2365
[7 empty] | 919 | 79 | 4.1701 | 3.1274
[7 empty] | 920 | 80 | 4.3432 | 3.268
[7 empty] | 921 | 81 | 5.5057 | 4.2125
[7 empty] | 922 | 82 | 6.5775 | 5.0833
[7 empty] | 923 | 83 | 7.3031 | 5.6728
[7 empty] | 924 | 84 | 8.5233 | 6.6642
[7 empty] | 925 | 85 | 8.2265 | 6.423
[7 empty] | 926 | 86 | 7.7235 | 6.0144
[7 empty] | 927 | 87 | 8.1605 | 6.3694
[7 empty] | 928 | 88 | 8.8118 | 6.8986
[7 empty] | 929 | 89 | 10.1392 | 7.9771
[7 empty] | 930 | 90 | 9.5621 | 7.5082
[7 empty] | 931 | 91 | 10.2382 | 8.0574
[7 empty] | 932 | 92 | 9.6446 | 7.5751
[7 empty] | 933 | 93 | 7.2701 | 5.646
[7 empty] | 934 | 94 | 6.3797 | 4.9225
[7 empty] | 935 | 95 | 4.5493 | 3.4355
[7 empty] | 936 | 96 | 3.5765 | 2.6451
[7 empty] | 937 | 97 | 3.527 | 2.6049
[7 empty] | 938 | 98 | 3.2384 | 2.3704
[7 empty] | 939 | 99 | 3.1807 | 2.3235
[7 empty] | 940 | 100 | 2.8345 | 2.0422
[7 empty] | 941 | 101 | 2.7767 | 1.9953
[7 empty] | 942 | 102 | 3.0076 | 2.1829
[7 empty] | 943 | 103 | 3.7414 | 2.779
[7 empty] | 944 | 104 | 3.9887 | 2.98
[7 empty] | 945 | 105 | 4.4669 | 3.3685
[7 empty] | 946 | 106 | 5.9015 | 4.534
[7 empty] | 947 | 107 | 6.2477 | 4.8154
[7 empty] | 948 | 108 | 7.7977 | 6.0747
[7 empty] | 949 | 109 | 7.1464 | 5.5455
[7 empty] | 950 | 110 | 6.7012 | 5.1838
[7 empty] | 951 | 111 | 6.5446 | 5.0565
[7 empty] | 952 | 112 | 6.6105 | 5.1101
[7 empty] | 953 | 113 | 6.2725 | 4.8355
[7 empty] | 954 | 114 | 6.4374 | 4.9694
[7 empty] | 955 | 115 | 5.9922 | 4.6077
[7 empty] | 956 | 116 | 6.66 | 5.1503
[7 empty] | 957 | 117 | 6.2477 | 4.8154
[7 empty] | 958 | 118 | 5.4892 | 4.1991
[7 empty] | 959 | 119 | 3.9227 | 2.9264
[7 empty] | 960 | 120 | 3.6106 | 2.6728
[7 empty] | 961 | 121 | 2.8922 | 2.0891
[7 empty] | 962 | 122 | 2.4882 | 1.7609
[7 empty] | 963 | 123 | 2.4057 | 1.6939
[7 empty] | 964 | 124 | 2.3727 | 1.6671
[7 empty] | 965 | 125 | 2.3315 | 1.6336
[7 empty] | 966 | 126 | 2.4717 | 1.7475
[7 empty] | 967 | 127 | 3.9557 | 2.9532
[7 empty] | 968 | 128 | 5.4892 | 4.1991
[7 empty] | 969 | 129 | 6.1571 | 4.7417
[7 empty] | 970 | 130 | 6.5858 | 5.09
[7 empty] | 971 | 131 | 6.7424 | 5.2173
[7 empty] | 972 | 132 | 6.4951 | 5.0163
[7 empty] | 973 | 133 | 7.1217 | 5.5254
[7 empty] | 974 | 134 | 7.4185 | 5.7666
[7 empty] | 975 | 135 | 7.4844 | 5.8201
[7 empty] | 976 | 136 | 6.6847 | 5.1704
[7 empty] | 977 | 137 | 6.5858 | 5.09
[7 empty] | 978 | 138 | 6.5363 | 5.0498
[7 empty] | 979 | 139 | 6.2065 | 4.7819
[7 empty] | 980 | 140 | 6.2148 | 4.7886
[7 empty] | 981 | 141 | 5.5717 | 4.2661
[7 empty] | 982 | 142 | 4.9451 | 3.757
[7 empty] | 983 | 143 | 4.0794 | 3.0537
[7 empty] | 984 | 144 | 3.4775 | 2.5647
[7 empty] | 985 | 145 | 3.0158 | 2.1896
[7 empty] | 986 | 146 | 2.8097 | 2.0221
[7 empty] | 987 | 147 | 2.7438 | 1.9685
[7 empty] | 988 | 148 | 2.7355 | 1.9618
[7 empty] | 989 | 149 | 2.7355 | 1.9618
[7 empty] | 990 | 150 | 2.7438 | 1.9685
[7 empty] | 991 | 151 | 3.8073 | 2.8326
[7 empty] | 992 | 152 | 5.3079 | 4.0517
[7 empty] | 993 | 153 | 5.9097 | 4.5407
[7 empty] | 994 | 154 | 6.4621 | 4.9895
[7 empty] | 995 | 155 | 6.3137 | 4.869
[7 empty] | 996 | 156 | 6.4786 | 5.0029
[7 empty] | 997 | 157 | 7.1794 | 5.5723
[7 empty] | 998 | 158 | 7.5009 | 5.8335
[7 empty] | 999 | 159 | 7.7648 | 6.0479
[7 empty] | 1000 | 160 | 7.6411 | 5.9474
[7 empty] | 1001 | 161 | 8.3914 | 6.557
[7 empty] | 1002 | 162 | 7.9049 | 6.1618
[7 empty] | 1003 | 163 | 8.2594 | 6.4498
[7 empty] | 1004 | 164 | 6.9321 | 5.3713
[7 empty] | 1005 | 165 | 10.0073 | 7.8699
[7 empty] | 1006 | 166 | 7.9956 | 6.2354
[7 empty] | 1007 | 167 | 4.4504 | 3.3551
[7 empty] | 1008 | 168 | 3.8156 | 2.8393
[7 empty] | 1009 | 1 | 2.381 | 1.6738
[7 empty] | 1010 | 2 | 2.2738 | 1.5867
[7 empty] | 1011 | 3 | 2.2656 | 1.58
[7 empty] | 1012 | 4 | 2.3975 | 1.6872
[7 empty] | 1013 | 5 | 2.414 | 1.7006
[7 empty] | 1014 | 6 | 2.8345 | 2.0422
[7 empty] | 1015 | 7 | 3.5435 | 2.6183
[7 empty] | 1016 | 8 | 4.2031 | 3.1541
[7 empty] | 1017 | 9 | 4.1783 | 3.134
[7 empty] | 1018 | 10 | 5.6706 | 4.3465
[7 empty] | 1019 | 11 | 7.7153 | 6.0077
[7 empty] | 1020 | 12 | 8.6634 | 6.778
[7 empty] | 1021 | 13 | 9.0344 | 7.0795
[7 empty] | 1022 | 14 | 8.8201 | 6.9053
[7 empty] | 1023 | 15 | 8.7294 | 6.8316
[7 empty] | 1024 | 16 | 9.8919 | 7.7761
[7 empty] | 1025 | 17 | 11.1946 | 8.8345
[7 empty] | 1026 | 18 | 10.9555 | 8.6402
[7 empty] | 1027 | 19 | 11.4749 | 9.0622
[7 empty] | 1028 | 20 | 11.4089 | 9.0086
[7 empty] | 1029 | 21 | 11.9696 | 9.4641
[7 empty] | 1030 | 22 | 8.0781 | 6.3024
[7 empty] | 1031 | 23 | 4.368 | 3.2881
[7 empty] | 1032 | 24 | 2.724 | 1.9525
[7 empty] | 1033 | 25 | 2.6283 | 1.8747
[7 empty] | 1034 | 26 | 2.5212 | 1.7877
[7 empty] | 1035 | 27 | 2.4222 | 1.7073
[7 empty] | 1036 | 28 | 2.5047 | 1.7743
[7 empty] | 1037 | 29 | 2.7438 | 1.9685
[7 empty] | 1038 | 30 | 2.9829 | 2.1628
[7 empty] | 1039 | 31 | 3.8156 | 2.8393
[7 empty] | 1040 | 32 | 4.1618 | 3.1207
[7 empty] | 1041 | 33 | 4.8132 | 3.6498
[7 empty] | 1042 | 34 | 5.6954 | 4.3666
[7 empty] | 1043 | 35 | 7.8307 | 6.1015
[7 empty] | 1044 | 36 | 8.8448 | 6.9254
[7 empty] | 1045 | 37 | 8.919 | 6.9857
[7 empty] | 1046 | 38 | 8.9932 | 7.046
[7 empty] | 1047 | 39 | 8.6717 | 6.7847
[7 empty] | 1048 | 40 | 9.7105 | 7.6287
[7 empty] | 1049 | 41 | 10.2547 | 8.0708
[7 empty] | 1050 | 42 | 10.2711 | 8.0842
[7 empty] | 1051 | 43 | 10.6339 | 8.379
[7 empty] | 1052 | 44 | 11.7717 | 9.3034
[7 empty] | 1053 | 45 | 11.3759 | 8.9818
[7 empty] | 1054 | 46 | 8.6717 | 6.7847
[7 empty] | 1055 | 47 | 5.1265 | 3.9044
[7 empty] | 1056 | 48 | 3.6507 | 2.7053
[7 empty] | 1057 | 49 | 2.9993 | 2.1762
[7 empty] | 1058 | 50 | 2.6943 | 1.9283
[7 empty] | 1059 | 51 | 2.5871 | 1.8412
[7 empty] | 1060 | 52 | 2.6201 | 1.868
[7 empty] | 1061 | 53 | 2.6448 | 1.8881
[7 empty] | 1062 | 54 | 3.2137 | 2.3503
[7 empty] | 1063 | 55 | 4.335 | 3.2613
[7 empty] | 1064 | 56 | 4.5741 | 3.4556
[7 empty] | 1065 | 57 | 5.5057 | 4.2125
[7 empty] | 1066 | 58 | 6.594 | 5.0967
[7 empty] | 1067 | 59 | 7.7813 | 6.0613
[7 empty] | 1068 | 60 | 8.3996 | 6.5637
[7 empty] | 1069 | 61 | 9.0674 | 7.1063
[7 empty] | 1070 | 62 | 8.8696 | 6.9455
[7 empty] | 1071 | 63 | 9.4549 | 7.4211
[7 empty] | 1072 | 64 | 10.3866 | 8.178
[7 empty] | 1073 | 65 | 10.9967 | 8.6737
[7 empty] | 1074 | 66 | 10.8977 | 8.5933
[7 empty] | 1075 | 67 | 11.6233 | 9.1828
[7 empty] | 1076 | 68 | 11.8624 | 9.377
[7 empty] | 1077 | 69 | 11.3594 | 8.9684
[7 empty] | 1078 | 70 | 9.1004 | 7.133
[7 empty] | 1079 | 71 | 4.6565 | 3.5226
[7 empty] | 1080 | 72 | 3.5894 | 2.6556
[7 empty] | 1081 | 73 | 2.8839 | 2.0824
[7 empty] | 1082 | 74 | 2.6613 | 1.9015
[7 empty] | 1083 | 75 | 2.5624 | 1.8211
[7 empty] | 1084 | 76 | 2.5047 | 1.7743
[7 empty] | 1085 | 77 | 2.6778 | 1.9149
[7 empty] | 1086 | 78 | 3.0735 | 2.2365
[7 empty] | 1087 | 79 | 4.1701 | 3.1274
[7 empty] | 1088 | 80 | 4.3432 | 3.268
[7 empty] | 1089 | 81 | 5.5057 | 4.2125
[7 empty] | 1090 | 82 | 6.5775 | 5.0833
[7 empty] | 1091 | 83 | 7.3031 | 5.6728
[7 empty] | 1092 | 84 | 8.5233 | 6.6642
[7 empty] | 1093 | 85 | 8.2265 | 6.423
[7 empty] | 1094 | 86 | 7.7235 | 6.0144
[7 empty] | 1095 | 87 | 8.1605 | 6.3694
[7 empty] | 1096 | 88 | 8.8118 | 6.8986
[7 empty] | 1097 | 89 | 10.1392 | 7.9771
[7 empty] | 1098 | 90 | 9.5621 | 7.5082
[7 empty] | 1099 | 91 | 10.2382 | 8.0574
[7 empty] | 1100 | 92 | 9.6446 | 7.5751
[7 empty] | 1101 | 93 | 7.2701 | 5.646
[7 empty] | 1102 | 94 | 6.3797 | 4.9225
[7 empty] | 1103 | 95 | 4.5493 | 3.4355
[7 empty] | 1104 | 96 | 3.5765 | 2.6451
[7 empty] | 1105 | 97 | 3.527 | 2.6049
[7 empty] | 1106 | 98 | 3.2384 | 2.3704
[7 empty] | 1107 | 99 | 3.1807 | 2.3235
[7 empty] | 1108 | 100 | 2.8345 | 2.0422
[7 empty] | 1109 | 101 | 2.7767 | 1.9953
[7 empty] | 1110 | 102 | 3.0076 | 2.1829
[7 empty] | 1111 | 103 | 3.7414 | 2.779
[7 empty] | 1112 | 104 | 3.9887 | 2.98
[7 empty] | 1113 | 105 | 4.4669 | 3.3685
[7 empty] | 1114 | 106 | 5.9015 | 4.534
[7 empty] | 1115 | 107 | 6.2477 | 4.8154
[7 empty] | 1116 | 108 | 7.7977 | 6.0747
[7 empty] | 1117 | 109 | 7.1464 | 5.5455
[7 empty] | 1118 | 110 | 6.7012 | 5.1838
[7 empty] | 1119 | 111 | 6.5446 | 5.0565
[7 empty] | 1120 | 112 | 6.6105 | 5.1101
[7 empty] | 1121 | 113 | 6.2725 | 4.8355
[7 empty] | 1122 | 114 | 6.4374 | 4.9694
[7 empty] | 1123 | 115 | 5.9922 | 4.6077
[7 empty] | 1124 | 116 | 6.66 | 5.1503
[7 empty] | 1125 | 117 | 6.2477 | 4.8154
[7 empty] | 1126 | 118 | 5.4892 | 4.1991
[7 empty] | 1127 | 119 | 3.9227 | 2.9264
[7 empty] | 1128 | 120 | 3.6106 | 2.6728
[7 empty] | 1129 | 121 | 2.8922 | 2.0891
[7 empty] | 1130 | 122 | 2.4882 | 1.7609
[7 empty] | 1131 | 123 | 2.4057 | 1.6939
[7 empty] | 1132 | 124 | 2.3727 | 1.6671
[7 empty] | 1133 | 125 | 2.3315 | 1.6336
[7 empty] | 1134 | 126 | 2.4717 | 1.7475
[7 empty] | 1135 | 127 | 3.9557 | 2.9532
[7 empty] | 1136 | 128 | 5.4892 | 4.1991
[7 empty] | 1137 | 129 | 6.1571 | 4.7417
[7 empty] | 1138 | 130 | 6.5858 | 5.09
[7 empty] | 1139 | 131 | 6.7424 | 5.2173
[7 empty] | 1140 | 132 | 6.4951 | 5.0163
[7 empty] | 1141 | 133 | 7.1217 | 5.5254
[7 empty] | 1142 | 134 | 7.4185 | 5.7666
[7 empty] | 1143 | 135 | 7.4844 | 5.8201
[7 empty] | 1144 | 136 | 6.6847 | 5.1704
[7 empty] | 1145 | 137 | 6.5858 | 5.09
[7 empty] | 1146 | 138 | 6.5363 | 5.0498
[7 empty] | 1147 | 139 | 6.2065 | 4.7819
[7 empty] | 1148 | 140 | 6.2148 | 4.7886
[7 empty] | 1149 | 141 | 5.5717 | 4.2661
[7 empty] | 1150 | 142 | 4.9451 | 3.757
[7 empty] | 1151 | 143 | 4.0794 | 3.0537
[7 empty] | 1152 | 144 | 3.4775 | 2.5647
[7 empty] | 1153 | 145 | 3.0158 | 2.1896
[7 empty] | 1154 | 146 | 2.8097 | 2.0221
[7 empty] | 1155 | 147 | 2.7438 | 1.9685
[7 empty] | 1156 | 148 | 2.7355 | 1.9618
[7 empty] | 1157 | 149 | 2.7355 | 1.9618
[7 empty] | 1158 | 150 | 2.7438 | 1.9685
[7 empty] | 1159 | 151 | 3.8073 | 2.8326
[7 empty] | 1160 | 152 | 5.3079 | 4.0517
[7 empty] | 1161 | 153 | 5.9097 | 4.5407
[7 empty] | 1162 | 154 | 6.4621 | 4.9895
[7 empty] | 1163 | 155 | 6.3137 | 4.869
[7 empty] | 1164 | 156 | 6.4786 | 5.0029
[7 empty] | 1165 | 157 | 7.1794 | 5.5723
[7 empty] | 1166 | 158 | 7.5009 | 5.8335
[7 empty] | 1167 | 159 | 7.7648 | 6.0479
[7 empty] | 1168 | 160 | 7.6411 | 5.9474
[7 empty] | 1169 | 161 | 8.3914 | 6.557
[7 empty] | 1170 | 162 | 7.9049 | 6.1618
[7 empty] | 1171 | 163 | 8.2594 | 6.4498
[7 empty] | 1172 | 164 | 6.9321 | 5.3713
[7 empty] | 1173 | 165 | 10.0073 | 7.8699
[7 empty] | 1174 | 166 | 7.9956 | 6.2354
[7 empty] | 1175 | 167 | 4.4504 | 3.3551
[7 empty] | 1176 | 168 | 3.8156 | 2.8393
[7 empty] | 1177 | 1 | 2.381 | 1.6738
[7 empty] | 1178 | 2 | 2.2738 | 1.5867
[7 empty] | 1179 | 3 | 2.2656 | 1.58
[7 empty] | 1180 | 4 | 2.3975 | 1.6872
[7 empty] | 1181 | 5 | 2.414 | 1.7006
[7 empty] | 1182 | 6 | 2.8345 | 2.0422
[7 empty] | 1183 | 7 | 3.5435 | 2.6183
[7 empty] | 1184 | 8 | 4.2031 | 3.1541
[7 empty] | 1185 | 9 | 4.1783 | 3.134
[7 empty] | 1186 | 10 | 5.6706 | 4.3465
[7 empty] | 1187 | 11 | 7.7153 | 6.0077
[7 empty] | 1188 | 12 | 8.6634 | 6.778
[7 empty] | 1189 | 13 | 9.0344 | 7.0795
[7 empty] | 1190 | 14 | 8.8201 | 6.9053
[7 empty] | 1191 | 15 | 8.7294 | 6.8316
[7 empty] | 1192 | 16 | 9.8919 | 7.7761
[7 empty] | 1193 | 17 | 11.1946 | 8.8345
[7 empty] | 1194 | 18 | 10.9555 | 8.6402
[7 empty] | 1195 | 19 | 11.4749 | 9.0622
[7 empty] | 1196 | 20 | 11.4089 | 9.0086
[7 empty] | 1197 | 21 | 11.9696 | 9.4641
[7 empty] | 1198 | 22 | 8.0781 | 6.3024
[7 empty] | 1199 | 23 | 4.368 | 3.2881
[7 empty] | 1200 | 24 | 2.724 | 1.9525
[7 empty] | 1201 | 25 | 2.6283 | 1.8747
[7 empty] | 1202 | 26 | 2.5212 | 1.7877
[7 empty] | 1203 | 27 | 2.4222 | 1.7073
[7 empty] | 1204 | 28 | 2.5047 | 1.7743
[7 empty] | 1205 | 29 | 2.7438 | 1.9685
[7 empty] | 1206 | 30 | 2.9829 | 2.1628
[7 empty] | 1207 | 31 | 3.8156 | 2.8393
[7 empty] | 1208 | 32 | 4.1618 | 3.1207
[7 empty] | 1209 | 33 | 4.8132 | 3.6498
[7 empty] | 1210 | 34 | 5.6954 | 4.3666
[7 empty] | 1211 | 35 | 7.8307 | 6.1015
[7 empty] | 1212 | 36 | 8.8448 | 6.9254
[7 empty] | 1213 | 37 | 8.919 | 6.9857
[7 empty] | 1214 | 38 | 8.9932 | 7.046
[7 empty] | 1215 | 39 | 8.6717 | 6.7847
[7 empty] | 1216 | 40 | 9.7105 | 7.6287
[7 empty] | 1217 | 41 | 10.2547 | 8.0708
[7 empty] | 1218 | 42 | 10.2711 | 8.0842
[7 empty] | 1219 | 43 | 10.6339 | 8.379
[7 empty] | 1220 | 44 | 11.7717 | 9.3034
[7 empty] | 1221 | 45 | 11.3759 | 8.9818
[7 empty] | 1222 | 46 | 8.6717 | 6.7847
[7 empty] | 1223 | 47 | 5.1265 | 3.9044
[7 empty] | 1224 | 48 | 3.6507 | 2.7053
[7 empty] | 1225 | 49 | 2.9993 | 2.1762
[7 empty] | 1226 | 50 | 2.6943 | 1.9283
[7 empty] | 1227 | 51 | 2.5871 | 1.8412
[7 empty] | 1228 | 52 | 2.6201 | 1.868
[7 empty] | 1229 | 53 | 2.6448 | 1.8881
[7 empty] | 1230 | 54 | 3.2137 | 2.3503
[7 empty] | 1231 | 55 | 4.335 | 3.2613
[7 empty] | 1232 | 56 | 4.5741 | 3.4556
[7 empty] | 1233 | 57 | 5.5057 | 4.2125
[7 empty] | 1234 | 58 | 6.594 | 5.0967
[7 empty] | 1235 | 59 | 7.7813 | 6.0613
[7 empty] | 1236 | 60 | 8.3996 | 6.5637
[7 empty] | 1237 | 61 | 9.0674 | 7.1063
[7 empty] | 1238 | 62 | 8.8696 | 6.9455
[7 empty] | 1239 | 63 | 9.4549 | 7.4211
[7 empty] | 1240 | 64 | 10.3866 | 8.178
[7 empty] | 1241 | 65 | 10.9967 | 8.6737
[7 empty] | 1242 | 66 | 10.8977 | 8.5933
[7 empty] | 1243 | 67 | 11.6233 | 9.1828
[7 empty] | 1244 | 68 | 11.8624 | 9.377
[7 empty] | 1245 | 69 | 11.3594 | 8.9684
[7 empty] | 1246 | 70 | 9.1004 | 7.133
[7 empty] | 1247 | 71 | 4.6565 | 3.5226
[7 empty] | 1248 | 72 | 3.5894 | 2.6556
[7 empty] | 1249 | 73 | 2.8839 | 2.0824
[7 empty] | 1250 | 74 | 2.6613 | 1.9015
[7 empty] | 1251 | 75 | 2.5624 | 1.8211
[7 empty] | 1252 | 76 | 2.5047 | 1.7743
[7 empty] | 1253 | 77 | 2.6778 | 1.9149
[7 empty] | 1254 | 78 | 3.0735 | 2.2365
[7 empty] | 1255 | 79 | 4.1701 | 3.1274
[7 empty] | 1256 | 80 | 4.3432 | 3.268
[7 empty] | 1257 | 81 | 5.5057 | 4.2125
[7 empty] | 1258 | 82 | 6.5775 | 5.0833
[7 empty] | 1259 | 83 | 7.3031 | 5.6728
[7 empty] | 1260 | 84 | 8.5233 | 6.6642
[7 empty] | 1261 | 85 | 8.2265 | 6.423
[7 empty] | 1262 | 86 | 7.7235 | 6.0144
[7 empty] | 1263 | 87 | 8.1605 | 6.3694
[7 empty] | 1264 | 88 | 8.8118 | 6.8986
[7 empty] | 1265 | 89 | 10.1392 | 7.9771
[7 empty] | 1266 | 90 | 9.5621 | 7.5082
[7 empty] | 1267 | 91 | 10.2382 | 8.0574
[7 empty] | 1268 | 92 | 9.6446 | 7.5751
[7 empty] | 1269 | 93 | 7.2701 | 5.646
[7 empty] | 1270 | 94 | 6.3797 | 4.9225
[7 empty] | 1271 | 95 | 4.5493 | 3.4355
[7 empty] | 1272 | 96 | 3.5765 | 2.6451
[7 empty] | 1273 | 97 | 3.527 | 2.6049
[7 empty] | 1274 | 98 | 3.2384 | 2.3704
[7 empty] | 1275 | 99 | 3.1807 | 2.3235
[7 empty] | 1276 | 100 | 2.8345 | 2.0422
[7 empty] | 1277 | 101 | 2.7767 | 1.9953
[7 empty] | 1278 | 102 | 3.0076 | 2.1829
[7 empty] | 1279 | 103 | 3.7414 | 2.779
[7 empty] | 1280 | 104 | 3.9887 | 2.98
[7 empty] | 1281 | 105 | 4.4669 | 3.3685
[7 empty] | 1282 | 106 | 5.9015 | 4.534
[7 empty] | 1283 | 107 | 6.2477 | 4.8154
[7 empty] | 1284 | 108 | 7.7977 | 6.0747
[7 empty] | 1285 | 109 | 7.1464 | 5.5455
[7 empty] | 1286 | 110 | 6.7012 | 5.1838
[7 empty] | 1287 | 111 | 6.5446 | 5.0565
[7 empty] | 1288 | 112 | 6.6105 | 5.1101
[7 empty] | 1289 | 113 | 6.2725 | 4.8355
[7 empty] | 1290 | 114 | 6.4374 | 4.9694
[7 empty] | 1291 | 115 | 5.9922 | 4.6077
[7 empty] | 1292 | 116 | 6.66 | 5.1503
[7 empty] | 1293 | 117 | 6.2477 | 4.8154
[7 empty] | 1294 | 118 | 5.4892 | 4.1991
[7 empty] | 1295 | 119 | 3.9227 | 2.9264
[7 empty] | 1296 | 120 | 3.6106 | 2.6728
[7 empty] | 1297 | 121 | 2.8922 | 2.0891
[7 empty] | 1298 | 122 | 2.4882 | 1.7609
[7 empty] | 1299 | 123 | 2.4057 | 1.6939
[7 empty] | 1300 | 124 | 2.3727 | 1.6671
[7 empty] | 1301 | 125 | 2.3315 | 1.6336
[7 empty] | 1302 | 126 | 2.4717 | 1.7475
[7 empty] | 1303 | 127 | 3.9557 | 2.9532
[7 empty] | 1304 | 128 | 5.4892 | 4.1991
[7 empty] | 1305 | 129 | 6.1571 | 4.7417
[7 empty] | 1306 | 130 | 6.5858 | 5.09
[7 empty] | 1307 | 131 | 6.7424 | 5.2173
[7 empty] | 1308 | 132 | 6.4951 | 5.0163
[7 empty] | 1309 | 133 | 7.1217 | 5.5254
[7 empty] | 1310 | 134 | 7.4185 | 5.7666
[7 empty] | 1311 | 135 | 7.4844 | 5.8201
[7 empty] | 1312 | 136 | 6.6847 | 5.1704
[7 empty] | 1313 | 137 | 6.5858 | 5.09
[7 empty] | 1314 | 138 | 6.5363 | 5.0498
[7 empty] | 1315 | 139 | 6.2065 | 4.7819
[7 empty] | 1316 | 140 | 6.2148 | 4.7886
[7 empty] | 1317 | 141 | 5.5717 | 4.2661
[7 empty] | 1318 | 142 | 4.9451 | 3.757
[7 empty] | 1319 | 143 | 4.0794 | 3.0537
[7 empty] | 1320 | 144 | 3.4775 | 2.5647
[7 empty] | 1321 | 145 | 3.0158 | 2.1896
[7 empty] | 1322 | 146 | 2.8097 | 2.0221
[7 empty] | 1323 | 147 | 2.7438 | 1.9685
[7 empty] | 1324 | 148 | 2.7355 | 1.9618
[7 empty] | 1325 | 149 | 2.7355 | 1.9618
[7 empty] | 1326 | 150 | 2.7438 | 1.9685
[7 empty] | 1327 | 151 | 3.8073 | 2.8326
[7 empty] | 1328 | 152 | 5.3079 | 4.0517
[7 empty] | 1329 | 153 | 5.9097 | 4.5407
[7 empty] | 1330 | 154 | 6.4621 | 4.9895
[7 empty] | 1331 | 155 | 6.3137 | 4.869
[7 empty] | 1332 | 156 | 6.4786 | 5.0029
[7 empty] | 1333 | 157 | 7.1794 | 5.5723
[7 empty] | 1334 | 158 | 7.5009 | 5.8335
[7 empty] | 1335 | 159 | 7.7648 | 6.0479
[7 empty] | 1336 | 160 | 7.6411 | 5.9474
[7 empty] | 1337 | 161 | 8.3914 | 6.557
[7 empty] | 1338 | 162 | 7.9049 | 6.1618
[7 empty] | 1339 | 163 | 8.2594 | 6.4498
[7 empty] | 1340 | 164 | 6.9321 | 5.3713
[7 empty] | 1341 | 165 | 10.0073 | 7.8699
[7 empty] | 1342 | 166 | 7.9956 | 6.2354
[7 empty] | 1343 | 167 | 4.4504 | 3.3551
[7 empty] | 1344 | 168 | 3.8156 | 2.8393
[7 empty] | 1345 | 1 | 2.381 | 1.6738
[7 empty] | 1346 | 2 | 2.2738 | 1.5867
[7 empty] | 1347 | 3 | 2.2656 | 1.58
[7 empty] | 1348 | 4 | 2.3975 | 1.6872
[7 empty] | 1349 | 5 | 2.414 | 1.7006
[7 empty] | 1350 | 6 | 2.8345 | 2.0422
[7 empty] | 1351 | 7 | 3.5435 | 2.6183
[7 empty] | 1352 | 8 | 4.2031 | 3.1541
[7 empty] | 1353 | 9 | 4.1783 | 3.134
[7 empty] | 1354 | 10 | 5.6706 | 4.3465
[7 empty] | 1355 | 11 | 7.7153 | 6.0077
[7 empty] | 1356 | 12 | 8.6634 | 6.778
[7 empty] | 1357 | 13 | 9.0344 | 7.0795
[7 empty] | 1358 | 14 | 8.8201 | 6.9053
[7 empty] | 1359 | 15 | 8.7294 | 6.8316
[7 empty] | 1360 | 16 | 9.8919 | 7.7761
[7 empty] | 1361 | 17 | 11.1946 | 8.8345
[7 empty] | 1362 | 18 | 10.9555 | 8.6402
[7 empty] | 1363 | 19 | 11.4749 | 9.0622
[7 empty] | 1364 | 20 | 11.4089 | 9.0086
[7 empty] | 1365 | 21 | 11.9696 | 9.4641
[7 empty] | 1366 | 22 | 8.0781 | 6.3024
[7 empty] | 1367 | 23 | 4.368 | 3.2881
[7 empty] | 1368 | 24 | 2.724 | 1.9525
[7 empty] | 1369 | 25 | 2.6283 | 1.8747
[7 empty] | 1370 | 26 | 2.5212 | 1.7877
[7 empty] | 1371 | 27 | 2.4222 | 1.7073
[7 empty] | 1372 | 28 | 2.5047 | 1.7743
[7 empty] | 1373 | 29 | 2.7438 | 1.9685
[7 empty] | 1374 | 30 | 2.9829 | 2.1628
[7 empty] | 1375 | 31 | 3.8156 | 2.8393
[7 empty] | 1376 | 32 | 4.1618 | 3.1207
[7 empty] | 1377 | 33 | 4.8132 | 3.6498
[7 empty] | 1378 | 34 | 5.6954 | 4.3666
[7 empty] | 1379 | 35 | 7.8307 | 6.1015
[7 empty] | 1380 | 36 | 8.8448 | 6.9254
[7 empty] | 1381 | 37 | 8.919 | 6.9857
[7 empty] | 1382 | 38 | 8.9932 | 7.046
[7 empty] | 1383 | 39 | 8.6717 | 6.7847
[7 empty] | 1384 | 40 | 9.7105 | 7.6287
[7 empty] | 1385 | 41 | 10.2547 | 8.0708
[7 empty] | 1386 | 42 | 10.2711 | 8.0842
[7 empty] | 1387 | 43 | 10.6339 | 8.379
[7 empty] | 1388 | 44 | 11.7717 | 9.3034
[7 empty] | 1389 | 45 | 11.3759 | 8.9818
[7 empty] | 1390 | 46 | 8.6717 | 6.7847
[7 empty] | 1391 | 47 | 5.1265 | 3.9044
[7 empty] | 1392 | 48 | 3.6507 | 2.7053
[7 empty] | 1393 | 49 | 2.9993 | 2.1762
[7 empty] | 1394 | 50 | 2.6943 | 1.9283
[7 empty] | 1395 | 51 | 2.5871 | 1.8412
[7 empty] | 1396 | 52 | 2.6201 | 1.868
[7 empty] | 1397 | 53 | 2.6448 | 1.8881
[7 empty] | 1398 | 54 | 3.2137 | 2.3503
[7 empty] | 1399 | 55 | 4.335 | 3.2613
[7 empty] | 1400 | 56 | 4.5741 | 3.4556
[7 empty] | 1401 | 57 | 5.5057 | 4.2125
[7 empty] | 1402 | 58 | 6.594 | 5.0967
[7 empty] | 1403 | 59 | 7.7813 | 6.0613
[7 empty] | 1404 | 60 | 8.3996 | 6.5637
[7 empty] | 1405 | 61 | 9.0674 | 7.1063
[7 empty] | 1406 | 62 | 8.8696 | 6.9455
[7 empty] | 1407 | 63 | 9.4549 | 7.4211
[7 empty] | 1408 | 64 | 10.3866 | 8.178
[7 empty] | 1409 | 65 | 10.9967 | 8.6737
[7 empty] | 1410 | 66 | 10.8977 | 8.5933
[7 empty] | 1411 | 67 | 11.6233 | 9.1828
[7 empty] | 1412 | 68 | 11.8624 | 9.377
[7 empty] | 1413 | 69 | 11.3594 | 8.9684
[7 empty] | 1414 | 70 | 9.1004 | 7.133
[7 empty] | 1415 | 71 | 4.6565 | 3.5226
[7 empty] | 1416 | 72 | 3.5894 | 2.6556
[7 empty] | 1417 | 73 | 2.8839 | 2.0824
[7 empty] | 1418 | 74 | 2.6613 | 1.9015
[7 empty] | 1419 | 75 | 2.5624 | 1.8211
[7 empty] | 1420 | 76 | 2.5047 | 1.7743
[7 empty] | 1421 | 77 | 2.6778 | 1.9149
[7 empty] | 1422 | 78 | 3.0735 | 2.2365
[7 empty] | 1423 | 79 | 4.1701 | 3.1274
[7 empty] | 1424 | 80 | 4.3432 | 3.268
[7 empty] | 1425 | 81 | 5.5057 | 4.2125
[7 empty] | 1426 | 82 | 6.5775 | 5.0833
[7 empty] | 1427 | 83 | 7.3031 | 5.6728
[7 empty] | 1428 | 84 | 8.5233 | 6.6642
[7 empty] | 1429 | 85 | 8.2265 | 6.423
[7 empty] | 1430 | 86 | 7.7235 | 6.0144
[7 empty] | 1431 | 87 | 8.1605 | 6.3694
[7 empty] | 1432 | 88 | 8.8118 | 6.8986
[7 empty] | 1433 | 89 | 10.1392 | 7.9771
[7 empty] | 1434 | 90 | 9.5621 | 7.5082
[7 empty] | 1435 | 91 | 10.2382 | 8.0574
[7 empty] | 1436 | 92 | 9.6446 | 7.5751
[7 empty] | 1437 | 93 | 7.2701 | 5.646
[7 empty] | 1438 | 94 | 6.3797 | 4.9225
[7 empty] | 1439 | 95 | 4.5493 | 3.4355
[7 empty] | 1440 | 96 | 3.5765 | 2.6451
[7 empty] | 1441 | 97 | 3.527 | 2.6049
[7 empty] | 1442 | 98 | 3.2384 | 2.3704
[7 empty] | 1443 | 99 | 3.1807 | 2.3235
[7 empty] | 1444 | 100 | 2.8345 | 2.0422
[7 empty] | 1445 | 101 | 2.7767 | 1.9953
[7 empty] | 1446 | 102 | 3.0076 | 2.1829
[7 empty] | 1447 | 103 | 3.7414 | 2.779
[7 empty] | 1448 | 104 | 3.9887 | 2.98
[7 empty] | 1449 | 105 | 4.4669 | 3.3685
[7 empty] | 1450 | 106 | 5.9015 | 4.534
[7 empty] | 1451 | 107 | 6.2477 | 4.8154
[7 empty] | 1452 | 108 | 7.7977 | 6.0747
[7 empty] | 1453 | 109 | 7.1464 | 5.5455
[7 empty] | 1454 | 110 | 6.7012 | 5.1838
[7 empty] | 1455 | 111 | 6.5446 | 5.0565
[7 empty] | 1456 | 112 | 6.6105 | 5.1101
[7 empty] | 1457 | 113 | 6.2725 | 4.8355
[7 empty] | 1458 | 114 | 6.4374 | 4.9694
[7 empty] | 1459 | 115 | 5.9922 | 4.6077
[7 empty] | 1460 | 116 | 6.66 | 5.1503
[7 empty] | 1461 | 117 | 6.2477 | 4.8154
[7 empty] | 1462 | 118 | 5.4892 | 4.1991
[7 empty] | 1463 | 119 | 3.9227 | 2.9264
[7 empty] | 1464 | 120 | 3.6106 | 2.6728
[7 empty] | 1465 | 121 | 2.8922 | 2.0891
[7 empty] | 1466 | 122 | 2.4882 | 1.7609
[7 empty] | 1467 | 123 | 2.4057 | 1.6939
[7 empty] | 1468 | 124 | 2.3727 | 1.6671
[7 empty] | 1469 | 125 | 2.3315 | 1.6336
[7 empty] | 1470 | 126 | 2.4717 | 1.7475
[7 empty] | 1471 | 127 | 3.9557 | 2.9532
[7 empty] | 1472 | 128 | 5.4892 | 4.1991
[7 empty] | 1473 | 129 | 6.1571 | 4.7417
[7 empty] | 1474 | 130 | 6.5858 | 5.09
[7 empty] | 1475 | 131 | 6.7424 | 5.2173
[7 empty] | 1476 | 132 | 6.4951 | 5.0163
[7 empty] | 1477 | 133 | 7.1217 | 5.5254
[7 empty] | 1478 | 134 | 7.4185 | 5.7666
[7 empty] | 1479 | 135 | 7.4844 | 5.8201
[7 empty] | 1480 | 136 | 6.6847 | 5.1704
[7 empty] | 1481 | 137 | 6.5858 | 5.09
[7 empty] | 1482 | 138 | 6.5363 | 5.0498
[7 empty] | 1483 | 139 | 6.2065 | 4.7819
[7 empty] | 1484 | 140 | 6.2148 | 4.7886
[7 empty] | 1485 | 141 | 5.5717 | 4.2661
[7 empty] | 1486 | 142 | 4.9451 | 3.757
[7 empty] | 1487 | 143 | 4.0794 | 3.0537
[7 empty] | 1488 | 144 | 3.4775 | 2.5647
[7 empty] | 1489 | 145 | 3.0158 | 2.1896
[7 empty] | 1490 | 146 | 2.8097 | 2.0221
[7 empty] | 1491 | 147 | 2.7438 | 1.9685
[7 empty] | 1492 | 148 | 2.7355 | 1.9618
[7 empty] | 1493 | 149 | 2.7355 | 1.9618
[7 empty] | 1494 | 150 | 2.7438 | 1.9685
[7 empty] | 1495 | 151 | 3.8073 | 2.8326
[7 empty] | 1496 | 152 | 5.3079 | 4.0517
[7 empty] | 1497 | 153 | 5.9097 | 4.5407
[7 empty] | 1498 | 154 | 6.4621 | 4.9895
[7 empty] | 1499 | 155 | 6.3137 | 4.869
[7 empty] | 1500 | 156 | 6.4786 | 5.0029
[7 empty] | 1501 | 157 | 7.1794 | 5.5723
[7 empty] | 1502 | 158 | 7.5009 | 5.8335
[7 empty] | 1503 | 159 | 7.7648 | 6.0479
[7 empty] | 1504 | 160 | 7.6411 | 5.9474
[7 empty] | 1505 | 161 | 8.3914 | 6.557
[7 empty] | 1506 | 162 | 7.9049 | 6.1618
[7 empty] | 1507 | 163 | 8.2594 | 6.4498
[7 empty] | 1508 | 164 | 6.9321 | 5.3713
[7 empty] | 1509 | 165 | 10.0073 | 7.8699
[7 empty] | 1510 | 166 | 7.9956 | 6.2354
[7 empty] | 1511 | 167 | 4.4504 | 3.3551
[7 empty] | 1512 | 168 | 3.8156 | 2.8393
[7 empty] | 1513 | 1 | 2.381 | 1.6738
[7 empty] | 1514 | 2 | 2.2738 | 1.5867
[7 empty] | 1515 | 3 | 2.2656 | 1.58
[7 empty] | 1516 | 4 | 2.3975 | 1.6872
[7 empty] | 1517 | 5 | 2.414 | 1.7006
[7 empty] | 1518 | 6 | 2.8345 | 2.0422
[7 empty] | 1519 | 7 | 3.5435 | 2.6183
[7 empty] | 1520 | 8 | 4.2031 | 3.1541
[7 empty] | 1521 | 9 | 4.1783 | 3.134
[7 empty] | 1522 | 10 | 5.6706 | 4.3465
[7 empty] | 1523 | 11 | 7.7153 | 6.0077
[7 empty] | 1524 | 12 | 8.6634 | 6.778
[7 empty] | 1525 | 13 | 9.0344 | 7.0795
[7 empty] | 1526 | 14 | 8.8201 | 6.9053
[7 empty] | 1527 | 15 | 8.7294 | 6.8316
[7 empty] | 1528 | 16 | 9.8919 | 7.7761
[7 empty] | 1529 | 17 | 11.1946 | 8.8345
[7 empty] | 1530 | 18 | 10.9555 | 8.6402
[7 empty] | 1531 | 19 | 11.4749 | 9.0622
[7 empty] | 1532 | 20 | 11.4089 | 9.0086
[7 empty] | 1533 | 21 | 11.9696 | 9.4641
[7 empty] | 1534 | 22 | 8.0781 | 6.3024
[7 empty] | 1535 | 23 | 4.368 | 3.2881
[7 empty] | 1536 | 24 | 2.724 | 1.9525
[7 empty] | 1537 | 25 | 2.6283 | 1.8747
[7 empty] | 1538 | 26 | 2.5212 | 1.7877
[7 empty] | 1539 | 27 | 2.4222 | 1.7073
[7 empty] | 1540 | 28 | 2.5047 | 1.7743
[7 empty] | 1541 | 29 | 2.7438 | 1.9685
[7 empty] | 1542 | 30 | 2.9829 | 2.1628
[7 empty] | 1543 | 31 | 3.8156 | 2.8393
[7 empty] | 1544 | 32 | 4.1618 | 3.1207
[7 empty] | 1545 | 33 | 4.8132 | 3.6498
[7 empty] | 1546 | 34 | 5.6954 | 4.3666
[7 empty] | 1547 | 35 | 7.8307 | 6.1015
[7 empty] | 1548 | 36 | 8.8448 | 6.9254
[7 empty] | 1549 | 37 | 8.919 | 6.9857
[7 empty] | 1550 | 38 | 8.9932 | 7.046
[7 empty] | 1551 | 39 | 8.6717 | 6.7847
[7 empty] | 1552 | 40 | 9.7105 | 7.6287
[7 empty] | 1553 | 41 | 10.2547 | 8.0708
[7 empty] | 1554 | 42 | 10.2711 | 8.0842
[7 empty] | 1555 | 43 | 10.6339 | 8.379
[7 empty] | 1556 | 44 | 11.7717 | 9.3034
[7 empty] | 1557 | 45 | 11.3759 | 8.9818
[7 empty] | 1558 | 46 | 8.6717 | 6.7847
[7 empty] | 1559 | 47 | 5.1265 | 3.9044
[7 empty] | 1560 | 48 | 3.6507 | 2.7053
[7 empty] | 1561 | 49 | 2.9993 | 2.1762
[7 empty] | 1562 | 50 | 2.6943 | 1.9283
[7 empty] | 1563 | 51 | 2.5871 | 1.8412
[7 empty] | 1564 | 52 | 2.6201 | 1.868
[7 empty] | 1565 | 53 | 2.6448 | 1.8881
[7 empty] | 1566 | 54 | 3.2137 | 2.3503
[7 empty] | 1567 | 55 | 4.335 | 3.2613
[7 empty] | 1568 | 56 | 4.5741 | 3.4556
[7 empty] | 1569 | 57 | 5.5057 | 4.2125
[7 empty] | 1570 | 58 | 6.594 | 5.0967
[7 empty] | 1571 | 59 | 7.7813 | 6.0613
[7 empty] | 1572 | 60 | 8.3996 | 6.5637
[7 empty] | 1573 | 61 | 9.0674 | 7.1063
[7 empty] | 1574 | 62 | 8.8696 | 6.9455
[7 empty] | 1575 | 63 | 9.4549 | 7.4211
[7 empty] | 1576 | 64 | 10.3866 | 8.178
[7 empty] | 1577 | 65 | 10.9967 | 8.6737
[7 empty] | 1578 | 66 | 10.8977 | 8.5933
[7 empty] | 1579 | 67 | 11.6233 | 9.1828
[7 empty] | 1580 | 68 | 11.8624 | 9.377
[7 empty] | 1581 | 69 | 11.3594 | 8.9684
[7 empty] | 1582 | 70 | 9.1004 | 7.133
[7 empty] | 1583 | 71 | 4.6565 | 3.5226
[7 empty] | 1584 | 72 | 3.5894 | 2.6556
[7 empty] | 1585 | 73 | 2.8839 | 2.0824
[7 empty] | 1586 | 74 | 2.6613 | 1.9015
[7 empty] | 1587 | 75 | 2.5624 | 1.8211
[7 empty] | 1588 | 76 | 2.5047 | 1.7743
[7 empty] | 1589 | 77 | 2.6778 | 1.9149
[7 empty] | 1590 | 78 | 3.0735 | 2.2365
[7 empty] | 1591 | 79 | 4.1701 | 3.1274
[7 empty] | 1592 | 80 | 4.3432 | 3.268
[7 empty] | 1593 | 81 | 5.5057 | 4.2125
[7 empty] | 1594 | 82 | 6.5775 | 5.0833
[7 empty] | 1595 | 83 | 7.3031 | 5.6728
[7 empty] | 1596 | 84 | 8.5233 | 6.6642
[7 empty] | 1597 | 85 | 8.2265 | 6.423
[7 empty] | 1598 | 86 | 7.7235 | 6.0144
[7 empty] | 1599 | 87 | 8.1605 | 6.3694
[7 empty] | 1600 | 88 | 8.8118 | 6.8986
[7 empty] | 1601 | 89 | 10.1392 | 7.9771
[7 empty] | 1602 | 90 | 9.5621 | 7.5082
[7 empty] | 1603 | 91 | 10.2382 | 8.0574
[7 empty] | 1604 | 92 | 9.6446 | 7.5751
[7 empty] | 1605 | 93 | 7.2701 | 5.646
[7 empty] | 1606 | 94 | 6.3797 | 4.9225
[7 empty] | 1607 | 95 | 4.5493 | 3.4355
[7 empty] | 1608 | 96 | 3.5765 | 2.6451
[7 empty] | 1609 | 97 | 3.527 | 2.6049
[7 empty] | 1610 | 98 | 3.2384 | 2.3704
[7 empty] | 1611 | 99 | 3.1807 | 2.3235
[7 empty] | 1612 | 100 | 2.8345 | 2.0422
[7 empty] | 1613 | 101 | 2.7767 | 1.9953
[7 empty] | 1614 | 102 | 3.0076 | 2.1829
[7 empty] | 1615 | 103 | 3.7414 | 2.779
[7 empty] | 1616 | 104 | 3.9887 | 2.98
[7 empty] | 1617 | 105 | 4.4669 | 3.3685
[7 empty] | 1618 | 106 | 5.9015 | 4.534
[7 empty] | 1619 | 107 | 6.2477 | 4.8154
[7 empty] | 1620 | 108 | 7.7977 | 6.0747
[7 empty] | 1621 | 109 | 7.1464 | 5.5455
[7 empty] | 1622 | 110 | 6.7012 | 5.1838
[7 empty] | 1623 | 111 | 6.5446 | 5.0565
[7 empty] | 1624 | 112 | 6.6105 | 5.1101
[7 empty] | 1625 | 113 | 6.2725 | 4.8355
[7 empty] | 1626 | 114 | 6.4374 | 4.9694
[7 empty] | 1627 | 115 | 5.9922 | 4.6077
[7 empty] | 1628 | 116 | 6.66 | 5.1503
[7 empty] | 1629 | 117 | 6.2477 | 4.8154
[7 empty] | 1630 | 118 | 5.4892 | 4.1991
[7 empty] | 1631 | 119 | 3.9227 | 2.9264
[7 empty] | 1632 | 120 | 3.6106 | 2.6728
[7 empty] | 1633 | 121 | 2.8922 | 2.0891
[7 empty] | 1634 | 122 | 2.4882 | 1.7609
[7 empty] | 1635 | 123 | 2.4057 | 1.6939
[7 empty] | 1636 | 124 | 2.3727 | 1.6671
[7 empty] | 1637 | 125 | 2.3315 | 1.6336
[7 empty] | 1638 | 126 | 2.4717 | 1.7475
[7 empty] | 1639 | 127 | 3.9557 | 2.9532
[7 empty] | 1640 | 128 | 5.4892 | 4.1991
[7 empty] | 1641 | 129 | 6.1571 | 4.7417
[7 empty] | 1642 | 130 | 6.5858 | 5.09
[7 empty] | 1643 | 131 | 6.7424 | 5.2173
[7 empty] | 1644 | 132 | 6.4951 | 5.0163
[7 empty] | 1645 | 133 | 7.1217 | 5.5254
[7 empty] | 1646 | 134 | 7.4185 | 5.7666
[7 empty] | 1647 | 135 | 7.4844 | 5.8201
[7 empty] | 1648 | 136 | 6.6847 | 5.1704
[7 empty] | 1649 | 137 | 6.5858 | 5.09
[7 empty] | 1650 | 138 | 6.5363 | 5.0498
[7 empty] | 1651 | 139 | 6.2065 | 4.7819
[7 empty] | 1652 | 140 | 6.2148 | 4.7886
[7 empty] | 1653 | 141 | 5.5717 | 4.2661
[7 empty] | 1654 | 142 | 4.9451 | 3.757
[7 empty] | 1655 | 143 | 4.0794 | 3.0537
[7 empty] | 1656 | 144 | 3.4775 | 2.5647
[7 empty] | 1657 | 145 | 3.0158 | 2.1896
[7 empty] | 1658 | 146 | 2.8097 | 2.0221
[7 empty] | 1659 | 147 | 2.7438 | 1.9685
[7 empty] | 1660 | 148 | 2.7355 | 1.9618
[7 empty] | 1661 | 149 | 2.7355 | 1.9618
[7 empty] | 1662 | 150 | 2.7438 | 1.9685
[7 empty] | 1663 | 151 | 3.8073 | 2.8326
[7 empty] | 1664 | 152 | 5.3079 | 4.0517
[7 empty] | 1665 | 153 | 5.9097 | 4.5407
[7 empty] | 1666 | 154 | 6.4621 | 4.9895
[7 empty] | 1667 | 155 | 6.3137 | 4.869
[7 empty] | 1668 | 156 | 6.4786 | 5.0029
[7 empty] | 1669 | 157 | 7.1794 | 5.5723
[7 empty] | 1670 | 158 | 7.5009 | 5.8335
[7 empty] | 1671 | 159 | 7.7648 | 6.0479
[7 empty] | 1672 | 160 | 7.6411 | 5.9474
[7 empty] | 1673 | 161 | 8.3914 | 6.557
[7 empty] | 1674 | 162 | 7.9049 | 6.1618
[7 empty] | 1675 | 163 | 8.2594 | 6.4498
[7 empty] | 1676 | 164 | 6.9321 | 5.3713
[7 empty] | 1677 | 165 | 10.0073 | 7.8699
[7 empty] | 1678 | 166 | 7.9956 | 6.2354
[7 empty] | 1679 | 167 | 4.4504 | 3.3551
[7 empty] | 1680 | 168 | 3.8156 | 2.8393
[7 empty] | 1681 | 1 | 2.381 | 1.6738
[7 empty] | 1682 | 2 | 2.2738 | 1.5867
[7 empty] | 1683 | 3 | 2.2656 | 1.58
[7 empty] | 1684 | 4 | 2.3975 | 1.6872
[7 empty] | 1685 | 5 | 2.414 | 1.7006
[7 empty] | 1686 | 6 | 2.8345 | 2.0422
[7 empty] | 1687 | 7 | 3.5435 | 2.6183
[7 empty] | 1688 | 8 | 4.2031 | 3.1541
[7 empty] | 1689 | 9 | 4.1783 | 3.134
[7 empty] | 1690 | 10 | 5.6706 | 4.3465
[7 empty] | 1691 | 11 | 7.7153 | 6.0077
[7 empty] | 1692 | 12 | 8.6634 | 6.778
[7 empty] | 1693 | 13 | 9.0344 | 7.0795
[7 empty] | 1694 | 14 | 8.8201 | 6.9053
[7 empty] | 1695 | 15 | 8.7294 | 6.8316
[7 empty] | 1696 | 16 | 9.8919 | 7.7761
[7 empty] | 1697 | 17 | 11.1946 | 8.8345
[7 empty] | 1698 | 18 | 10.9555 | 8.6402
[7 empty] | 1699 | 19 | 11.4749 | 9.0622
[7 empty] | 1700 | 20 | 11.4089 | 9.0086
[7 empty] | 1701 | 21 | 11.9696 | 9.4641
[7 empty] | 1702 | 22 | 8.0781 | 6.3024
[7 empty] | 1703 | 23 | 4.368 | 3.2881
[7 empty] | 1704 | 24 | 2.724 | 1.9525
[7 empty] | 1705 | 25 | 2.6283 | 1.8747
[7 empty] | 1706 | 26 | 2.5212 | 1.7877
[7 empty] | 1707 | 27 | 2.4222 | 1.7073
[7 empty] | 1708 | 28 | 2.5047 | 1.7743
[7 empty] | 1709 | 29 | 2.7438 | 1.9685
[7 empty] | 1710 | 30 | 2.9829 | 2.1628
[7 empty] | 1711 | 31 | 3.8156 | 2.8393
[7 empty] | 1712 | 32 | 4.1618 | 3.1207
[7 empty] | 1713 | 33 | 4.8132 | 3.6498
[7 empty] | 1714 | 34 | 5.6954 | 4.3666
[7 empty] | 1715 | 35 | 7.8307 | 6.1015
[7 empty] | 1716 | 36 | 8.8448 | 6.9254
[7 empty] | 1717 | 37 | 8.919 | 6.9857
[7 empty] | 1718 | 38 | 8.9932 | 7.046
[7 empty] | 1719 | 39 | 8.6717 | 6.7847
[7 empty] | 1720 | 40 | 9.7105 | 7.6287
[7 empty] | 1721 | 41 | 10.2547 | 8.0708
[7 empty] | 1722 | 42 | 10.2711 | 8.0842
[7 empty] | 1723 | 43 | 10.6339 | 8.379
[7 empty] | 1724 | 44 | 11.7717 | 9.3034
[7 empty] | 1725 | 45 | 11.3759 | 8.9818
[7 empty] | 1726 | 46 | 8.6717 | 6.7847
[7 empty] | 1727 | 47 | 5.1265 | 3.9044
[7 empty] | 1728 | 48 | 3.6507 | 2.7053
[7 empty] | 1729 | 49 | 2.9993 | 2.1762
[7 empty] | 1730 | 50 | 2.6943 | 1.9283
[7 empty] | 1731 | 51 | 2.5871 | 1.8412
[7 empty] | 1732 | 52 | 2.6201 | 1.868
[7 empty] | 1733 | 53 | 2.6448 | 1.8881
[7 empty] | 1734 | 54 | 3.2137 | 2.3503
[7 empty] | 1735 | 55 | 4.335 | 3.2613
[7 empty] | 1736 | 56 | 4.5741 | 3.4556
[7 empty] | 1737 | 57 | 5.5057 | 4.2125
[7 empty] | 1738 | 58 | 6.594 | 5.0967
[7 empty] | 1739 | 59 | 7.7813 | 6.0613
[7 empty] | 1740 | 60 | 8.3996 | 6.5637
[7 empty] | 1741 | 61 | 9.0674 | 7.1063
[7 empty] | 1742 | 62 | 8.8696 | 6.9455
[7 empty] | 1743 | 63 | 9.4549 | 7.4211
[7 empty] | 1744 | 64 | 10.3866 | 8.178
[7 empty] | 1745 | 65 | 10.9967 | 8.6737
[7 empty] | 1746 | 66 | 10.8977 | 8.5933
[7 empty] | 1747 | 67 | 11.6233 | 9.1828
[7 empty] | 1748 | 68 | 11.8624 | 9.377
[7 empty] | 1749 | 69 | 11.3594 | 8.9684
[7 empty] | 1750 | 70 | 9.1004 | 7.133
[7 empty] | 1751 | 71 | 4.6565 | 3.5226
[7 empty] | 1752 | 72 | 3.5894 | 2.6556
[7 empty] | 1753 | 73 | 2.8839 | 2.0824
[7 empty] | 1754 | 74 | 2.6613 | 1.9015
[7 empty] | 1755 | 75 | 2.5624 | 1.8211
[7 empty] | 1756 | 76 | 2.5047 | 1.7743
[7 empty] | 1757 | 77 | 2.6778 | 1.9149
[7 empty] | 1758 | 78 | 3.0735 | 2.2365
[7 empty] | 1759 | 79 | 4.1701 | 3.1274
[7 empty] | 1760 | 80 | 4.3432 | 3.268
[7 empty] | 1761 | 81 | 5.5057 | 4.2125
[7 empty] | 1762 | 82 | 6.5775 | 5.0833
[7 empty] | 1763 | 83 | 7.3031 | 5.6728
[7 empty] | 1764 | 84 | 8.5233 | 6.6642
[7 empty] | 1765 | 85 | 8.2265 | 6.423
[7 empty] | 1766 | 86 | 7.7235 | 6.0144
[7 empty] | 1767 | 87 | 8.1605 | 6.3694
[7 empty] | 1768 | 88 | 8.8118 | 6.8986
[7 empty] | 1769 | 89 | 10.1392 | 7.9771
[7 empty] | 1770 | 90 | 9.5621 | 7.5082
[7 empty] | 1771 | 91 | 10.2382 | 8.0574
[7 empty] | 1772 | 92 | 9.6446 | 7.5751
[7 empty] | 1773 | 93 | 7.2701 | 5.646
[7 empty] | 1774 | 94 | 6.3797 | 4.9225
[7 empty] | 1775 | 95 | 4.5493 | 3.4355
[7 empty] | 1776 | 96 | 3.5765 | 2.6451
[7 empty] | 1777 | 97 | 3.527 | 2.6049
[7 empty] | 1778 | 98 | 3.2384 | 2.3704
[7 empty] | 1779 | 99 | 3.1807 | 2.3235
[7 empty] | 1780 | 100 | 2.8345 | 2.0422
[7 empty] | 1781 | 101 | 2.7767 | 1.9953
[7 empty] | 1782 | 102 | 3.0076 | 2.1829
[7 empty] | 1783 | 103 | 3.7414 | 2.779
[7 empty] | 1784 | 104 | 3.9887 | 2.98
[7 empty] | 1785 | 105 | 4.4669 | 3.3685
[7 empty] | 1786 | 106 | 5.9015 | 4.534
[7 empty] | 1787 | 107 | 6.2477 | 4.8154
[7 empty] | 1788 | 108 | 7.7977 | 6.0747
[7 empty] | 1789 | 109 | 7.1464 | 5.5455
[7 empty] | 1790 | 110 | 6.7012 | 5.1838
[7 empty] | 1791 | 111 | 6.5446 | 5.0565
[7 empty] | 1792 | 112 | 6.6105 | 5.1101
[7 empty] | 1793 | 113 | 6.2725 | 4.8355
[7 empty] | 1794 | 114 | 6.4374 | 4.9694
[7 empty] | 1795 | 115 | 5.9922 | 4.6077
[7 empty] | 1796 | 116 | 6.66 | 5.1503
[7 empty] | 1797 | 117 | 6.2477 | 4.8154
[7 empty] | 1798 | 118 | 5.4892 | 4.1991
[7 empty] | 1799 | 119 | 3.9227 | 2.9264
[7 empty] | 1800 | 120 | 3.6106 | 2.6728
[7 empty] | 1801 | 121 | 2.8922 | 2.0891
[7 empty] | 1802 | 122 | 2.4882 | 1.7609
[7 empty] | 1803 | 123 | 2.4057 | 1.6939
[7 empty] | 1804 | 124 | 2.3727 | 1.6671
[7 empty] | 1805 | 125 | 2.3315 | 1.6336
[7 empty] | 1806 | 126 | 2.4717 | 1.7475
[7 empty] | 1807 | 127 | 3.9557 | 2.9532
[7 empty] | 1808 | 128 | 5.4892 | 4.1991
[7 empty] | 1809 | 129 | 6.1571 | 4.7417
[7 empty] | 1810 | 130 | 6.5858 | 5.09
[7 empty] | 1811 | 131 | 6.7424 | 5.2173
[7 empty] | 1812 | 132 | 6.4951 | 5.0163
[7 empty] | 1813 | 133 | 7.1217 | 5.5254
[7 empty] | 1814 | 134 | 7.4185 | 5.7666
[7 empty] | 1815 | 135 | 7.4844 | 5.8201
[7 empty] | 1816 | 136 | 6.6847 | 5.1704
[7 empty] | 1817 | 137 | 6.5858 | 5.09
[7 empty] | 1818 | 138 | 6.5363 | 5.0498
[7 empty] | 1819 | 139 | 6.2065 | 4.7819
[7 empty] | 1820 | 140 | 6.2148 | 4.7886
[7 empty] | 1821 | 141 | 5.5717 | 4.2661
[7 empty] | 1822 | 142 | 4.9451 | 3.757
[7 empty] | 1823 | 143 | 4.0794 | 3.0537
[7 empty] | 1824 | 144 | 3.4775 | 2.5647
[7 empty] | 1825 | 145 | 3.0158 | 2.1896
[7 empty] | 1826 | 146 | 2.8097 | 2.0221
[7 empty] | 1827 | 147 | 2.7438 | 1.9685
[7 empty] | 1828 | 148 | 2.7355 | 1.9618
[7 empty] | 1829 | 149 | 2.7355 | 1.9618
[7 empty] | 1830 | 150 | 2.7438 | 1.9685
[7 empty] | 1831 | 151 | 3.8073 | 2.8326
[7 empty] | 1832 | 152 | 5.3079 | 4.0517
[7 empty] | 1833 | 153 | 5.9097 | 4.5407
[7 empty] | 1834 | 154 | 6.4621 | 4.9895
[7 empty] | 1835 | 155 | 6.3137 | 4.869
[7 empty] | 1836 | 156 | 6.4786 | 5.0029
[7 empty] | 1837 | 157 | 7.1794 | 5.5723
[7 empty] | 1838 | 158 | 7.5009 | 5.8335
[7 empty] | 1839 | 159 | 7.7648 | 6.0479
[7 empty] | 1840 | 160 | 7.6411 | 5.9474
[7 empty] | 1841 | 161 | 8.3914 | 6.557
[7 empty] | 1842 | 162 | 7.9049 | 6.1618
[7 empty] | 1843 | 163 | 8.2594 | 6.4498
[7 empty] | 1844 | 164 | 6.9321 | 5.3713
[7 empty] | 1845 | 165 | 10.0073 | 7.8699
[7 empty] | 1846 | 166 | 7.9956 | 6.2354
[7 empty] | 1847 | 167 | 4.4504 | 3.3551
[7 empty] | 1848 | 168 | 3.8156 | 2.8393
[7 empty] | 1849 | 1 | 2.381 | 1.6738
[7 empty] | 1850 | 2 | 2.2738 | 1.5867
[7 empty] | 1851 | 3 | 2.2656 | 1.58
[7 empty] | 1852 | 4 | 2.3975 | 1.6872
[7 empty] | 1853 | 5 | 2.414 | 1.7006
[7 empty] | 1854 | 6 | 2.8345 | 2.0422
[7 empty] | 1855 | 7 | 3.5435 | 2.6183
[7 empty] | 1856 | 8 | 4.2031 | 3.1541
[7 empty] | 1857 | 9 | 4.1783 | 3.134
[7 empty] | 1858 | 10 | 5.6706 | 4.3465
[7 empty] | 1859 | 11 | 7.7153 | 6.0077
[7 empty] | 1860 | 12 | 8.6634 | 6.778
[7 empty] | 1861 | 13 | 9.0344 | 7.0795
[7 empty] | 1862 | 14 | 8.8201 | 6.9053
[7 empty] | 1863 | 15 | 8.7294 | 6.8316
[7 empty] | 1864 | 16 | 9.8919 | 7.7761
[7 empty] | 1865 | 17 | 11.1946 | 8.8345
[7 empty] | 1866 | 18 | 10.9555 | 8.6402
[7 empty] | 1867 | 19 | 11.4749 | 9.0622
[7 empty] | 1868 | 20 | 11.4089 | 9.0086
[7 empty] | 1869 | 21 | 11.9696 | 9.4641
[7 empty] | 1870 | 22 | 8.0781 | 6.3024
[7 empty] | 1871 | 23 | 4.368 | 3.2881
[7 empty] | 1872 | 24 | 2.724 | 1.9525
[7 empty] | 1873 | 25 | 2.6283 | 1.8747
[7 empty] | 1874 | 26 | 2.5212 | 1.7877
[7 empty] | 1875 | 27 | 2.4222 | 1.7073
[7 empty] | 1876 | 28 | 2.5047 | 1.7743
[7 empty] | 1877 | 29 | 2.7438 | 1.9685
[7 empty] | 1878 | 30 | 2.9829 | 2.1628
[7 empty] | 1879 | 31 | 3.8156 | 2.8393
[7 empty] | 1880 | 32 | 4.1618 | 3.1207
[7 empty] | 1881 | 33 | 4.8132 | 3.6498
[7 empty] | 1882 | 34 | 5.6954 | 4.3666
[7 empty] | 1883 | 35 | 7.8307 | 6.1015
[7 empty] | 1884 | 36 | 8.8448 | 6.9254
[7 empty] | 1885 | 37 | 8.919 | 6.9857
[7 empty] | 1886 | 38 | 8.9932 | 7.046
[7 empty] | 1887 | 39 | 8.6717 | 6.7847
[7 empty] | 1888 | 40 | 9.7105 | 7.6287
[7 empty] | 1889 | 41 | 10.2547 | 8.0708
[7 empty] | 1890 | 42 | 10.2711 | 8.0842
[7 empty] | 1891 | 43 | 10.6339 | 8.379
[7 empty] | 1892 | 44 | 11.7717 | 9.3034
[7 empty] | 1893 | 45 | 11.3759 | 8.9818
[7 empty] | 1894 | 46 | 8.6717 | 6.7847
[7 empty] | 1895 | 47 | 5.1265 | 3.9044
[7 empty] | 1896 | 48 | 3.6507 | 2.7053
[7 empty] | 1897 | 49 | 2.9993 | 2.1762
[7 empty] | 1898 | 50 | 2.6943 | 1.9283
[7 empty] | 1899 | 51 | 2.5871 | 1.8412
[7 empty] | 1900 | 52 | 2.6201 | 1.868
[7 empty] | 1901 | 53 | 2.6448 | 1.8881
[7 empty] | 1902 | 54 | 3.2137 | 2.3503
[7 empty] | 1903 | 55 | 4.335 | 3.2613
[7 empty] | 1904 | 56 | 4.5741 | 3.4556
[7 empty] | 1905 | 57 | 5.5057 | 4.2125
[7 empty] | 1906 | 58 | 6.594 | 5.0967
[7 empty] | 1907 | 59 | 7.7813 | 6.0613
[7 empty] | 1908 | 60 | 8.3996 | 6.5637
[7 empty] | 1909 | 61 | 9.0674 | 7.1063
[7 empty] | 1910 | 62 | 8.8696 | 6.9455
[7 empty] | 1911 | 63 | 9.4549 | 7.4211
[7 empty] | 1912 | 64 | 10.3866 | 8.178
[7 empty] | 1913 | 65 | 10.9967 | 8.6737
[7 empty] | 1914 | 66 | 10.8977 | 8.5933
[7 empty] | 1915 | 67 | 11.6233 | 9.1828
[7 empty] | 1916 | 68 | 11.8624 | 9.377
[7 empty] | 1917 | 69 | 11.3594 | 8.9684
[7 empty] | 1918 | 70 | 9.1004 | 7.133
[7 empty] | 1919 | 71 | 4.6565 | 3.5226
[7 empty] | 1920 | 72 | 3.5894 | 2.6556
[7 empty] | 1921 | 73 | 2.8839 | 2.0824
[7 empty] | 1922 | 74 | 2.6613 | 1.9015
[7 empty] | 1923 | 75 | 2.5624 | 1.8211
[7 empty] | 1924 | 76 | 2.5047 | 1.7743
[7 empty] | 1925 | 77 | 2.6778 | 1.9149
[7 empty] | 1926 | 78 | 3.0735 | 2.2365
[7 empty] | 1927 | 79 | 4.1701 | 3.1274
[7 empty] | 1928 | 80 | 4.3432 | 3.268
[7 empty] | 1929 | 81 | 5.5057 | 4.2125
[7 empty] | 1930 | 82 | 6.5775 | 5.0833
[7 empty] | 1931 | 83 | 7.3031 | 5.6728
[7 empty] | 1932 | 84 | 8.5233 | 6.6642
[7 empty] | 1933 | 85 | 8.2265 | 6.423
[7 empty] | 1934 | 86 | 7.7235 | 6.0144
[7 empty] | 1935 | 87 | 8.1605 | 6.3694
[7 empty] | 1936 | 88 | 8.8118 | 6.8986
[7 empty] | 1937 | 89 | 10.1392 | 7.9771
[7 empty] | 1938 | 90 | 9.5621 | 7.5082
[7 empty] | 1939 | 91 | 10.2382 | 8.0574
[7 empty] | 1940 | 92 | 9.6446 | 7.5751
[7 empty] | 1941 | 93 | 7.2701 | 5.646
[7 empty] | 1942 | 94 | 6.3797 | 4.9225
[7 empty] | 1943 | 95 | 4.5493 | 3.4355
[7 empty] | 1944 | 96 | 3.5765 | 2.6451
[7 empty] | 1945 | 97 | 3.527 | 2.6049
[7 empty] | 1946 | 98 | 3.2384 | 2.3704
[7 empty] | 1947 | 99 | 3.1807 | 2.3235
[7 empty] | 1948 | 100 | 2.8345 | 2.0422
[7 empty] | 1949 | 101 | 2.7767 | 1.9953
[7 empty] | 1950 | 102 | 3.0076 | 2.1829
[7 empty] | 1951 | 103 | 3.7414 | 2.779
[7 empty] | 1952 | 104 | 3.9887 | 2.98
[7 empty] | 1953 | 105 | 4.4669 | 3.3685
[7 empty] | 1954 | 106 | 5.9015 | 4.534
[7 empty] | 1955 | 107 | 6.2477 | 4.8154
[7 empty] | 1956 | 108 | 7.7977 | 6.0747
[7 empty] | 1957 | 109 | 7.1464 | 5.5455
[7 empty] | 1958 | 110 | 6.7012 | 5.1838
[7 empty] | 1959 | 111 | 6.5446 | 5.0565
[7 empty] | 1960 | 112 | 6.6105 | 5.1101
[7 empty] | 1961 | 113 | 6.2725 | 4.8355
[7 empty] | 1962 | 114 | 6.4374 | 4.9694
[7 empty] | 1963 | 115 | 5.9922 | 4.6077
[7 empty] | 1964 | 116 | 6.66 | 5.1503
[7 empty] | 1965 | 117 | 6.2477 | 4.8154
[7 empty] | 1966 | 118 | 5.4892 | 4.1991
[7 empty] | 1967 | 119 | 3.9227 | 2.9264
[7 empty] | 1968 | 120 | 3.6106 | 2.6728
[7 empty] | 1969 | 121 | 2.8922 | 2.0891
[7 empty] | 1970 | 122 | 2.4882 | 1.7609
[7 empty] | 1971 | 123 | 2.4057 | 1.6939
[7 empty] | 1972 | 124 | 2.3727 | 1.6671
[7 empty] | 1973 | 125 | 2.3315 | 1.6336
[7 empty] | 1974 | 126 | 2.4717 | 1.7475
[7 empty] | 1975 | 127 | 3.9557 | 2.9532
[7 empty] | 1976 | 128 | 5.4892 | 4.1991
[7 empty] | 1977 | 129 | 6.1571 | 4.7417
[7 empty] | 1978 | 130 | 6.5858 | 5.09
[7 empty] | 1979 | 131 | 6.7424 | 5.2173
[7 empty] | 1980 | 132 | 6.4951 | 5.0163
[7 empty] | 1981 | 133 | 7.1217 | 5.5254
[7 empty] | 1982 | 134 | 7.4185 | 5.7666
[7 empty] | 1983 | 135 | 7.4844 | 5.8201
[7 empty] | 1984 | 136 | 6.6847 | 5.1704
[7 empty] | 1985 | 137 | 6.5858 | 5.09
[7 empty] | 1986 | 138 | 6.5363 | 5.0498
[7 empty] | 1987 | 139 | 6.2065 | 4.7819
[7 empty] | 1988 | 140 | 6.2148 | 4.7886
[7 empty] | 1989 | 141 | 5.5717 | 4.2661
[7 empty] | 1990 | 142 | 4.9451 | 3.757
[7 empty] | 1991 | 143 | 4.0794 | 3.0537
[7 empty] | 1992 | 144 | 3.4775 | 2.5647
[7 empty] | 1993 | 145 | 3.0158 | 2.1896
[7 empty] | 1994 | 146 | 2.8097 | 2.0221
[7 empty] | 1995 | 147 | 2.7438 | 1.9685
[7 empty] | 1996 | 148 | 2.7355 | 1.9618
[7 empty] | 1997 | 149 | 2.7355 | 1.9618
[7 empty] | 1998 | 150 | 2.7438 | 1.9685
[7 empty] | 1999 | 151 | 3.8073 | 2.8326
[7 empty] | 2000 | 152 | 5.3079 | 4.0517
[7 empty] | 2001 | 153 | 5.9097 | 4.5407
[7 empty] | 2002 | 154 | 6.4621 | 4.9895
[7 empty] | 2003 | 155 | 6.3137 | 4.869
[7 empty] | 2004 | 156 | 6.4786 | 5.0029
[7 empty] | 2005 | 157 | 7.1794 | 5.5723
[7 empty] | 2006 | 158 | 7.5009 | 5.8335
[7 empty] | 2007 | 159 | 7.7648 | 6.0479
[7 empty] | 2008 | 160 | 7.6411 | 5.9474
[7 empty] | 2009 | 161 | 8.3914 | 6.557
[7 empty] | 2010 | 162 | 7.9049 | 6.1618
[7 empty] | 2011 | 163 | 8.2594 | 6.4498
[7 empty] | 2012 | 164 | 6.9321 | 5.3713
[7 empty] | 2013 | 165 | 10.0073 | 7.8699
[7 empty] | 2014 | 166 | 7.9956 | 6.2354
[7 empty] | 2015 | 167 | 4.4504 | 3.3551
[7 empty] | 2016 | 168 | 3.8156 | 2.8393
[7 empty] | 2017 | 1 | 2.381 | 1.6738
[7 empty] | 2018 | 2 | 2.2738 | 1.5867
[7 empty] | 2019 | 3 | 2.2656 | 1.58
[7 empty] | 2020 | 4 | 2.3975 | 1.6872
[7 empty] | 2021 | 5 | 2.414 | 1.7006
[7 empty] | 2022 | 6 | 2.8345 | 2.0422
[7 empty] | 2023 | 7 | 3.5435 | 2.6183
[7 empty] | 2024 | 8 | 4.2031 | 3.1541
[7 empty] | 2025 | 9 | 4.1783 | 3.134
[7 empty] | 2026 | 10 | 5.6706 | 4.3465
[7 empty] | 2027 | 11 | 7.7153 | 6.0077
[7 empty] | 2028 | 12 | 8.6634 | 6.778
[7 empty] | 2029 | 13 | 9.0344 | 7.0795
[7 empty] | 2030 | 14 | 8.8201 | 6.9053
[7 empty] | 2031 | 15 | 8.7294 | 6.8316
[7 empty] | 2032 | 16 | 9.8919 | 7.7761
[7 empty] | 2033 | 17 | 11.1946 | 8.8345
[7 empty] | 2034 | 18 | 10.9555 | 8.6402
[7 empty] | 2035 | 19 | 11.4749 | 9.0622
[7 empty] | 2036 | 20 | 11.4089 | 9.0086
[7 empty] | 2037 | 21 | 11.9696 | 9.4641
[7 empty] | 2038 | 22 | 8.0781 | 6.3024
[7 empty] | 2039 | 23 | 4.368 | 3.2881
[7 empty] | 2040 | 24 | 2.724 | 1.9525
[7 empty] | 2041 | 25 | 2.6283 | 1.8747
[7 empty] | 2042 | 26 | 2.5212 | 1.7877
[7 empty] | 2043 | 27 | 2.4222 | 1.7073
[7 empty] | 2044 | 28 | 2.5047 | 1.7743
[7 empty] | 2045 | 29 | 2.7438 | 1.9685
[7 empty] | 2046 | 30 | 2.9829 | 2.1628
[7 empty] | 2047 | 31 | 3.8156 | 2.8393
[7 empty] | 2048 | 32 | 4.1618 | 3.1207
[7 empty] | 2049 | 33 | 4.8132 | 3.6498
[7 empty] | 2050 | 34 | 5.6954 | 4.3666
[7 empty] | 2051 | 35 | 7.8307 | 6.1015
[7 empty] | 2052 | 36 | 8.8448 | 6.9254
[7 empty] | 2053 | 37 | 8.919 | 6.9857
[7 empty] | 2054 | 38 | 8.9932 | 7.046
[7 empty] | 2055 | 39 | 8.6717 | 6.7847
[7 empty] | 2056 | 40 | 9.7105 | 7.6287
[7 empty] | 2057 | 41 | 10.2547 | 8.0708
[7 empty] | 2058 | 42 | 10.2711 | 8.0842
[7 empty] | 2059 | 43 | 10.6339 | 8.379
[7 empty] | 2060 | 44 | 11.7717 | 9.3034
[7 empty] | 2061 | 45 | 11.3759 | 8.9818
[7 empty] | 2062 | 46 | 8.6717 | 6.7847
[7 empty] | 2063 | 47 | 5.1265 | 3.9044
[7 empty] | 2064 | 48 | 3.6507 | 2.7053
[7 empty] | 2065 | 49 | 2.9993 | 2.1762
[7 empty] | 2066 | 50 | 2.6943 | 1.9283
[7 empty] | 2067 | 51 | 2.5871 | 1.8412
[7 empty] | 2068 | 52 | 2.6201 | 1.868
[7 empty] | 2069 | 53 | 2.6448 | 1.8881
[7 empty] | 2070 | 54 | 3.2137 | 2.3503
[7 empty] | 2071 | 55 | 4.335 | 3.2613
[7 empty] | 2072 | 56 | 4.5741 | 3.4556
[7 empty] | 2073 | 57 | 5.5057 | 4.2125
[7 empty] | 2074 | 58 | 6.594 | 5.0967
[7 empty] | 2075 | 59 | 7.7813 | 6.0613
[7 empty] | 2076 | 60 | 8.3996 | 6.5637
[7 empty] | 2077 | 61 | 9.0674 | 7.1063
[7 empty] | 2078 | 62 | 8.8696 | 6.9455
[7 empty] | 2079 | 63 | 9.4549 | 7.4211
[7 empty] | 2080 | 64 | 10.3866 | 8.178
[7 empty] | 2081 | 65 | 10.9967 | 8.6737
[7 empty] | 2082 | 66 | 10.8977 | 8.5933
[7 empty] | 2083 | 67 | 11.6233 | 9.1828
[7 empty] | 2084 | 68 | 11.8624 | 9.377
[7 empty] | 2085 | 69 | 11.3594 | 8.9684
[7 empty] | 2086 | 70 | 9.1004 | 7.133
[7 empty] | 2087 | 71 | 4.6565 | 3.5226
[7 empty] | 2088 | 72 | 3.5894 | 2.6556
[7 empty] | 2089 | 73 | 2.8839 | 2.0824
[7 empty] | 2090 | 74 | 2.6613 | 1.9015
[7 empty] | 2091 | 75 | 2.5624 | 1.8211
[7 empty] | 2092 | 76 | 2.5047 | 1.7743
[7 empty] | 2093 | 77 | 2.6778 | 1.9149
[7 empty] | 2094 | 78 | 3.0735 | 2.2365
[7 empty] | 2095 | 79 | 4.1701 | 3.1274
[7 empty] | 2096 | 80 | 4.3432 | 3.268
[7 empty] | 2097 | 81 | 5.5057 | 4.2125
[7 empty] | 2098 | 82 | 6.5775 | 5.0833
[7 empty] | 2099 | 83 | 7.3031 | 5.6728
[7 empty] | 2100 | 84 | 8.5233 | 6.6642
[7 empty] | 2101 | 85 | 8.2265 | 6.423
[7 empty] | 2102 | 86 | 7.7235 | 6.0144
[7 empty] | 2103 | 87 | 8.1605 | 6.3694
[7 empty] | 2104 | 88 | 8.8118 | 6.8986
[7 empty] | 2105 | 89 | 10.1392 | 7.9771
[7 empty] | 2106 | 90 | 9.5621 | 7.5082
[7 empty] | 2107 | 91 | 10.2382 | 8.0574
[7 empty] | 2108 | 92 | 9.6446 | 7.5751
[7 empty] | 2109 | 93 | 7.2701 | 5.646
[7 empty] | 2110 | 94 | 6.3797 | 4.9225
[7 empty] | 2111 | 95 | 4.5493 | 3.4355
[7 empty] | 2112 | 96 | 3.5765 | 2.6451
[7 empty] | 2113 | 97 | 3.527 | 2.6049
[7 empty] | 2114 | 98 | 3.2384 | 2.3704
[7 empty] | 2115 | 99 | 3.1807 | 2.3235
[7 empty] | 2116 | 100 | 2.8345 | 2.0422
[7 empty] | 2117 | 101 | 2.7767 | 1.9953
[7 empty] | 2118 | 102 | 3.0076 | 2.1829
[7 empty] | 2119 | 103 | 3.7414 | 2.779
[7 empty] | 2120 | 104 | 3.9887 | 2.98
[7 empty] | 2121 | 105 | 4.4669 | 3.3685
[7 empty] | 2122 | 106 | 5.9015 | 4.534
[7 empty] | 2123 | 107 | 6.2477 | 4.8154
[7 empty] | 2124 | 108 | 7.7977 | 6.0747
[7 empty] | 2125 | 109 | 7.1464 | 5.5455
[7 empty] | 2126 | 110 | 6.7012 | 5.1838
[7 empty] | 2127 | 111 | 6.5446 | 5.0565
[7 empty] | 2128 | 112 | 6.6105 | 5.1101
[7 empty] | 2129 | 113 | 6.2725 | 4.8355
[7 empty] | 2130 | 114 | 6.4374 | 4.9694
[7 empty] | 2131 | 115 | 5.9922 | 4.6077
[7 empty] | 2132 | 116 | 6.66 | 5.1503
[7 empty] | 2133 | 117 | 6.2477 | 4.8154
[7 empty] | 2134 | 118 | 5.4892 | 4.1991
[7 empty] | 2135 | 119 | 3.9227 | 2.9264
[7 empty] | 2136 | 120 | 3.6106 | 2.6728
[7 empty] | 2137 | 121 | 2.8922 | 2.0891
[7 empty] | 2138 | 122 | 2.4882 | 1.7609
[7 empty] | 2139 | 123 | 2.4057 | 1.6939
[7 empty] | 2140 | 124 | 2.3727 | 1.6671
[7 empty] | 2141 | 125 | 2.3315 | 1.6336
[7 empty] | 2142 | 126 | 2.4717 | 1.7475
[7 empty] | 2143 | 127 | 3.9557 | 2.9532
[7 empty] | 2144 | 128 | 5.4892 | 4.1991
[7 empty] | 2145 | 129 | 6.1571 | 4.7417
[7 empty] | 2146 | 130 | 6.5858 | 5.09
[7 empty] | 2147 | 131 | 6.7424 | 5.2173
[7 empty] | 2148 | 132 | 6.4951 | 5.0163
[7 empty] | 2149 | 133 | 7.1217 | 5.5254
[7 empty] | 2150 | 134 | 7.4185 | 5.7666
[7 empty] | 2151 | 135 | 7.4844 | 5.8201
[7 empty] | 2152 | 136 | 6.6847 | 5.1704
[7 empty] | 2153 | 137 | 6.5858 | 5.09
[7 empty] | 2154 | 138 | 6.5363 | 5.0498
[7 empty] | 2155 | 139 | 6.2065 | 4.7819
[7 empty] | 2156 | 140 | 6.2148 | 4.7886
[7 empty] | 2157 | 141 | 5.5717 | 4.2661
[7 empty] | 2158 | 142 | 4.9451 | 3.757
[7 empty] | 2159 | 143 | 4.0794 | 3.0537
[7 empty] | 2160 | 144 | 3.4775 | 2.5647
[7 empty] | 2161 | 145 | 3.0158 | 2.1896
[7 empty] | 2162 | 146 | 2.8097 | 2.0221
[7 empty] | 2163 | 147 | 2.7438 | 1.9685
[7 empty] | 2164 | 148 | 2.7355 | 1.9618
[7 empty] | 2165 | 149 | 2.7355 | 1.9618
[7 empty] | 2166 | 150 | 2.7438 | 1.9685
[7 empty] | 2167 | 151 | 3.8073 | 2.8326
[7 empty] | 2168 | 152 | 5.3079 | 4.0517
[7 empty] | 2169 | 153 | 5.9097 | 4.5407
[7 empty] | 2170 | 154 | 6.4621 | 4.9895
[7 empty] | 2171 | 155 | 6.3137 | 4.869
[7 empty] | 2172 | 156 | 6.4786 | 5.0029
[7 empty] | 2173 | 157 | 7.1794 | 5.5723
[7 empty] | 2174 | 158 | 7.5009 | 5.8335
[7 empty] | 2175 | 159 | 7.7648 | 6.0479
[7 empty] | 2176 | 160 | 7.6411 | 5.9474
[7 empty] | 2177 | 161 | 8.3914 | 6.557
[7 empty] | 2178 | 162 | 7.9049 | 6.1618
[7 empty] | 2179 | 163 | 8.2594 | 6.4498
[7 empty] | 2180 | 164 | 6.9321 | 5.3713
[7 empty] | 2181 | 165 | 10.0073 | 7.8699
[7 empty] | 2182 | 166 | 7.9956 | 6.2354
[7 empty] | 2183 | 167 | 4.4504 | 3.3551
[7 empty] | 2184 | 168 | 3.8156 | 2.8393
[7 empty] | 2185 | 1 | 2.381 | 1.6738
[7 empty] | 2186 | 2 | 2.2738 | 1.5867
[7 empty] | 2187 | 3 | 2.2656 | 1.58
[7 empty] | 2188 | 4 | 2.3975 | 1.6872
[7 empty] | 2189 | 5 | 2.414 | 1.7006
[7 empty] | 2190 | 6 | 2.8345 | 2.0422
[7 empty] | 2191 | 7 | 3.5435 | 2.6183
[7 empty] | 2192 | 8 | 4.2031 | 3.1541
[7 empty] | 2193 | 9 | 4.1783 | 3.134
[7 empty] | 2194 | 10 | 5.6706 | 4.3465
[7 empty] | 2195 | 11 | 7.7153 | 6.0077
[7 empty] | 2196 | 12 | 8.6634 | 6.778
[7 empty] | 2197 | 13 | 9.0344 | 7.0795
[7 empty] | 2198 | 14 | 8.8201 | 6.9053
[7 empty] | 2199 | 15 | 8.7294 | 6.8316
[7 empty] | 2200 | 16 | 9.8919 | 7.7761
[7 empty] | 2201 | 17 | 11.1946 | 8.8345
[7 empty] | 2202 | 18 | 10.9555 | 8.6402
[7 empty] | 2203 | 19 | 11.4749 | 9.0622
[7 empty] | 2204 | 20 | 11.4089 | 9.0086
[7 empty] | 2205 | 21 | 11.9696 | 9.4641
[7 empty] | 2206 | 22 | 8.0781 | 6.3024
[7 empty] | 2207 | 23 | 4.368 | 3.2881
[7 empty] | 2208 | 24 | 2.724 | 1.9525
[7 empty] | 2209 | 25 | 2.6283 | 1.8747
[7 empty] | 2210 | 26 | 2.5212 | 1.7877
[7 empty] | 2211 | 27 | 2.4222 | 1.7073
[7 empty] | 2212 | 28 | 2.5047 | 1.7743
[7 empty] | 2213 | 29 | 2.7438 | 1.9685
[7 empty] | 2214 | 30 | 2.9829 | 2.1628
[7 empty] | 2215 | 31 | 3.8156 | 2.8393
[7 empty] | 2216 | 32 | 4.1618 | 3.1207
[7 empty] | 2217 | 33 | 4.8132 | 3.6498
[7 empty] | 2218 | 34 | 5.6954 | 4.3666
[7 empty] | 2219 | 35 | 7.8307 | 6.1015
[7 empty] | 2220 | 36 | 8.8448 | 6.9254
[7 empty] | 2221 | 37 | 8.919 | 6.9857
[7 empty] | 2222 | 38 | 8.9932 | 7.046
[7 empty] | 2223 | 39 | 8.6717 | 6.7847
[7 empty] | 2224 | 40 | 9.7105 | 7.6287
[7 empty] | 2225 | 41 | 10.2547 | 8.0708
[7 empty] | 2226 | 42 | 10.2711 | 8.0842
[7 empty] | 2227 | 43 | 10.6339 | 8.379
[7 empty] | 2228 | 44 | 11.7717 | 9.3034
[7 empty] | 2229 | 45 | 11.3759 | 8.9818
[7 empty] | 2230 | 46 | 8.6717 | 6.7847
[7 empty] | 2231 | 47 | 5.1265 | 3.9044
[7 empty] | 2232 | 48 | 3.6507 | 2.7053
[7 empty] | 2233 | 49 | 2.9993 | 2.1762
[7 empty] | 2234 | 50 | 2.6943 | 1.9283
[7 empty] | 2235 | 51 | 2.5871 | 1.8412
[7 empty] | 2236 | 52 | 2.6201 | 1.868
[7 empty] | 2237 | 53 | 2.6448 | 1.8881
[7 empty] | 2238 | 54 | 3.2137 | 2.3503
[7 empty] | 2239 | 55 | 4.335 | 3.2613
[7 empty] | 2240 | 56 | 4.5741 | 3.4556
[7 empty] | 2241 | 57 | 5.5057 | 4.2125
[7 empty] | 2242 | 58 | 6.594 | 5.0967
[7 empty] | 2243 | 59 | 7.7813 | 6.0613
[7 empty] | 2244 | 60 | 8.3996 | 6.5637
[7 empty] | 2245 | 61 | 9.0674 | 7.1063
[7 empty] | 2246 | 62 | 8.8696 | 6.9455
[7 empty] | 2247 | 63 | 9.4549 | 7.4211
[7 empty] | 2248 | 64 | 10.3866 | 8.178
[7 empty] | 2249 | 65 | 10.9967 | 8.6737
[7 empty] | 2250 | 66 | 10.8977 | 8.5933
[7 empty] | 2251 | 67 | 11.6233 | 9.1828
[7 empty] | 2252 | 68 | 11.8624 | 9.377
[7 empty] | 2253 | 69 | 11.3594 | 8.9684
[7 empty] | 2254 | 70 | 9.1004 | 7.133
[7 empty] | 2255 | 71 | 4.6565 | 3.5226
[7 empty] | 2256 | 72 | 3.5894 | 2.6556
[7 empty] | 2257 | 73 | 2.8839 | 2.0824
[7 empty] | 2258 | 74 | 2.6613 | 1.9015
[7 empty] | 2259 | 75 | 2.5624 | 1.8211
[7 empty] | 2260 | 76 | 2.5047 | 1.7743
[7 empty] | 2261 | 77 | 2.6778 | 1.9149
[7 empty] | 2262 | 78 | 3.0735 | 2.2365
[7 empty] | 2263 | 79 | 4.1701 | 3.1274
[7 empty] | 2264 | 80 | 4.3432 | 3.268
[7 empty] | 2265 | 81 | 5.5057 | 4.2125
[7 empty] | 2266 | 82 | 6.5775 | 5.0833
[7 empty] | 2267 | 83 | 7.3031 | 5.6728
[7 empty] | 2268 | 84 | 8.5233 | 6.6642
[7 empty] | 2269 | 85 | 8.2265 | 6.423
[7 empty] | 2270 | 86 | 7.7235 | 6.0144
[7 empty] | 2271 | 87 | 8.1605 | 6.3694
[7 empty] | 2272 | 88 | 8.8118 | 6.8986
[7 empty] | 2273 | 89 | 10.1392 | 7.9771
[7 empty] | 2274 | 90 | 9.5621 | 7.5082
[7 empty] | 2275 | 91 | 10.2382 | 8.0574
[7 empty] | 2276 | 92 | 9.6446 | 7.5751
[7 empty] | 2277 | 93 | 7.2701 | 5.646
[7 empty] | 2278 | 94 | 6.3797 | 4.9225
[7 empty] | 2279 | 95 | 4.5493 | 3.4355
[7 empty] | 2280 | 96 | 3.5765 | 2.6451
[7 empty] | 2281 | 97 | 3.527 | 2.6049
[7 empty] | 2282 | 98 | 3.2384 | 2.3704
[7 empty] | 2283 | 99 | 3.1807 | 2.3235
[7 empty] | 2284 | 100 | 2.8345 | 2.0422
[7 empty] | 2285 | 101 | 2.7767 | 1.9953
[7 empty] | 2286 | 102 | 3.0076 | 2.1829
[7 empty] | 2287 | 103 | 3.7414 | 2.779
[7 empty] | 2288 | 104 | 3.9887 | 2.98
[7 empty] | 2289 | 105 | 4.4669 | 3.3685
[7 empty] | 2290 | 106 | 5.9015 | 4.534
[7 empty] | 2291 | 107 | 6.2477 | 4.8154
[7 empty] | 2292 | 108 | 7.7977 | 6.0747
[7 empty] | 2293 | 109 | 7.1464 | 5.5455
[7 empty] | 2294 | 110 | 6.7012 | 5.1838
[7 empty] | 2295 | 111 | 6.5446 | 5.0565
[7 empty] | 2296 | 112 | 6.6105 | 5.1101
[7 empty] | 2297 | 113 | 6.2725 | 4.8355
[7 empty] | 2298 | 114 | 6.4374 | 4.9694
[7 empty] | 2299 | 115 | 5.9922 | 4.6077
[7 empty] | 2300 | 116 | 6.66 | 5.1503
[7 empty] | 2301 | 117 | 6.2477 | 4.8154
[7 empty] | 2302 | 118 | 5.4892 | 4.1991
[7 empty] | 2303 | 119 | 3.9227 | 2.9264
[7 empty] | 2304 | 120 | 3.6106 | 2.6728
[7 empty] | 2305 | 121 | 2.8922 | 2.0891
[7 empty] | 2306 | 122 | 2.4882 | 1.7609
[7 empty] | 2307 | 123 | 2.4057 | 1.6939
[7 empty] | 2308 | 124 | 2.3727 | 1.6671
[7 empty] | 2309 | 125 | 2.3315 | 1.6336
[7 empty] | 2310 | 126 | 2.4717 | 1.7475
[7 empty] | 2311 | 127 | 3.9557 | 2.9532
[7 empty] | 2312 | 128 | 5.4892 | 4.1991
[7 empty] | 2313 | 129 | 6.1571 | 4.7417
[7 empty] | 2314 | 130 | 6.5858 | 5.09
[7 empty] | 2315 | 131 | 6.7424 | 5.2173
[7 empty] | 2316 | 132 | 6.4951 | 5.0163
[7 empty] | 2317 | 133 | 7.1217 | 5.5254
[7 empty] | 2318 | 134 | 7.4185 | 5.7666
[7 empty] | 2319 | 135 | 7.4844 | 5.8201
[7 empty] | 2320 | 136 | 6.6847 | 5.1704
[7 empty] | 2321 | 137 | 6.5858 | 5.09
[7 empty] | 2322 | 138 | 6.5363 | 5.0498
[7 empty] | 2323 | 139 | 6.2065 | 4.7819
[7 empty] | 2324 | 140 | 6.2148 | 4.7886
[7 empty] | 2325 | 141 | 5.5717 | 4.2661
[7 empty] | 2326 | 142 | 4.9451 | 3.757
[7 empty] | 2327 | 143 | 4.0794 | 3.0537
[7 empty] | 2328 | 144 | 3.4775 | 2.5647
[7 empty] | 2329 | 145 | 3.0158 | 2.1896
[7 empty] | 2330 | 146 | 2.8097 | 2.0221
[7 empty] | 2331 | 147 | 2.7438 | 1.9685
[7 empty] | 2332 | 148 | 2.7355 | 1.9618
[7 empty] | 2333 | 149 | 2.7355 | 1.9618
[7 empty] | 2334 | 150 | 2.7438 | 1.9685
[7 empty] | 2335 | 151 | 3.8073 | 2.8326
[7 empty] | 2336 | 152 | 5.3079 | 4.0517
[7 empty] | 2337 | 153 | 5.9097 | 4.5407
[7 empty] | 2338 | 154 | 6.4621 | 4.9895
[7 empty] | 2339 | 155 | 6.3137 | 4.869
[7 empty] | 2340 | 156 | 6.4786 | 5.0029
[7 empty] | 2341 | 157 | 7.1794 | 5.5723
[7 empty] | 2342 | 158 | 7.5009 | 5.8335
[7 empty] | 2343 | 159 | 7.7648 | 6.0479
[7 empty] | 2344 | 160 | 7.6411 | 5.9474
[7 empty] | 2345 | 161 | 8.3914 | 6.557
[7 empty] | 2346 | 162 | 7.9049 | 6.1618
[7 empty] | 2347 | 163 | 8.2594 | 6.4498
[7 empty] | 2348 | 164 | 6.9321 | 5.3713
[7 empty] | 2349 | 165 | 10.0073 | 7.8699
[7 empty] | 2350 | 166 | 7.9956 | 6.2354
[7 empty] | 2351 | 167 | 4.4504 | 3.3551
[7 empty] | 2352 | 168 | 3.8156 | 2.8393
[7 empty] | 2353 | 1 | 2.381 | 1.6738
[7 empty] | 2354 | 2 | 2.2738 | 1.5867
[7 empty] | 2355 | 3 | 2.2656 | 1.58
[7 empty] | 2356 | 4 | 2.3975 | 1.6872
[7 empty] | 2357 | 5 | 2.414 | 1.7006
[7 empty] | 2358 | 6 | 2.8345 | 2.0422
[7 empty] | 2359 | 7 | 3.5435 | 2.6183
[7 empty] | 2360 | 8 | 4.2031 | 3.1541
[7 empty] | 2361 | 9 | 4.1783 | 3.134
[7 empty] | 2362 | 10 | 5.6706 | 4.3465
[7 empty] | 2363 | 11 | 7.7153 | 6.0077
[7 empty] | 2364 | 12 | 8.6634 | 6.778
[7 empty] | 2365 | 13 | 9.0344 | 7.0795
[7 empty] | 2366 | 14 | 8.8201 | 6.9053
[7 empty] | 2367 | 15 | 8.7294 | 6.8316
[7 empty] | 2368 | 16 | 9.8919 | 7.7761
[7 empty] | 2369 | 17 | 11.1946 | 8.8345
[7 empty] | 2370 | 18 | 10.9555 | 8.6402
[7 empty] | 2371 | 19 | 11.4749 | 9.0622
[7 empty] | 2372 | 20 | 11.4089 | 9.0086
[7 empty] | 2373 | 21 | 11.9696 | 9.4641
[7 empty] | 2374 | 22 | 8.0781 | 6.3024
[7 empty] | 2375 | 23 | 4.368 | 3.2881
[7 empty] | 2376 | 24 | 2.724 | 1.9525
[7 empty] | 2377 | 25 | 2.6283 | 1.8747
[7 empty] | 2378 | 26 | 2.5212 | 1.7877
[7 empty] | 2379 | 27 | 2.4222 | 1.7073
[7 empty] | 2380 | 28 | 2.5047 | 1.7743
[7 empty] | 2381 | 29 | 2.7438 | 1.9685
[7 empty] | 2382 | 30 | 2.9829 | 2.1628
[7 empty] | 2383 | 31 | 3.8156 | 2.8393
[7 empty] | 2384 | 32 | 4.1618 | 3.1207
[7 empty] | 2385 | 33 | 4.8132 | 3.6498
[7 empty] | 2386 | 34 | 5.6954 | 4.3666
[7 empty] | 2387 | 35 | 7.8307 | 6.1015
[7 empty] | 2388 | 36 | 8.8448 | 6.9254
[7 empty] | 2389 | 37 | 8.919 | 6.9857
[7 empty] | 2390 | 38 | 8.9932 | 7.046
[7 empty] | 2391 | 39 | 8.6717 | 6.7847
[7 empty] | 2392 | 40 | 9.7105 | 7.6287
[7 empty] | 2393 | 41 | 10.2547 | 8.0708
[7 empty] | 2394 | 42 | 10.2711 | 8.0842
[7 empty] | 2395 | 43 | 10.6339 | 8.379
[7 empty] | 2396 | 44 | 11.7717 | 9.3034
[7 empty] | 2397 | 45 | 11.3759 | 8.9818
[7 empty] | 2398 | 46 | 8.6717 | 6.7847
[7 empty] | 2399 | 47 | 5.1265 | 3.9044
[7 empty] | 2400 | 48 | 3.6507 | 2.7053
[7 empty] | 2401 | 49 | 2.9993 | 2.1762
[7 empty] | 2402 | 50 | 2.6943 | 1.9283
[7 empty] | 2403 | 51 | 2.5871 | 1.8412
[7 empty] | 2404 | 52 | 2.6201 | 1.868
[7 empty] | 2405 | 53 | 2.6448 | 1.8881
[7 empty] | 2406 | 54 | 3.2137 | 2.3503
[7 empty] | 2407 | 55 | 4.335 | 3.2613
[7 empty] | 2408 | 56 | 4.5741 | 3.4556
[7 empty] | 2409 | 57 | 5.5057 | 4.2125
[7 empty] | 2410 | 58 | 6.594 | 5.0967
[7 empty] | 2411 | 59 | 7.7813 | 6.0613
[7 empty] | 2412 | 60 | 8.3996 | 6.5637
[7 empty] | 2413 | 61 | 9.0674 | 7.1063
[7 empty] | 2414 | 62 | 8.8696 | 6.9455
[7 empty] | 2415 | 63 | 9.4549 | 7.4211
[7 empty] | 2416 | 64 | 10.3866 | 8.178
[7 empty] | 2417 | 65 | 10.9967 | 8.6737
[7 empty] | 2418 | 66 | 10.8977 | 8.5933
[7 empty] | 2419 | 67 | 11.6233 | 9.1828
[7 empty] | 2420 | 68 | 11.8624 | 9.377
[7 empty] | 2421 | 69 | 11.3594 | 8.9684
[7 empty] | 2422 | 70 | 9.1004 | 7.133
[7 empty] | 2423 | 71 | 4.6565 | 3.5226
[7 empty] | 2424 | 72 | 3.5894 | 2.6556
[7 empty] | 2425 | 73 | 2.8839 | 2.0824
[7 empty] | 2426 | 74 | 2.6613 | 1.9015
[7 empty] | 2427 | 75 | 2.5624 | 1.8211
[7 empty] | 2428 | 76 | 2.5047 | 1.7743
[7 empty] | 2429 | 77 | 2.6778 | 1.9149
[7 empty] | 2430 | 78 | 3.0735 | 2.2365
[7 empty] | 2431 | 79 | 4.1701 | 3.1274
[7 empty] | 2432 | 80 | 4.3432 | 3.268
[7 empty] | 2433 | 81 | 5.5057 | 4.2125
[7 empty] | 2434 | 82 | 6.5775 | 5.0833
[7 empty] | 2435 | 83 | 7.3031 | 5.6728
[7 empty] | 2436 | 84 | 8.5233 | 6.6642
[7 empty] | 2437 | 85 | 8.2265 | 6.423
[7 empty] | 2438 | 86 | 7.7235 | 6.0144
[7 empty] | 2439 | 87 | 8.1605 | 6.3694
[7 empty] | 2440 | 88 | 8.8118 | 6.8986
[7 empty] | 2441 | 89 | 10.1392 | 7.9771
[7 empty] | 2442 | 90 | 9.5621 | 7.5082
[7 empty] | 2443 | 91 | 10.2382 | 8.0574
[7 empty] | 2444 | 92 | 9.6446 | 7.5751
[7 empty] | 2445 | 93 | 7.2701 | 5.646
[7 empty] | 2446 | 94 | 6.3797 | 4.9225
[7 empty] | 2447 | 95 | 4.5493 | 3.4355
[7 empty] | 2448 | 96 | 3.5765 | 2.6451
[7 empty] | 2449 | 97 | 3.527 | 2.6049
[7 empty] | 2450 | 98 | 3.2384 | 2.3704
[7 empty] | 2451 | 99 | 3.1807 | 2.3235
[7 empty] | 2452 | 100 | 2.8345 | 2.0422
[7 empty] | 2453 | 101 | 2.7767 | 1.9953
[7 empty] | 2454 | 102 | 3.0076 | 2.1829
[7 empty] | 2455 | 103 | 3.7414 | 2.779
[7 empty] | 2456 | 104 | 3.9887 | 2.98
[7 empty] | 2457 | 105 | 4.4669 | 3.3685
[7 empty] | 2458 | 106 | 5.9015 | 4.534
[7 empty] | 2459 | 107 | 6.2477 | 4.8154
[7 empty] | 2460 | 108 | 7.7977 | 6.0747
[7 empty] | 2461 | 109 | 7.1464 | 5.5455
[7 empty] | 2462 | 110 | 6.7012 | 5.1838
[7 empty] | 2463 | 111 | 6.5446 | 5.0565
[7 empty] | 2464 | 112 | 6.6105 | 5.1101
[7 empty] | 2465 | 113 | 6.2725 | 4.8355
[7 empty] | 2466 | 114 | 6.4374 | 4.9694
[7 empty] | 2467 | 115 | 5.9922 | 4.6077
[7 empty] | 2468 | 116 | 6.66 | 5.1503
[7 empty] | 2469 | 117 | 6.2477 | 4.8154
[7 empty] | 2470 | 118 | 5.4892 | 4.1991
[7 empty] | 2471 | 119 | 3.9227 | 2.9264
[7 empty] | 2472 | 120 | 3.6106 | 2.6728
[7 empty] | 2473 | 121 | 2.8922 | 2.0891
[7 empty] | 2474 | 122 | 2.4882 | 1.7609
[7 empty] | 2475 | 123 | 2.4057 | 1.6939
[7 empty] | 2476 | 124 | 2.3727 | 1.6671
[7 empty] | 2477 | 125 | 2.3315 | 1.6336
[7 empty] | 2478 | 126 | 2.4717 | 1.7475
[7 empty] | 2479 | 127 | 3.9557 | 2.9532
[7 empty] | 2480 | 128 | 5.4892 | 4.1991
[7 empty] | 2481 | 129 | 6.1571 | 4.7417
[7 empty] | 2482 | 130 | 6.5858 | 5.09
[7 empty] | 2483 | 131 | 6.7424 | 5.2173
[7 empty] | 2484 | 132 | 6.4951 | 5.0163
[7 empty] | 2485 | 133 | 7.1217 | 5.5254
[7 empty] | 2486 | 134 | 7.4185 | 5.7666
[7 empty] | 2487 | 135 | 7.4844 | 5.8201
[7 empty] | 2488 | 136 | 6.6847 | 5.1704
[7 empty] | 2489 | 137 | 6.5858 | 5.09
[7 empty] | 2490 | 138 | 6.5363 | 5.0498
[7 empty] | 2491 | 139 | 6.2065 | 4.7819
[7 empty] | 2492 | 140 | 6.2148 | 4.7886
[7 empty] | 2493 | 141 | 5.5717 | 4.2661
[7 empty] | 2494 | 142 | 4.9451 | 3.757
[7 empty] | 2495 | 143 | 4.0794 | 3.0537
[7 empty] | 2496 | 144 | 3.4775 | 2.5647
[7 empty] | 2497 | 145 | 3.0158 | 2.1896
[7 empty] | 2498 | 146 | 2.8097 | 2.0221
[7 empty] | 2499 | 147 | 2.7438 | 1.9685
[7 empty] | 2500 | 148 | 2.7355 | 1.9618
[7 empty] | 2501 | 149 | 2.7355 | 1.9618
[7 empty] | 2502 | 150 | 2.7438 | 1.9685
[7 empty] | 2503 | 151 | 3.8073 | 2.8326
[7 empty] | 2504 | 152 | 5.3079 | 4.0517
[7 empty] | 2505 | 153 | 5.9097 | 4.5407
[7 empty] | 2506 | 154 | 6.4621 | 4.9895
[7 empty] | 2507 | 155 | 6.3137 | 4.869
[7 empty] | 2508 | 156 | 6.4786 | 5.0029
[7 empty] | 2509 | 157 | 7.1794 | 5.5723
[7 empty] | 2510 | 158 | 7.5009 | 5.8335
[7 empty] | 2511 | 159 | 7.7648 | 6.0479
[7 empty] | 2512 | 160 | 7.6411 | 5.9474
[7 empty] | 2513 | 161 | 8.3914 | 6.557
[7 empty] | 2514 | 162 | 7.9049 | 6.1618
[7 empty] | 2515 | 163 | 8.2594 | 6.4498
[7 empty] | 2516 | 164 | 6.9321 | 5.3713
[7 empty] | 2517 | 165 | 10.0073 | 7.8699
[7 empty] | 2518 | 166 | 7.9956 | 6.2354
[7 empty] | 2519 | 167 | 4.4504 | 3.3551
[7 empty] | 2520 | 168 | 3.8156 | 2.8393
[7 empty] | 2521 | 1 | 2.381 | 1.6738
[7 empty] | 2522 | 2 | 2.2738 | 1.5867
[7 empty] | 2523 | 3 | 2.2656 | 1.58
[7 empty] | 2524 | 4 | 2.3975 | 1.6872
[7 empty] | 2525 | 5 | 2.414 | 1.7006
[7 empty] | 2526 | 6 | 2.8345 | 2.0422
[7 empty] | 2527 | 7 | 3.5435 | 2.6183
[7 empty] | 2528 | 8 | 4.2031 | 3.1541
[7 empty] | 2529 | 9 | 4.1783 | 3.134
[7 empty] | 2530 | 10 | 5.6706 | 4.3465
[7 empty] | 2531 | 11 | 7.7153 | 6.0077
[7 empty] | 2532 | 12 | 8.6634 | 6.778
[7 empty] | 2533 | 13 | 9.0344 | 7.0795
[7 empty] | 2534 | 14 | 8.8201 | 6.9053
[7 empty] | 2535 | 15 | 8.7294 | 6.8316
[7 empty] | 2536 | 16 | 9.8919 | 7.7761
[7 empty] | 2537 | 17 | 11.1946 | 8.8345
[7 empty] | 2538 | 18 | 10.9555 | 8.6402
[7 empty] | 2539 | 19 | 11.4749 | 9.0622
[7 empty] | 2540 | 20 | 11.4089 | 9.0086
[7 empty] | 2541 | 21 | 11.9696 | 9.4641
[7 empty] | 2542 | 22 | 8.0781 | 6.3024
[7 empty] | 2543 | 23 | 4.368 | 3.2881
[7 empty] | 2544 | 24 | 2.724 | 1.9525
[7 empty] | 2545 | 25 | 2.6283 | 1.8747
[7 empty] | 2546 | 26 | 2.5212 | 1.7877
[7 empty] | 2547 | 27 | 2.4222 | 1.7073
[7 empty] | 2548 | 28 | 2.5047 | 1.7743
[7 empty] | 2549 | 29 | 2.7438 | 1.9685
[7 empty] | 2550 | 30 | 2.9829 | 2.1628
[7 empty] | 2551 | 31 | 3.8156 | 2.8393
[7 empty] | 2552 | 32 | 4.1618 | 3.1207
[7 empty] | 2553 | 33 | 4.8132 | 3.6498
[7 empty] | 2554 | 34 | 5.6954 | 4.3666
[7 empty] | 2555 | 35 | 7.8307 | 6.1015
[7 empty] | 2556 | 36 | 8.8448 | 6.9254
[7 empty] | 2557 | 37 | 8.919 | 6.9857
[7 empty] | 2558 | 38 | 8.9932 | 7.046
[7 empty] | 2559 | 39 | 8.6717 | 6.7847
[7 empty] | 2560 | 40 | 9.7105 | 7.6287
[7 empty] | 2561 | 41 | 10.2547 | 8.0708
[7 empty] | 2562 | 42 | 10.2711 | 8.0842
[7 empty] | 2563 | 43 | 10.6339 | 8.379
[7 empty] | 2564 | 44 | 11.7717 | 9.3034
[7 empty] | 2565 | 45 | 11.3759 | 8.9818
[7 empty] | 2566 | 46 | 8.6717 | 6.7847
[7 empty] | 2567 | 47 | 5.1265 | 3.9044
[7 empty] | 2568 | 48 | 3.6507 | 2.7053
[7 empty] | 2569 | 49 | 2.9993 | 2.1762
[7 empty] | 2570 | 50 | 2.6943 | 1.9283
[7 empty] | 2571 | 51 | 2.5871 | 1.8412
[7 empty] | 2572 | 52 | 2.6201 | 1.868
[7 empty] | 2573 | 53 | 2.6448 | 1.8881
[7 empty] | 2574 | 54 | 3.2137 | 2.3503
[7 empty] | 2575 | 55 | 4.335 | 3.2613
[7 empty] | 2576 | 56 | 4.5741 | 3.4556
[7 empty] | 2577 | 57 | 5.5057 | 4.2125
[7 empty] | 2578 | 58 | 6.594 | 5.0967
[7 empty] | 2579 | 59 | 7.7813 | 6.0613
[7 empty] | 2580 | 60 | 8.3996 | 6.5637
[7 empty] | 2581 | 61 | 9.0674 | 7.1063
[7 empty] | 2582 | 62 | 8.8696 | 6.9455
[7 empty] | 2583 | 63 | 9.4549 | 7.4211
[7 empty] | 2584 | 64 | 10.3866 | 8.178
[7 empty] | 2585 | 65 | 10.9967 | 8.6737
[7 empty] | 2586 | 66 | 10.8977 | 8.5933
[7 empty] | 2587 | 67 | 11.6233 | 9.1828
[7 empty] | 2588 | 68 | 11.8624 | 9.377
[7 empty] | 2589 | 69 | 11.3594 | 8.9684
[7 empty] | 2590 | 70 | 9.1004 | 7.133
[7 empty] | 2591 | 71 | 4.6565 | 3.5226
[7 empty] | 2592 | 72 | 3.5894 | 2.6556
[7 empty] | 2593 | 73 | 2.8839 | 2.0824
[7 empty] | 2594 | 74 | 2.6613 | 1.9015
[7 empty] | 2595 | 75 | 2.5624 | 1.8211
[7 empty] | 2596 | 76 | 2.5047 | 1.7743
[7 empty] | 2597 | 77 | 2.6778 | 1.9149
[7 empty] | 2598 | 78 | 3.0735 | 2.2365
[7 empty] | 2599 | 79 | 4.1701 | 3.1274
[7 empty] | 2600 | 80 | 4.3432 | 3.268
[7 empty] | 2601 | 81 | 5.5057 | 4.2125
[7 empty] | 2602 | 82 | 6.5775 | 5.0833
[7 empty] | 2603 | 83 | 7.3031 | 5.6728
[7 empty] | 2604 | 84 | 8.5233 | 6.6642
[7 empty] | 2605 | 85 | 8.2265 | 6.423
[7 empty] | 2606 | 86 | 7.7235 | 6.0144
[7 empty] | 2607 | 87 | 8.1605 | 6.3694
[7 empty] | 2608 | 88 | 8.8118 | 6.8986
[7 empty] | 2609 | 89 | 10.1392 | 7.9771
[7 empty] | 2610 | 90 | 9.5621 | 7.5082
[7 empty] | 2611 | 91 | 10.2382 | 8.0574
[7 empty] | 2612 | 92 | 9.6446 | 7.5751
[7 empty] | 2613 | 93 | 7.2701 | 5.646
[7 empty] | 2614 | 94 | 6.3797 | 4.9225
[7 empty] | 2615 | 95 | 4.5493 | 3.4355
[7 empty] | 2616 | 96 | 3.5765 | 2.6451
[7 empty] | 2617 | 97 | 3.527 | 2.6049
[7 empty] | 2618 | 98 | 3.2384 | 2.3704
[7 empty] | 2619 | 99 | 3.1807 | 2.3235
[7 empty] | 2620 | 100 | 2.8345 | 2.0422
[7 empty] | 2621 | 101 | 2.7767 | 1.9953
[7 empty] | 2622 | 102 | 3.0076 | 2.1829
[7 empty] | 2623 | 103 | 3.7414 | 2.779
[7 empty] | 2624 | 104 | 3.9887 | 2.98
[7 empty] | 2625 | 105 | 4.4669 | 3.3685
[7 empty] | 2626 | 106 | 5.9015 | 4.534
[7 empty] | 2627 | 107 | 6.2477 | 4.8154
[7 empty] | 2628 | 108 | 7.7977 | 6.0747
[7 empty] | 2629 | 109 | 7.1464 | 5.5455
[7 empty] | 2630 | 110 | 6.7012 | 5.1838
[7 empty] | 2631 | 111 | 6.5446 | 5.0565
[7 empty] | 2632 | 112 | 6.6105 | 5.1101
[7 empty] | 2633 | 113 | 6.2725 | 4.8355
[7 empty] | 2634 | 114 | 6.4374 | 4.9694
[7 empty] | 2635 | 115 | 5.9922 | 4.6077
[7 empty] | 2636 | 116 | 6.66 | 5.1503
[7 empty] | 2637 | 117 | 6.2477 | 4.8154
[7 empty] | 2638 | 118 | 5.4892 | 4.1991
[7 empty] | 2639 | 119 | 3.9227 | 2.9264
[7 empty] | 2640 | 120 | 3.6106 | 2.6728
[7 empty] | 2641 | 121 | 2.8922 | 2.0891
[7 empty] | 2642 | 122 | 2.4882 | 1.7609
[7 empty] | 2643 | 123 | 2.4057 | 1.6939
[7 empty] | 2644 | 124 | 2.3727 | 1.6671
[7 empty] | 2645 | 125 | 2.3315 | 1.6336
[7 empty] | 2646 | 126 | 2.4717 | 1.7475
[7 empty] | 2647 | 127 | 3.9557 | 2.9532
[7 empty] | 2648 | 128 | 5.4892 | 4.1991
[7 empty] | 2649 | 129 | 6.1571 | 4.7417
[7 empty] | 2650 | 130 | 6.5858 | 5.09
[7 empty] | 2651 | 131 | 6.7424 | 5.2173
[7 empty] | 2652 | 132 | 6.4951 | 5.0163
[7 empty] | 2653 | 133 | 7.1217 | 5.5254
[7 empty] | 2654 | 134 | 7.4185 | 5.7666
[7 empty] | 2655 | 135 | 7.4844 | 5.8201
[7 empty] | 2656 | 136 | 6.6847 | 5.1704
[7 empty] | 2657 | 137 | 6.5858 | 5.09
[7 empty] | 2658 | 138 | 6.5363 | 5.0498
[7 empty] | 2659 | 139 | 6.2065 | 4.7819
[7 empty] | 2660 | 140 | 6.2148 | 4.7886
[7 empty] | 2661 | 141 | 5.5717 | 4.2661
[7 empty] | 2662 | 142 | 4.9451 | 3.757
[7 empty] | 2663 | 143 | 4.0794 | 3.0537
[7 empty] | 2664 | 144 | 3.4775 | 2.5647
[7 empty] | 2665 | 145 | 3.0158 | 2.1896
[7 empty] | 2666 | 146 | 2.8097 | 2.0221
[7 empty] | 2667 | 147 | 2.7438 | 1.9685
[7 empty] | 2668 | 148 | 2.7355 | 1.9618
[7 empty] | 2669 | 149 | 2.7355 | 1.9618
[7 empty] | 2670 | 150 | 2.7438 | 1.9685
[7 empty] | 2671 | 151 | 3.8073 | 2.8326
[7 empty] | 2672 | 152 | 5.3079 | 4.0517
[7 empty] | 2673 | 153 | 5.9097 | 4.5407
[7 empty] | 2674 | 154 | 6.4621 | 4.9895
[7 empty] | 2675 | 155 | 6.3137 | 4.869
[7 empty] | 2676 | 156 | 6.4786 | 5.0029
[7 empty] | 2677 | 157 | 7.1794 | 5.5723
[7 empty] | 2678 | 158 | 7.5009 | 5.8335
[7 empty] | 2679 | 159 | 7.7648 | 6.0479
[7 empty] | 2680 | 160 | 7.6411 | 5.9474
[7 empty] | 2681 | 161 | 8.3914 | 6.557
[7 empty] | 2682 | 162 | 7.9049 | 6.1618
[7 empty] | 2683 | 163 | 8.2594 | 6.4498
[7 empty] | 2684 | 164 | 6.9321 | 5.3713
[7 empty] | 2685 | 165 | 10.0073 | 7.8699
[7 empty] | 2686 | 166 | 7.9956 | 6.2354
[7 empty] | 2687 | 167 | 4.4504 | 3.3551
[7 empty] | 2688 | 168 | 3.8156 | 2.8393
[7 empty] | 2689 | 1 | 2.381 | 1.6738
[7 empty] | 2690 | 2 | 2.2738 | 1.5867
[7 empty] | 2691 | 3 | 2.2656 | 1.58
[7 empty] | 2692 | 4 | 2.3975 | 1.6872
[7 empty] | 2693 | 5 | 2.414 | 1.7006
[7 empty] | 2694 | 6 | 2.8345 | 2.0422
[7 empty] | 2695 | 7 | 3.5435 | 2.6183
[7 empty] | 2696 | 8 | 4.2031 | 3.1541
[7 empty] | 2697 | 9 | 4.1783 | 3.134
[7 empty] | 2698 | 10 | 5.6706 | 4.3465
[7 empty] | 2699 | 11 | 7.7153 | 6.0077
[7 empty] | 2700 | 12 | 8.6634 | 6.778
[7 empty] | 2701 | 13 | 9.0344 | 7.0795
[7 empty] | 2702 | 14 | 8.8201 | 6.9053
[7 empty] | 2703 | 15 | 8.7294 | 6.8316
[7 empty] | 2704 | 16 | 9.8919 | 7.7761
[7 empty] | 2705 | 17 | 11.1946 | 8.8345
[7 empty] | 2706 | 18 | 10.9555 | 8.6402
[7 empty] | 2707 | 19 | 11.4749 | 9.0622
[7 empty] | 2708 | 20 | 11.4089 | 9.0086
[7 empty] | 2709 | 21 | 11.9696 | 9.4641
[7 empty] | 2710 | 22 | 8.0781 | 6.3024
[7 empty] | 2711 | 23 | 4.368 | 3.2881
[7 empty] | 2712 | 24 | 2.724 | 1.9525
[7 empty] | 2713 | 25 | 2.6283 | 1.8747
[7 empty] | 2714 | 26 | 2.5212 | 1.7877
[7 empty] | 2715 | 27 | 2.4222 | 1.7073
[7 empty] | 2716 | 28 | 2.5047 | 1.7743
[7 empty] | 2717 | 29 | 2.7438 | 1.9685
[7 empty] | 2718 | 30 | 2.9829 | 2.1628
[7 empty] | 2719 | 31 | 3.8156 | 2.8393
[7 empty] | 2720 | 32 | 4.1618 | 3.1207
[7 empty] | 2721 | 33 | 4.8132 | 3.6498
[7 empty] | 2722 | 34 | 5.6954 | 4.3666
[7 empty] | 2723 | 35 | 7.8307 | 6.1015
[7 empty] | 2724 | 36 | 8.8448 | 6.9254
[7 empty] | 2725 | 37 | 8.919 | 6.9857
[7 empty] | 2726 | 38 | 8.9932 | 7.046
[7 empty] | 2727 | 39 | 8.6717 | 6.7847
[7 empty] | 2728 | 40 | 9.7105 | 7.6287
[7 empty] | 2729 | 41 | 10.2547 | 8.0708
[7 empty] | 2730 | 42 | 10.2711 | 8.0842
[7 empty] | 2731 | 43 | 10.6339 | 8.379
[7 empty] | 2732 | 44 | 11.7717 | 9.3034
[7 empty] | 2733 | 45 | 11.3759 | 8.9818
[7 empty] | 2734 | 46 | 8.6717 | 6.7847
[7 empty] | 2735 | 47 | 5.1265 | 3.9044
[7 empty] | 2736 | 48 | 3.6507 | 2.7053
[7 empty] | 2737 | 49 | 2.9993 | 2.1762
[7 empty] | 2738 | 50 | 2.6943 | 1.9283
[7 empty] | 2739 | 51 | 2.5871 | 1.8412
[7 empty] | 2740 | 52 | 2.6201 | 1.868
[7 empty] | 2741 | 53 | 2.6448 | 1.8881
[7 empty] | 2742 | 54 | 3.2137 | 2.3503
[7 empty] | 2743 | 55 | 4.335 | 3.2613
[7 empty] | 2744 | 56 | 4.5741 | 3.4556
[7 empty] | 2745 | 57 | 5.5057 | 4.2125
[7 empty] | 2746 | 58 | 6.594 | 5.0967
[7 empty] | 2747 | 59 | 7.7813 | 6.0613
[7 empty] | 2748 | 60 | 8.3996 | 6.5637
[7 empty] | 2749 | 61 | 9.0674 | 7.1063
[7 empty] | 2750 | 62 | 8.8696 | 6.9455
[7 empty] | 2751 | 63 | 9.4549 | 7.4211
[7 empty] | 2752 | 64 | 10.3866 | 8.178
[7 empty] | 2753 | 65 | 10.9967 | 8.6737
[7 empty] | 2754 | 66 | 10.8977 | 8.5933
[7 empty] | 2755 | 67 | 11.6233 | 9.1828
[7 empty] | 2756 | 68 | 11.8624 | 9.377
[7 empty] | 2757 | 69 | 11.3594 | 8.9684
[7 empty] | 2758 | 70 | 9.1004 | 7.133
[7 empty] | 2759 | 71 | 4.6565 | 3.5226
[7 empty] | 2760 | 72 | 3.5894 | 2.6556
[7 empty] | 2761 | 73 | 2.8839 | 2.0824
[7 empty] | 2762 | 74 | 2.6613 | 1.9015
[7 empty] | 2763 | 75 | 2.5624 | 1.8211
[7 empty] | 2764 | 76 | 2.5047 | 1.7743
[7 empty] | 2765 | 77 | 2.6778 | 1.9149
[7 empty] | 2766 | 78 | 3.0735 | 2.2365
[7 empty] | 2767 | 79 | 4.1701 | 3.1274
[7 empty] | 2768 | 80 | 4.3432 | 3.268
[7 empty] | 2769 | 81 | 5.5057 | 4.2125
[7 empty] | 2770 | 82 | 6.5775 | 5.0833
[7 empty] | 2771 | 83 | 7.3031 | 5.6728
[7 empty] | 2772 | 84 | 8.5233 | 6.6642
[7 empty] | 2773 | 85 | 8.2265 | 6.423
[7 empty] | 2774 | 86 | 7.7235 | 6.0144
[7 empty] | 2775 | 87 | 8.1605 | 6.3694
[7 empty] | 2776 | 88 | 8.8118 | 6.8986
[7 empty] | 2777 | 89 | 10.1392 | 7.9771
[7 empty] | 2778 | 90 | 9.5621 | 7.5082
[7 empty] | 2779 | 91 | 10.2382 | 8.0574
[7 empty] | 2780 | 92 | 9.6446 | 7.5751
[7 empty] | 2781 | 93 | 7.2701 | 5.646
[7 empty] | 2782 | 94 | 6.3797 | 4.9225
[7 empty] | 2783 | 95 | 4.5493 | 3.4355
[7 empty] | 2784 | 96 | 3.5765 | 2.6451
[7 empty] | 2785 | 97 | 3.527 | 2.6049
[7 empty] | 2786 | 98 | 3.2384 | 2.3704
[7 empty] | 2787 | 99 | 3.1807 | 2.3235
[7 empty] | 2788 | 100 | 2.8345 | 2.0422
[7 empty] | 2789 | 101 | 2.7767 | 1.9953
[7 empty] | 2790 | 102 | 3.0076 | 2.1829
[7 empty] | 2791 | 103 | 3.7414 | 2.779
[7 empty] | 2792 | 104 | 3.9887 | 2.98
[7 empty] | 2793 | 105 | 4.4669 | 3.3685
[7 empty] | 2794 | 106 | 5.9015 | 4.534
[7 empty] | 2795 | 107 | 6.2477 | 4.8154
[7 empty] | 2796 | 108 | 7.7977 | 6.0747
[7 empty] | 2797 | 109 | 7.1464 | 5.5455
[7 empty] | 2798 | 110 | 6.7012 | 5.1838
[7 empty] | 2799 | 111 | 6.5446 | 5.0565
[7 empty] | 2800 | 112 | 6.6105 | 5.1101
[7 empty] | 2801 | 113 | 6.2725 | 4.8355
[7 empty] | 2802 | 114 | 6.4374 | 4.9694
[7 empty] | 2803 | 115 | 5.9922 | 4.6077
[7 empty] | 2804 | 116 | 6.66 | 5.1503
[7 empty] | 2805 | 117 | 6.2477 | 4.8154
[7 empty] | 2806 | 118 | 5.4892 | 4.1991
[7 empty] | 2807 | 119 | 3.9227 | 2.9264
[7 empty] | 2808 | 120 | 3.6106 | 2.6728
[7 empty] | 2809 | 121 | 2.8922 | 2.0891
[7 empty] | 2810 | 122 | 2.4882 | 1.7609
[7 empty] | 2811 | 123 | 2.4057 | 1.6939
[7 empty] | 2812 | 124 | 2.3727 | 1.6671
[7 empty] | 2813 | 125 | 2.3315 | 1.6336
[7 empty] | 2814 | 126 | 2.4717 | 1.7475
[7 empty] | 2815 | 127 | 3.9557 | 2.9532
[7 empty] | 2816 | 128 | 5.4892 | 4.1991
[7 empty] | 2817 | 129 | 6.1571 | 4.7417
[7 empty] | 2818 | 130 | 6.5858 | 5.09
[7 empty] | 2819 | 131 | 6.7424 | 5.2173
[7 empty] | 2820 | 132 | 6.4951 | 5.0163
[7 empty] | 2821 | 133 | 7.1217 | 5.5254
[7 empty] | 2822 | 134 | 7.4185 | 5.7666
[7 empty] | 2823 | 135 | 7.4844 | 5.8201
[7 empty] | 2824 | 136 | 6.6847 | 5.1704
[7 empty] | 2825 | 137 | 6.5858 | 5.09
[7 empty] | 2826 | 138 | 6.5363 | 5.0498
[7 empty] | 2827 | 139 | 6.2065 | 4.7819
[7 empty] | 2828 | 140 | 6.2148 | 4.7886
[7 empty] | 2829 | 141 | 5.5717 | 4.2661
[7 empty] | 2830 | 142 | 4.9451 | 3.757
[7 empty] | 2831 | 143 | 4.0794 | 3.0537
[7 empty] | 2832 | 144 | 3.4775 | 2.5647
[7 empty] | 2833 | 145 | 3.0158 | 2.1896
[7 empty] | 2834 | 146 | 2.8097 | 2.0221
[7 empty] | 2835 | 147 | 2.7438 | 1.9685
[7 empty] | 2836 | 148 | 2.7355 | 1.9618
[7 empty] | 2837 | 149 | 2.7355 | 1.9618
[7 empty] | 2838 | 150 | 2.7438 | 1.9685
[7 empty] | 2839 | 151 | 3.8073 | 2.8326
[7 empty] | 2840 | 152 | 5.3079 | 4.0517
[7 empty] | 2841 | 153 | 5.9097 | 4.5407
[7 empty] | 2842 | 154 | 6.4621 | 4.9895
[7 empty] | 2843 | 155 | 6.3137 | 4.869
[7 empty] | 2844 | 156 | 6.4786 | 5.0029
[7 empty] | 2845 | 157 | 7.1794 | 5.5723
[7 empty] | 2846 | 158 | 7.5009 | 5.8335
[7 empty] | 2847 | 159 | 7.7648 | 6.0479
[7 empty] | 2848 | 160 | 7.6411 | 5.9474
[7 empty] | 2849 | 161 | 8.3914 | 6.557
[7 empty] | 2850 | 162 | 7.9049 | 6.1618
[7 empty] | 2851 | 163 | 8.2594 | 6.4498
[7 empty] | 2852 | 164 | 6.9321 | 5.3713
[7 empty] | 2853 | 165 | 10.0073 | 7.8699
[7 empty] | 2854 | 166 | 7.9956 | 6.2354
[7 empty] | 2855 | 167 | 4.4504 | 3.3551
[7 empty] | 2856 | 168 | 3.8156 | 2.8393
[7 empty] | 2857 | 1 | 2.381 | 1.6738
[7 empty] | 2858 | 2 | 2.2738 | 1.5867
[7 empty] | 2859 | 3 | 2.2656 | 1.58
[7 empty] | 2860 | 4 | 2.3975 | 1.6872
[7 empty] | 2861 | 5 | 2.414 | 1.7006
[7 empty] | 2862 | 6 | 2.8345 | 2.0422
[7 empty] | 2863 | 7 | 3.5435 | 2.6183
[7 empty] | 2864 | 8 | 4.2031 | 3.1541
[7 empty] | 2865 | 9 | 4.1783 | 3.134
[7 empty] | 2866 | 10 | 5.6706 | 4.3465
[7 empty] | 2867 | 11 | 7.7153 | 6.0077
[7 empty] | 2868 | 12 | 8.6634 | 6.778
[7 empty] | 2869 | 13 | 9.0344 | 7.0795
[7 empty] | 2870 | 14 | 8.8201 | 6.9053
[7 empty] | 2871 | 15 | 8.7294 | 6.8316
[7 empty] | 2872 | 16 | 9.8919 | 7.7761
[7 empty] | 2873 | 17 | 11.1946 | 8.8345
[7 empty] | 2874 | 18 | 10.9555 | 8.6402
[7 empty] | 2875 | 19 | 11.4749 | 9.0622
[7 empty] | 2876 | 20 | 11.4089 | 9.0086
[7 empty] | 2877 | 21 | 11.9696 | 9.4641
[7 empty] | 2878 | 22 | 8.0781 | 6.3024
[7 empty] | 2879 | 23 | 4.368 | 3.2881
[7 empty] | 2880 | 24 | 2.724 | 1.9525
[7 empty] | 2881 | 25 | 2.6283 | 1.8747
[7 empty] | 2882 | 26 | 2.5212 | 1.7877
[7 empty] | 2883 | 27 | 2.4222 | 1.7073
[7 empty] | 2884 | 28 | 2.5047 | 1.7743
[7 empty] | 2885 | 29 | 2.7438 | 1.9685
[7 empty] | 2886 | 30 | 2.9829 | 2.1628
[7 empty] | 2887 | 31 | 3.8156 | 2.8393
[7 empty] | 2888 | 32 | 4.1618 | 3.1207
[7 empty] | 2889 | 33 | 4.8132 | 3.6498
[7 empty] | 2890 | 34 | 5.6954 | 4.3666
[7 empty] | 2891 | 35 | 7.8307 | 6.1015
[7 empty] | 2892 | 36 | 8.8448 | 6.9254
[7 empty] | 2893 | 37 | 8.919 | 6.9857
[7 empty] | 2894 | 38 | 8.9932 | 7.046
[7 empty] | 2895 | 39 | 8.6717 | 6.7847
[7 empty] | 2896 | 40 | 9.7105 | 7.6287
[7 empty] | 2897 | 41 | 10.2547 | 8.0708
[7 empty] | 2898 | 42 | 10.2711 | 8.0842
[7 empty] | 2899 | 43 | 10.6339 | 8.379
[7 empty] | 2900 | 44 | 11.7717 | 9.3034
[7 empty] | 2901 | 45 | 11.3759 | 8.9818
[7 empty] | 2902 | 46 | 8.6717 | 6.7847
[7 empty] | 2903 | 47 | 5.1265 | 3.9044
[7 empty] | 2904 | 48 | 3.6507 | 2.7053
[7 empty] | 2905 | 49 | 2.9993 | 2.1762
[7 empty] | 2906 | 50 | 2.6943 | 1.9283
[7 empty] | 2907 | 51 | 2.5871 | 1.8412
[7 empty] | 2908 | 52 | 2.6201 | 1.868
[7 empty] | 2909 | 53 | 2.6448 | 1.8881
[7 empty] | 2910 | 54 | 3.2137 | 2.3503
[7 empty] | 2911 | 55 | 4.335 | 3.2613
[7 empty] | 2912 | 56 | 4.5741 | 3.4556
[7 empty] | 2913 | 57 | 5.5057 | 4.2125
[7 empty] | 2914 | 58 | 6.594 | 5.0967
[7 empty] | 2915 | 59 | 7.7813 | 6.0613
[7 empty] | 2916 | 60 | 8.3996 | 6.5637
[7 empty] | 2917 | 61 | 9.0674 | 7.1063
[7 empty] | 2918 | 62 | 8.8696 | 6.9455
[7 empty] | 2919 | 63 | 9.4549 | 7.4211
[7 empty] | 2920 | 64 | 10.3866 | 8.178
[7 empty] | 2921 | 65 | 10.9967 | 8.6737
[7 empty] | 2922 | 66 | 10.8977 | 8.5933
[7 empty] | 2923 | 67 | 11.6233 | 9.1828
[7 empty] | 2924 | 68 | 11.8624 | 9.377
[7 empty] | 2925 | 69 | 11.3594 | 8.9684
[7 empty] | 2926 | 70 | 9.1004 | 7.133
[7 empty] | 2927 | 71 | 4.6565 | 3.5226
[7 empty] | 2928 | 72 | 3.5894 | 2.6556
[7 empty] | 2929 | 73 | 2.8839 | 2.0824
[7 empty] | 2930 | 74 | 2.6613 | 1.9015
[7 empty] | 2931 | 75 | 2.5624 | 1.8211
[7 empty] | 2932 | 76 | 2.5047 | 1.7743
[7 empty] | 2933 | 77 | 2.6778 | 1.9149
[7 empty] | 2934 | 78 | 3.0735 | 2.2365
[7 empty] | 2935 | 79 | 4.1701 | 3.1274
[7 empty] | 2936 | 80 | 4.3432 | 3.268
[7 empty] | 2937 | 81 | 5.5057 | 4.2125
[7 empty] | 2938 | 82 | 6.5775 | 5.0833
[7 empty] | 2939 | 83 | 7.3031 | 5.6728
[7 empty] | 2940 | 84 | 8.5233 | 6.6642
[7 empty] | 2941 | 85 | 8.2265 | 6.423
[7 empty] | 2942 | 86 | 7.7235 | 6.0144
[7 empty] | 2943 | 87 | 8.1605 | 6.3694
[7 empty] | 2944 | 88 | 8.8118 | 6.8986
[7 empty] | 2945 | 89 | 10.1392 | 7.9771
[7 empty] | 2946 | 90 | 9.5621 | 7.5082
[7 empty] | 2947 | 91 | 10.2382 | 8.0574
[7 empty] | 2948 | 92 | 9.6446 | 7.5751
[7 empty] | 2949 | 93 | 7.2701 | 5.646
[7 empty] | 2950 | 94 | 6.3797 | 4.9225
[7 empty] | 2951 | 95 | 4.5493 | 3.4355
[7 empty] | 2952 | 96 | 3.5765 | 2.6451
[7 empty] | 2953 | 97 | 3.527 | 2.6049
[7 empty] | 2954 | 98 | 3.2384 | 2.3704
[7 empty] | 2955 | 99 | 3.1807 | 2.3235
[7 empty] | 2956 | 100 | 2.8345 | 2.0422
[7 empty] | 2957 | 101 | 2.7767 | 1.9953
[7 empty] | 2958 | 102 | 3.0076 | 2.1829
[7 empty] | 2959 | 103 | 3.7414 | 2.779
[7 empty] | 2960 | 104 | 3.9887 | 2.98
[7 empty] | 2961 | 105 | 4.4669 | 3.3685
[7 empty] | 2962 | 106 | 5.9015 | 4.534
[7 empty] | 2963 | 107 | 6.2477 | 4.8154
[7 empty] | 2964 | 108 | 7.7977 | 6.0747
[7 empty] | 2965 | 109 | 7.1464 | 5.5455
[7 empty] | 2966 | 110 | 6.7012 | 5.1838
[7 empty] | 2967 | 111 | 6.5446 | 5.0565
[7 empty] | 2968 | 112 | 6.6105 | 5.1101
[7 empty] | 2969 | 113 | 6.2725 | 4.8355
[7 empty] | 2970 | 114 | 6.4374 | 4.9694
[7 empty] | 2971 | 115 | 5.9922 | 4.6077
[7 empty] | 2972 | 116 | 6.66 | 5.1503
[7 empty] | 2973 | 117 | 6.2477 | 4.8154
[7 empty] | 2974 | 118 | 5.4892 | 4.1991
[7 empty] | 2975 | 119 | 3.9227 | 2.9264
[7 empty] | 2976 | 120 | 3.6106 | 2.6728
[7 empty] | 2977 | 121 | 2.8922 | 2.0891
[7 empty] | 2978 | 122 | 2.4882 | 1.7609
[7 empty] | 2979 | 123 | 2.4057 | 1.6939
[7 empty] | 2980 | 124 | 2.3727 | 1.6671
[7 empty] | 2981 | 125 | 2.3315 | 1.6336
[7 empty] | 2982 | 126 | 2.4717 | 1.7475
[7 empty] | 2983 | 127 | 3.9557 | 2.9532
[7 empty] | 2984 | 128 | 5.4892 | 4.1991
[7 empty] | 2985 | 129 | 6.1571 | 4.7417
[7 empty] | 2986 | 130 | 6.5858 | 5.09
[7 empty] | 2987 | 131 | 6.7424 | 5.2173
[7 empty] | 2988 | 132 | 6.4951 | 5.0163
[7 empty] | 2989 | 133 | 7.1217 | 5.5254
[7 empty] | 2990 | 134 | 7.4185 | 5.7666
[7 empty] | 2991 | 135 | 7.4844 | 5.8201
[7 empty] | 2992 | 136 | 6.6847 | 5.1704
[7 empty] | 2993 | 137 | 6.5858 | 5.09
[7 empty] | 2994 | 138 | 6.5363 | 5.0498
[7 empty] | 2995 | 139 | 6.2065 | 4.7819
[7 empty] | 2996 | 140 | 6.2148 | 4.7886
[7 empty] | 2997 | 141 | 5.5717 | 4.2661
[7 empty] | 2998 | 142 | 4.9451 | 3.757
[7 empty] | 2999 | 143 | 4.0794 | 3.0537
[7 empty] | 3000 | 144 | 3.4775 | 2.5647
[7 empty] | 3001 | 145 | 3.0158 | 2.1896
[7 empty] | 3002 | 146 | 2.8097 | 2.0221
[7 empty] | 3003 | 147 | 2.7438 | 1.9685
[7 empty] | 3004 | 148 | 2.7355 | 1.9618
[7 empty] | 3005 | 149 | 2.7355 | 1.9618
[7 empty] | 3006 | 150 | 2.7438 | 1.9685
[7 empty] | 3007 | 151 | 3.8073 | 2.8326
[7 empty] | 3008 | 152 | 5.3079 | 4.0517
[7 empty] | 3009 | 153 | 5.9097 | 4.5407
[7 empty] | 3010 | 154 | 6.4621 | 4.9895
[7 empty] | 3011 | 155 | 6.3137 | 4.869
[7 empty] | 3012 | 156 | 6.4786 | 5.0029
[7 empty] | 3013 | 157 | 7.1794 | 5.5723
[7 empty] | 3014 | 158 | 7.5009 | 5.8335
[7 empty] | 3015 | 159 | 7.7648 | 6.0479
[7 empty] | 3016 | 160 | 7.6411 | 5.9474
[7 empty] | 3017 | 161 | 8.3914 | 6.557
[7 empty] | 3018 | 162 | 7.9049 | 6.1618
[7 empty] | 3019 | 163 | 8.2594 | 6.4498
[7 empty] | 3020 | 164 | 6.9321 | 5.3713
[7 empty] | 3021 | 165 | 10.0073 | 7.8699
[7 empty] | 3022 | 166 | 7.9956 | 6.2354
[7 empty] | 3023 | 167 | 4.4504 | 3.3551
[7 empty] | 3024 | 168 | 3.8156 | 2.8393
[7 empty] | 3025 | 1 | 2.381 | 1.6738
[7 empty] | 3026 | 2 | 2.2738 | 1.5867
[7 empty] | 3027 | 3 | 2.2656 | 1.58
[7 empty] | 3028 | 4 | 2.3975 | 1.6872
[7 empty] | 3029 | 5 | 2.414 | 1.7006
[7 empty] | 3030 | 6 | 2.8345 | 2.0422
[7 empty] | 3031 | 7 | 3.5435 | 2.6183
[7 empty] | 3032 | 8 | 4.2031 | 3.1541
[7 empty] | 3033 | 9 | 4.1783 | 3.134
[7 empty] | 3034 | 10 | 5.6706 | 4.3465
[7 empty] | 3035 | 11 | 7.7153 | 6.0077
[7 empty] | 3036 | 12 | 8.6634 | 6.778
[7 empty] | 3037 | 13 | 9.0344 | 7.0795
[7 empty] | 3038 | 14 | 8.8201 | 6.9053
[7 empty] | 3039 | 15 | 8.7294 | 6.8316
[7 empty] | 3040 | 16 | 9.8919 | 7.7761
[7 empty] | 3041 | 17 | 11.1946 | 8.8345
[7 empty] | 3042 | 18 | 10.9555 | 8.6402
[7 empty] | 3043 | 19 | 11.4749 | 9.0622
[7 empty] | 3044 | 20 | 11.4089 | 9.0086
[7 empty] | 3045 | 21 | 11.9696 | 9.4641
[7 empty] | 3046 | 22 | 8.0781 | 6.3024
[7 empty] | 3047 | 23 | 4.368 | 3.2881
[7 empty] | 3048 | 24 | 2.724 | 1.9525
[7 empty] | 3049 | 25 | 2.6283 | 1.8747
[7 empty] | 3050 | 26 | 2.5212 | 1.7877
[7 empty] | 3051 | 27 | 2.4222 | 1.7073
[7 empty] | 3052 | 28 | 2.5047 | 1.7743
[7 empty] | 3053 | 29 | 2.7438 | 1.9685
[7 empty] | 3054 | 30 | 2.9829 | 2.1628
[7 empty] | 3055 | 31 | 3.8156 | 2.8393
[7 empty] | 3056 | 32 | 4.1618 | 3.1207
[7 empty] | 3057 | 33 | 4.8132 | 3.6498
[7 empty] | 3058 | 34 | 5.6954 | 4.3666
[7 empty] | 3059 | 35 | 7.8307 | 6.1015
[7 empty] | 3060 | 36 | 8.8448 | 6.9254
[7 empty] | 3061 | 37 | 8.919 | 6.9857
[7 empty] | 3062 | 38 | 8.9932 | 7.046
[7 empty] | 3063 | 39 | 8.6717 | 6.7847
[7 empty] | 3064 | 40 | 9.7105 | 7.6287
[7 empty] | 3065 | 41 | 10.2547 | 8.0708
[7 empty] | 3066 | 42 | 10.2711 | 8.0842
[7 empty] | 3067 | 43 | 10.6339 | 8.379
[7 empty] | 3068 | 44 | 11.7717 | 9.3034
[7 empty] | 3069 | 45 | 11.3759 | 8.9818
[7 empty] | 3070 | 46 | 8.6717 | 6.7847
[7 empty] | 3071 | 47 | 5.1265 | 3.9044
[7 empty] | 3072 | 48 | 3.6507 | 2.7053
[7 empty] | 3073 | 49 | 2.9993 | 2.1762
[7 empty] | 3074 | 50 | 2.6943 | 1.9283
[7 empty] | 3075 | 51 | 2.5871 | 1.8412
[7 empty] | 3076 | 52 | 2.6201 | 1.868
[7 empty] | 3077 | 53 | 2.6448 | 1.8881
[7 empty] | 3078 | 54 | 3.2137 | 2.3503
[7 empty] | 3079 | 55 | 4.335 | 3.2613
[7 empty] | 3080 | 56 | 4.5741 | 3.4556
[7 empty] | 3081 | 57 | 5.5057 | 4.2125
[7 empty] | 3082 | 58 | 6.594 | 5.0967
[7 empty] | 3083 | 59 | 7.7813 | 6.0613
[7 empty] | 3084 | 60 | 8.3996 | 6.5637
[7 empty] | 3085 | 61 | 9.0674 | 7.1063
[7 empty] | 3086 | 62 | 8.8696 | 6.9455
[7 empty] | 3087 | 63 | 9.4549 | 7.4211
[7 empty] | 3088 | 64 | 10.3866 | 8.178
[7 empty] | 3089 | 65 | 10.9967 | 8.6737
[7 empty] | 3090 | 66 | 10.8977 | 8.5933
[7 empty] | 3091 | 67 | 11.6233 | 9.1828
[7 empty] | 3092 | 68 | 11.8624 | 9.377
[7 empty] | 3093 | 69 | 11.3594 | 8.9684
[7 empty] | 3094 | 70 | 9.1004 | 7.133
[7 empty] | 3095 | 71 | 4.6565 | 3.5226
[7 empty] | 3096 | 72 | 3.5894 | 2.6556
[7 empty] | 3097 | 73 | 2.8839 | 2.0824
[7 empty] | 3098 | 74 | 2.6613 | 1.9015
[7 empty] | 3099 | 75 | 2.5624 | 1.8211
[7 empty] | 3100 | 76 | 2.5047 | 1.7743
[7 empty] | 3101 | 77 | 2.6778 | 1.9149
[7 empty] | 3102 | 78 | 3.0735 | 2.2365
[7 empty] | 3103 | 79 | 4.1701 | 3.1274
[7 empty] | 3104 | 80 | 4.3432 | 3.268
[7 empty] | 3105 | 81 | 5.5057 | 4.2125
[7 empty] | 3106 | 82 | 6.5775 | 5.0833
[7 empty] | 3107 | 83 | 7.3031 | 5.6728
[7 empty] | 3108 | 84 | 8.5233 | 6.6642
[7 empty] | 3109 | 85 | 8.2265 | 6.423
[7 empty] | 3110 | 86 | 7.7235 | 6.0144
[7 empty] | 3111 | 87 | 8.1605 | 6.3694
[7 empty] | 3112 | 88 | 8.8118 | 6.8986
[7 empty] | 3113 | 89 | 10.1392 | 7.9771
[7 empty] | 3114 | 90 | 9.5621 | 7.5082
[7 empty] | 3115 | 91 | 10.2382 | 8.0574
[7 empty] | 3116 | 92 | 9.6446 | 7.5751
[7 empty] | 3117 | 93 | 7.2701 | 5.646
[7 empty] | 3118 | 94 | 6.3797 | 4.9225
[7 empty] | 3119 | 95 | 4.5493 | 3.4355
[7 empty] | 3120 | 96 | 3.5765 | 2.6451
[7 empty] | 3121 | 97 | 3.527 | 2.6049
[7 empty] | 3122 | 98 | 3.2384 | 2.3704
[7 empty] | 3123 | 99 | 3.1807 | 2.3235
[7 empty] | 3124 | 100 | 2.8345 | 2.0422
[7 empty] | 3125 | 101 | 2.7767 | 1.9953
[7 empty] | 3126 | 102 | 3.0076 | 2.1829
[7 empty] | 3127 | 103 | 3.7414 | 2.779
[7 empty] | 3128 | 104 | 3.9887 | 2.98
[7 empty] | 3129 | 105 | 4.4669 | 3.3685
[7 empty] | 3130 | 106 | 5.9015 | 4.534
[7 empty] | 3131 | 107 | 6.2477 | 4.8154
[7 empty] | 3132 | 108 | 7.7977 | 6.0747
[7 empty] | 3133 | 109 | 7.1464 | 5.5455
[7 empty] | 3134 | 110 | 6.7012 | 5.1838
[7 empty] | 3135 | 111 | 6.5446 | 5.0565
[7 empty] | 3136 | 112 | 6.6105 | 5.1101
[7 empty] | 3137 | 113 | 6.2725 | 4.8355
[7 empty] | 3138 | 114 | 6.4374 | 4.9694
[7 empty] | 3139 | 115 | 5.9922 | 4.6077
[7 empty] | 3140 | 116 | 6.66 | 5.1503
[7 empty] | 3141 | 117 | 6.2477 | 4.8154
[7 empty] | 3142 | 118 | 5.4892 | 4.1991
[7 empty] | 3143 | 119 | 3.9227 | 2.9264
[7 empty] | 3144 | 120 | 3.6106 | 2.6728
[7 empty] | 3145 | 121 | 2.8922 | 2.0891
[7 empty] | 3146 | 122 | 2.4882 | 1.7609
[7 empty] | 3147 | 123 | 2.4057 | 1.6939
[7 empty] | 3148 | 124 | 2.3727 | 1.6671
[7 empty] | 3149 | 125 | 2.3315 | 1.6336
[7 empty] | 3150 | 126 | 2.4717 | 1.7475
[7 empty] | 3151 | 127 | 3.9557 | 2.9532
[7 empty] | 3152 | 128 | 5.4892 | 4.1991
[7 empty] | 3153 | 129 | 6.1571 | 4.7417
[7 empty] | 3154 | 130 | 6.5858 | 5.09
[7 empty] | 3155 | 131 | 6.7424 | 5.2173
[7 empty] | 3156 | 132 | 6.4951 | 5.0163
[7 empty] | 3157 | 133 | 7.1217 | 5.5254
[7 empty] | 3158 | 134 | 7.4185 | 5.7666
[7 empty] | 3159 | 135 | 7.4844 | 5.8201
[7 empty] | 3160 | 136 | 6.6847 | 5.1704
[7 empty] | 3161 | 137 | 6.5858 | 5.09
[7 empty] | 3162 | 138 | 6.5363 | 5.0498
[7 empty] | 3163 | 139 | 6.2065 | 4.7819
[7 empty] | 3164 | 140 | 6.2148 | 4.7886
[7 empty] | 3165 | 141 | 5.5717 | 4.2661
[7 empty] | 3166 | 142 | 4.9451 | 3.757
[7 empty] | 3167 | 143 | 4.0794 | 3.0537
[7 empty] | 3168 | 144 | 3.4775 | 2.5647
[7 empty] | 3169 | 145 | 3.0158 | 2.1896
[7 empty] | 3170 | 146 | 2.8097 | 2.0221
[7 empty] | 3171 | 147 | 2.7438 | 1.9685
[7 empty] | 3172 | 148 | 2.7355 | 1.9618
[7 empty] | 3173 | 149 | 2.7355 | 1.9618
[7 empty] | 3174 | 150 | 2.7438 | 1.9685
[7 empty] | 3175 | 151 | 3.8073 | 2.8326
[7 empty] | 3176 | 152 | 5.3079 | 4.0517
[7 empty] | 3177 | 153 | 5.9097 | 4.5407
[7 empty] | 3178 | 154 | 6.4621 | 4.9895
[7 empty] | 3179 | 155 | 6.3137 | 4.869
[7 empty] | 3180 | 156 | 6.4786 | 5.0029
[7 empty] | 3181 | 157 | 7.1794 | 5.5723
[7 empty] | 3182 | 158 | 7.5009 | 5.8335
[7 empty] | 3183 | 159 | 7.7648 | 6.0479
[7 empty] | 3184 | 160 | 7.6411 | 5.9474
[7 empty] | 3185 | 161 | 8.3914 | 6.557
[7 empty] | 3186 | 162 | 7.9049 | 6.1618
[7 empty] | 3187 | 163 | 8.2594 | 6.4498
[7 empty] | 3188 | 164 | 6.9321 | 5.3713
[7 empty] | 3189 | 165 | 10.0073 | 7.8699
[7 empty] | 3190 | 166 | 7.9956 | 6.2354
[7 empty] | 3191 | 167 | 4.4504 | 3.3551
[7 empty] | 3192 | 168 | 3.8156 | 2.8393
[7 empty] | 3193 | 1 | 2.381 | 1.6738
[7 empty] | 3194 | 2 | 2.2738 | 1.5867
[7 empty] | 3195 | 3 | 2.2656 | 1.58
[7 empty] | 3196 | 4 | 2.3975 | 1.6872
[7 empty] | 3197 | 5 | 2.414 | 1.7006
[7 empty] | 3198 | 6 | 2.8345 | 2.0422
[7 empty] | 3199 | 7 | 3.5435 | 2.6183
[7 empty] | 3200 | 8 | 4.2031 | 3.1541
[7 empty] | 3201 | 9 | 4.1783 | 3.134
[7 empty] | 3202 | 10 | 5.6706 | 4.3465
[7 empty] | 3203 | 11 | 7.7153 | 6.0077
[7 empty] | 3204 | 12 | 8.6634 | 6.778
[7 empty] | 3205 | 13 | 9.0344 | 7.0795
[7 empty] | 3206 | 14 | 8.8201 | 6.9053
[7 empty] | 3207 | 15 | 8.7294 | 6.8316
[7 empty] | 3208 | 16 | 9.8919 | 7.7761
[7 empty] | 3209 | 17 | 11.1946 | 8.8345
[7 empty] | 3210 | 18 | 10.9555 | 8.6402
[7 empty] | 3211 | 19 | 11.4749 | 9.0622
[7 empty] | 3212 | 20 | 11.4089 | 9.0086
[7 empty] | 3213 | 21 | 11.9696 | 9.4641
[7 empty] | 3214 | 22 | 8.0781 | 6.3024
[7 empty] | 3215 | 23 | 4.368 | 3.2881
[7 empty] | 3216 | 24 | 2.724 | 1.9525
[7 empty] | 3217 | 25 | 2.6283 | 1.8747
[7 empty] | 3218 | 26 | 2.5212 | 1.7877
[7 empty] | 3219 | 27 | 2.4222 | 1.7073
[7 empty] | 3220 | 28 | 2.5047 | 1.7743
[7 empty] | 3221 | 29 | 2.7438 | 1.9685
[7 empty] | 3222 | 30 | 2.9829 | 2.1628
[7 empty] | 3223 | 31 | 3.8156 | 2.8393
[7 empty] | 3224 | 32 | 4.1618 | 3.1207
[7 empty] | 3225 | 33 | 4.8132 | 3.6498
[7 empty] | 3226 | 34 | 5.6954 | 4.3666
[7 empty] | 3227 | 35 | 7.8307 | 6.1015
[7 empty] | 3228 | 36 | 8.8448 | 6.9254
[7 empty] | 3229 | 37 | 8.919 | 6.9857
[7 empty] | 3230 | 38 | 8.9932 | 7.046
[7 empty] | 3231 | 39 | 8.6717 | 6.7847
[7 empty] | 3232 | 40 | 9.7105 | 7.6287
[7 empty] | 3233 | 41 | 10.2547 | 8.0708
[7 empty] | 3234 | 42 | 10.2711 | 8.0842
[7 empty] | 3235 | 43 | 10.6339 | 8.379
[7 empty] | 3236 | 44 | 11.7717 | 9.3034
[7 empty] | 3237 | 45 | 11.3759 | 8.9818
[7 empty] | 3238 | 46 | 8.6717 | 6.7847
[7 empty] | 3239 | 47 | 5.1265 | 3.9044
[7 empty] | 3240 | 48 | 3.6507 | 2.7053
[7 empty] | 3241 | 49 | 2.9993 | 2.1762
[7 empty] | 3242 | 50 | 2.6943 | 1.9283
[7 empty] | 3243 | 51 | 2.5871 | 1.8412
[7 empty] | 3244 | 52 | 2.6201 | 1.868
[7 empty] | 3245 | 53 | 2.6448 | 1.8881
[7 empty] | 3246 | 54 | 3.2137 | 2.3503
[7 empty] | 3247 | 55 | 4.335 | 3.2613
[7 empty] | 3248 | 56 | 4.5741 | 3.4556
[7 empty] | 3249 | 57 | 5.5057 | 4.2125
[7 empty] | 3250 | 58 | 6.594 | 5.0967
[7 empty] | 3251 | 59 | 7.7813 | 6.0613
[7 empty] | 3252 | 60 | 8.3996 | 6.5637
[7 empty] | 3253 | 61 | 9.0674 | 7.1063
[7 empty] | 3254 | 62 | 8.8696 | 6.9455
[7 empty] | 3255 | 63 | 9.4549 | 7.4211
[7 empty] | 3256 | 64 | 10.3866 | 8.178
[7 empty] | 3257 | 65 | 10.9967 | 8.6737
[7 empty] | 3258 | 66 | 10.8977 | 8.5933
[7 empty] | 3259 | 67 | 11.6233 | 9.1828
[7 empty] | 3260 | 68 | 11.8624 | 9.377
[7 empty] | 3261 | 69 | 11.3594 | 8.9684
[7 empty] | 3262 | 70 | 9.1004 | 7.133
[7 empty] | 3263 | 71 | 4.6565 | 3.5226
[7 empty] | 3264 | 72 | 3.5894 | 2.6556
[7 empty] | 3265 | 73 | 2.8839 | 2.0824
[7 empty] | 3266 | 74 | 2.6613 | 1.9015
[7 empty] | 3267 | 75 | 2.5624 | 1.8211
[7 empty] | 3268 | 76 | 2.5047 | 1.7743
[7 empty] | 3269 | 77 | 2.6778 | 1.9149
[7 empty] | 3270 | 78 | 3.0735 | 2.2365
[7 empty] | 3271 | 79 | 4.1701 | 3.1274
[7 empty] | 3272 | 80 | 4.3432 | 3.268
[7 empty] | 3273 | 81 | 5.5057 | 4.2125
[7 empty] | 3274 | 82 | 6.5775 | 5.0833
[7 empty] | 3275 | 83 | 7.3031 | 5.6728
[7 empty] | 3276 | 84 | 8.5233 | 6.6642
[7 empty] | 3277 | 85 | 8.2265 | 6.423
[7 empty] | 3278 | 86 | 7.7235 | 6.0144
[7 empty] | 3279 | 87 | 8.1605 | 6.3694
[7 empty] | 3280 | 88 | 8.8118 | 6.8986
[7 empty] | 3281 | 89 | 10.1392 | 7.9771
[7 empty] | 3282 | 90 | 9.5621 | 7.5082
[7 empty] | 3283 | 91 | 10.2382 | 8.0574
[7 empty] | 3284 | 92 | 9.6446 | 7.5751
[7 empty] | 3285 | 93 | 7.2701 | 5.646
[7 empty] | 3286 | 94 | 6.3797 | 4.9225
[7 empty] | 3287 | 95 | 4.5493 | 3.4355
[7 empty] | 3288 | 96 | 3.5765 | 2.6451
[7 empty] | 3289 | 97 | 3.527 | 2.6049
[7 empty] | 3290 | 98 | 3.2384 | 2.3704
[7 empty] | 3291 | 99 | 3.1807 | 2.3235
[7 empty] | 3292 | 100 | 2.8345 | 2.0422
[7 empty] | 3293 | 101 | 2.7767 | 1.9953
[7 empty] | 3294 | 102 | 3.0076 | 2.1829
[7 empty] | 3295 | 103 | 3.7414 | 2.779
[7 empty] | 3296 | 104 | 3.9887 | 2.98
[7 empty] | 3297 | 105 | 4.4669 | 3.3685
[7 empty] | 3298 | 106 | 5.9015 | 4.534
[7 empty] | 3299 | 107 | 6.2477 | 4.8154
[7 empty] | 3300 | 108 | 7.7977 | 6.0747
[7 empty] | 3301 | 109 | 7.1464 | 5.5455
[7 empty] | 3302 | 110 | 6.7012 | 5.1838
[7 empty] | 3303 | 111 | 6.5446 | 5.0565
[7 empty] | 3304 | 112 | 6.6105 | 5.1101
[7 empty] | 3305 | 113 | 6.2725 | 4.8355
[7 empty] | 3306 | 114 | 6.4374 | 4.9694
[7 empty] | 3307 | 115 | 5.9922 | 4.6077
[7 empty] | 3308 | 116 | 6.66 | 5.1503
[7 empty] | 3309 | 117 | 6.2477 | 4.8154
[7 empty] | 3310 | 118 | 5.4892 | 4.1991
[7 empty] | 3311 | 119 | 3.9227 | 2.9264
[7 empty] | 3312 | 120 | 3.6106 | 2.6728
[7 empty] | 3313 | 121 | 2.8922 | 2.0891
[7 empty] | 3314 | 122 | 2.4882 | 1.7609
[7 empty] | 3315 | 123 | 2.4057 | 1.6939
[7 empty] | 3316 | 124 | 2.3727 | 1.6671
[7 empty] | 3317 | 125 | 2.3315 | 1.6336
[7 empty] | 3318 | 126 | 2.4717 | 1.7475
[7 empty] | 3319 | 127 | 3.9557 | 2.9532
[7 empty] | 3320 | 128 | 5.4892 | 4.1991
[7 empty] | 3321 | 129 | 6.1571 | 4.7417
[7 empty] | 3322 | 130 | 6.5858 | 5.09
[7 empty] | 3323 | 131 | 6.7424 | 5.2173
[7 empty] | 3324 | 132 | 6.4951 | 5.0163
[7 empty] | 3325 | 133 | 7.1217 | 5.5254
[7 empty] | 3326 | 134 | 7.4185 | 5.7666
[7 empty] | 3327 | 135 | 7.4844 | 5.8201
[7 empty] | 3328 | 136 | 6.6847 | 5.1704
[7 empty] | 3329 | 137 | 6.5858 | 5.09
[7 empty] | 3330 | 138 | 6.5363 | 5.0498
[7 empty] | 3331 | 139 | 6.2065 | 4.7819
[7 empty] | 3332 | 140 | 6.2148 | 4.7886
[7 empty] | 3333 | 141 | 5.5717 | 4.2661
[7 empty] | 3334 | 142 | 4.9451 | 3.757
[7 empty] | 3335 | 143 | 4.0794 | 3.0537
[7 empty] | 3336 | 144 | 3.4775 | 2.5647
[7 empty] | 3337 | 145 | 3.0158 | 2.1896
[7 empty] | 3338 | 146 | 2.8097 | 2.0221
[7 empty] | 3339 | 147 | 2.7438 | 1.9685
[7 empty] | 3340 | 148 | 2.7355 | 1.9618
[7 empty] | 3341 | 149 | 2.7355 | 1.9618
[7 empty] | 3342 | 150 | 2.7438 | 1.9685
[7 empty] | 3343 | 151 | 3.8073 | 2.8326
[7 empty] | 3344 | 152 | 5.3079 | 4.0517
[7 empty] | 3345 | 153 | 5.9097 | 4.5407
[7 empty] | 3346 | 154 | 6.4621 | 4.9895
[7 empty] | 3347 | 155 | 6.3137 | 4.869
[7 empty] | 3348 | 156 | 6.4786 | 5.0029
[7 empty] | 3349 | 157 | 7.1794 | 5.5723
[7 empty] | 3350 | 158 | 7.5009 | 5.8335
[7 empty] | 3351 | 159 | 7.7648 | 6.0479
[7 empty] | 3352 | 160 | 7.6411 | 5.9474
[7 empty] | 3353 | 161 | 8.3914 | 6.557
[7 empty] | 3354 | 162 | 7.9049 | 6.1618
[7 empty] | 3355 | 163 | 8.2594 | 6.4498
[7 empty] | 3356 | 164 | 6.9321 | 5.3713
[7 empty] | 3357 | 165 | 10.0073 | 7.8699
[7 empty] | 3358 | 166 | 7.9956 | 6.2354
[7 empty] | 3359 | 167 | 4.4504 | 3.3551
[7 empty] | 3360 | 168 | 3.8156 | 2.8393
[7 empty] | 3361 | 1 | 2.381 | 1.6738
[7 empty] | 3362 | 2 | 2.2738 | 1.5867
[7 empty] | 3363 | 3 | 2.2656 | 1.58
[7 empty] | 3364 | 4 | 2.3975 | 1.6872
[7 empty] | 3365 | 5 | 2.414 | 1.7006
[7 empty] | 3366 | 6 | 2.8345 | 2.0422
[7 empty] | 3367 | 7 | 3.5435 | 2.6183
[7 empty] | 3368 | 8 | 4.2031 | 3.1541
[7 empty] | 3369 | 9 | 4.1783 | 3.134
[7 empty] | 3370 | 10 | 5.6706 | 4.3465
[7 empty] | 3371 | 11 | 7.7153 | 6.0077
[7 empty] | 3372 | 12 | 8.6634 | 6.778
[7 empty] | 3373 | 13 | 9.0344 | 7.0795
[7 empty] | 3374 | 14 | 8.8201 | 6.9053
[7 empty] | 3375 | 15 | 8.7294 | 6.8316
[7 empty] | 3376 | 16 | 9.8919 | 7.7761
[7 empty] | 3377 | 17 | 11.1946 | 8.8345
[7 empty] | 3378 | 18 | 10.9555 | 8.6402
[7 empty] | 3379 | 19 | 11.4749 | 9.0622
[7 empty] | 3380 | 20 | 11.4089 | 9.0086
[7 empty] | 3381 | 21 | 11.9696 | 9.4641
[7 empty] | 3382 | 22 | 8.0781 | 6.3024
[7 empty] | 3383 | 23 | 4.368 | 3.2881
[7 empty] | 3384 | 24 | 2.724 | 1.9525
[7 empty] | 3385 | 25 | 2.6283 | 1.8747
[7 empty] | 3386 | 26 | 2.5212 | 1.7877
[7 empty] | 3387 | 27 | 2.4222 | 1.7073
[7 empty] | 3388 | 28 | 2.5047 | 1.7743
[7 empty] | 3389 | 29 | 2.7438 | 1.9685
[7 empty] | 3390 | 30 | 2.9829 | 2.1628
[7 empty] | 3391 | 31 | 3.8156 | 2.8393
[7 empty] | 3392 | 32 | 4.1618 | 3.1207
[7 empty] | 3393 | 33 | 4.8132 | 3.6498
[7 empty] | 3394 | 34 | 5.6954 | 4.3666
[7 empty] | 3395 | 35 | 7.8307 | 6.1015
[7 empty] | 3396 | 36 | 8.8448 | 6.9254
[7 empty] | 3397 | 37 | 8.919 | 6.9857
[7 empty] | 3398 | 38 | 8.9932 | 7.046
[7 empty] | 3399 | 39 | 8.6717 | 6.7847
[7 empty] | 3400 | 40 | 9.7105 | 7.6287
[7 empty] | 3401 | 41 | 10.2547 | 8.0708
[7 empty] | 3402 | 42 | 10.2711 | 8.0842
[7 empty] | 3403 | 43 | 10.6339 | 8.379
[7 empty] | 3404 | 44 | 11.7717 | 9.3034
[7 empty] | 3405 | 45 | 11.3759 | 8.9818
[7 empty] | 3406 | 46 | 8.6717 | 6.7847
[7 empty] | 3407 | 47 | 5.1265 | 3.9044
[7 empty] | 3408 | 48 | 3.6507 | 2.7053
[7 empty] | 3409 | 49 | 2.9993 | 2.1762
[7 empty] | 3410 | 50 | 2.6943 | 1.9283
[7 empty] | 3411 | 51 | 2.5871 | 1.8412
[7 empty] | 3412 | 52 | 2.6201 | 1.868
[7 empty] | 3413 | 53 | 2.6448 | 1.8881
[7 empty] | 3414 | 54 | 3.2137 | 2.3503
[7 empty] | 3415 | 55 | 4.335 | 3.2613
[7 empty] | 3416 | 56 | 4.5741 | 3.4556
[7 empty] | 3417 | 57 | 5.5057 | 4.2125
[7 empty] | 3418 | 58 | 6.594 | 5.0967
[7 empty] | 3419 | 59 | 7.7813 | 6.0613
[7 empty] | 3420 | 60 | 8.3996 | 6.5637
[7 empty] | 3421 | 61 | 9.0674 | 7.1063
[7 empty] | 3422 | 62 | 8.8696 | 6.9455
[7 empty] | 3423 | 63 | 9.4549 | 7.4211
[7 empty] | 3424 | 64 | 10.3866 | 8.178
[7 empty] | 3425 | 65 | 10.9967 | 8.6737
[7 empty] | 3426 | 66 | 10.8977 | 8.5933
[7 empty] | 3427 | 67 | 11.6233 | 9.1828
[7 empty] | 3428 | 68 | 11.8624 | 9.377
[7 empty] | 3429 | 69 | 11.3594 | 8.9684
[7 empty] | 3430 | 70 | 9.1004 | 7.133
[7 empty] | 3431 | 71 | 4.6565 | 3.5226
[7 empty] | 3432 | 72 | 3.5894 | 2.6556
[7 empty] | 3433 | 73 | 2.8839 | 2.0824
[7 empty] | 3434 | 74 | 2.6613 | 1.9015
[7 empty] | 3435 | 75 | 2.5624 | 1.8211
[7 empty] | 3436 | 76 | 2.5047 | 1.7743
[7 empty] | 3437 | 77 | 2.6778 | 1.9149
[7 empty] | 3438 | 78 | 3.0735 | 2.2365
[7 empty] | 3439 | 79 | 4.1701 | 3.1274
[7 empty] | 3440 | 80 | 4.3432 | 3.268
[7 empty] | 3441 | 81 | 5.5057 | 4.2125
[7 empty] | 3442 | 82 | 6.5775 | 5.0833
[7 empty] | 3443 | 83 | 7.3031 | 5.6728
[7 empty] | 3444 | 84 | 8.5233 | 6.6642
[7 empty] | 3445 | 85 | 8.2265 | 6.423
[7 empty] | 3446 | 86 | 7.7235 | 6.0144
[7 empty] | 3447 | 87 | 8.1605 | 6.3694
[7 empty] | 3448 | 88 | 8.8118 | 6.8986
[7 empty] | 3449 | 89 | 10.1392 | 7.9771
[7 empty] | 3450 | 90 | 9.5621 | 7.5082
[7 empty] | 3451 | 91 | 10.2382 | 8.0574
[7 empty] | 3452 | 92 | 9.6446 | 7.5751
[7 empty] | 3453 | 93 | 7.2701 | 5.646
[7 empty] | 3454 | 94 | 6.3797 | 4.9225
[7 empty] | 3455 | 95 | 4.5493 | 3.4355
[7 empty] | 3456 | 96 | 3.5765 | 2.6451
[7 empty] | 3457 | 97 | 3.527 | 2.6049
[7 empty] | 3458 | 98 | 3.2384 | 2.3704
[7 empty] | 3459 | 99 | 3.1807 | 2.3235
[7 empty] | 3460 | 100 | 2.8345 | 2.0422
[7 empty] | 3461 | 101 | 2.7767 | 1.9953
[7 empty] | 3462 | 102 | 3.0076 | 2.1829
[7 empty] | 3463 | 103 | 3.7414 | 2.779
[7 empty] | 3464 | 104 | 3.9887 | 2.98
[7 empty] | 3465 | 105 | 4.4669 | 3.3685
[7 empty] | 3466 | 106 | 5.9015 | 4.534
[7 empty] | 3467 | 107 | 6.2477 | 4.8154
[7 empty] | 3468 | 108 | 7.7977 | 6.0747
[7 empty] | 3469 | 109 | 7.1464 | 5.5455
[7 empty] | 3470 | 110 | 6.7012 | 5.1838
[7 empty] | 3471 | 111 | 6.5446 | 5.0565
[7 empty] | 3472 | 112 | 6.6105 | 5.1101
[7 empty] | 3473 | 113 | 6.2725 | 4.8355
[7 empty] | 3474 | 114 | 6.4374 | 4.9694
[7 empty] | 3475 | 115 | 5.9922 | 4.6077
[7 empty] | 3476 | 116 | 6.66 | 5.1503
[7 empty] | 3477 | 117 | 6.2477 | 4.8154
[7 empty] | 3478 | 118 | 5.4892 | 4.1991
[7 empty] | 3479 | 119 | 3.9227 | 2.9264
[7 empty] | 3480 | 120 | 3.6106 | 2.6728
[7 empty] | 3481 | 121 | 2.8922 | 2.0891
[7 empty] | 3482 | 122 | 2.4882 | 1.7609
[7 empty] | 3483 | 123 | 2.4057 | 1.6939
[7 empty] | 3484 | 124 | 2.3727 | 1.6671
[7 empty] | 3485 | 125 | 2.3315 | 1.6336
[7 empty] | 3486 | 126 | 2.4717 | 1.7475
[7 empty] | 3487 | 127 | 3.9557 | 2.9532
[7 empty] | 3488 | 128 | 5.4892 | 4.1991
[7 empty] | 3489 | 129 | 6.1571 | 4.7417
[7 empty] | 3490 | 130 | 6.5858 | 5.09
[7 empty] | 3491 | 131 | 6.7424 | 5.2173
[7 empty] | 3492 | 132 | 6.4951 | 5.0163
[7 empty] | 3493 | 133 | 7.1217 | 5.5254
[7 empty] | 3494 | 134 | 7.4185 | 5.7666
[7 empty] | 3495 | 135 | 7.4844 | 5.8201
[7 empty] | 3496 | 136 | 6.6847 | 5.1704
[7 empty] | 3497 | 137 | 6.5858 | 5.09
[7 empty] | 3498 | 138 | 6.5363 | 5.0498
[7 empty] | 3499 | 139 | 6.2065 | 4.7819
[7 empty] | 3500 | 140 | 6.2148 | 4.7886
[7 empty] | 3501 | 141 | 5.5717 | 4.2661
[7 empty] | 3502 | 142 | 4.9451 | 3.757
[7 empty] | 3503 | 143 | 4.0794 | 3.0537
[7 empty] | 3504 | 144 | 3.4775 | 2.5647
[7 empty] | 3505 | 145 | 3.0158 | 2.1896
[7 empty] | 3506 | 146 | 2.8097 | 2.0221
[7 empty] | 3507 | 147 | 2.7438 | 1.9685
[7 empty] | 3508 | 148 | 2.7355 | 1.9618
[7 empty] | 3509 | 149 | 2.7355 | 1.9618
[7 empty] | 3510 | 150 | 2.7438 | 1.9685
[7 empty] | 3511 | 151 | 3.8073 | 2.8326
[7 empty] | 3512 | 152 | 5.3079 | 4.0517
[7 empty] | 3513 | 153 | 5.9097 | 4.5407
[7 empty] | 3514 | 154 | 6.4621 | 4.9895
[7 empty] | 3515 | 155 | 6.3137 | 4.869
[7 empty] | 3516 | 156 | 6.4786 | 5.0029
[7 empty] | 3517 | 157 | 7.1794 | 5.5723
[7 empty] | 3518 | 158 | 7.5009 | 5.8335
[7 empty] | 3519 | 159 | 7.7648 | 6.0479
[7 empty] | 3520 | 160 | 7.6411 | 5.9474
[7 empty] | 3521 | 161 | 8.3914 | 6.557
[7 empty] | 3522 | 162 | 7.9049 | 6.1618
[7 empty] | 3523 | 163 | 8.2594 | 6.4498
[7 empty] | 3524 | 164 | 6.9321 | 5.3713
[7 empty] | 3525 | 165 | 10.0073 | 7.8699
[7 empty] | 3526 | 166 | 7.9956 | 6.2354
[7 empty] | 3527 | 167 | 4.4504 | 3.3551
[7 empty] | 3528 | 168 | 3.8156 | 2.8393
[7 empty] | 3529 | 1 | 2.381 | 1.6738
[7 empty] | 3530 | 2 | 2.2738 | 1.5867
[7 empty] | 3531 | 3 | 2.2656 | 1.58
[7 empty] | 3532 | 4 | 2.3975 | 1.6872
[7 empty] | 3533 | 5 | 2.414 | 1.7006
[7 empty] | 3534 | 6 | 2.8345 | 2.0422
[7 empty] | 3535 | 7 | 3.5435 | 2.6183
[7 empty] | 3536 | 8 | 4.2031 | 3.1541
[7 empty] | 3537 | 9 | 4.1783 | 3.134
[7 empty] | 3538 | 10 | 5.6706 | 4.3465
[7 empty] | 3539 | 11 | 7.7153 | 6.0077
[7 empty] | 3540 | 12 | 8.6634 | 6.778
[7 empty] | 3541 | 13 | 9.0344 | 7.0795
[7 empty] | 3542 | 14 | 8.8201 | 6.9053
[7 empty] | 3543 | 15 | 8.7294 | 6.8316
[7 empty] | 3544 | 16 | 9.8919 | 7.7761
[7 empty] | 3545 | 17 | 11.1946 | 8.8345
[7 empty] | 3546 | 18 | 10.9555 | 8.6402
[7 empty] | 3547 | 19 | 11.4749 | 9.0622
[7 empty] | 3548 | 20 | 11.4089 | 9.0086
[7 empty] | 3549 | 21 | 11.9696 | 9.4641
[7 empty] | 3550 | 22 | 8.0781 | 6.3024
[7 empty] | 3551 | 23 | 4.368 | 3.2881
[7 empty] | 3552 | 24 | 2.724 | 1.9525
[7 empty] | 3553 | 25 | 2.6283 | 1.8747
[7 empty] | 3554 | 26 | 2.5212 | 1.7877
[7 empty] | 3555 | 27 | 2.4222 | 1.7073
[7 empty] | 3556 | 28 | 2.5047 | 1.7743
[7 empty] | 3557 | 29 | 2.7438 | 1.9685
[7 empty] | 3558 | 30 | 2.9829 | 2.1628
[7 empty] | 3559 | 31 | 3.8156 | 2.8393
[7 empty] | 3560 | 32 | 4.1618 | 3.1207
[7 empty] | 3561 | 33 | 4.8132 | 3.6498
[7 empty] | 3562 | 34 | 5.6954 | 4.3666
[7 empty] | 3563 | 35 | 7.8307 | 6.1015
[7 empty] | 3564 | 36 | 8.8448 | 6.9254
[7 empty] | 3565 | 37 | 8.919 | 6.9857
[7 empty] | 3566 | 38 | 8.9932 | 7.046
[7 empty] | 3567 | 39 | 8.6717 | 6.7847
[7 empty] | 3568 | 40 | 9.7105 | 7.6287
[7 empty] | 3569 | 41 | 10.2547 | 8.0708
[7 empty] | 3570 | 42 | 10.2711 | 8.0842
[7 empty] | 3571 | 43 | 10.6339 | 8.379
[7 empty] | 3572 | 44 | 11.7717 | 9.3034
[7 empty] | 3573 | 45 | 11.3759 | 8.9818
[7 empty] | 3574 | 46 | 8.6717 | 6.7847
[7 empty] | 3575 | 47 | 5.1265 | 3.9044
[7 empty] | 3576 | 48 | 3.6507 | 2.7053
[7 empty] | 3577 | 49 | 2.9993 | 2.1762
[7 empty] | 3578 | 50 | 2.6943 | 1.9283
[7 empty] | 3579 | 51 | 2.5871 | 1.8412
[7 empty] | 3580 | 52 | 2.6201 | 1.868
[7 empty] | 3581 | 53 | 2.6448 | 1.8881
[7 empty] | 3582 | 54 | 3.2137 | 2.3503
[7 empty] | 3583 | 55 | 4.335 | 3.2613
[7 empty] | 3584 | 56 | 4.5741 | 3.4556
[7 empty] | 3585 | 57 | 5.5057 | 4.2125
[7 empty] | 3586 | 58 | 6.594 | 5.0967
[7 empty] | 3587 | 59 | 7.7813 | 6.0613
[7 empty] | 3588 | 60 | 8.3996 | 6.5637
[7 empty] | 3589 | 61 | 9.0674 | 7.1063
[7 empty] | 3590 | 62 | 8.8696 | 6.9455
[7 empty] | 3591 | 63 | 9.4549 | 7.4211
[7 empty] | 3592 | 64 | 10.3866 | 8.178
[7 empty] | 3593 | 65 | 10.9967 | 8.6737
[7 empty] | 3594 | 66 | 10.8977 | 8.5933
[7 empty] | 3595 | 67 | 11.6233 | 9.1828
[7 empty] | 3596 | 68 | 11.8624 | 9.377
[7 empty] | 3597 | 69 | 11.3594 | 8.9684
[7 empty] | 3598 | 70 | 9.1004 | 7.133
[7 empty] | 3599 | 71 | 4.6565 | 3.5226
[7 empty] | 3600 | 72 | 3.5894 | 2.6556
[7 empty] | 3601 | 73 | 2.8839 | 2.0824
[7 empty] | 3602 | 74 | 2.6613 | 1.9015
[7 empty] | 3603 | 75 | 2.5624 | 1.8211
[7 empty] | 3604 | 76 | 2.5047 | 1.7743
[7 empty] | 3605 | 77 | 2.6778 | 1.9149
[7 empty] | 3606 | 78 | 3.0735 | 2.2365
[7 empty] | 3607 | 79 | 4.1701 | 3.1274
[7 empty] | 3608 | 80 | 4.3432 | 3.268
[7 empty] | 3609 | 81 | 5.5057 | 4.2125
[7 empty] | 3610 | 82 | 6.5775 | 5.0833
[7 empty] | 3611 | 83 | 7.3031 | 5.6728
[7 empty] | 3612 | 84 | 8.5233 | 6.6642
[7 empty] | 3613 | 85 | 8.2265 | 6.423
[7 empty] | 3614 | 86 | 7.7235 | 6.0144
[7 empty] | 3615 | 87 | 8.1605 | 6.3694
[7 empty] | 3616 | 88 | 8.8118 | 6.8986
[7 empty] | 3617 | 89 | 10.1392 | 7.9771
[7 empty] | 3618 | 90 | 9.5621 | 7.5082
[7 empty] | 3619 | 91 | 10.2382 | 8.0574
[7 empty] | 3620 | 92 | 9.6446 | 7.5751
[7 empty] | 3621 | 93 | 7.2701 | 5.646
[7 empty] | 3622 | 94 | 6.3797 | 4.9225
[7 empty] | 3623 | 95 | 4.5493 | 3.4355
[7 empty] | 3624 | 96 | 3.5765 | 2.6451
[7 empty] | 3625 | 97 | 3.527 | 2.6049
[7 empty] | 3626 | 98 | 3.2384 | 2.3704
[7 empty] | 3627 | 99 | 3.1807 | 2.3235
[7 empty] | 3628 | 100 | 2.8345 | 2.0422
[7 empty] | 3629 | 101 | 2.7767 | 1.9953
[7 empty] | 3630 | 102 | 3.0076 | 2.1829
[7 empty] | 3631 | 103 | 3.7414 | 2.779
[7 empty] | 3632 | 104 | 3.9887 | 2.98
[7 empty] | 3633 | 105 | 4.4669 | 3.3685
[7 empty] | 3634 | 106 | 5.9015 | 4.534
[7 empty] | 3635 | 107 | 6.2477 | 4.8154
[7 empty] | 3636 | 108 | 7.7977 | 6.0747
[7 empty] | 3637 | 109 | 7.1464 | 5.5455
[7 empty] | 3638 | 110 | 6.7012 | 5.1838
[7 empty] | 3639 | 111 | 6.5446 | 5.0565
[7 empty] | 3640 | 112 | 6.6105 | 5.1101
[7 empty] | 3641 | 113 | 6.2725 | 4.8355
[7 empty] | 3642 | 114 | 6.4374 | 4.9694
[7 empty] | 3643 | 115 | 5.9922 | 4.6077
[7 empty] | 3644 | 116 | 6.66 | 5.1503
[7 empty] | 3645 | 117 | 6.2477 | 4.8154
[7 empty] | 3646 | 118 | 5.4892 | 4.1991
[7 empty] | 3647 | 119 | 3.9227 | 2.9264
[7 empty] | 3648 | 120 | 3.6106 | 2.6728
[7 empty] | 3649 | 121 | 2.8922 | 2.0891
[7 empty] | 3650 | 122 | 2.4882 | 1.7609
[7 empty] | 3651 | 123 | 2.4057 | 1.6939
[7 empty] | 3652 | 124 | 2.3727 | 1.6671
[7 empty] | 3653 | 125 | 2.3315 | 1.6336
[7 empty] | 3654 | 126 | 2.4717 | 1.7475
[7 empty] | 3655 | 127 | 3.9557 | 2.9532
[7 empty] | 3656 | 128 | 5.4892 | 4.1991
[7 empty] | 3657 | 129 | 6.1571 | 4.7417
[7 empty] | 3658 | 130 | 6.5858 | 5.09
[7 empty] | 3659 | 131 | 6.7424 | 5.2173
[7 empty] | 3660 | 132 | 6.4951 | 5.0163
[7 empty] | 3661 | 133 | 7.1217 | 5.5254
[7 empty] | 3662 | 134 | 7.4185 | 5.7666
[7 empty] | 3663 | 135 | 7.4844 | 5.8201
[7 empty] | 3664 | 136 | 6.6847 | 5.1704
[7 empty] | 3665 | 137 | 6.5858 | 5.09
[7 empty] | 3666 | 138 | 6.5363 | 5.0498
[7 empty] | 3667 | 139 | 6.2065 | 4.7819
[7 empty] | 3668 | 140 | 6.2148 | 4.7886
[7 empty] | 3669 | 141 | 5.5717 | 4.2661
[7 empty] | 3670 | 142 | 4.9451 | 3.757
[7 empty] | 3671 | 143 | 4.0794 | 3.0537
[7 empty] | 3672 | 144 | 3.4775 | 2.5647
[7 empty] | 3673 | 145 | 3.0158 | 2.1896
[7 empty] | 3674 | 146 | 2.8097 | 2.0221
[7 empty] | 3675 | 147 | 2.7438 | 1.9685
[7 empty] | 3676 | 148 | 2.7355 | 1.9618
[7 empty] | 3677 | 149 | 2.7355 | 1.9618
[7 empty] | 3678 | 150 | 2.7438 | 1.9685
[7 empty] | 3679 | 151 | 3.8073 | 2.8326
[7 empty] | 3680 | 152 | 5.3079 | 4.0517
[7 empty] | 3681 | 153 | 5.9097 | 4.5407
[7 empty] | 3682 | 154 | 6.4621 | 4.9895
[7 empty] | 3683 | 155 | 6.3137 | 4.869
[7 empty] | 3684 | 156 | 6.4786 | 5.0029
[7 empty] | 3685 | 157 | 7.1794 | 5.5723
[7 empty] | 3686 | 158 | 7.5009 | 5.8335
[7 empty] | 3687 | 159 | 7.7648 | 6.0479
[7 empty] | 3688 | 160 | 7.6411 | 5.9474
[7 empty] | 3689 | 161 | 8.3914 | 6.557
[7 empty] | 3690 | 162 | 7.9049 | 6.1618
[7 empty] | 3691 | 163 | 8.2594 | 6.4498
[7 empty] | 3692 | 164 | 6.9321 | 5.3713
[7 empty] | 3693 | 165 | 10.0073 | 7.8699
[7 empty] | 3694 | 166 | 7.9956 | 6.2354
[7 empty] | 3695 | 167 | 4.4504 | 3.3551
[7 empty] | 3696 | 168 | 3.8156 | 2.8393
[7 empty] | 3697 | 1 | 2.381 | 1.6738
[7 empty] | 3698 | 2 | 2.2738 | 1.5867
[7 empty] | 3699 | 3 | 2.2656 | 1.58
[7 empty] | 3700 | 4 | 2.3975 | 1.6872
[7 empty] | 3701 | 5 | 2.414 | 1.7006
[7 empty] | 3702 | 6 | 2.8345 | 2.0422
[7 empty] | 3703 | 7 | 3.5435 | 2.6183
[7 empty] | 3704 | 8 | 4.2031 | 3.1541
[7 empty] | 3705 | 9 | 4.1783 | 3.134
[7 empty] | 3706 | 10 | 5.6706 | 4.3465
[7 empty] | 3707 | 11 | 7.7153 | 6.0077
[7 empty] | 3708 | 12 | 8.6634 | 6.778
[7 empty] | 3709 | 13 | 9.0344 | 7.0795
[7 empty] | 3710 | 14 | 8.8201 | 6.9053
[7 empty] | 3711 | 15 | 8.7294 | 6.8316
[7 empty] | 3712 | 16 | 9.8919 | 7.7761
[7 empty] | 3713 | 17 | 11.1946 | 8.8345
[7 empty] | 3714 | 18 | 10.9555 | 8.6402
[7 empty] | 3715 | 19 | 11.4749 | 9.0622
[7 empty] | 3716 | 20 | 11.4089 | 9.0086
[7 empty] | 3717 | 21 | 11.9696 | 9.4641
[7 empty] | 3718 | 22 | 8.0781 | 6.3024
[7 empty] | 3719 | 23 | 4.368 | 3.2881
[7 empty] | 3720 | 24 | 2.724 | 1.9525
[7 empty] | 3721 | 25 | 2.6283 | 1.8747
[7 empty] | 3722 | 26 | 2.5212 | 1.7877
[7 empty] | 3723 | 27 | 2.4222 | 1.7073
[7 empty] | 3724 | 28 | 2.5047 | 1.7743
[7 empty] | 3725 | 29 | 2.7438 | 1.9685
[7 empty] | 3726 | 30 | 2.9829 | 2.1628
[7 empty] | 3727 | 31 | 3.8156 | 2.8393
[7 empty] | 3728 | 32 | 4.1618 | 3.1207
[7 empty] | 3729 | 33 | 4.8132 | 3.6498
[7 empty] | 3730 | 34 | 5.6954 | 4.3666
[7 empty] | 3731 | 35 | 7.8307 | 6.1015
[7 empty] | 3732 | 36 | 8.8448 | 6.9254
[7 empty] | 3733 | 37 | 8.919 | 6.9857
[7 empty] | 3734 | 38 | 8.9932 | 7.046
[7 empty] | 3735 | 39 | 8.6717 | 6.7847
[7 empty] | 3736 | 40 | 9.7105 | 7.6287
[7 empty] | 3737 | 41 | 10.2547 | 8.0708
[7 empty] | 3738 | 42 | 10.2711 | 8.0842
[7 empty] | 3739 | 43 | 10.6339 | 8.379
[7 empty] | 3740 | 44 | 11.7717 | 9.3034
[7 empty] | 3741 | 45 | 11.3759 | 8.9818
[7 empty] | 3742 | 46 | 8.6717 | 6.7847
[7 empty] | 3743 | 47 | 5.1265 | 3.9044
[7 empty] | 3744 | 48 | 3.6507 | 2.7053
[7 empty] | 3745 | 49 | 2.9993 | 2.1762
[7 empty] | 3746 | 50 | 2.6943 | 1.9283
[7 empty] | 3747 | 51 | 2.5871 | 1.8412
[7 empty] | 3748 | 52 | 2.6201 | 1.868
[7 empty] | 3749 | 53 | 2.6448 | 1.8881
[7 empty] | 3750 | 54 | 3.2137 | 2.3503
[7 empty] | 3751 | 55 | 4.335 | 3.2613
[7 empty] | 3752 | 56 | 4.5741 | 3.4556
[7 empty] | 3753 | 57 | 5.5057 | 4.2125
[7 empty] | 3754 | 58 | 6.594 | 5.0967
[7 empty] | 3755 | 59 | 7.7813 | 6.0613
[7 empty] | 3756 | 60 | 8.3996 | 6.5637
[7 empty] | 3757 | 61 | 9.0674 | 7.1063
[7 empty] | 3758 | 62 | 8.8696 | 6.9455
[7 empty] | 3759 | 63 | 9.4549 | 7.4211
[7 empty] | 3760 | 64 | 10.3866 | 8.178
[7 empty] | 3761 | 65 | 10.9967 | 8.6737
[7 empty] | 3762 | 66 | 10.8977 | 8.5933
[7 empty] | 3763 | 67 | 11.6233 | 9.1828
[7 empty] | 3764 | 68 | 11.8624 | 9.377
[7 empty] | 3765 | 69 | 11.3594 | 8.9684
[7 empty] | 3766 | 70 | 9.1004 | 7.133
[7 empty] | 3767 | 71 | 4.6565 | 3.5226
[7 empty] | 3768 | 72 | 3.5894 | 2.6556
[7 empty] | 3769 | 73 | 2.8839 | 2.0824
[7 empty] | 3770 | 74 | 2.6613 | 1.9015
[7 empty] | 3771 | 75 | 2.5624 | 1.8211
[7 empty] | 3772 | 76 | 2.5047 | 1.7743
[7 empty] | 3773 | 77 | 2.6778 | 1.9149
[7 empty] | 3774 | 78 | 3.0735 | 2.2365
[7 empty] | 3775 | 79 | 4.1701 | 3.1274
[7 empty] | 3776 | 80 | 4.3432 | 3.268
[7 empty] | 3777 | 81 | 5.5057 | 4.2125
[7 empty] | 3778 | 82 | 6.5775 | 5.0833
[7 empty] | 3779 | 83 | 7.3031 | 5.6728
[7 empty] | 3780 | 84 | 8.5233 | 6.6642
[7 empty] | 3781 | 85 | 8.2265 | 6.423
[7 empty] | 3782 | 86 | 7.7235 | 6.0144
[7 empty] | 3783 | 87 | 8.1605 | 6.3694
[7 empty] | 3784 | 88 | 8.8118 | 6.8986
[7 empty] | 3785 | 89 | 10.1392 | 7.9771
[7 empty] | 3786 | 90 | 9.5621 | 7.5082
[7 empty] | 3787 | 91 | 10.2382 | 8.0574
[7 empty] | 3788 | 92 | 9.6446 | 7.5751
[7 empty] | 3789 | 93 | 7.2701 | 5.646
[7 empty] | 3790 | 94 | 6.3797 | 4.9225
[7 empty] | 3791 | 95 | 4.5493 | 3.4355
[7 empty] | 3792 | 96 | 3.5765 | 2.6451
[7 empty] | 3793 | 97 | 3.527 | 2.6049
[7 empty] | 3794 | 98 | 3.2384 | 2.3704
[7 empty] | 3795 | 99 | 3.1807 | 2.3235
[7 empty] | 3796 | 100 | 2.8345 | 2.0422
[7 empty] | 3797 | 101 | 2.7767 | 1.9953
[7 empty] | 3798 | 102 | 3.0076 | 2.1829
[7 empty] | 3799 | 103 | 3.7414 | 2.779
[7 empty] | 3800 | 104 | 3.9887 | 2.98
[7 empty] | 3801 | 105 | 4.4669 | 3.3685
[7 empty] | 3802 | 106 | 5.9015 | 4.534
[7 empty] | 3803 | 107 | 6.2477 | 4.8154
[7 empty] | 3804 | 108 | 7.7977 | 6.0747
[7 empty] | 3805 | 109 | 7.1464 | 5.5455
[7 empty] | 3806 | 110 | 6.7012 | 5.1838
[7 empty] | 3807 | 111 | 6.5446 | 5.0565
[7 empty] | 3808 | 112 | 6.6105 | 5.1101
[7 empty] | 3809 | 113 | 6.2725 | 4.8355
[7 empty] | 3810 | 114 | 6.4374 | 4.9694
[7 empty] | 3811 | 115 | 5.9922 | 4.6077
[7 empty] | 3812 | 116 | 6.66 | 5.1503
[7 empty] | 3813 | 117 | 6.2477 | 4.8154
[7 empty] | 3814 | 118 | 5.4892 | 4.1991
[7 empty] | 3815 | 119 | 3.9227 | 2.9264
[7 empty] | 3816 | 120 | 3.6106 | 2.6728
[7 empty] | 3817 | 121 | 2.8922 | 2.0891
[7 empty] | 3818 | 122 | 2.4882 | 1.7609
[7 empty] | 3819 | 123 | 2.4057 | 1.6939
[7 empty] | 3820 | 124 | 2.3727 | 1.6671
[7 empty] | 3821 | 125 | 2.3315 | 1.6336
[7 empty] | 3822 | 126 | 2.4717 | 1.7475
[7 empty] | 3823 | 127 | 3.9557 | 2.9532
[7 empty] | 3824 | 128 | 5.4892 | 4.1991
[7 empty] | 3825 | 129 | 6.1571 | 4.7417
[7 empty] | 3826 | 130 | 6.5858 | 5.09
[7 empty] | 3827 | 131 | 6.7424 | 5.2173
[7 empty] | 3828 | 132 | 6.4951 | 5.0163
[7 empty] | 3829 | 133 | 7.1217 | 5.5254
[7 empty] | 3830 | 134 | 7.4185 | 5.7666
[7 empty] | 3831 | 135 | 7.4844 | 5.8201
[7 empty] | 3832 | 136 | 6.6847 | 5.1704
[7 empty] | 3833 | 137 | 6.5858 | 5.09
[7 empty] | 3834 | 138 | 6.5363 | 5.0498
[7 empty] | 3835 | 139 | 6.2065 | 4.7819
[7 empty] | 3836 | 140 | 6.2148 | 4.7886
[7 empty] | 3837 | 141 | 5.5717 | 4.2661
[7 empty] | 3838 | 142 | 4.9451 | 3.757
[7 empty] | 3839 | 143 | 4.0794 | 3.0537
[7 empty] | 3840 | 144 | 3.4775 | 2.5647
[7 empty] | 3841 | 145 | 3.0158 | 2.1896
[7 empty] | 3842 | 146 | 2.8097 | 2.0221
[7 empty] | 3843 | 147 | 2.7438 | 1.9685
[7 empty] | 3844 | 148 | 2.7355 | 1.9618
[7 empty] | 3845 | 149 | 2.7355 | 1.9618
[7 empty] | 3846 | 150 | 2.7438 | 1.9685
[7 empty] | 3847 | 151 | 3.8073 | 2.8326
[7 empty] | 3848 | 152 | 5.3079 | 4.0517
[7 empty] | 3849 | 153 | 5.9097 | 4.5407
[7 empty] | 3850 | 154 | 6.4621 | 4.9895
[7 empty] | 3851 | 155 | 6.3137 | 4.869
[7 empty] | 3852 | 156 | 6.4786 | 5.0029
[7 empty] | 3853 | 157 | 7.1794 | 5.5723
[7 empty] | 3854 | 158 | 7.5009 | 5.8335
[7 empty] | 3855 | 159 | 7.7648 | 6.0479
[7 empty] | 3856 | 160 | 7.6411 | 5.9474
[7 empty] | 3857 | 161 | 8.3914 | 6.557
[7 empty] | 3858 | 162 | 7.9049 | 6.1618
[7 empty] | 3859 | 163 | 8.2594 | 6.4498
[7 empty] | 3860 | 164 | 6.9321 | 5.3713
[7 empty] | 3861 | 165 | 10.0073 | 7.8699
[7 empty] | 3862 | 166 | 7.9956 | 6.2354
[7 empty] | 3863 | 167 | 4.4504 | 3.3551
[7 empty] | 3864 | 168 | 3.8156 | 2.8393
[7 empty] | 3865 | 1 | 2.381 | 1.6738
[7 empty] | 3866 | 2 | 2.2738 | 1.5867
[7 empty] | 3867 | 3 | 2.2656 | 1.58
[7 empty] | 3868 | 4 | 2.3975 | 1.6872
[7 empty] | 3869 | 5 | 2.414 | 1.7006
[7 empty] | 3870 | 6 | 2.8345 | 2.0422
[7 empty] | 3871 | 7 | 3.5435 | 2.6183
[7 empty] | 3872 | 8 | 4.2031 | 3.1541
[7 empty] | 3873 | 9 | 4.1783 | 3.134
[7 empty] | 3874 | 10 | 5.6706 | 4.3465
[7 empty] | 3875 | 11 | 7.7153 | 6.0077
[7 empty] | 3876 | 12 | 8.6634 | 6.778
[7 empty] | 3877 | 13 | 9.0344 | 7.0795
[7 empty] | 3878 | 14 | 8.8201 | 6.9053
[7 empty] | 3879 | 15 | 8.7294 | 6.8316
[7 empty] | 3880 | 16 | 9.8919 | 7.7761
[7 empty] | 3881 | 17 | 11.1946 | 8.8345
[7 empty] | 3882 | 18 | 10.9555 | 8.6402
[7 empty] | 3883 | 19 | 11.4749 | 9.0622
[7 empty] | 3884 | 20 | 11.4089 | 9.0086
[7 empty] | 3885 | 21 | 11.9696 | 9.4641
[7 empty] | 3886 | 22 | 8.0781 | 6.3024
[7 empty] | 3887 | 23 | 4.368 | 3.2881
[7 empty] | 3888 | 24 | 2.724 | 1.9525
[7 empty] | 3889 | 25 | 2.6283 | 1.8747
[7 empty] | 3890 | 26 | 2.5212 | 1.7877
[7 empty] | 3891 | 27 | 2.4222 | 1.7073
[7 empty] | 3892 | 28 | 2.5047 | 1.7743
[7 empty] | 3893 | 29 | 2.7438 | 1.9685
[7 empty] | 3894 | 30 | 2.9829 | 2.1628
[7 empty] | 3895 | 31 | 3.8156 | 2.8393
[7 empty] | 3896 | 32 | 4.1618 | 3.1207
[7 empty] | 3897 | 33 | 4.8132 | 3.6498
[7 empty] | 3898 | 34 | 5.6954 | 4.3666
[7 empty] | 3899 | 35 | 7.8307 | 6.1015
[7 empty] | 3900 | 36 | 8.8448 | 6.9254
[7 empty] | 3901 | 37 | 8.919 | 6.9857
[7 empty] | 3902 | 38 | 8.9932 | 7.046
[7 empty] | 3903 | 39 | 8.6717 | 6.7847
[7 empty] | 3904 | 40 | 9.7105 | 7.6287
[7 empty] | 3905 | 41 | 10.2547 | 8.0708
[7 empty] | 3906 | 42 | 10.2711 | 8.0842
[7 empty] | 3907 | 43 | 10.6339 | 8.379
[7 empty] | 3908 | 44 | 11.7717 | 9.3034
[7 empty] | 3909 | 45 | 11.3759 | 8.9818
[7 empty] | 3910 | 46 | 8.6717 | 6.7847
[7 empty] | 3911 | 47 | 5.1265 | 3.9044
[7 empty] | 3912 | 48 | 3.6507 | 2.7053
[7 empty] | 3913 | 49 | 2.9993 | 2.1762
[7 empty] | 3914 | 50 | 2.6943 | 1.9283
[7 empty] | 3915 | 51 | 2.5871 | 1.8412
[7 empty] | 3916 | 52 | 2.6201 | 1.868
[7 empty] | 3917 | 53 | 2.6448 | 1.8881
[7 empty] | 3918 | 54 | 3.2137 | 2.3503
[7 empty] | 3919 | 55 | 4.335 | 3.2613
[7 empty] | 3920 | 56 | 4.5741 | 3.4556
[7 empty] | 3921 | 57 | 5.5057 | 4.2125
[7 empty] | 3922 | 58 | 6.594 | 5.0967
[7 empty] | 3923 | 59 | 7.7813 | 6.0613
[7 empty] | 3924 | 60 | 8.3996 | 6.5637
[7 empty] | 3925 | 61 | 9.0674 | 7.1063
[7 empty] | 3926 | 62 | 8.8696 | 6.9455
[7 empty] | 3927 | 63 | 9.4549 | 7.4211
[7 empty] | 3928 | 64 | 10.3866 | 8.178
[7 empty] | 3929 | 65 | 10.9967 | 8.6737
[7 empty] | 3930 | 66 | 10.8977 | 8.5933
[7 empty] | 3931 | 67 | 11.6233 | 9.1828
[7 empty] | 3932 | 68 | 11.8624 | 9.377
[7 empty] | 3933 | 69 | 11.3594 | 8.9684
[7 empty] | 3934 | 70 | 9.1004 | 7.133
[7 empty] | 3935 | 71 | 4.6565 | 3.5226
[7 empty] | 3936 | 72 | 3.5894 | 2.6556
[7 empty] | 3937 | 73 | 2.8839 | 2.0824
[7 empty] | 3938 | 74 | 2.6613 | 1.9015
[7 empty] | 3939 | 75 | 2.5624 | 1.8211
[7 empty] | 3940 | 76 | 2.5047 | 1.7743
[7 empty] | 3941 | 77 | 2.6778 | 1.9149
[7 empty] | 3942 | 78 | 3.0735 | 2.2365
[7 empty] | 3943 | 79 | 4.1701 | 3.1274
[7 empty] | 3944 | 80 | 4.3432 | 3.268
[7 empty] | 3945 | 81 | 5.5057 | 4.2125
[7 empty] | 3946 | 82 | 6.5775 | 5.0833
[7 empty] | 3947 | 83 | 7.3031 | 5.6728
[7 empty] | 3948 | 84 | 8.5233 | 6.6642
[7 empty] | 3949 | 85 | 8.2265 | 6.423
[7 empty] | 3950 | 86 | 7.7235 | 6.0144
[7 empty] | 3951 | 87 | 8.1605 | 6.3694
[7 empty] | 3952 | 88 | 8.8118 | 6.8986
[7 empty] | 3953 | 89 | 10.1392 | 7.9771
[7 empty] | 3954 | 90 | 9.5621 | 7.5082
[7 empty] | 3955 | 91 | 10.2382 | 8.0574
[7 empty] | 3956 | 92 | 9.6446 | 7.5751
[7 empty] | 3957 | 93 | 7.2701 | 5.646
[7 empty] | 3958 | 94 | 6.3797 | 4.9225
[7 empty] | 3959 | 95 | 4.5493 | 3.4355
[7 empty] | 3960 | 96 | 3.5765 | 2.6451
[7 empty] | 3961 | 97 | 3.527 | 2.6049
[7 empty] | 3962 | 98 | 3.2384 | 2.3704
[7 empty] | 3963 | 99 | 3.1807 | 2.3235
[7 empty] | 3964 | 100 | 2.8345 | 2.0422
[7 empty] | 3965 | 101 | 2.7767 | 1.9953
[7 empty] | 3966 | 102 | 3.0076 | 2.1829
[7 empty] | 3967 | 103 | 3.7414 | 2.779
[7 empty] | 3968 | 104 | 3.9887 | 2.98
[7 empty] | 3969 | 105 | 4.4669 | 3.3685
[7 empty] | 3970 | 106 | 5.9015 | 4.534
[7 empty] | 3971 | 107 | 6.2477 | 4.8154
[7 empty] | 3972 | 108 | 7.7977 | 6.0747
[7 empty] | 3973 | 109 | 7.1464 | 5.5455
[7 empty] | 3974 | 110 | 6.7012 | 5.1838
[7 empty] | 3975 | 111 | 6.5446 | 5.0565
[7 empty] | 3976 | 112 | 6.6105 | 5.1101
[7 empty] | 3977 | 113 | 6.2725 | 4.8355
[7 empty] | 3978 | 114 | 6.4374 | 4.9694
[7 empty] | 3979 | 115 | 5.9922 | 4.6077
[7 empty] | 3980 | 116 | 6.66 | 5.1503
[7 empty] | 3981 | 117 | 6.2477 | 4.8154
[7 empty] | 3982 | 118 | 5.4892 | 4.1991
[7 empty] | 3983 | 119 | 3.9227 | 2.9264
[7 empty] | 3984 | 120 | 3.6106 | 2.6728
[7 empty] | 3985 | 121 | 2.8922 | 2.0891
[7 empty] | 3986 | 122 | 2.4882 | 1.7609
[7 empty] | 3987 | 123 | 2.4057 | 1.6939
[7 empty] | 3988 | 124 | 2.3727 | 1.6671
[7 empty] | 3989 | 125 | 2.3315 | 1.6336
[7 empty] | 3990 | 126 | 2.4717 | 1.7475
[7 empty] | 3991 | 127 | 3.9557 | 2.9532
[7 empty] | 3992 | 128 | 5.4892 | 4.1991
[7 empty] | 3993 | 129 | 6.1571 | 4.7417
[7 empty] | 3994 | 130 | 6.5858 | 5.09
[7 empty] | 3995 | 131 | 6.7424 | 5.2173
[7 empty] | 3996 | 132 | 6.4951 | 5.0163
[7 empty] | 3997 | 133 | 7.1217 | 5.5254
[7 empty] | 3998 | 134 | 7.4185 | 5.7666
[7 empty] | 3999 | 135 | 7.4844 | 5.8201
[7 empty] | 4000 | 136 | 6.6847 | 5.1704
[7 empty] | 4001 | 137 | 6.5858 | 5.09
[7 empty] | 4002 | 138 | 6.5363 | 5.0498
[7 empty] | 4003 | 139 | 6.2065 | 4.7819
[7 empty] | 4004 | 140 | 6.2148 | 4.7886
[7 empty] | 4005 | 141 | 5.5717 | 4.2661
[7 empty] | 4006 | 142 | 4.9451 | 3.757
[7 empty] | 4007 | 143 | 4.0794 | 3.0537
[7 empty] | 4008 | 144 | 3.4775 | 2.5647
[7 empty] | 4009 | 145 | 3.0158 | 2.1896
[7 empty] | 4010 | 146 | 2.8097 | 2.0221
[7 empty] | 4011 | 147 | 2.7438 | 1.9685
[7 empty] | 4012 | 148 | 2.7355 | 1.9618
[7 empty] | 4013 | 149 | 2.7355 | 1.9618
[7 empty] | 4014 | 150 | 2.7438 | 1.9685
[7 empty] | 4015 | 151 | 3.8073 | 2.8326
[7 empty] | 4016 | 152 | 5.3079 | 4.0517
[7 empty] | 4017 | 153 | 5.9097 | 4.5407
[7 empty] | 4018 | 154 | 6.4621 | 4.9895
[7 empty] | 4019 | 155 | 6.3137 | 4.869
[7 empty] | 4020 | 156 | 6.4786 | 5.0029
[7 empty] | 4021 | 157 | 7.1794 | 5.5723
[7 empty] | 4022 | 158 | 7.5009 | 5.8335
[7 empty] | 4023 | 159 | 7.7648 | 6.0479
[7 empty] | 4024 | 160 | 7.6411 | 5.9474
[7 empty] | 4025 | 161 | 8.3914 | 6.557
[7 empty] | 4026 | 162 | 7.9049 | 6.1618
[7 empty] | 4027 | 163 | 8.2594 | 6.4498
[7 empty] | 4028 | 164 | 6.9321 | 5.3713
[7 empty] | 4029 | 165 | 10.0073 | 7.8699
[7 empty] | 4030 | 166 | 7.9956 | 6.2354
[7 empty] | 4031 | 167 | 4.4504 | 3.3551
[7 empty] | 4032 | 168 | 3.8156 | 2.8393
[7 empty] | 4033 | 1 | 2.381 | 1.6738
[7 empty] | 4034 | 2 | 2.2738 | 1.5867
[7 empty] | 4035 | 3 | 2.2656 | 1.58
[7 empty] | 4036 | 4 | 2.3975 | 1.6872
[7 empty] | 4037 | 5 | 2.414 | 1.7006
[7 empty] | 4038 | 6 | 2.8345 | 2.0422
[7 empty] | 4039 | 7 | 3.5435 | 2.6183
[7 empty] | 4040 | 8 | 4.2031 | 3.1541
[7 empty] | 4041 | 9 | 4.1783 | 3.134
[7 empty] | 4042 | 10 | 5.6706 | 4.3465
[7 empty] | 4043 | 11 | 7.7153 | 6.0077
[7 empty] | 4044 | 12 | 8.6634 | 6.778
[7 empty] | 4045 | 13 | 9.0344 | 7.0795
[7 empty] | 4046 | 14 | 8.8201 | 6.9053
[7 empty] | 4047 | 15 | 8.7294 | 6.8316
[7 empty] | 4048 | 16 | 9.8919 | 7.7761
[7 empty] | 4049 | 17 | 11.1946 | 8.8345
[7 empty] | 4050 | 18 | 10.9555 | 8.6402
[7 empty] | 4051 | 19 | 11.4749 | 9.0622
[7 empty] | 4052 | 20 | 11.4089 | 9.0086
[7 empty] | 4053 | 21 | 11.9696 | 9.4641
[7 empty] | 4054 | 22 | 8.0781 | 6.3024
[7 empty] | 4055 | 23 | 4.368 | 3.2881
[7 empty] | 4056 | 24 | 2.724 | 1.9525
[7 empty] | 4057 | 25 | 2.6283 | 1.8747
[7 empty] | 4058 | 26 | 2.5212 | 1.7877
[7 empty] | 4059 | 27 | 2.4222 | 1.7073
[7 empty] | 4060 | 28 | 2.5047 | 1.7743
[7 empty] | 4061 | 29 | 2.7438 | 1.9685
[7 empty] | 4062 | 30 | 2.9829 | 2.1628
[7 empty] | 4063 | 31 | 3.8156 | 2.8393
[7 empty] | 4064 | 32 | 4.1618 | 3.1207
[7 empty] | 4065 | 33 | 4.8132 | 3.6498
[7 empty] | 4066 | 34 | 5.6954 | 4.3666
[7 empty] | 4067 | 35 | 7.8307 | 6.1015
[7 empty] | 4068 | 36 | 8.8448 | 6.9254
[7 empty] | 4069 | 37 | 8.919 | 6.9857
[7 empty] | 4070 | 38 | 8.9932 | 7.046
[7 empty] | 4071 | 39 | 8.6717 | 6.7847
[7 empty] | 4072 | 40 | 9.7105 | 7.6287
[7 empty] | 4073 | 41 | 10.2547 | 8.0708
[7 empty] | 4074 | 42 | 10.2711 | 8.0842
[7 empty] | 4075 | 43 | 10.6339 | 8.379
[7 empty] | 4076 | 44 | 11.7717 | 9.3034
[7 empty] | 4077 | 45 | 11.3759 | 8.9818
[7 empty] | 4078 | 46 | 8.6717 | 6.7847
[7 empty] | 4079 | 47 | 5.1265 | 3.9044
[7 empty] | 4080 | 48 | 3.6507 | 2.7053
[7 empty] | 4081 | 49 | 2.9993 | 2.1762
[7 empty] | 4082 | 50 | 2.6943 | 1.9283
[7 empty] | 4083 | 51 | 2.5871 | 1.8412
[7 empty] | 4084 | 52 | 2.6201 | 1.868
[7 empty] | 4085 | 53 | 2.6448 | 1.8881
[7 empty] | 4086 | 54 | 3.2137 | 2.3503
[7 empty] | 4087 | 55 | 4.335 | 3.2613
[7 empty] | 4088 | 56 | 4.5741 | 3.4556
[7 empty] | 4089 | 57 | 5.5057 | 4.2125
[7 empty] | 4090 | 58 | 6.594 | 5.0967
[7 empty] | 4091 | 59 | 7.7813 | 6.0613
[7 empty] | 4092 | 60 | 8.3996 | 6.5637
[7 empty] | 4093 | 61 | 9.0674 | 7.1063
[7 empty] | 4094 | 62 | 8.8696 | 6.9455
[7 empty] | 4095 | 63 | 9.4549 | 7.4211
[7 empty] | 4096 | 64 | 10.3866 | 8.178
[7 empty] | 4097 | 65 | 10.9967 | 8.6737
[7 empty] | 4098 | 66 | 10.8977 | 8.5933
[7 empty] | 4099 | 67 | 11.6233 | 9.1828
[7 empty] | 4100 | 68 | 11.8624 | 9.377
[7 empty] | 4101 | 69 | 11.3594 | 8.9684
[7 empty] | 4102 | 70 | 9.1004 | 7.133
[7 empty] | 4103 | 71 | 4.6565 | 3.5226
[7 empty] | 4104 | 72 | 3.5894 | 2.6556
[7 empty] | 4105 | 73 | 2.8839 | 2.0824
[7 empty] | 4106 | 74 | 2.6613 | 1.9015
[7 empty] | 4107 | 75 | 2.5624 | 1.8211
[7 empty] | 4108 | 76 | 2.5047 | 1.7743
[7 empty] | 4109 | 77 | 2.6778 | 1.9149
[7 empty] | 4110 | 78 | 3.0735 | 2.2365
[7 empty] | 4111 | 79 | 4.1701 | 3.1274
[7 empty] | 4112 | 80 | 4.3432 | 3.268
[7 empty] | 4113 | 81 | 5.5057 | 4.2125
[7 empty] | 4114 | 82 | 6.5775 | 5.0833
[7 empty] | 4115 | 83 | 7.3031 | 5.6728
[7 empty] | 4116 | 84 | 8.5233 | 6.6642
[7 empty] | 4117 | 85 | 8.2265 | 6.423
[7 empty] | 4118 | 86 | 7.7235 | 6.0144
[7 empty] | 4119 | 87 | 8.1605 | 6.3694
[7 empty] | 4120 | 88 | 8.8118 | 6.8986
[7 empty] | 4121 | 89 | 10.1392 | 7.9771
[7 empty] | 4122 | 90 | 9.5621 | 7.5082
[7 empty] | 4123 | 91 | 10.2382 | 8.0574
[7 empty] | 4124 | 92 | 9.6446 | 7.5751
[7 empty] | 4125 | 93 | 7.2701 | 5.646
[7 empty] | 4126 | 94 | 6.3797 | 4.9225
[7 empty] | 4127 | 95 | 4.5493 | 3.4355
[7 empty] | 4128 | 96 | 3.5765 | 2.6451
[7 empty] | 4129 | 97 | 3.527 | 2.6049
[7 empty] | 4130 | 98 | 3.2384 | 2.3704
[7 empty] | 4131 | 99 | 3.1807 | 2.3235
[7 empty] | 4132 | 100 | 2.8345 | 2.0422
[7 empty] | 4133 | 101 | 2.7767 | 1.9953
[7 empty] | 4134 | 102 | 3.0076 | 2.1829
[7 empty] | 4135 | 103 | 3.7414 | 2.779
[7 empty] | 4136 | 104 | 3.9887 | 2.98
[7 empty] | 4137 | 105 | 4.4669 | 3.3685
[7 empty] | 4138 | 106 | 5.9015 | 4.534
[7 empty] | 4139 | 107 | 6.2477 | 4.8154
[7 empty] | 4140 | 108 | 7.7977 | 6.0747
[7 empty] | 4141 | 109 | 7.1464 | 5.5455
[7 empty] | 4142 | 110 | 6.7012 | 5.1838
[7 empty] | 4143 | 111 | 6.5446 | 5.0565
[7 empty] | 4144 | 112 | 6.6105 | 5.1101
[7 empty] | 4145 | 113 | 6.2725 | 4.8355
[7 empty] | 4146 | 114 | 6.4374 | 4.9694
[7 empty] | 4147 | 115 | 5.9922 | 4.6077
[7 empty] | 4148 | 116 | 6.66 | 5.1503
[7 empty] | 4149 | 117 | 6.2477 | 4.8154
[7 empty] | 4150 | 118 | 5.4892 | 4.1991
[7 empty] | 4151 | 119 | 3.9227 | 2.9264
[7 empty] | 4152 | 120 | 3.6106 | 2.6728
[7 empty] | 4153 | 121 | 2.8922 | 2.0891
[7 empty] | 4154 | 122 | 2.4882 | 1.7609
[7 empty] | 4155 | 123 | 2.4057 | 1.6939
[7 empty] | 4156 | 124 | 2.3727 | 1.6671
[7 empty] | 4157 | 125 | 2.3315 | 1.6336
[7 empty] | 4158 | 126 | 2.4717 | 1.7475
[7 empty] | 4159 | 127 | 3.9557 | 2.9532
[7 empty] | 4160 | 128 | 5.4892 | 4.1991
[7 empty] | 4161 | 129 | 6.1571 | 4.7417
[7 empty] | 4162 | 130 | 6.5858 | 5.09
[7 empty] | 4163 | 131 | 6.7424 | 5.2173
[7 empty] | 4164 | 132 | 6.4951 | 5.0163
[7 empty] | 4165 | 133 | 7.1217 | 5.5254
[7 empty] | 4166 | 134 | 7.4185 | 5.7666
[7 empty] | 4167 | 135 | 7.4844 | 5.8201
[7 empty] | 4168 | 136 | 6.6847 | 5.1704
[7 empty] | 4169 | 137 | 6.5858 | 5.09
[7 empty] | 4170 | 138 | 6.5363 | 5.0498
[7 empty] | 4171 | 139 | 6.2065 | 4.7819
[7 empty] | 4172 | 140 | 6.2148 | 4.7886
[7 empty] | 4173 | 141 | 5.5717 | 4.2661
[7 empty] | 4174 | 142 | 4.9451 | 3.757
[7 empty] | 4175 | 143 | 4.0794 | 3.0537
[7 empty] | 4176 | 144 | 3.4775 | 2.5647
[7 empty] | 4177 | 145 | 3.0158 | 2.1896
[7 empty] | 4178 | 146 | 2.8097 | 2.0221
[7 empty] | 4179 | 147 | 2.7438 | 1.9685
[7 empty] | 4180 | 148 | 2.7355 | 1.9618
[7 empty] | 4181 | 149 | 2.7355 | 1.9618
[7 empty] | 4182 | 150 | 2.7438 | 1.9685
[7 empty] | 4183 | 151 | 3.8073 | 2.8326
[7 empty] | 4184 | 152 | 5.3079 | 4.0517
[7 empty] | 4185 | 153 | 5.9097 | 4.5407
[7 empty] | 4186 | 154 | 6.4621 | 4.9895
[7 empty] | 4187 | 155 | 6.3137 | 4.869
[7 empty] | 4188 | 156 | 6.4786 | 5.0029
[7 empty] | 4189 | 157 | 7.1794 | 5.5723
[7 empty] | 4190 | 158 | 7.5009 | 5.8335
[7 empty] | 4191 | 159 | 7.7648 | 6.0479
[7 empty] | 4192 | 160 | 7.6411 | 5.9474
[7 empty] | 4193 | 161 | 8.3914 | 6.557
[7 empty] | 4194 | 162 | 7.9049 | 6.1618
[7 empty] | 4195 | 163 | 8.2594 | 6.4498
[7 empty] | 4196 | 164 | 6.9321 | 5.3713
[7 empty] | 4197 | 165 | 10.0073 | 7.8699
[7 empty] | 4198 | 166 | 7.9956 | 6.2354
[7 empty] | 4199 | 167 | 4.4504 | 3.3551
[7 empty] | 4200 | 168 | 3.8156 | 2.8393
[7 empty] | 4201 | 1 | 2.381 | 1.6738
[7 empty] | 4202 | 2 | 2.2738 | 1.5867
[7 empty] | 4203 | 3 | 2.2656 | 1.58
[7 empty] | 4204 | 4 | 2.3975 | 1.6872
[7 empty] | 4205 | 5 | 2.414 | 1.7006
[7 empty] | 4206 | 6 | 2.8345 | 2.0422
[7 empty] | 4207 | 7 | 3.5435 | 2.6183
[7 empty] | 4208 | 8 | 4.2031 | 3.1541
[7 empty] | 4209 | 9 | 4.1783 | 3.134
[7 empty] | 4210 | 10 | 5.6706 | 4.3465
[7 empty] | 4211 | 11 | 7.7153 | 6.0077
[7 empty] | 4212 | 12 | 8.6634 | 6.778
[7 empty] | 4213 | 13 | 9.0344 | 7.0795
[7 empty] | 4214 | 14 | 8.8201 | 6.9053
[7 empty] | 4215 | 15 | 8.7294 | 6.8316
[7 empty] | 4216 | 16 | 9.8919 | 7.7761
[7 empty] | 4217 | 17 | 11.1946 | 8.8345
[7 empty] | 4218 | 18 | 10.9555 | 8.6402
[7 empty] | 4219 | 19 | 11.4749 | 9.0622
[7 empty] | 4220 | 20 | 11.4089 | 9.0086
[7 empty] | 4221 | 21 | 11.9696 | 9.4641
[7 empty] | 4222 | 22 | 8.0781 | 6.3024
[7 empty] | 4223 | 23 | 4.368 | 3.2881
[7 empty] | 4224 | 24 | 2.724 | 1.9525
[7 empty] | 4225 | 25 | 2.6283 | 1.8747
[7 empty] | 4226 | 26 | 2.5212 | 1.7877
[7 empty] | 4227 | 27 | 2.4222 | 1.7073
[7 empty] | 4228 | 28 | 2.5047 | 1.7743
[7 empty] | 4229 | 29 | 2.7438 | 1.9685
[7 empty] | 4230 | 30 | 2.9829 | 2.1628
[7 empty] | 4231 | 31 | 3.8156 | 2.8393
[7 empty] | 4232 | 32 | 4.1618 | 3.1207
[7 empty] | 4233 | 33 | 4.8132 | 3.6498
[7 empty] | 4234 | 34 | 5.6954 | 4.3666
[7 empty] | 4235 | 35 | 7.8307 | 6.1015
[7 empty] | 4236 | 36 | 8.8448 | 6.9254
[7 empty] | 4237 | 37 | 8.919 | 6.9857
[7 empty] | 4238 | 38 | 8.9932 | 7.046
[7 empty] | 4239 | 39 | 8.6717 | 6.7847
[7 empty] | 4240 | 40 | 9.7105 | 7.6287
[7 empty] | 4241 | 41 | 10.2547 | 8.0708
[7 empty] | 4242 | 42 | 10.2711 | 8.0842
[7 empty] | 4243 | 43 | 10.6339 | 8.379
[7 empty] | 4244 | 44 | 11.7717 | 9.3034
[7 empty] | 4245 | 45 | 11.3759 | 8.9818
[7 empty] | 4246 | 46 | 8.6717 | 6.7847
[7 empty] | 4247 | 47 | 5.1265 | 3.9044
[7 empty] | 4248 | 48 | 3.6507 | 2.7053
[7 empty] | 4249 | 49 | 2.9993 | 2.1762
[7 empty] | 4250 | 50 | 2.6943 | 1.9283
[7 empty] | 4251 | 51 | 2.5871 | 1.8412
[7 empty] | 4252 | 52 | 2.6201 | 1.868
[7 empty] | 4253 | 53 | 2.6448 | 1.8881
[7 empty] | 4254 | 54 | 3.2137 | 2.3503
[7 empty] | 4255 | 55 | 4.335 | 3.2613
[7 empty] | 4256 | 56 | 4.5741 | 3.4556
[7 empty] | 4257 | 57 | 5.5057 | 4.2125
[7 empty] | 4258 | 58 | 6.594 | 5.0967
[7 empty] | 4259 | 59 | 7.7813 | 6.0613
[7 empty] | 4260 | 60 | 8.3996 | 6.5637
[7 empty] | 4261 | 61 | 9.0674 | 7.1063
[7 empty] | 4262 | 62 | 8.8696 | 6.9455
[7 empty] | 4263 | 63 | 9.4549 | 7.4211
[7 empty] | 4264 | 64 | 10.3866 | 8.178
[7 empty] | 4265 | 65 | 10.9967 | 8.6737
[7 empty] | 4266 | 66 | 10.8977 | 8.5933
[7 empty] | 4267 | 67 | 11.6233 | 9.1828
[7 empty] | 4268 | 68 | 11.8624 | 9.377
[7 empty] | 4269 | 69 | 11.3594 | 8.9684
[7 empty] | 4270 | 70 | 9.1004 | 7.133
[7 empty] | 4271 | 71 | 4.6565 | 3.5226
[7 empty] | 4272 | 72 | 3.5894 | 2.6556
[7 empty] | 4273 | 73 | 2.8839 | 2.0824
[7 empty] | 4274 | 74 | 2.6613 | 1.9015
[7 empty] | 4275 | 75 | 2.5624 | 1.8211
[7 empty] | 4276 | 76 | 2.5047 | 1.7743
[7 empty] | 4277 | 77 | 2.6778 | 1.9149
[7 empty] | 4278 | 78 | 3.0735 | 2.2365
[7 empty] | 4279 | 79 | 4.1701 | 3.1274
[7 empty] | 4280 | 80 | 4.3432 | 3.268
[7 empty] | 4281 | 81 | 5.5057 | 4.2125
[7 empty] | 4282 | 82 | 6.5775 | 5.0833
[7 empty] | 4283 | 83 | 7.3031 | 5.6728
[7 empty] | 4284 | 84 | 8.5233 | 6.6642
[7 empty] | 4285 | 85 | 8.2265 | 6.423
[7 empty] | 4286 | 86 | 7.7235 | 6.0144
[7 empty] | 4287 | 87 | 8.1605 | 6.3694
[7 empty] | 4288 | 88 | 8.8118 | 6.8986
[7 empty] | 4289 | 89 | 10.1392 | 7.9771
[7 empty] | 4290 | 90 | 9.5621 | 7.5082
[7 empty] | 4291 | 91 | 10.2382 | 8.0574
[7 empty] | 4292 | 92 | 9.6446 | 7.5751
[7 empty] | 4293 | 93 | 7.2701 | 5.646
[7 empty] | 4294 | 94 | 6.3797 | 4.9225
[7 empty] | 4295 | 95 | 4.5493 | 3.4355
[7 empty] | 4296 | 96 | 3.5765 | 2.6451
[7 empty] | 4297 | 97 | 3.527 | 2.6049
[7 empty] | 4298 | 98 | 3.2384 | 2.3704
[7 empty] | 4299 | 99 | 3.1807 | 2.3235
[7 empty] | 4300 | 100 | 2.8345 | 2.0422
[7 empty] | 4301 | 101 | 2.7767 | 1.9953
[7 empty] | 4302 | 102 | 3.0076 | 2.1829
[7 empty] | 4303 | 103 | 3.7414 | 2.779
[7 empty] | 4304 | 104 | 3.9887 | 2.98
[7 empty] | 4305 | 105 | 4.4669 | 3.3685
[7 empty] | 4306 | 106 | 5.9015 | 4.534
[7 empty] | 4307 | 107 | 6.2477 | 4.8154
[7 empty] | 4308 | 108 | 7.7977 | 6.0747
[7 empty] | 4309 | 109 | 7.1464 | 5.5455
[7 empty] | 4310 | 110 | 6.7012 | 5.1838
[7 empty] | 4311 | 111 | 6.5446 | 5.0565
[7 empty] | 4312 | 112 | 6.6105 | 5.1101
[7 empty] | 4313 | 113 | 6.2725 | 4.8355
[7 empty] | 4314 | 114 | 6.4374 | 4.9694
[7 empty] | 4315 | 115 | 5.9922 | 4.6077
[7 empty] | 4316 | 116 | 6.66 | 5.1503
[7 empty] | 4317 | 117 | 6.2477 | 4.8154
[7 empty] | 4318 | 118 | 5.4892 | 4.1991
[7 empty] | 4319 | 119 | 3.9227 | 2.9264
[7 empty] | 4320 | 120 | 3.6106 | 2.6728
[7 empty] | 4321 | 121 | 2.8922 | 2.0891
[7 empty] | 4322 | 122 | 2.4882 | 1.7609
[7 empty] | 4323 | 123 | 2.4057 | 1.6939
[7 empty] | 4324 | 124 | 2.3727 | 1.6671
[7 empty] | 4325 | 125 | 2.3315 | 1.6336
[7 empty] | 4326 | 126 | 2.4717 | 1.7475
[7 empty] | 4327 | 127 | 3.9557 | 2.9532
[7 empty] | 4328 | 128 | 5.4892 | 4.1991
[7 empty] | 4329 | 129 | 6.1571 | 4.7417
[7 empty] | 4330 | 130 | 6.5858 | 5.09
[7 empty] | 4331 | 131 | 6.7424 | 5.2173
[7 empty] | 4332 | 132 | 6.4951 | 5.0163
[7 empty] | 4333 | 133 | 7.1217 | 5.5254
[7 empty] | 4334 | 134 | 7.4185 | 5.7666
[7 empty] | 4335 | 135 | 7.4844 | 5.8201
[7 empty] | 4336 | 136 | 6.6847 | 5.1704
[7 empty] | 4337 | 137 | 6.5858 | 5.09
[7 empty] | 4338 | 138 | 6.5363 | 5.0498
[7 empty] | 4339 | 139 | 6.2065 | 4.7819
[7 empty] | 4340 | 140 | 6.2148 | 4.7886
[7 empty] | 4341 | 141 | 5.5717 | 4.2661
[7 empty] | 4342 | 142 | 4.9451 | 3.757
[7 empty] | 4343 | 143 | 4.0794 | 3.0537
[7 empty] | 4344 | 144 | 3.4775 | 2.5647
[7 empty] | 4345 | 145 | 3.0158 | 2.1896
[7 empty] | 4346 | 146 | 2.8097 | 2.0221
[7 empty] | 4347 | 147 | 2.7438 | 1.9685
[7 empty] | 4348 | 148 | 2.7355 | 1.9618
[7 empty] | 4349 | 149 | 2.7355 | 1.9618
[7 empty] | 4350 | 150 | 2.7438 | 1.9685
[7 empty] | 4351 | 151 | 3.8073 | 2.8326
[7 empty] | 4352 | 152 | 5.3079 | 4.0517
[7 empty] | 4353 | 153 | 5.9097 | 4.5407
[7 empty] | 4354 | 154 | 6.4621 | 4.9895
[7 empty] | 4355 | 155 | 6.3137 | 4.869
[7 empty] | 4356 | 156 | 6.4786 | 5.0029
[7 empty] | 4357 | 157 | 7.1794 | 5.5723
[7 empty] | 4358 | 158 | 7.5009 | 5.8335
[7 empty] | 4359 | 159 | 7.7648 | 6.0479
[7 empty] | 4360 | 160 | 7.6411 | 5.9474
[7 empty] | 4361 | 161 | 8.3914 | 6.557
[7 empty] | 4362 | 162 | 7.9049 | 6.1618
[7 empty] | 4363 | 163 | 8.2594 | 6.4498
[7 empty] | 4364 | 164 | 6.9321 | 5.3713
[7 empty] | 4365 | 165 | 10.0073 | 7.8699
[7 empty] | 4366 | 166 | 7.9956 | 6.2354
[7 empty] | 4367 | 167 | 4.4504 | 3.3551
[7 empty] | 4368 | 168 | 3.8156 | 2.8393
[7 empty] | 4369 | 1 | 2.381 | 1.6738
[7 empty] | 4370 | 2 | 2.2738 | 1.5867
[7 empty] | 4371 | 3 | 2.2656 | 1.58
[7 empty] | 4372 | 4 | 2.3975 | 1.6872
[7 empty] | 4373 | 5 | 2.414 | 1.7006
[7 empty] | 4374 | 6 | 2.8345 | 2.0422
[7 empty] | 4375 | 7 | 3.5435 | 2.6183
[7 empty] | 4376 | 8 | 4.2031 | 3.1541
[7 empty] | 4377 | 9 | 4.1783 | 3.134
[7 empty] | 4378 | 10 | 5.6706 | 4.3465
[7 empty] | 4379 | 11 | 7.7153 | 6.0077
[7 empty] | 4380 | 12 | 8.6634 | 6.778
[7 empty] | 4381 | 13 | 9.0344 | 7.0795
[7 empty] | 4382 | 14 | 8.8201 | 6.9053
[7 empty] | 4383 | 15 | 8.7294 | 6.8316
[7 empty] | 4384 | 16 | 9.8919 | 7.7761
[7 empty] | 4385 | 17 | 11.1946 | 8.8345
[7 empty] | 4386 | 18 | 10.9555 | 8.6402
[7 empty] | 4387 | 19 | 11.4749 | 9.0622
[7 empty] | 4388 | 20 | 11.4089 | 9.0086
[7 empty] | 4389 | 21 | 11.9696 | 9.4641
[7 empty] | 4390 | 22 | 8.0781 | 6.3024
[7 empty] | 4391 | 23 | 4.368 | 3.2881
[7 empty] | 4392 | 24 | 2.724 | 1.9525
[7 empty] | 4393 | 25 | 2.6283 | 1.8747
[7 empty] | 4394 | 26 | 2.5212 | 1.7877
[7 empty] | 4395 | 27 | 2.4222 | 1.7073
[7 empty] | 4396 | 28 | 2.5047 | 1.7743
[7 empty] | 4397 | 29 | 2.7438 | 1.9685
[7 empty] | 4398 | 30 | 2.9829 | 2.1628
[7 empty] | 4399 | 31 | 3.8156 | 2.8393
[7 empty] | 4400 | 32 | 4.1618 | 3.1207
[7 empty] | 4401 | 33 | 4.8132 | 3.6498
[7 empty] | 4402 | 34 | 5.6954 | 4.3666
[7 empty] | 4403 | 35 | 7.8307 | 6.1015
[7 empty] | 4404 | 36 | 8.8448 | 6.9254
[7 empty] | 4405 | 37 | 8.919 | 6.9857
[7 empty] | 4406 | 38 | 8.9932 | 7.046
[7 empty] | 4407 | 39 | 8.6717 | 6.7847
[7 empty] | 4408 | 40 | 9.7105 | 7.6287
[7 empty] | 4409 | 41 | 10.2547 | 8.0708
[7 empty] | 4410 | 42 | 10.2711 | 8.0842
[7 empty] | 4411 | 43 | 10.6339 | 8.379
[7 empty] | 4412 | 44 | 11.7717 | 9.3034
[7 empty] | 4413 | 45 | 11.3759 | 8.9818
[7 empty] | 4414 | 46 | 8.6717 | 6.7847
[7 empty] | 4415 | 47 | 5.1265 | 3.9044
[7 empty] | 4416 | 48 | 3.6507 | 2.7053
[7 empty] | 4417 | 49 | 2.9993 | 2.1762
[7 empty] | 4418 | 50 | 2.6943 | 1.9283
[7 empty] | 4419 | 51 | 2.5871 | 1.8412
[7 empty] | 4420 | 52 | 2.6201 | 1.868
[7 empty] | 4421 | 53 | 2.6448 | 1.8881
[7 empty] | 4422 | 54 | 3.2137 | 2.3503
[7 empty] | 4423 | 55 | 4.335 | 3.2613
[7 empty] | 4424 | 56 | 4.5741 | 3.4556
[7 empty] | 4425 | 57 | 5.5057 | 4.2125
[7 empty] | 4426 | 58 | 6.594 | 5.0967
[7 empty] | 4427 | 59 | 7.7813 | 6.0613
[7 empty] | 4428 | 60 | 8.3996 | 6.5637
[7 empty] | 4429 | 61 | 9.0674 | 7.1063
[7 empty] | 4430 | 62 | 8.8696 | 6.9455
[7 empty] | 4431 | 63 | 9.4549 | 7.4211
[7 empty] | 4432 | 64 | 10.3866 | 8.178
[7 empty] | 4433 | 65 | 10.9967 | 8.6737
[7 empty] | 4434 | 66 | 10.8977 | 8.5933
[7 empty] | 4435 | 67 | 11.6233 | 9.1828
[7 empty] | 4436 | 68 | 11.8624 | 9.377
[7 empty] | 4437 | 69 | 11.3594 | 8.9684
[7 empty] | 4438 | 70 | 9.1004 | 7.133
[7 empty] | 4439 | 71 | 4.6565 | 3.5226
[7 empty] | 4440 | 72 | 3.5894 | 2.6556
[7 empty] | 4441 | 73 | 2.8839 | 2.0824
[7 empty] | 4442 | 74 | 2.6613 | 1.9015
[7 empty] | 4443 | 75 | 2.5624 | 1.8211
[7 empty] | 4444 | 76 | 2.5047 | 1.7743
[7 empty] | 4445 | 77 | 2.6778 | 1.9149
[7 empty] | 4446 | 78 | 3.0735 | 2.2365
[7 empty] | 4447 | 79 | 4.1701 | 3.1274
[7 empty] | 4448 | 80 | 4.3432 | 3.268
[7 empty] | 4449 | 81 | 5.5057 | 4.2125
[7 empty] | 4450 | 82 | 6.5775 | 5.0833
[7 empty] | 4451 | 83 | 7.3031 | 5.6728
[7 empty] | 4452 | 84 | 8.5233 | 6.6642
[7 empty] | 4453 | 85 | 8.2265 | 6.423
[7 empty] | 4454 | 86 | 7.7235 | 6.0144
[7 empty] | 4455 | 87 | 8.1605 | 6.3694
[7 empty] | 4456 | 88 | 8.8118 | 6.8986
[7 empty] | 4457 | 89 | 10.1392 | 7.9771
[7 empty] | 4458 | 90 | 9.5621 | 7.5082
[7 empty] | 4459 | 91 | 10.2382 | 8.0574
[7 empty] | 4460 | 92 | 9.6446 | 7.5751
[7 empty] | 4461 | 93 | 7.2701 | 5.646
[7 empty] | 4462 | 94 | 6.3797 | 4.9225
[7 empty] | 4463 | 95 | 4.5493 | 3.4355
[7 empty] | 4464 | 96 | 3.5765 | 2.6451
[7 empty] | 4465 | 97 | 3.527 | 2.6049
[7 empty] | 4466 | 98 | 3.2384 | 2.3704
[7 empty] | 4467 | 99 | 3.1807 | 2.3235
[7 empty] | 4468 | 100 | 2.8345 | 2.0422
[7 empty] | 4469 | 101 | 2.7767 | 1.9953
[7 empty] | 4470 | 102 | 3.0076 | 2.1829
[7 empty] | 4471 | 103 | 3.7414 | 2.779
[7 empty] | 4472 | 104 | 3.9887 | 2.98
[7 empty] | 4473 | 105 | 4.4669 | 3.3685
[7 empty] | 4474 | 106 | 5.9015 | 4.534
[7 empty] | 4475 | 107 | 6.2477 | 4.8154
[7 empty] | 4476 | 108 | 7.7977 | 6.0747
[7 empty] | 4477 | 109 | 7.1464 | 5.5455
[7 empty] | 4478 | 110 | 6.7012 | 5.1838
[7 empty] | 4479 | 111 | 6.5446 | 5.0565
[7 empty] | 4480 | 112 | 6.6105 | 5.1101
[7 empty] | 4481 | 113 | 6.2725 | 4.8355
[7 empty] | 4482 | 114 | 6.4374 | 4.9694
[7 empty] | 4483 | 115 | 5.9922 | 4.6077
[7 empty] | 4484 | 116 | 6.66 | 5.1503
[7 empty] | 4485 | 117 | 6.2477 | 4.8154
[7 empty] | 4486 | 118 | 5.4892 | 4.1991
[7 empty] | 4487 | 119 | 3.9227 | 2.9264
[7 empty] | 4488 | 120 | 3.6106 | 2.6728
[7 empty] | 4489 | 121 | 2.8922 | 2.0891
[7 empty] | 4490 | 122 | 2.4882 | 1.7609
[7 empty] | 4491 | 123 | 2.4057 | 1.6939
[7 empty] | 4492 | 124 | 2.3727 | 1.6671
[7 empty] | 4493 | 125 | 2.3315 | 1.6336
[7 empty] | 4494 | 126 | 2.4717 | 1.7475
[7 empty] | 4495 | 127 | 3.9557 | 2.9532
[7 empty] | 4496 | 128 | 5.4892 | 4.1991
[7 empty] | 4497 | 129 | 6.1571 | 4.7417
[7 empty] | 4498 | 130 | 6.5858 | 5.09
[7 empty] | 4499 | 131 | 6.7424 | 5.2173
[7 empty] | 4500 | 132 | 6.4951 | 5.0163
[7 empty] | 4501 | 133 | 7.1217 | 5.5254
[7 empty] | 4502 | 134 | 7.4185 | 5.7666
[7 empty] | 4503 | 135 | 7.4844 | 5.8201
[7 empty] | 4504 | 136 | 6.6847 | 5.1704
[7 empty] | 4505 | 137 | 6.5858 | 5.09
[7 empty] | 4506 | 138 | 6.5363 | 5.0498
[7 empty] | 4507 | 139 | 6.2065 | 4.7819
[7 empty] | 4508 | 140 | 6.2148 | 4.7886
[7 empty] | 4509 | 141 | 5.5717 | 4.2661
[7 empty] | 4510 | 142 | 4.9451 | 3.757
[7 empty] | 4511 | 143 | 4.0794 | 3.0537
[7 empty] | 4512 | 144 | 3.4775 | 2.5647
[7 empty] | 4513 | 145 | 3.0158 | 2.1896
[7 empty] | 4514 | 146 | 2.8097 | 2.0221
[7 empty] | 4515 | 147 | 2.7438 | 1.9685
[7 empty] | 4516 | 148 | 2.7355 | 1.9618
[7 empty] | 4517 | 149 | 2.7355 | 1.9618
[7 empty] | 4518 | 150 | 2.7438 | 1.9685
[7 empty] | 4519 | 151 | 3.8073 | 2.8326
[7 empty] | 4520 | 152 | 5.3079 | 4.0517
[7 empty] | 4521 | 153 | 5.9097 | 4.5407
[7 empty] | 4522 | 154 | 6.4621 | 4.9895
[7 empty] | 4523 | 155 | 6.3137 | 4.869
[7 empty] | 4524 | 156 | 6.4786 | 5.0029
[7 empty] | 4525 | 157 | 7.1794 | 5.5723
[7 empty] | 4526 | 158 | 7.5009 | 5.8335
[7 empty] | 4527 | 159 | 7.7648 | 6.0479
[7 empty] | 4528 | 160 | 7.6411 | 5.9474
[7 empty] | 4529 | 161 | 8.3914 | 6.557
[7 empty] | 4530 | 162 | 7.9049 | 6.1618
[7 empty] | 4531 | 163 | 8.2594 | 6.4498
[7 empty] | 4532 | 164 | 6.9321 | 5.3713
[7 empty] | 4533 | 165 | 10.0073 | 7.8699
[7 empty] | 4534 | 166 | 7.9956 | 6.2354
[7 empty] | 4535 | 167 | 4.4504 | 3.3551
[7 empty] | 4536 | 168 | 3.8156 | 2.8393
[7 empty] | 4537 | 1 | 2.381 | 1.6738
[7 empty] | 4538 | 2 | 2.2738 | 1.5867
[7 empty] | 4539 | 3 | 2.2656 | 1.58
[7 empty] | 4540 | 4 | 2.3975 | 1.6872
[7 empty] | 4541 | 5 | 2.414 | 1.7006
[7 empty] | 4542 | 6 | 2.8345 | 2.0422
[7 empty] | 4543 | 7 | 3.5435 | 2.6183
[7 empty] | 4544 | 8 | 4.2031 | 3.1541
[7 empty] | 4545 | 9 | 4.1783 | 3.134
[7 empty] | 4546 | 10 | 5.6706 | 4.3465
[7 empty] | 4547 | 11 | 7.7153 | 6.0077
[7 empty] | 4548 | 12 | 8.6634 | 6.778
[7 empty] | 4549 | 13 | 9.0344 | 7.0795
[7 empty] | 4550 | 14 | 8.8201 | 6.9053
[7 empty] | 4551 | 15 | 8.7294 | 6.8316
[7 empty] | 4552 | 16 | 9.8919 | 7.7761
[7 empty] | 4553 | 17 | 11.1946 | 8.8345
[7 empty] | 4554 | 18 | 10.9555 | 8.6402
[7 empty] | 4555 | 19 | 11.4749 | 9.0622
[7 empty] | 4556 | 20 | 11.4089 | 9.0086
[7 empty] | 4557 | 21 | 11.9696 | 9.4641
[7 empty] | 4558 | 22 | 8.0781 | 6.3024
[7 empty] | 4559 | 23 | 4.368 | 3.2881
[7 empty] | 4560 | 24 | 2.724 | 1.9525
[7 empty] | 4561 | 25 | 2.6283 | 1.8747
[7 empty] | 4562 | 26 | 2.5212 | 1.7877
[7 empty] | 4563 | 27 | 2.4222 | 1.7073
[7 empty] | 4564 | 28 | 2.5047 | 1.7743
[7 empty] | 4565 | 29 | 2.7438 | 1.9685
[7 empty] | 4566 | 30 | 2.9829 | 2.1628
[7 empty] | 4567 | 31 | 3.8156 | 2.8393
[7 empty] | 4568 | 32 | 4.1618 | 3.1207
[7 empty] | 4569 | 33 | 4.8132 | 3.6498
[7 empty] | 4570 | 34 | 5.6954 | 4.3666
[7 empty] | 4571 | 35 | 7.8307 | 6.1015
[7 empty] | 4572 | 36 | 8.8448 | 6.9254
[7 empty] | 4573 | 37 | 8.919 | 6.9857
[7 empty] | 4574 | 38 | 8.9932 | 7.046
[7 empty] | 4575 | 39 | 8.6717 | 6.7847
[7 empty] | 4576 | 40 | 9.7105 | 7.6287
[7 empty] | 4577 | 41 | 10.2547 | 8.0708
[7 empty] | 4578 | 42 | 10.2711 | 8.0842
[7 empty] | 4579 | 43 | 10.6339 | 8.379
[7 empty] | 4580 | 44 | 11.7717 | 9.3034
[7 empty] | 4581 | 45 | 11.3759 | 8.9818
[7 empty] | 4582 | 46 | 8.6717 | 6.7847
[7 empty] | 4583 | 47 | 5.1265 | 3.9044
[7 empty] | 4584 | 48 | 3.6507 | 2.7053
[7 empty] | 4585 | 49 | 2.9993 | 2.1762
[7 empty] | 4586 | 50 | 2.6943 | 1.9283
[7 empty] | 4587 | 51 | 2.5871 | 1.8412
[7 empty] | 4588 | 52 | 2.6201 | 1.868
[7 empty] | 4589 | 53 | 2.6448 | 1.8881
[7 empty] | 4590 | 54 | 3.2137 | 2.3503
[7 empty] | 4591 | 55 | 4.335 | 3.2613
[7 empty] | 4592 | 56 | 4.5741 | 3.4556
[7 empty] | 4593 | 57 | 5.5057 | 4.2125
[7 empty] | 4594 | 58 | 6.594 | 5.0967
[7 empty] | 4595 | 59 | 7.7813 | 6.0613
[7 empty] | 4596 | 60 | 8.3996 | 6.5637
[7 empty] | 4597 | 61 | 9.0674 | 7.1063
[7 empty] | 4598 | 62 | 8.8696 | 6.9455
[7 empty] | 4599 | 63 | 9.4549 | 7.4211
[7 empty] | 4600 | 64 | 10.3866 | 8.178
[7 empty] | 4601 | 65 | 10.9967 | 8.6737
[7 empty] | 4602 | 66 | 10.8977 | 8.5933
[7 empty] | 4603 | 67 | 11.6233 | 9.1828
[7 empty] | 4604 | 68 | 11.8624 | 9.377
[7 empty] | 4605 | 69 | 11.3594 | 8.9684
[7 empty] | 4606 | 70 | 9.1004 | 7.133
[7 empty] | 4607 | 71 | 4.6565 | 3.5226
[7 empty] | 4608 | 72 | 3.5894 | 2.6556
[7 empty] | 4609 | 73 | 2.8839 | 2.0824
[7 empty] | 4610 | 74 | 2.6613 | 1.9015
[7 empty] | 4611 | 75 | 2.5624 | 1.8211
[7 empty] | 4612 | 76 | 2.5047 | 1.7743
[7 empty] | 4613 | 77 | 2.6778 | 1.9149
[7 empty] | 4614 | 78 | 3.0735 | 2.2365
[7 empty] | 4615 | 79 | 4.1701 | 3.1274
[7 empty] | 4616 | 80 | 4.3432 | 3.268
[7 empty] | 4617 | 81 | 5.5057 | 4.2125
[7 empty] | 4618 | 82 | 6.5775 | 5.0833
[7 empty] | 4619 | 83 | 7.3031 | 5.6728
[7 empty] | 4620 | 84 | 8.5233 | 6.6642
[7 empty] | 4621 | 85 | 8.2265 | 6.423
[7 empty] | 4622 | 86 | 7.7235 | 6.0144
[7 empty] | 4623 | 87 | 8.1605 | 6.3694
[7 empty] | 4624 | 88 | 8.8118 | 6.8986
[7 empty] | 4625 | 89 | 10.1392 | 7.9771
[7 empty] | 4626 | 90 | 9.5621 | 7.5082
[7 empty] | 4627 | 91 | 10.2382 | 8.0574
[7 empty] | 4628 | 92 | 9.6446 | 7.5751
[7 empty] | 4629 | 93 | 7.2701 | 5.646
[7 empty] | 4630 | 94 | 6.3797 | 4.9225
[7 empty] | 4631 | 95 | 4.5493 | 3.4355
[7 empty] | 4632 | 96 | 3.5765 | 2.6451
[7 empty] | 4633 | 97 | 3.527 | 2.6049
[7 empty] | 4634 | 98 | 3.2384 | 2.3704
[7 empty] | 4635 | 99 | 3.1807 | 2.3235
[7 empty] | 4636 | 100 | 2.8345 | 2.0422
[7 empty] | 4637 | 101 | 2.7767 | 1.9953
[7 empty] | 4638 | 102 | 3.0076 | 2.1829
[7 empty] | 4639 | 103 | 3.7414 | 2.779
[7 empty] | 4640 | 104 | 3.9887 | 2.98
[7 empty] | 4641 | 105 | 4.4669 | 3.3685
[7 empty] | 4642 | 106 | 5.9015 | 4.534
[7 empty] | 4643 | 107 | 6.2477 | 4.8154
[7 empty] | 4644 | 108 | 7.7977 | 6.0747
[7 empty] | 4645 | 109 | 7.1464 | 5.5455
[7 empty] | 4646 | 110 | 6.7012 | 5.1838
[7 empty] | 4647 | 111 | 6.5446 | 5.0565
[7 empty] | 4648 | 112 | 6.6105 | 5.1101
[7 empty] | 4649 | 113 | 6.2725 | 4.8355
[7 empty] | 4650 | 114 | 6.4374 | 4.9694
[7 empty] | 4651 | 115 | 5.9922 | 4.6077
[7 empty] | 4652 | 116 | 6.66 | 5.1503
[7 empty] | 4653 | 117 | 6.2477 | 4.8154
[7 empty] | 4654 | 118 | 5.4892 | 4.1991
[7 empty] | 4655 | 119 | 3.9227 | 2.9264
[7 empty] | 4656 | 120 | 3.6106 | 2.6728
[7 empty] | 4657 | 121 | 2.8922 | 2.0891
[7 empty] | 4658 | 122 | 2.4882 | 1.7609
[7 empty] | 4659 | 123 | 2.4057 | 1.6939
[7 empty] | 4660 | 124 | 2.3727 | 1.6671
[7 empty] | 4661 | 125 | 2.3315 | 1.6336
[7 empty] | 4662 | 126 | 2.4717 | 1.7475
[7 empty] | 4663 | 127 | 3.9557 | 2.9532
[7 empty] | 4664 | 128 | 5.4892 | 4.1991
[7 empty] | 4665 | 129 | 6.1571 | 4.7417
[7 empty] | 4666 | 130 | 6.5858 | 5.09
[7 empty] | 4667 | 131 | 6.7424 | 5.2173
[7 empty] | 4668 | 132 | 6.4951 | 5.0163
[7 empty] | 4669 | 133 | 7.1217 | 5.5254
[7 empty] | 4670 | 134 | 7.4185 | 5.7666
[7 empty] | 4671 | 135 | 7.4844 | 5.8201
[7 empty] | 4672 | 136 | 6.6847 | 5.1704
[7 empty] | 4673 | 137 | 6.5858 | 5.09
[7 empty] | 4674 | 138 | 6.5363 | 5.0498
[7 empty] | 4675 | 139 | 6.2065 | 4.7819
[7 empty] | 4676 | 140 | 6.2148 | 4.7886
[7 empty] | 4677 | 141 | 5.5717 | 4.2661
[7 empty] | 4678 | 142 | 4.9451 | 3.757
[7 empty] | 4679 | 143 | 4.0794 | 3.0537
[7 empty] | 4680 | 144 | 3.4775 | 2.5647
[7 empty] | 4681 | 145 | 3.0158 | 2.1896
[7 empty] | 4682 | 146 | 2.8097 | 2.0221
[7 empty] | 4683 | 147 | 2.7438 | 1.9685
[7 empty] | 4684 | 148 | 2.7355 | 1.9618
[7 empty] | 4685 | 149 | 2.7355 | 1.9618
[7 empty] | 4686 | 150 | 2.7438 | 1.9685
[7 empty] | 4687 | 151 | 3.8073 | 2.8326
[7 empty] | 4688 | 152 | 5.3079 | 4.0517
[7 empty] | 4689 | 153 | 5.9097 | 4.5407
[7 empty] | 4690 | 154 | 6.4621 | 4.9895
[7 empty] | 4691 | 155 | 6.3137 | 4.869
[7 empty] | 4692 | 156 | 6.4786 | 5.0029
[7 empty] | 4693 | 157 | 7.1794 | 5.5723
[7 empty] | 4694 | 158 | 7.5009 | 5.8335
[7 empty] | 4695 | 159 | 7.7648 | 6.0479
[7 empty] | 4696 | 160 | 7.6411 | 5.9474
[7 empty] | 4697 | 161 | 8.3914 | 6.557
[7 empty] | 4698 | 162 | 7.9049 | 6.1618
[7 empty] | 4699 | 163 | 8.2594 | 6.4498
[7 empty] | 4700 | 164 | 6.9321 | 5.3713
[7 empty] | 4701 | 165 | 10.0073 | 7.8699
[7 empty] | 4702 | 166 | 7.9956 | 6.2354
[7 empty] | 4703 | 167 | 4.4504 | 3.3551
[7 empty] | 4704 | 168 | 3.8156 | 2.8393
[7 empty] | 4705 | 1 | 2.381 | 1.6738
[7 empty] | 4706 | 2 | 2.2738 | 1.5867
[7 empty] | 4707 | 3 | 2.2656 | 1.58
[7 empty] | 4708 | 4 | 2.3975 | 1.6872
[7 empty] | 4709 | 5 | 2.414 | 1.7006
[7 empty] | 4710 | 6 | 2.8345 | 2.0422
[7 empty] | 4711 | 7 | 3.5435 | 2.6183
[7 empty] | 4712 | 8 | 4.2031 | 3.1541
[7 empty] | 4713 | 9 | 4.1783 | 3.134
[7 empty] | 4714 | 10 | 5.6706 | 4.3465
[7 empty] | 4715 | 11 | 7.7153 | 6.0077
[7 empty] | 4716 | 12 | 8.6634 | 6.778
[7 empty] | 4717 | 13 | 9.0344 | 7.0795
[7 empty] | 4718 | 14 | 8.8201 | 6.9053
[7 empty] | 4719 | 15 | 8.7294 | 6.8316
[7 empty] | 4720 | 16 | 9.8919 | 7.7761
[7 empty] | 4721 | 17 | 11.1946 | 8.8345
[7 empty] | 4722 | 18 | 10.9555 | 8.6402
[7 empty] | 4723 | 19 | 11.4749 | 9.0622
[7 empty] | 4724 | 20 | 11.4089 | 9.0086
[7 empty] | 4725 | 21 | 11.9696 | 9.4641
[7 empty] | 4726 | 22 | 8.0781 | 6.3024
[7 empty] | 4727 | 23 | 4.368 | 3.2881
[7 empty] | 4728 | 24 | 2.724 | 1.9525
[7 empty] | 4729 | 25 | 2.6283 | 1.8747
[7 empty] | 4730 | 26 | 2.5212 | 1.7877
[7 empty] | 4731 | 27 | 2.4222 | 1.7073
[7 empty] | 4732 | 28 | 2.5047 | 1.7743
[7 empty] | 4733 | 29 | 2.7438 | 1.9685
[7 empty] | 4734 | 30 | 2.9829 | 2.1628
[7 empty] | 4735 | 31 | 3.8156 | 2.8393
[7 empty] | 4736 | 32 | 4.1618 | 3.1207
[7 empty] | 4737 | 33 | 4.8132 | 3.6498
[7 empty] | 4738 | 34 | 5.6954 | 4.3666
[7 empty] | 4739 | 35 | 7.8307 | 6.1015
[7 empty] | 4740 | 36 | 8.8448 | 6.9254
[7 empty] | 4741 | 37 | 8.919 | 6.9857
[7 empty] | 4742 | 38 | 8.9932 | 7.046
[7 empty] | 4743 | 39 | 8.6717 | 6.7847
[7 empty] | 4744 | 40 | 9.7105 | 7.6287
[7 empty] | 4745 | 41 | 10.2547 | 8.0708
[7 empty] | 4746 | 42 | 10.2711 | 8.0842
[7 empty] | 4747 | 43 | 10.6339 | 8.379
[7 empty] | 4748 | 44 | 11.7717 | 9.3034
[7 empty] | 4749 | 45 | 11.3759 | 8.9818
[7 empty] | 4750 | 46 | 8.6717 | 6.7847
[7 empty] | 4751 | 47 | 5.1265 | 3.9044
[7 empty] | 4752 | 48 | 3.6507 | 2.7053
[7 empty] | 4753 | 49 | 2.9993 | 2.1762
[7 empty] | 4754 | 50 | 2.6943 | 1.9283
[7 empty] | 4755 | 51 | 2.5871 | 1.8412
[7 empty] | 4756 | 52 | 2.6201 | 1.868
[7 empty] | 4757 | 53 | 2.6448 | 1.8881
[7 empty] | 4758 | 54 | 3.2137 | 2.3503
[7 empty] | 4759 | 55 | 4.335 | 3.2613
[7 empty] | 4760 | 56 | 4.5741 | 3.4556
[7 empty] | 4761 | 57 | 5.5057 | 4.2125
[7 empty] | 4762 | 58 | 6.594 | 5.0967
[7 empty] | 4763 | 59 | 7.7813 | 6.0613
[7 empty] | 4764 | 60 | 8.3996 | 6.5637
[7 empty] | 4765 | 61 | 9.0674 | 7.1063
[7 empty] | 4766 | 62 | 8.8696 | 6.9455
[7 empty] | 4767 | 63 | 9.4549 | 7.4211
[7 empty] | 4768 | 64 | 10.3866 | 8.178
[7 empty] | 4769 | 65 | 10.9967 | 8.6737
[7 empty] | 4770 | 66 | 10.8977 | 8.5933
[7 empty] | 4771 | 67 | 11.6233 | 9.1828
[7 empty] | 4772 | 68 | 11.8624 | 9.377
[7 empty] | 4773 | 69 | 11.3594 | 8.9684
[7 empty] | 4774 | 70 | 9.1004 | 7.133
[7 empty] | 4775 | 71 | 4.6565 | 3.5226
[7 empty] | 4776 | 72 | 3.5894 | 2.6556
[7 empty] | 4777 | 73 | 2.8839 | 2.0824
[7 empty] | 4778 | 74 | 2.6613 | 1.9015
[7 empty] | 4779 | 75 | 2.5624 | 1.8211
[7 empty] | 4780 | 76 | 2.5047 | 1.7743
[7 empty] | 4781 | 77 | 2.6778 | 1.9149
[7 empty] | 4782 | 78 | 3.0735 | 2.2365
[7 empty] | 4783 | 79 | 4.1701 | 3.1274
[7 empty] | 4784 | 80 | 4.3432 | 3.268
[7 empty] | 4785 | 81 | 5.5057 | 4.2125
[7 empty] | 4786 | 82 | 6.5775 | 5.0833
[7 empty] | 4787 | 83 | 7.3031 | 5.6728
[7 empty] | 4788 | 84 | 8.5233 | 6.6642
[7 empty] | 4789 | 85 | 8.2265 | 6.423
[7 empty] | 4790 | 86 | 7.7235 | 6.0144
[7 empty] | 4791 | 87 | 8.1605 | 6.3694
[7 empty] | 4792 | 88 | 8.8118 | 6.8986
[7 empty] | 4793 | 89 | 10.1392 | 7.9771
[7 empty] | 4794 | 90 | 9.5621 | 7.5082
[7 empty] | 4795 | 91 | 10.2382 | 8.0574
[7 empty] | 4796 | 92 | 9.6446 | 7.5751
[7 empty] | 4797 | 93 | 7.2701 | 5.646
[7 empty] | 4798 | 94 | 6.3797 | 4.9225
[7 empty] | 4799 | 95 | 4.5493 | 3.4355
[7 empty] | 4800 | 96 | 3.5765 | 2.6451
[7 empty] | 4801 | 97 | 3.527 | 2.6049
[7 empty] | 4802 | 98 | 3.2384 | 2.3704
[7 empty] | 4803 | 99 | 3.1807 | 2.3235
[7 empty] | 4804 | 100 | 2.8345 | 2.0422
[7 empty] | 4805 | 101 | 2.7767 | 1.9953
[7 empty] | 4806 | 102 | 3.0076 | 2.1829
[7 empty] | 4807 | 103 | 3.7414 | 2.779
[7 empty] | 4808 | 104 | 3.9887 | 2.98
[7 empty] | 4809 | 105 | 4.4669 | 3.3685
[7 empty] | 4810 | 106 | 5.9015 | 4.534
[7 empty] | 4811 | 107 | 6.2477 | 4.8154
[7 empty] | 4812 | 108 | 7.7977 | 6.0747
[7 empty] | 4813 | 109 | 7.1464 | 5.5455
[7 empty] | 4814 | 110 | 6.7012 | 5.1838
[7 empty] | 4815 | 111 | 6.5446 | 5.0565
[7 empty] | 4816 | 112 | 6.6105 | 5.1101
[7 empty] | 4817 | 113 | 6.2725 | 4.8355
[7 empty] | 4818 | 114 | 6.4374 | 4.9694
[7 empty] | 4819 | 115 | 5.9922 | 4.6077
[7 empty] | 4820 | 116 | 6.66 | 5.1503
[7 empty] | 4821 | 117 | 6.2477 | 4.8154
[7 empty] | 4822 | 118 | 5.4892 | 4.1991
[7 empty] | 4823 | 119 | 3.9227 | 2.9264
[7 empty] | 4824 | 120 | 3.6106 | 2.6728
[7 empty] | 4825 | 121 | 2.8922 | 2.0891
[7 empty] | 4826 | 122 | 2.4882 | 1.7609
[7 empty] | 4827 | 123 | 2.4057 | 1.6939
[7 empty] | 4828 | 124 | 2.3727 | 1.6671
[7 empty] | 4829 | 125 | 2.3315 | 1.6336
[7 empty] | 4830 | 126 | 2.4717 | 1.7475
[7 empty] | 4831 | 127 | 3.9557 | 2.9532
[7 empty] | 4832 | 128 | 5.4892 | 4.1991
[7 empty] | 4833 | 129 | 6.1571 | 4.7417
[7 empty] | 4834 | 130 | 6.5858 | 5.09
[7 empty] | 4835 | 131 | 6.7424 | 5.2173
[7 empty] | 4836 | 132 | 6.4951 | 5.0163
[7 empty] | 4837 | 133 | 7.1217 | 5.5254
[7 empty] | 4838 | 134 | 7.4185 | 5.7666
[7 empty] | 4839 | 135 | 7.4844 | 5.8201
[7 empty] | 4840 | 136 | 6.6847 | 5.1704
[7 empty] | 4841 | 137 | 6.5858 | 5.09
[7 empty] | 4842 | 138 | 6.5363 | 5.0498
[7 empty] | 4843 | 139 | 6.2065 | 4.7819
[7 empty] | 4844 | 140 | 6.2148 | 4.7886
[7 empty] | 4845 | 141 | 5.5717 | 4.2661
[7 empty] | 4846 | 142 | 4.9451 | 3.757
[7 empty] | 4847 | 143 | 4.0794 | 3.0537
[7 empty] | 4848 | 144 | 3.4775 | 2.5647
[7 empty] | 4849 | 145 | 3.0158 | 2.1896
[7 empty] | 4850 | 146 | 2.8097 | 2.0221
[7 empty] | 4851 | 147 | 2.7438 | 1.9685
[7 empty] | 4852 | 148 | 2.7355 | 1.9618
[7 empty] | 4853 | 149 | 2.7355 | 1.9618
[7 empty] | 4854 | 150 | 2.7438 | 1.9685
[7 empty] | 4855 | 151 | 3.8073 | 2.8326
[7 empty] | 4856 | 152 | 5.3079 | 4.0517
[7 empty] | 4857 | 153 | 5.9097 | 4.5407
[7 empty] | 4858 | 154 | 6.4621 | 4.9895
[7 empty] | 4859 | 155 | 6.3137 | 4.869
[7 empty] | 4860 | 156 | 6.4786 | 5.0029
[7 empty] | 4861 | 157 | 7.1794 | 5.5723
[7 empty] | 4862 | 158 | 7.5009 | 5.8335
[7 empty] | 4863 | 159 | 7.7648 | 6.0479
[7 empty] | 4864 | 160 | 7.6411 | 5.9474
[7 empty] | 4865 | 161 | 8.3914 | 6.557
[7 empty] | 4866 | 162 | 7.9049 | 6.1618
[7 empty] | 4867 | 163 | 8.2594 | 6.4498
[7 empty] | 4868 | 164 | 6.9321 | 5.3713
[7 empty] | 4869 | 165 | 10.0073 | 7.8699
[7 empty] | 4870 | 166 | 7.9956 | 6.2354
[7 empty] | 4871 | 167 | 4.4504 | 3.3551
[7 empty] | 4872 | 168 | 3.8156 | 2.8393
[7 empty] | 4873 | 1 | 2.381 | 1.6738
[7 empty] | 4874 | 2 | 2.2738 | 1.5867
[7 empty] | 4875 | 3 | 2.2656 | 1.58
[7 empty] | 4876 | 4 | 2.3975 | 1.6872
[7 empty] | 4877 | 5 | 2.414 | 1.7006
[7 empty] | 4878 | 6 | 2.8345 | 2.0422
[7 empty] | 4879 | 7 | 3.5435 | 2.6183
[7 empty] | 4880 | 8 | 4.2031 | 3.1541
[7 empty] | 4881 | 9 | 4.1783 | 3.134
[7 empty] | 4882 | 10 | 5.6706 | 4.3465
[7 empty] | 4883 | 11 | 7.7153 | 6.0077
[7 empty] | 4884 | 12 | 8.6634 | 6.778
[7 empty] | 4885 | 13 | 9.0344 | 7.0795
[7 empty] | 4886 | 14 | 8.8201 | 6.9053
[7 empty] | 4887 | 15 | 8.7294 | 6.8316
[7 empty] | 4888 | 16 | 9.8919 | 7.7761
[7 empty] | 4889 | 17 | 11.1946 | 8.8345
[7 empty] | 4890 | 18 | 10.9555 | 8.6402
[7 empty] | 4891 | 19 | 11.4749 | 9.0622
[7 empty] | 4892 | 20 | 11.4089 | 9.0086
[7 empty] | 4893 | 21 | 11.9696 | 9.4641
[7 empty] | 4894 | 22 | 8.0781 | 6.3024
[7 empty] | 4895 | 23 | 4.368 | 3.2881
[7 empty] | 4896 | 24 | 2.724 | 1.9525
[7 empty] | 4897 | 25 | 2.6283 | 1.8747
[7 empty] | 4898 | 26 | 2.5212 | 1.7877
[7 empty] | 4899 | 27 | 2.4222 | 1.7073
[7 empty] | 4900 | 28 | 2.5047 | 1.7743
[7 empty] | 4901 | 29 | 2.7438 | 1.9685
[7 empty] | 4902 | 30 | 2.9829 | 2.1628
[7 empty] | 4903 | 31 | 3.8156 | 2.8393
[7 empty] | 4904 | 32 | 4.1618 | 3.1207
[7 empty] | 4905 | 33 | 4.8132 | 3.6498
[7 empty] | 4906 | 34 | 5.6954 | 4.3666
[7 empty] | 4907 | 35 | 7.8307 | 6.1015
[7 empty] | 4908 | 36 | 8.8448 | 6.9254
[7 empty] | 4909 | 37 | 8.919 | 6.9857
[7 empty] | 4910 | 38 | 8.9932 | 7.046
[7 empty] | 4911 | 39 | 8.6717 | 6.7847
[7 empty] | 4912 | 40 | 9.7105 | 7.6287
[7 empty] | 4913 | 41 | 10.2547 | 8.0708
[7 empty] | 4914 | 42 | 10.2711 | 8.0842
[7 empty] | 4915 | 43 | 10.6339 | 8.379
[7 empty] | 4916 | 44 | 11.7717 | 9.3034
[7 empty] | 4917 | 45 | 11.3759 | 8.9818
[7 empty] | 4918 | 46 | 8.6717 | 6.7847
[7 empty] | 4919 | 47 | 5.1265 | 3.9044
[7 empty] | 4920 | 48 | 3.6507 | 2.7053
[7 empty] | 4921 | 49 | 2.9993 | 2.1762
[7 empty] | 4922 | 50 | 2.6943 | 1.9283
[7 empty] | 4923 | 51 | 2.5871 | 1.8412
[7 empty] | 4924 | 52 | 2.6201 | 1.868
[7 empty] | 4925 | 53 | 2.6448 | 1.8881
[7 empty] | 4926 | 54 | 3.2137 | 2.3503
[7 empty] | 4927 | 55 | 4.335 | 3.2613
[7 empty] | 4928 | 56 | 4.5741 | 3.4556
[7 empty] | 4929 | 57 | 5.5057 | 4.2125
[7 empty] | 4930 | 58 | 6.594 | 5.0967
[7 empty] | 4931 | 59 | 7.7813 | 6.0613
[7 empty] | 4932 | 60 | 8.3996 | 6.5637
[7 empty] | 4933 | 61 | 9.0674 | 7.1063
[7 empty] | 4934 | 62 | 8.8696 | 6.9455
[7 empty] | 4935 | 63 | 9.4549 | 7.4211
[7 empty] | 4936 | 64 | 10.3866 | 8.178
[7 empty] | 4937 | 65 | 10.9967 | 8.6737
[7 empty] | 4938 | 66 | 10.8977 | 8.5933
[7 empty] | 4939 | 67 | 11.6233 | 9.1828
[7 empty] | 4940 | 68 | 11.8624 | 9.377
[7 empty] | 4941 | 69 | 11.3594 | 8.9684
[7 empty] | 4942 | 70 | 9.1004 | 7.133
[7 empty] | 4943 | 71 | 4.6565 | 3.5226
[7 empty] | 4944 | 72 | 3.5894 | 2.6556
[7 empty] | 4945 | 73 | 2.8839 | 2.0824
[7 empty] | 4946 | 74 | 2.6613 | 1.9015
[7 empty] | 4947 | 75 | 2.5624 | 1.8211
[7 empty] | 4948 | 76 | 2.5047 | 1.7743
[7 empty] | 4949 | 77 | 2.6778 | 1.9149
[7 empty] | 4950 | 78 | 3.0735 | 2.2365
[7 empty] | 4951 | 79 | 4.1701 | 3.1274
[7 empty] | 4952 | 80 | 4.3432 | 3.268
[7 empty] | 4953 | 81 | 5.5057 | 4.2125
[7 empty] | 4954 | 82 | 6.5775 | 5.0833
[7 empty] | 4955 | 83 | 7.3031 | 5.6728
[7 empty] | 4956 | 84 | 8.5233 | 6.6642
[7 empty] | 4957 | 85 | 8.2265 | 6.423
[7 empty] | 4958 | 86 | 7.7235 | 6.0144
[7 empty] | 4959 | 87 | 8.1605 | 6.3694
[7 empty] | 4960 | 88 | 8.8118 | 6.8986
[7 empty] | 4961 | 89 | 10.1392 | 7.9771
[7 empty] | 4962 | 90 | 9.5621 | 7.5082
[7 empty] | 4963 | 91 | 10.2382 | 8.0574
[7 empty] | 4964 | 92 | 9.6446 | 7.5751
[7 empty] | 4965 | 93 | 7.2701 | 5.646
[7 empty] | 4966 | 94 | 6.3797 | 4.9225
[7 empty] | 4967 | 95 | 4.5493 | 3.4355
[7 empty] | 4968 | 96 | 3.5765 | 2.6451
[7 empty] | 4969 | 97 | 3.527 | 2.6049
[7 empty] | 4970 | 98 | 3.2384 | 2.3704
[7 empty] | 4971 | 99 | 3.1807 | 2.3235
[7 empty] | 4972 | 100 | 2.8345 | 2.0422
[7 empty] | 4973 | 101 | 2.7767 | 1.9953
[7 empty] | 4974 | 102 | 3.0076 | 2.1829
[7 empty] | 4975 | 103 | 3.7414 | 2.779
[7 empty] | 4976 | 104 | 3.9887 | 2.98
[7 empty] | 4977 | 105 | 4.4669 | 3.3685
[7 empty] | 4978 | 106 | 5.9015 | 4.534
[7 empty] | 4979 | 107 | 6.2477 | 4.8154
[7 empty] | 4980 | 108 | 7.7977 | 6.0747
[7 empty] | 4981 | 109 | 7.1464 | 5.5455
[7 empty] | 4982 | 110 | 6.7012 | 5.1838
[7 empty] | 4983 | 111 | 6.5446 | 5.0565
[7 empty] | 4984 | 112 | 6.6105 | 5.1101
[7 empty] | 4985 | 113 | 6.2725 | 4.8355
[7 empty] | 4986 | 114 | 6.4374 | 4.9694
[7 empty] | 4987 | 115 | 5.9922 | 4.6077
[7 empty] | 4988 | 116 | 6.66 | 5.1503
[7 empty] | 4989 | 117 | 6.2477 | 4.8154
[7 empty] | 4990 | 118 | 5.4892 | 4.1991
[7 empty] | 4991 | 119 | 3.9227 | 2.9264
[7 empty] | 4992 | 120 | 3.6106 | 2.6728
[7 empty] | 4993 | 121 | 2.8922 | 2.0891
[7 empty] | 4994 | 122 | 2.4882 | 1.7609
[7 empty] | 4995 | 123 | 2.4057 | 1.6939
[7 empty] | 4996 | 124 | 2.3727 | 1.6671
[7 empty] | 4997 | 125 | 2.3315 | 1.6336
[7 empty] | 4998 | 126 | 2.4717 | 1.7475
[7 empty] | 4999 | 127 | 3.9557 | 2.9532
[7 empty] | 5000 | 128 | 5.4892 | 4.1991
[7 empty] | 5001 | 129 | 6.1571 | 4.7417
[7 empty] | 5002 | 130 | 6.5858 | 5.09
[7 empty] | 5003 | 131 | 6.7424 | 5.2173
[7 empty] | 5004 | 132 | 6.4951 | 5.0163
[7 empty] | 5005 | 133 | 7.1217 | 5.5254
[7 empty] | 5006 | 134 | 7.4185 | 5.7666
[7 empty] | 5007 | 135 | 7.4844 | 5.8201
[7 empty] | 5008 | 136 | 6.6847 | 5.1704
[7 empty] | 5009 | 137 | 6.5858 | 5.09
[7 empty] | 5010 | 138 | 6.5363 | 5.0498
[7 empty] | 5011 | 139 | 6.2065 | 4.7819
[7 empty] | 5012 | 140 | 6.2148 | 4.7886
[7 empty] | 5013 | 141 | 5.5717 | 4.2661
[7 empty] | 5014 | 142 | 4.9451 | 3.757
[7 empty] | 5015 | 143 | 4.0794 | 3.0537
[7 empty] | 5016 | 144 | 3.4775 | 2.5647
[7 empty] | 5017 | 145 | 3.0158 | 2.1896
[7 empty] | 5018 | 146 | 2.8097 | 2.0221
[7 empty] | 5019 | 147 | 2.7438 | 1.9685
[7 empty] | 5020 | 148 | 2.7355 | 1.9618
[7 empty] | 5021 | 149 | 2.7355 | 1.9618
[7 empty] | 5022 | 150 | 2.7438 | 1.9685
[7 empty] | 5023 | 151 | 3.8073 | 2.8326
[7 empty] | 5024 | 152 | 5.3079 | 4.0517
[7 empty] | 5025 | 153 | 5.9097 | 4.5407
[7 empty] | 5026 | 154 | 6.4621 | 4.9895
[7 empty] | 5027 | 155 | 6.3137 | 4.869
[7 empty] | 5028 | 156 | 6.4786 | 5.0029
[7 empty] | 5029 | 157 | 7.1794 | 5.5723
[7 empty] | 5030 | 158 | 7.5009 | 5.8335
[7 empty] | 5031 | 159 | 7.7648 | 6.0479
[7 empty] | 5032 | 160 | 7.6411 | 5.9474
[7 empty] | 5033 | 161 | 8.3914 | 6.557
[7 empty] | 5034 | 162 | 7.9049 | 6.1618
[7 empty] | 5035 | 163 | 8.2594 | 6.4498
[7 empty] | 5036 | 164 | 6.9321 | 5.3713
[7 empty] | 5037 | 165 | 10.0073 | 7.8699
[7 empty] | 5038 | 166 | 7.9956 | 6.2354
[7 empty] | 5039 | 167 | 4.4504 | 3.3551
[7 empty] | 5040 | 168 | 3.8156 | 2.8393
[7 empty] | 5041 | 1 | 2.381 | 1.6738
[7 empty] | 5042 | 2 | 2.2738 | 1.5867
[7 empty] | 5043 | 3 | 2.2656 | 1.58
[7 empty] | 5044 | 4 | 2.3975 | 1.6872
[7 empty] | 5045 | 5 | 2.414 | 1.7006
[7 empty] | 5046 | 6 | 2.8345 | 2.0422
[7 empty] | 5047 | 7 | 3.5435 | 2.6183
[7 empty] | 5048 | 8 | 4.2031 | 3.1541
[7 empty] | 5049 | 9 | 4.1783 | 3.134
[7 empty] | 5050 | 10 | 5.6706 | 4.3465
[7 empty] | 5051 | 11 | 7.7153 | 6.0077
[7 empty] | 5052 | 12 | 8.6634 | 6.778
[7 empty] | 5053 | 13 | 9.0344 | 7.0795
[7 empty] | 5054 | 14 | 8.8201 | 6.9053
[7 empty] | 5055 | 15 | 8.7294 | 6.8316
[7 empty] | 5056 | 16 | 9.8919 | 7.7761
[7 empty] | 5057 | 17 | 11.1946 | 8.8345
[7 empty] | 5058 | 18 | 10.9555 | 8.6402
[7 empty] | 5059 | 19 | 11.4749 | 9.0622
[7 empty] | 5060 | 20 | 11.4089 | 9.0086
[7 empty] | 5061 | 21 | 11.9696 | 9.4641
[7 empty] | 5062 | 22 | 8.0781 | 6.3024
[7 empty] | 5063 | 23 | 4.368 | 3.2881
[7 empty] | 5064 | 24 | 2.724 | 1.9525
[7 empty] | 5065 | 25 | 2.6283 | 1.8747
[7 empty] | 5066 | 26 | 2.5212 | 1.7877
[7 empty] | 5067 | 27 | 2.4222 | 1.7073
[7 empty] | 5068 | 28 | 2.5047 | 1.7743
[7 empty] | 5069 | 29 | 2.7438 | 1.9685
[7 empty] | 5070 | 30 | 2.9829 | 2.1628
[7 empty] | 5071 | 31 | 3.8156 | 2.8393
[7 empty] | 5072 | 32 | 4.1618 | 3.1207
[7 empty] | 5073 | 33 | 4.8132 | 3.6498
[7 empty] | 5074 | 34 | 5.6954 | 4.3666
[7 empty] | 5075 | 35 | 7.8307 | 6.1015
[7 empty] | 5076 | 36 | 8.8448 | 6.9254
[7 empty] | 5077 | 37 | 8.919 | 6.9857
[7 empty] | 5078 | 38 | 8.9932 | 7.046
[7 empty] | 5079 | 39 | 8.6717 | 6.7847
[7 empty] | 5080 | 40 | 9.7105 | 7.6287
[7 empty] | 5081 | 41 | 10.2547 | 8.0708
[7 empty] | 5082 | 42 | 10.2711 | 8.0842
[7 empty] | 5083 | 43 | 10.6339 | 8.379
[7 empty] | 5084 | 44 | 11.7717 | 9.3034
[7 empty] | 5085 | 45 | 11.3759 | 8.9818
[7 empty] | 5086 | 46 | 8.6717 | 6.7847
[7 empty] | 5087 | 47 | 5.1265 | 3.9044
[7 empty] | 5088 | 48 | 3.6507 | 2.7053
[7 empty] | 5089 | 49 | 2.9993 | 2.1762
[7 empty] | 5090 | 50 | 2.6943 | 1.9283
[7 empty] | 5091 | 51 | 2.5871 | 1.8412
[7 empty] | 5092 | 52 | 2.6201 | 1.868
[7 empty] | 5093 | 53 | 2.6448 | 1.8881
[7 empty] | 5094 | 54 | 3.2137 | 2.3503
[7 empty] | 5095 | 55 | 4.335 | 3.2613
[7 empty] | 5096 | 56 | 4.5741 | 3.4556
[7 empty] | 5097 | 57 | 5.5057 | 4.2125
[7 empty] | 5098 | 58 | 6.594 | 5.0967
[7 empty] | 5099 | 59 | 7.7813 | 6.0613
[7 empty] | 5100 | 60 | 8.3996 | 6.5637
[7 empty] | 5101 | 61 | 9.0674 | 7.1063
[7 empty] | 5102 | 62 | 8.8696 | 6.9455
[7 empty] | 5103 | 63 | 9.4549 | 7.4211
[7 empty] | 5104 | 64 | 10.3866 | 8.178
[7 empty] | 5105 | 65 | 10.9967 | 8.6737
[7 empty] | 5106 | 66 | 10.8977 | 8.5933
[7 empty] | 5107 | 67 | 11.6233 | 9.1828
[7 empty] | 5108 | 68 | 11.8624 | 9.377
[7 empty] | 5109 | 69 | 11.3594 | 8.9684
[7 empty] | 5110 | 70 | 9.1004 | 7.133
[7 empty] | 5111 | 71 | 4.6565 | 3.5226
[7 empty] | 5112 | 72 | 3.5894 | 2.6556
[7 empty] | 5113 | 73 | 2.8839 | 2.0824
[7 empty] | 5114 | 74 | 2.6613 | 1.9015
[7 empty] | 5115 | 75 | 2.5624 | 1.8211
[7 empty] | 5116 | 76 | 2.5047 | 1.7743
[7 empty] | 5117 | 77 | 2.6778 | 1.9149
[7 empty] | 5118 | 78 | 3.0735 | 2.2365
[7 empty] | 5119 | 79 | 4.1701 | 3.1274
[7 empty] | 5120 | 80 | 4.3432 | 3.268
[7 empty] | 5121 | 81 | 5.5057 | 4.2125
[7 empty] | 5122 | 82 | 6.5775 | 5.0833
[7 empty] | 5123 | 83 | 7.3031 | 5.6728
[7 empty] | 5124 | 84 | 8.5233 | 6.6642
[7 empty] | 5125 | 85 | 8.2265 | 6.423
[7 empty] | 5126 | 86 | 7.7235 | 6.0144
[7 empty] | 5127 | 87 | 8.1605 | 6.3694
[7 empty] | 5128 | 88 | 8.8118 | 6.8986
[7 empty] | 5129 | 89 | 10.1392 | 7.9771
[7 empty] | 5130 | 90 | 9.5621 | 7.5082
[7 empty] | 5131 | 91 | 10.2382 | 8.0574
[7 empty] | 5132 | 92 | 9.6446 | 7.5751
[7 empty] | 5133 | 93 | 7.2701 | 5.646
[7 empty] | 5134 | 94 | 6.3797 | 4.9225
[7 empty] | 5135 | 95 | 4.5493 | 3.4355
[7 empty] | 5136 | 96 | 3.5765 | 2.6451
[7 empty] | 5137 | 97 | 3.527 | 2.6049
[7 empty] | 5138 | 98 | 3.2384 | 2.3704
[7 empty] | 5139 | 99 | 3.1807 | 2.3235
[7 empty] | 5140 | 100 | 2.8345 | 2.0422
[7 empty] | 5141 | 101 | 2.7767 | 1.9953
[7 empty] | 5142 | 102 | 3.0076 | 2.1829
[7 empty] | 5143 | 103 | 3.7414 | 2.779
[7 empty] | 5144 | 104 | 3.9887 | 2.98
[7 empty] | 5145 | 105 | 4.4669 | 3.3685
[7 empty] | 5146 | 106 | 5.9015 | 4.534
[7 empty] | 5147 | 107 | 6.2477 | 4.8154
[7 empty] | 5148 | 108 | 7.7977 | 6.0747
[7 empty] | 5149 | 109 | 7.1464 | 5.5455
[7 empty] | 5150 | 110 | 6.7012 | 5.1838
[7 empty] | 5151 | 111 | 6.5446 | 5.0565
[7 empty] | 5152 | 112 | 6.6105 | 5.1101
[7 empty] | 5153 | 113 | 6.2725 | 4.8355
[7 empty] | 5154 | 114 | 6.4374 | 4.9694
[7 empty] | 5155 | 115 | 5.9922 | 4.6077
[7 empty] | 5156 | 116 | 6.66 | 5.1503
[7 empty] | 5157 | 117 | 6.2477 | 4.8154
[7 empty] | 5158 | 118 | 5.4892 | 4.1991
[7 empty] | 5159 | 119 | 3.9227 | 2.9264
[7 empty] | 5160 | 120 | 3.6106 | 2.6728
[7 empty] | 5161 | 121 | 2.8922 | 2.0891
[7 empty] | 5162 | 122 | 2.4882 | 1.7609
[7 empty] | 5163 | 123 | 2.4057 | 1.6939
[7 empty] | 5164 | 124 | 2.3727 | 1.6671
[7 empty] | 5165 | 125 | 2.3315 | 1.6336
[7 empty] | 5166 | 126 | 2.4717 | 1.7475
[7 empty] | 5167 | 127 | 3.9557 | 2.9532
[7 empty] | 5168 | 128 | 5.4892 | 4.1991
[7 empty] | 5169 | 129 | 6.1571 | 4.7417
[7 empty] | 5170 | 130 | 6.5858 | 5.09
[7 empty] | 5171 | 131 | 6.7424 | 5.2173
[7 empty] | 5172 | 132 | 6.4951 | 5.0163
[7 empty] | 5173 | 133 | 7.1217 | 5.5254
[7 empty] | 5174 | 134 | 7.4185 | 5.7666
[7 empty] | 5175 | 135 | 7.4844 | 5.8201
[7 empty] | 5176 | 136 | 6.6847 | 5.1704
[7 empty] | 5177 | 137 | 6.5858 | 5.09
[7 empty] | 5178 | 138 | 6.5363 | 5.0498
[7 empty] | 5179 | 139 | 6.2065 | 4.7819
[7 empty] | 5180 | 140 | 6.2148 | 4.7886
[7 empty] | 5181 | 141 | 5.5717 | 4.2661
[7 empty] | 5182 | 142 | 4.9451 | 3.757
[7 empty] | 5183 | 143 | 4.0794 | 3.0537
[7 empty] | 5184 | 144 | 3.4775 | 2.5647
[7 empty] | 5185 | 145 | 3.0158 | 2.1896
[7 empty] | 5186 | 146 | 2.8097 | 2.0221
[7 empty] | 5187 | 147 | 2.7438 | 1.9685
[7 empty] | 5188 | 148 | 2.7355 | 1.9618
[7 empty] | 5189 | 149 | 2.7355 | 1.9618
[7 empty] | 5190 | 150 | 2.7438 | 1.9685
[7 empty] | 5191 | 151 | 3.8073 | 2.8326
[7 empty] | 5192 | 152 | 5.3079 | 4.0517
[7 empty] | 5193 | 153 | 5.9097 | 4.5407
[7 empty] | 5194 | 154 | 6.4621 | 4.9895
[7 empty] | 5195 | 155 | 6.3137 | 4.869
[7 empty] | 5196 | 156 | 6.4786 | 5.0029
[7 empty] | 5197 | 157 | 7.1794 | 5.5723
[7 empty] | 5198 | 158 | 7.5009 | 5.8335
[7 empty] | 5199 | 159 | 7.7648 | 6.0479
[7 empty] | 5200 | 160 | 7.6411 | 5.9474
[7 empty] | 5201 | 161 | 8.3914 | 6.557
[7 empty] | 5202 | 162 | 7.9049 | 6.1618
[7 empty] | 5203 | 163 | 8.2594 | 6.4498
[7 empty] | 5204 | 164 | 6.9321 | 5.3713
[7 empty] | 5205 | 165 | 10.0073 | 7.8699
[7 empty] | 5206 | 166 | 7.9956 | 6.2354
[7 empty] | 5207 | 167 | 4.4504 | 3.3551
[7 empty] | 5208 | 168 | 3.8156 | 2.8393
[7 empty] | 5209 | 1 | 2.381 | 1.6738
[7 empty] | 5210 | 2 | 2.2738 | 1.5867
[7 empty] | 5211 | 3 | 2.2656 | 1.58
[7 empty] | 5212 | 4 | 2.3975 | 1.6872
[7 empty] | 5213 | 5 | 2.414 | 1.7006
[7 empty] | 5214 | 6 | 2.8345 | 2.0422
[7 empty] | 5215 | 7 | 3.5435 | 2.6183
[7 empty] | 5216 | 8 | 4.2031 | 3.1541
[7 empty] | 5217 | 9 | 4.1783 | 3.134
[7 empty] | 5218 | 10 | 5.6706 | 4.3465
[7 empty] | 5219 | 11 | 7.7153 | 6.0077
[7 empty] | 5220 | 12 | 8.6634 | 6.778
[7 empty] | 5221 | 13 | 9.0344 | 7.0795
[7 empty] | 5222 | 14 | 8.8201 | 6.9053
[7 empty] | 5223 | 15 | 8.7294 | 6.8316
[7 empty] | 5224 | 16 | 9.8919 | 7.7761
[7 empty] | 5225 | 17 | 11.1946 | 8.8345
[7 empty] | 5226 | 18 | 10.9555 | 8.6402
[7 empty] | 5227 | 19 | 11.4749 | 9.0622
[7 empty] | 5228 | 20 | 11.4089 | 9.0086
[7 empty] | 5229 | 21 | 11.9696 | 9.4641
[7 empty] | 5230 | 22 | 8.0781 | 6.3024
[7 empty] | 5231 | 23 | 4.368 | 3.2881
[7 empty] | 5232 | 24 | 2.724 | 1.9525
[7 empty] | 5233 | 25 | 2.6283 | 1.8747
[7 empty] | 5234 | 26 | 2.5212 | 1.7877
[7 empty] | 5235 | 27 | 2.4222 | 1.7073
[7 empty] | 5236 | 28 | 2.5047 | 1.7743
[7 empty] | 5237 | 29 | 2.7438 | 1.9685
[7 empty] | 5238 | 30 | 2.9829 | 2.1628
[7 empty] | 5239 | 31 | 3.8156 | 2.8393
[7 empty] | 5240 | 32 | 4.1618 | 3.1207
[7 empty] | 5241 | 33 | 4.8132 | 3.6498
[7 empty] | 5242 | 34 | 5.6954 | 4.3666
[7 empty] | 5243 | 35 | 7.8307 | 6.1015
[7 empty] | 5244 | 36 | 8.8448 | 6.9254
[7 empty] | 5245 | 37 | 8.919 | 6.9857
[7 empty] | 5246 | 38 | 8.9932 | 7.046
[7 empty] | 5247 | 39 | 8.6717 | 6.7847
[7 empty] | 5248 | 40 | 9.7105 | 7.6287
[7 empty] | 5249 | 41 | 10.2547 | 8.0708
[7 empty] | 5250 | 42 | 10.2711 | 8.0842
[7 empty] | 5251 | 43 | 10.6339 | 8.379
[7 empty] | 5252 | 44 | 11.7717 | 9.3034
[7 empty] | 5253 | 45 | 11.3759 | 8.9818
[7 empty] | 5254 | 46 | 8.6717 | 6.7847
[7 empty] | 5255 | 47 | 5.1265 | 3.9044
[7 empty] | 5256 | 48 | 3.6507 | 2.7053
[7 empty] | 5257 | 49 | 2.9993 | 2.1762
[7 empty] | 5258 | 50 | 2.6943 | 1.9283
[7 empty] | 5259 | 51 | 2.5871 | 1.8412
[7 empty] | 5260 | 52 | 2.6201 | 1.868
[7 empty] | 5261 | 53 | 2.6448 | 1.8881
[7 empty] | 5262 | 54 | 3.2137 | 2.3503
[7 empty] | 5263 | 55 | 4.335 | 3.2613
[7 empty] | 5264 | 56 | 4.5741 | 3.4556
[7 empty] | 5265 | 57 | 5.5057 | 4.2125
[7 empty] | 5266 | 58 | 6.594 | 5.0967
[7 empty] | 5267 | 59 | 7.7813 | 6.0613
[7 empty] | 5268 | 60 | 8.3996 | 6.5637
[7 empty] | 5269 | 61 | 9.0674 | 7.1063
[7 empty] | 5270 | 62 | 8.8696 | 6.9455
[7 empty] | 5271 | 63 | 9.4549 | 7.4211
[7 empty] | 5272 | 64 | 10.3866 | 8.178
[7 empty] | 5273 | 65 | 10.9967 | 8.6737
[7 empty] | 5274 | 66 | 10.8977 | 8.5933
[7 empty] | 5275 | 67 | 11.6233 | 9.1828
[7 empty] | 5276 | 68 | 11.8624 | 9.377
[7 empty] | 5277 | 69 | 11.3594 | 8.9684
[7 empty] | 5278 | 70 | 9.1004 | 7.133
[7 empty] | 5279 | 71 | 4.6565 | 3.5226
[7 empty] | 5280 | 72 | 3.5894 | 2.6556
[7 empty] | 5281 | 73 | 2.8839 | 2.0824
[7 empty] | 5282 | 74 | 2.6613 | 1.9015
[7 empty] | 5283 | 75 | 2.5624 | 1.8211
[7 empty] | 5284 | 76 | 2.5047 | 1.7743
[7 empty] | 5285 | 77 | 2.6778 | 1.9149
[7 empty] | 5286 | 78 | 3.0735 | 2.2365
[7 empty] | 5287 | 79 | 4.1701 | 3.1274
[7 empty] | 5288 | 80 | 4.3432 | 3.268
[7 empty] | 5289 | 81 | 5.5057 | 4.2125
[7 empty] | 5290 | 82 | 6.5775 | 5.0833
[7 empty] | 5291 | 83 | 7.3031 | 5.6728
[7 empty] | 5292 | 84 | 8.5233 | 6.6642
[7 empty] | 5293 | 85 | 8.2265 | 6.423
[7 empty] | 5294 | 86 | 7.7235 | 6.0144
[7 empty] | 5295 | 87 | 8.1605 | 6.3694
[7 empty] | 5296 | 88 | 8.8118 | 6.8986
[7 empty] | 5297 | 89 | 10.1392 | 7.9771
[7 empty] | 5298 | 90 | 9.5621 | 7.5082
[7 empty] | 5299 | 91 | 10.2382 | 8.0574
[7 empty] | 5300 | 92 | 9.6446 | 7.5751
[7 empty] | 5301 | 93 | 7.2701 | 5.646
[7 empty] | 5302 | 94 | 6.3797 | 4.9225
[7 empty] | 5303 | 95 | 4.5493 | 3.4355
[7 empty] | 5304 | 96 | 3.5765 | 2.6451
[7 empty] | 5305 | 97 | 3.527 | 2.6049
[7 empty] | 5306 | 98 | 3.2384 | 2.3704
[7 empty] | 5307 | 99 | 3.1807 | 2.3235
[7 empty] | 5308 | 100 | 2.8345 | 2.0422
[7 empty] | 5309 | 101 | 2.7767 | 1.9953
[7 empty] | 5310 | 102 | 3.0076 | 2.1829
[7 empty] | 5311 | 103 | 3.7414 | 2.779
[7 empty] | 5312 | 104 | 3.9887 | 2.98
[7 empty] | 5313 | 105 | 4.4669 | 3.3685
[7 empty] | 5314 | 106 | 5.9015 | 4.534
[7 empty] | 5315 | 107 | 6.2477 | 4.8154
[7 empty] | 5316 | 108 | 7.7977 | 6.0747
[7 empty] | 5317 | 109 | 7.1464 | 5.5455
[7 empty] | 5318 | 110 | 6.7012 | 5.1838
[7 empty] | 5319 | 111 | 6.5446 | 5.0565
[7 empty] | 5320 | 112 | 6.6105 | 5.1101
[7 empty] | 5321 | 113 | 6.2725 | 4.8355
[7 empty] | 5322 | 114 | 6.4374 | 4.9694
[7 empty] | 5323 | 115 | 5.9922 | 4.6077
[7 empty] | 5324 | 116 | 6.66 | 5.1503
[7 empty] | 5325 | 117 | 6.2477 | 4.8154
[7 empty] | 5326 | 118 | 5.4892 | 4.1991
[7 empty] | 5327 | 119 | 3.9227 | 2.9264
[7 empty] | 5328 | 120 | 3.6106 | 2.6728
[7 empty] | 5329 | 121 | 2.8922 | 2.0891
[7 empty] | 5330 | 122 | 2.4882 | 1.7609
[7 empty] | 5331 | 123 | 2.4057 | 1.6939
[7 empty] | 5332 | 124 | 2.3727 | 1.6671
[7 empty] | 5333 | 125 | 2.3315 | 1.6336
[7 empty] | 5334 | 126 | 2.4717 | 1.7475
[7 empty] | 5335 | 127 | 3.9557 | 2.9532
[7 empty] | 5336 | 128 | 5.4892 | 4.1991
[7 empty] | 5337 | 129 | 6.1571 | 4.7417
[7 empty] | 5338 | 130 | 6.5858 | 5.09
[7 empty] | 5339 | 131 | 6.7424 | 5.2173
[7 empty] | 5340 | 132 | 6.4951 | 5.0163
[7 empty] | 5341 | 133 | 7.1217 | 5.5254
[7 empty] | 5342 | 134 | 7.4185 | 5.7666
[7 empty] | 5343 | 135 | 7.4844 | 5.8201
[7 empty] | 5344 | 136 | 6.6847 | 5.1704
[7 empty] | 5345 | 137 | 6.5858 | 5.09
[7 empty] | 5346 | 138 | 6.5363 | 5.0498
[7 empty] | 5347 | 139 | 6.2065 | 4.7819
[7 empty] | 5348 | 140 | 6.2148 | 4.7886
[7 empty] | 5349 | 141 | 5.5717 | 4.2661
[7 empty] | 5350 | 142 | 4.9451 | 3.757
[7 empty] | 5351 | 143 | 4.0794 | 3.0537
[7 empty] | 5352 | 144 | 3.4775 | 2.5647
[7 empty] | 5353 | 145 | 3.0158 | 2.1896
[7 empty] | 5354 | 146 | 2.8097 | 2.0221
[7 empty] | 5355 | 147 | 2.7438 | 1.9685
[7 empty] | 5356 | 148 | 2.7355 | 1.9618
[7 empty] | 5357 | 149 | 2.7355 | 1.9618
[7 empty] | 5358 | 150 | 2.7438 | 1.9685
[7 empty] | 5359 | 151 | 3.8073 | 2.8326
[7 empty] | 5360 | 152 | 5.3079 | 4.0517
[7 empty] | 5361 | 153 | 5.9097 | 4.5407
[7 empty] | 5362 | 154 | 6.4621 | 4.9895
[7 empty] | 5363 | 155 | 6.3137 | 4.869
[7 empty] | 5364 | 156 | 6.4786 | 5.0029
[7 empty] | 5365 | 157 | 7.1794 | 5.5723
[7 empty] | 5366 | 158 | 7.5009 | 5.8335
[7 empty] | 5367 | 159 | 7.7648 | 6.0479
[7 empty] | 5368 | 160 | 7.6411 | 5.9474
[7 empty] | 5369 | 161 | 8.3914 | 6.557
[7 empty] | 5370 | 162 | 7.9049 | 6.1618
[7 empty] | 5371 | 163 | 8.2594 | 6.4498
[7 empty] | 5372 | 164 | 6.9321 | 5.3713
[7 empty] | 5373 | 165 | 10.0073 | 7.8699
[7 empty] | 5374 | 166 | 7.9956 | 6.2354
[7 empty] | 5375 | 167 | 4.4504 | 3.3551
[7 empty] | 5376 | 168 | 3.8156 | 2.8393
[7 empty] | 5377 | 1 | 2.381 | 1.6738
[7 empty] | 5378 | 2 | 2.2738 | 1.5867
[7 empty] | 5379 | 3 | 2.2656 | 1.58
[7 empty] | 5380 | 4 | 2.3975 | 1.6872
[7 empty] | 5381 | 5 | 2.414 | 1.7006
[7 empty] | 5382 | 6 | 2.8345 | 2.0422
[7 empty] | 5383 | 7 | 3.5435 | 2.6183
[7 empty] | 5384 | 8 | 4.2031 | 3.1541
[7 empty] | 5385 | 9 | 4.1783 | 3.134
[7 empty] | 5386 | 10 | 5.6706 | 4.3465
[7 empty] | 5387 | 11 | 7.7153 | 6.0077
[7 empty] | 5388 | 12 | 8.6634 | 6.778
[7 empty] | 5389 | 13 | 9.0344 | 7.0795
[7 empty] | 5390 | 14 | 8.8201 | 6.9053
[7 empty] | 5391 | 15 | 8.7294 | 6.8316
[7 empty] | 5392 | 16 | 9.8919 | 7.7761
[7 empty] | 5393 | 17 | 11.1946 | 8.8345
[7 empty] | 5394 | 18 | 10.9555 | 8.6402
[7 empty] | 5395 | 19 | 11.4749 | 9.0622
[7 empty] | 5396 | 20 | 11.4089 | 9.0086
[7 empty] | 5397 | 21 | 11.9696 | 9.4641
[7 empty] | 5398 | 22 | 8.0781 | 6.3024
[7 empty] | 5399 | 23 | 4.368 | 3.2881
[7 empty] | 5400 | 24 | 2.724 | 1.9525
[7 empty] | 5401 | 25 | 2.6283 | 1.8747
[7 empty] | 5402 | 26 | 2.5212 | 1.7877
[7 empty] | 5403 | 27 | 2.4222 | 1.7073
[7 empty] | 5404 | 28 | 2.5047 | 1.7743
[7 empty] | 5405 | 29 | 2.7438 | 1.9685
[7 empty] | 5406 | 30 | 2.9829 | 2.1628
[7 empty] | 5407 | 31 | 3.8156 | 2.8393
[7 empty] | 5408 | 32 | 4.1618 | 3.1207
[7 empty] | 5409 | 33 | 4.8132 | 3.6498
[7 empty] | 5410 | 34 | 5.6954 | 4.3666
[7 empty] | 5411 | 35 | 7.8307 | 6.1015
[7 empty] | 5412 | 36 | 8.8448 | 6.9254
[7 empty] | 5413 | 37 | 8.919 | 6.9857
[7 empty] | 5414 | 38 | 8.9932 | 7.046
[7 empty] | 5415 | 39 | 8.6717 | 6.7847
[7 empty] | 5416 | 40 | 9.7105 | 7.6287
[7 empty] | 5417 | 41 | 10.2547 | 8.0708
[7 empty] | 5418 | 42 | 10.2711 | 8.0842
[7 empty] | 5419 | 43 | 10.6339 | 8.379
[7 empty] | 5420 | 44 | 11.7717 | 9.3034
[7 empty] | 5421 | 45 | 11.3759 | 8.9818
[7 empty] | 5422 | 46 | 8.6717 | 6.7847
[7 empty] | 5423 | 47 | 5.1265 | 3.9044
[7 empty] | 5424 | 48 | 3.6507 | 2.7053
[7 empty] | 5425 | 49 | 2.9993 | 2.1762
[7 empty] | 5426 | 50 | 2.6943 | 1.9283
[7 empty] | 5427 | 51 | 2.5871 | 1.8412
[7 empty] | 5428 | 52 | 2.6201 | 1.868
[7 empty] | 5429 | 53 | 2.6448 | 1.8881
[7 empty] | 5430 | 54 | 3.2137 | 2.3503
[7 empty] | 5431 | 55 | 4.335 | 3.2613
[7 empty] | 5432 | 56 | 4.5741 | 3.4556
[7 empty] | 5433 | 57 | 5.5057 | 4.2125
[7 empty] | 5434 | 58 | 6.594 | 5.0967
[7 empty] | 5435 | 59 | 7.7813 | 6.0613
[7 empty] | 5436 | 60 | 8.3996 | 6.5637
[7 empty] | 5437 | 61 | 9.0674 | 7.1063
[7 empty] | 5438 | 62 | 8.8696 | 6.9455
[7 empty] | 5439 | 63 | 9.4549 | 7.4211
[7 empty] | 5440 | 64 | 10.3866 | 8.178
[7 empty] | 5441 | 65 | 10.9967 | 8.6737
[7 empty] | 5442 | 66 | 10.8977 | 8.5933
[7 empty] | 5443 | 67 | 11.6233 | 9.1828
[7 empty] | 5444 | 68 | 11.8624 | 9.377
[7 empty] | 5445 | 69 | 11.3594 | 8.9684
[7 empty] | 5446 | 70 | 9.1004 | 7.133
[7 empty] | 5447 | 71 | 4.6565 | 3.5226
[7 empty] | 5448 | 72 | 3.5894 | 2.6556
[7 empty] | 5449 | 73 | 2.8839 | 2.0824
[7 empty] | 5450 | 74 | 2.6613 | 1.9015
[7 empty] | 5451 | 75 | 2.5624 | 1.8211
[7 empty] | 5452 | 76 | 2.5047 | 1.7743
[7 empty] | 5453 | 77 | 2.6778 | 1.9149
[7 empty] | 5454 | 78 | 3.0735 | 2.2365
[7 empty] | 5455 | 79 | 4.1701 | 3.1274
[7 empty] | 5456 | 80 | 4.3432 | 3.268
[7 empty] | 5457 | 81 | 5.5057 | 4.2125
[7 empty] | 5458 | 82 | 6.5775 | 5.0833
[7 empty] | 5459 | 83 | 7.3031 | 5.6728
[7 empty] | 5460 | 84 | 8.5233 | 6.6642
[7 empty] | 5461 | 85 | 8.2265 | 6.423
[7 empty] | 5462 | 86 | 7.7235 | 6.0144
[7 empty] | 5463 | 87 | 8.1605 | 6.3694
[7 empty] | 5464 | 88 | 8.8118 | 6.8986
[7 empty] | 5465 | 89 | 10.1392 | 7.9771
[7 empty] | 5466 | 90 | 9.5621 | 7.5082
[7 empty] | 5467 | 91 | 10.2382 | 8.0574
[7 empty] | 5468 | 92 | 9.6446 | 7.5751
[7 empty] | 5469 | 93 | 7.2701 | 5.646
[7 empty] | 5470 | 94 | 6.3797 | 4.9225
[7 empty] | 5471 | 95 | 4.5493 | 3.4355
[7 empty] | 5472 | 96 | 3.5765 | 2.6451
[7 empty] | 5473 | 97 | 3.527 | 2.6049
[7 empty] | 5474 | 98 | 3.2384 | 2.3704
[7 empty] | 5475 | 99 | 3.1807 | 2.3235
[7 empty] | 5476 | 100 | 2.8345 | 2.0422
[7 empty] | 5477 | 101 | 2.7767 | 1.9953
[7 empty] | 5478 | 102 | 3.0076 | 2.1829
[7 empty] | 5479 | 103 | 3.7414 | 2.779
[7 empty] | 5480 | 104 | 3.9887 | 2.98
[7 empty] | 5481 | 105 | 4.4669 | 3.3685
[7 empty] | 5482 | 106 | 5.9015 | 4.534
[7 empty] | 5483 | 107 | 6.2477 | 4.8154
[7 empty] | 5484 | 108 | 7.7977 | 6.0747
[7 empty] | 5485 | 109 | 7.1464 | 5.5455
[7 empty] | 5486 | 110 | 6.7012 | 5.1838
[7 empty] | 5487 | 111 | 6.5446 | 5.0565
[7 empty] | 5488 | 112 | 6.6105 | 5.1101
[7 empty] | 5489 | 113 | 6.2725 | 4.8355
[7 empty] | 5490 | 114 | 6.4374 | 4.9694
[7 empty] | 5491 | 115 | 5.9922 | 4.6077
[7 empty] | 5492 | 116 | 6.66 | 5.1503
[7 empty] | 5493 | 117 | 6.2477 | 4.8154
[7 empty] | 5494 | 118 | 5.4892 | 4.1991
[7 empty] | 5495 | 119 | 3.9227 | 2.9264
[7 empty] | 5496 | 120 | 3.6106 | 2.6728
[7 empty] | 5497 | 121 | 2.8922 | 2.0891
[7 empty] | 5498 | 122 | 2.4882 | 1.7609
[7 empty] | 5499 | 123 | 2.4057 | 1.6939
[7 empty] | 5500 | 124 | 2.3727 | 1.6671
[7 empty] | 5501 | 125 | 2.3315 | 1.6336
[7 empty] | 5502 | 126 | 2.4717 | 1.7475
[7 empty] | 5503 | 127 | 3.9557 | 2.9532
[7 empty] | 5504 | 128 | 5.4892 | 4.1991
[7 empty] | 5505 | 129 | 6.1571 | 4.7417
[7 empty] | 5506 | 130 | 6.5858 | 5.09
[7 empty] | 5507 | 131 | 6.7424 | 5.2173
[7 empty] | 5508 | 132 | 6.4951 | 5.0163
[7 empty] | 5509 | 133 | 7.1217 | 5.5254
[7 empty] | 5510 | 134 | 7.4185 | 5.7666
[7 empty] | 5511 | 135 | 7.4844 | 5.8201
[7 empty] | 5512 | 136 | 6.6847 | 5.1704
[7 empty] | 5513 | 137 | 6.5858 | 5.09
[7 empty] | 5514 | 138 | 6.5363 | 5.0498
[7 empty] | 5515 | 139 | 6.2065 | 4.7819
[7 empty] | 5516 | 140 | 6.2148 | 4.7886
[7 empty] | 5517 | 141 | 5.5717 | 4.2661
[7 empty] | 5518 | 142 | 4.9451 | 3.757
[7 empty] | 5519 | 143 | 4.0794 | 3.0537
[7 empty] | 5520 | 144 | 3.4775 | 2.5647
[7 empty] | 5521 | 145 | 3.0158 | 2.1896
[7 empty] | 5522 | 146 | 2.8097 | 2.0221
[7 empty] | 5523 | 147 | 2.7438 | 1.9685
[7 empty] | 5524 | 148 | 2.7355 | 1.9618
[7 empty] | 5525 | 149 | 2.7355 | 1.9618
[7 empty] | 5526 | 150 | 2.7438 | 1.9685
[7 empty] | 5527 | 151 | 3.8073 | 2.8326
[7 empty] | 5528 | 152 | 5.3079 | 4.0517
[7 empty] | 5529 | 153 | 5.9097 | 4.5407
[7 empty] | 5530 | 154 | 6.4621 | 4.9895
[7 empty] | 5531 | 155 | 6.3137 | 4.869
[7 empty] | 5532 | 156 | 6.4786 | 5.0029
[7 empty] | 5533 | 157 | 7.1794 | 5.5723
[7 empty] | 5534 | 158 | 7.5009 | 5.8335
[7 empty] | 5535 | 159 | 7.7648 | 6.0479
[7 empty] | 5536 | 160 | 7.6411 | 5.9474
[7 empty] | 5537 | 161 | 8.3914 | 6.557
[7 empty] | 5538 | 162 | 7.9049 | 6.1618
[7 empty] | 5539 | 163 | 8.2594 | 6.4498
[7 empty] | 5540 | 164 | 6.9321 | 5.3713
[7 empty] | 5541 | 165 | 10.0073 | 7.8699
[7 empty] | 5542 | 166 | 7.9956 | 6.2354
[7 empty] | 5543 | 167 | 4.4504 | 3.3551
[7 empty] | 5544 | 168 | 3.8156 | 2.8393
[7 empty] | 5545 | 1 | 2.381 | 1.6738
[7 empty] | 5546 | 2 | 2.2738 | 1.5867
[7 empty] | 5547 | 3 | 2.2656 | 1.58
[7 empty] | 5548 | 4 | 2.3975 | 1.6872
[7 empty] | 5549 | 5 | 2.414 | 1.7006
[7 empty] | 5550 | 6 | 2.8345 | 2.0422
[7 empty] | 5551 | 7 | 3.5435 | 2.6183
[7 empty] | 5552 | 8 | 4.2031 | 3.1541
[7 empty] | 5553 | 9 | 4.1783 | 3.134
[7 empty] | 5554 | 10 | 5.6706 | 4.3465
[7 empty] | 5555 | 11 | 7.7153 | 6.0077
[7 empty] | 5556 | 12 | 8.6634 | 6.778
[7 empty] | 5557 | 13 | 9.0344 | 7.0795
[7 empty] | 5558 | 14 | 8.8201 | 6.9053
[7 empty] | 5559 | 15 | 8.7294 | 6.8316
[7 empty] | 5560 | 16 | 9.8919 | 7.7761
[7 empty] | 5561 | 17 | 11.1946 | 8.8345
[7 empty] | 5562 | 18 | 10.9555 | 8.6402
[7 empty] | 5563 | 19 | 11.4749 | 9.0622
[7 empty] | 5564 | 20 | 11.4089 | 9.0086
[7 empty] | 5565 | 21 | 11.9696 | 9.4641
[7 empty] | 5566 | 22 | 8.0781 | 6.3024
[7 empty] | 5567 | 23 | 4.368 | 3.2881
[7 empty] | 5568 | 24 | 2.724 | 1.9525
[7 empty] | 5569 | 25 | 2.6283 | 1.8747
[7 empty] | 5570 | 26 | 2.5212 | 1.7877
[7 empty] | 5571 | 27 | 2.4222 | 1.7073
[7 empty] | 5572 | 28 | 2.5047 | 1.7743
[7 empty] | 5573 | 29 | 2.7438 | 1.9685
[7 empty] | 5574 | 30 | 2.9829 | 2.1628
[7 empty] | 5575 | 31 | 3.8156 | 2.8393
[7 empty] | 5576 | 32 | 4.1618 | 3.1207
[7 empty] | 5577 | 33 | 4.8132 | 3.6498
[7 empty] | 5578 | 34 | 5.6954 | 4.3666
[7 empty] | 5579 | 35 | 7.8307 | 6.1015
[7 empty] | 5580 | 36 | 8.8448 | 6.9254
[7 empty] | 5581 | 37 | 8.919 | 6.9857
[7 empty] | 5582 | 38 | 8.9932 | 7.046
[7 empty] | 5583 | 39 | 8.6717 | 6.7847
[7 empty] | 5584 | 40 | 9.7105 | 7.6287
[7 empty] | 5585 | 41 | 10.2547 | 8.0708
[7 empty] | 5586 | 42 | 10.2711 | 8.0842
[7 empty] | 5587 | 43 | 10.6339 | 8.379
[7 empty] | 5588 | 44 | 11.7717 | 9.3034
[7 empty] | 5589 | 45 | 11.3759 | 8.9818
[7 empty] | 5590 | 46 | 8.6717 | 6.7847
[7 empty] | 5591 | 47 | 5.1265 | 3.9044
[7 empty] | 5592 | 48 | 3.6507 | 2.7053
[7 empty] | 5593 | 49 | 2.9993 | 2.1762
[7 empty] | 5594 | 50 | 2.6943 | 1.9283
[7 empty] | 5595 | 51 | 2.5871 | 1.8412
[7 empty] | 5596 | 52 | 2.6201 | 1.868
[7 empty] | 5597 | 53 | 2.6448 | 1.8881
[7 empty] | 5598 | 54 | 3.2137 | 2.3503
[7 empty] | 5599 | 55 | 4.335 | 3.2613
[7 empty] | 5600 | 56 | 4.5741 | 3.4556
[7 empty] | 5601 | 57 | 5.5057 | 4.2125
[7 empty] | 5602 | 58 | 6.594 | 5.0967
[7 empty] | 5603 | 59 | 7.7813 | 6.0613
[7 empty] | 5604 | 60 | 8.3996 | 6.5637
[7 empty] | 5605 | 61 | 9.0674 | 7.1063
[7 empty] | 5606 | 62 | 8.8696 | 6.9455
[7 empty] | 5607 | 63 | 9.4549 | 7.4211
[7 empty] | 5608 | 64 | 10.3866 | 8.178
[7 empty] | 5609 | 65 | 10.9967 | 8.6737
[7 empty] | 5610 | 66 | 10.8977 | 8.5933
[7 empty] | 5611 | 67 | 11.6233 | 9.1828
[7 empty] | 5612 | 68 | 11.8624 | 9.377
[7 empty] | 5613 | 69 | 11.3594 | 8.9684
[7 empty] | 5614 | 70 | 9.1004 | 7.133
[7 empty] | 5615 | 71 | 4.6565 | 3.5226
[7 empty] | 5616 | 72 | 3.5894 | 2.6556
[7 empty] | 5617 | 73 | 2.8839 | 2.0824
[7 empty] | 5618 | 74 | 2.6613 | 1.9015
[7 empty] | 5619 | 75 | 2.5624 | 1.8211
[7 empty] | 5620 | 76 | 2.5047 | 1.7743
[7 empty] | 5621 | 77 | 2.6778 | 1.9149
[7 empty] | 5622 | 78 | 3.0735 | 2.2365
[7 empty] | 5623 | 79 | 4.1701 | 3.1274
[7 empty] | 5624 | 80 | 4.3432 | 3.268
[7 empty] | 5625 | 81 | 5.5057 | 4.2125
[7 empty] | 5626 | 82 | 6.5775 | 5.0833
[7 empty] | 5627 | 83 | 7.3031 | 5.6728
[7 empty] | 5628 | 84 | 8.5233 | 6.6642
[7 empty] | 5629 | 85 | 8.2265 | 6.423
[7 empty] | 5630 | 86 | 7.7235 | 6.0144
[7 empty] | 5631 | 87 | 8.1605 | 6.3694
[7 empty] | 5632 | 88 | 8.8118 | 6.8986
[7 empty] | 5633 | 89 | 10.1392 | 7.9771
[7 empty] | 5634 | 90 | 9.5621 | 7.5082
[7 empty] | 5635 | 91 | 10.2382 | 8.0574
[7 empty] | 5636 | 92 | 9.6446 | 7.5751
[7 empty] | 5637 | 93 | 7.2701 | 5.646
[7 empty] | 5638 | 94 | 6.3797 | 4.9225
[7 empty] | 5639 | 95 | 4.5493 | 3.4355
[7 empty] | 5640 | 96 | 3.5765 | 2.6451
[7 empty] | 5641 | 97 | 3.527 | 2.6049
[7 empty] | 5642 | 98 | 3.2384 | 2.3704
[7 empty] | 5643 | 99 | 3.1807 | 2.3235
[7 empty] | 5644 | 100 | 2.8345 | 2.0422
[7 empty] | 5645 | 101 | 2.7767 | 1.9953
[7 empty] | 5646 | 102 | 3.0076 | 2.1829
[7 empty] | 5647 | 103 | 3.7414 | 2.779
[7 empty] | 5648 | 104 | 3.9887 | 2.98
[7 empty] | 5649 | 105 | 4.4669 | 3.3685
[7 empty] | 5650 | 106 | 5.9015 | 4.534
[7 empty] | 5651 | 107 | 6.2477 | 4.8154
[7 empty] | 5652 | 108 | 7.7977 | 6.0747
[7 empty] | 5653 | 109 | 7.1464 | 5.5455
[7 empty] | 5654 | 110 | 6.7012 | 5.1838
[7 empty] | 5655 | 111 | 6.5446 | 5.0565
[7 empty] | 5656 | 112 | 6.6105 | 5.1101
[7 empty] | 5657 | 113 | 6.2725 | 4.8355
[7 empty] | 5658 | 114 | 6.4374 | 4.9694
[7 empty] | 5659 | 115 | 5.9922 | 4.6077
[7 empty] | 5660 | 116 | 6.66 | 5.1503
[7 empty] | 5661 | 117 | 6.2477 | 4.8154
[7 empty] | 5662 | 118 | 5.4892 | 4.1991
[7 empty] | 5663 | 119 | 3.9227 | 2.9264
[7 empty] | 5664 | 120 | 3.6106 | 2.6728
[7 empty] | 5665 | 121 | 2.8922 | 2.0891
[7 empty] | 5666 | 122 | 2.4882 | 1.7609
[7 empty] | 5667 | 123 | 2.4057 | 1.6939
[7 empty] | 5668 | 124 | 2.3727 | 1.6671
[7 empty] | 5669 | 125 | 2.3315 | 1.6336
[7 empty] | 5670 | 126 | 2.4717 | 1.7475
[7 empty] | 5671 | 127 | 3.9557 | 2.9532
[7 empty] | 5672 | 128 | 5.4892 | 4.1991
[7 empty] | 5673 | 129 | 6.1571 | 4.7417
[7 empty] | 5674 | 130 | 6.5858 | 5.09
[7 empty] | 5675 | 131 | 6.7424 | 5.2173
[7 empty] | 5676 | 132 | 6.4951 | 5.0163
[7 empty] | 5677 | 133 | 7.1217 | 5.5254
[7 empty] | 5678 | 134 | 7.4185 | 5.7666
[7 empty] | 5679 | 135 | 7.4844 | 5.8201
[7 empty] | 5680 | 136 | 6.6847 | 5.1704
[7 empty] | 5681 | 137 | 6.5858 | 5.09
[7 empty] | 5682 | 138 | 6.5363 | 5.0498
[7 empty] | 5683 | 139 | 6.2065 | 4.7819
[7 empty] | 5684 | 140 | 6.2148 | 4.7886
[7 empty] | 5685 | 141 | 5.5717 | 4.2661
[7 empty] | 5686 | 142 | 4.9451 | 3.757
[7 empty] | 5687 | 143 | 4.0794 | 3.0537
[7 empty] | 5688 | 144 | 3.4775 | 2.5647
[7 empty] | 5689 | 145 | 3.0158 | 2.1896
[7 empty] | 5690 | 146 | 2.8097 | 2.0221
[7 empty] | 5691 | 147 | 2.7438 | 1.9685
[7 empty] | 5692 | 148 | 2.7355 | 1.9618
[7 empty] | 5693 | 149 | 2.7355 | 1.9618
[7 empty] | 5694 | 150 | 2.7438 | 1.9685
[7 empty] | 5695 | 151 | 3.8073 | 2.8326
[7 empty] | 5696 | 152 | 5.3079 | 4.0517
[7 empty] | 5697 | 153 | 5.9097 | 4.5407
[7 empty] | 5698 | 154 | 6.4621 | 4.9895
[7 empty] | 5699 | 155 | 6.3137 | 4.869
[7 empty] | 5700 | 156 | 6.4786 | 5.0029
[7 empty] | 5701 | 157 | 7.1794 | 5.5723
[7 empty] | 5702 | 158 | 7.5009 | 5.8335
[7 empty] | 5703 | 159 | 7.7648 | 6.0479
[7 empty] | 5704 | 160 | 7.6411 | 5.9474
[7 empty] | 5705 | 161 | 8.3914 | 6.557
[7 empty] | 5706 | 162 | 7.9049 | 6.1618
[7 empty] | 5707 | 163 | 8.2594 | 6.4498
[7 empty] | 5708 | 164 | 6.9321 | 5.3713
[7 empty] | 5709 | 165 | 10.0073 | 7.8699
[7 empty] | 5710 | 166 | 7.9956 | 6.2354
[7 empty] | 5711 | 167 | 4.4504 | 3.3551
[7 empty] | 5712 | 168 | 3.8156 | 2.8393
[7 empty] | 5713 | 1 | 2.381 | 1.6738
[7 empty] | 5714 | 2 | 2.2738 | 1.5867
[7 empty] | 5715 | 3 | 2.2656 | 1.58
[7 empty] | 5716 | 4 | 2.3975 | 1.6872
[7 empty] | 5717 | 5 | 2.414 | 1.7006
[7 empty] | 5718 | 6 | 2.8345 | 2.0422
[7 empty] | 5719 | 7 | 3.5435 | 2.6183
[7 empty] | 5720 | 8 | 4.2031 | 3.1541
[7 empty] | 5721 | 9 | 4.1783 | 3.134
[7 empty] | 5722 | 10 | 5.6706 | 4.3465
[7 empty] | 5723 | 11 | 7.7153 | 6.0077
[7 empty] | 5724 | 12 | 8.6634 | 6.778
[7 empty] | 5725 | 13 | 9.0344 | 7.0795
[7 empty] | 5726 | 14 | 8.8201 | 6.9053
[7 empty] | 5727 | 15 | 8.7294 | 6.8316
[7 empty] | 5728 | 16 | 9.8919 | 7.7761
[7 empty] | 5729 | 17 | 11.1946 | 8.8345
[7 empty] | 5730 | 18 | 10.9555 | 8.6402
[7 empty] | 5731 | 19 | 11.4749 | 9.0622
[7 empty] | 5732 | 20 | 11.4089 | 9.0086
[7 empty] | 5733 | 21 | 11.9696 | 9.4641
[7 empty] | 5734 | 22 | 8.0781 | 6.3024
[7 empty] | 5735 | 23 | 4.368 | 3.2881
[7 empty] | 5736 | 24 | 2.724 | 1.9525
[7 empty] | 5737 | 25 | 2.6283 | 1.8747
[7 empty] | 5738 | 26 | 2.5212 | 1.7877
[7 empty] | 5739 | 27 | 2.4222 | 1.7073
[7 empty] | 5740 | 28 | 2.5047 | 1.7743
[7 empty] | 5741 | 29 | 2.7438 | 1.9685
[7 empty] | 5742 | 30 | 2.9829 | 2.1628
[7 empty] | 5743 | 31 | 3.8156 | 2.8393
[7 empty] | 5744 | 32 | 4.1618 | 3.1207
[7 empty] | 5745 | 33 | 4.8132 | 3.6498
[7 empty] | 5746 | 34 | 5.6954 | 4.3666
[7 empty] | 5747 | 35 | 7.8307 | 6.1015
[7 empty] | 5748 | 36 | 8.8448 | 6.9254
[7 empty] | 5749 | 37 | 8.919 | 6.9857
[7 empty] | 5750 | 38 | 8.9932 | 7.046
[7 empty] | 5751 | 39 | 8.6717 | 6.7847
[7 empty] | 5752 | 40 | 9.7105 | 7.6287
[7 empty] | 5753 | 41 | 10.2547 | 8.0708
[7 empty] | 5754 | 42 | 10.2711 | 8.0842
[7 empty] | 5755 | 43 | 10.6339 | 8.379
[7 empty] | 5756 | 44 | 11.7717 | 9.3034
[7 empty] | 5757 | 45 | 11.3759 | 8.9818
[7 empty] | 5758 | 46 | 8.6717 | 6.7847
[7 empty] | 5759 | 47 | 5.1265 | 3.9044
[7 empty] | 5760 | 48 | 3.6507 | 2.7053
[7 empty] | 5761 | 49 | 2.9993 | 2.1762
[7 empty] | 5762 | 50 | 2.6943 | 1.9283
[7 empty] | 5763 | 51 | 2.5871 | 1.8412
[7 empty] | 5764 | 52 | 2.6201 | 1.868
[7 empty] | 5765 | 53 | 2.6448 | 1.8881
[7 empty] | 5766 | 54 | 3.2137 | 2.3503
[7 empty] | 5767 | 55 | 4.335 | 3.2613
[7 empty] | 5768 | 56 | 4.5741 | 3.4556
[7 empty] | 5769 | 57 | 5.5057 | 4.2125
[7 empty] | 5770 | 58 | 6.594 | 5.0967
[7 empty] | 5771 | 59 | 7.7813 | 6.0613
[7 empty] | 5772 | 60 | 8.3996 | 6.5637
[7 empty] | 5773 | 61 | 9.0674 | 7.1063
[7 empty] | 5774 | 62 | 8.8696 | 6.9455
[7 empty] | 5775 | 63 | 9.4549 | 7.4211
[7 empty] | 5776 | 64 | 10.3866 | 8.178
[7 empty] | 5777 | 65 | 10.9967 | 8.6737
[7 empty] | 5778 | 66 | 10.8977 | 8.5933
[7 empty] | 5779 | 67 | 11.6233 | 9.1828
[7 empty] | 5780 | 68 | 11.8624 | 9.377
[7 empty] | 5781 | 69 | 11.3594 | 8.9684
[7 empty] | 5782 | 70 | 9.1004 | 7.133
[7 empty] | 5783 | 71 | 4.6565 | 3.5226
[7 empty] | 5784 | 72 | 3.5894 | 2.6556
[7 empty] | 5785 | 73 | 2.8839 | 2.0824
[7 empty] | 5786 | 74 | 2.6613 | 1.9015
[7 empty] | 5787 | 75 | 2.5624 | 1.8211
[7 empty] | 5788 | 76 | 2.5047 | 1.7743
[7 empty] | 5789 | 77 | 2.6778 | 1.9149
[7 empty] | 5790 | 78 | 3.0735 | 2.2365
[7 empty] | 5791 | 79 | 4.1701 | 3.1274
[7 empty] | 5792 | 80 | 4.3432 | 3.268
[7 empty] | 5793 | 81 | 5.5057 | 4.2125
[7 empty] | 5794 | 82 | 6.5775 | 5.0833
[7 empty] | 5795 | 83 | 7.3031 | 5.6728
[7 empty] | 5796 | 84 | 8.5233 | 6.6642
[7 empty] | 5797 | 85 | 8.2265 | 6.423
[7 empty] | 5798 | 86 | 7.7235 | 6.0144
[7 empty] | 5799 | 87 | 8.1605 | 6.3694
[7 empty] | 5800 | 88 | 8.8118 | 6.8986
[7 empty] | 5801 | 89 | 10.1392 | 7.9771
[7 empty] | 5802 | 90 | 9.5621 | 7.5082
[7 empty] | 5803 | 91 | 10.2382 | 8.0574
[7 empty] | 5804 | 92 | 9.6446 | 7.5751
[7 empty] | 5805 | 93 | 7.2701 | 5.646
[7 empty] | 5806 | 94 | 6.3797 | 4.9225
[7 empty] | 5807 | 95 | 4.5493 | 3.4355
[7 empty] | 5808 | 96 | 3.5765 | 2.6451
[7 empty] | 5809 | 97 | 3.527 | 2.6049
[7 empty] | 5810 | 98 | 3.2384 | 2.3704
[7 empty] | 5811 | 99 | 3.1807 | 2.3235
[7 empty] | 5812 | 100 | 2.8345 | 2.0422
[7 empty] | 5813 | 101 | 2.7767 | 1.9953
[7 empty] | 5814 | 102 | 3.0076 | 2.1829
[7 empty] | 5815 | 103 | 3.7414 | 2.779
[7 empty] | 5816 | 104 | 3.9887 | 2.98
[7 empty] | 5817 | 105 | 4.4669 | 3.3685
[7 empty] | 5818 | 106 | 5.9015 | 4.534
[7 empty] | 5819 | 107 | 6.2477 | 4.8154
[7 empty] | 5820 | 108 | 7.7977 | 6.0747
[7 empty] | 5821 | 109 | 7.1464 | 5.5455
[7 empty] | 5822 | 110 | 6.7012 | 5.1838
[7 empty] | 5823 | 111 | 6.5446 | 5.0565
[7 empty] | 5824 | 112 | 6.6105 | 5.1101
[7 empty] | 5825 | 113 | 6.2725 | 4.8355
[7 empty] | 5826 | 114 | 6.4374 | 4.9694
[7 empty] | 5827 | 115 | 5.9922 | 4.6077
[7 empty] | 5828 | 116 | 6.66 | 5.1503
[7 empty] | 5829 | 117 | 6.2477 | 4.8154
[7 empty] | 5830 | 118 | 5.4892 | 4.1991
[7 empty] | 5831 | 119 | 3.9227 | 2.9264
[7 empty] | 5832 | 120 | 3.6106 | 2.6728
[7 empty] | 5833 | 121 | 2.8922 | 2.0891
[7 empty] | 5834 | 122 | 2.4882 | 1.7609
[7 empty] | 5835 | 123 | 2.4057 | 1.6939
[7 empty] | 5836 | 124 | 2.3727 | 1.6671
[7 empty] | 5837 | 125 | 2.3315 | 1.6336
[7 empty] | 5838 | 126 | 2.4717 | 1.7475
[7 empty] | 5839 | 127 | 3.9557 | 2.9532
[7 empty] | 5840 | 128 | 5.4892 | 4.1991
[7 empty] | 5841 | 129 | 6.1571 | 4.7417
[7 empty] | 5842 | 130 | 6.5858 | 5.09
[7 empty] | 5843 | 131 | 6.7424 | 5.2173
[7 empty] | 5844 | 132 | 6.4951 | 5.0163
[7 empty] | 5845 | 133 | 7.1217 | 5.5254
[7 empty] | 5846 | 134 | 7.4185 | 5.7666
[7 empty] | 5847 | 135 | 7.4844 | 5.8201
[7 empty] | 5848 | 136 | 6.6847 | 5.1704
[7 empty] | 5849 | 137 | 6.5858 | 5.09
[7 empty] | 5850 | 138 | 6.5363 | 5.0498
[7 empty] | 5851 | 139 | 6.2065 | 4.7819
[7 empty] | 5852 | 140 | 6.2148 | 4.7886
[7 empty] | 5853 | 141 | 5.5717 | 4.2661
[7 empty] | 5854 | 142 | 4.9451 | 3.757
[7 empty] | 5855 | 143 | 4.0794 | 3.0537
[7 empty] | 5856 | 144 | 3.4775 | 2.5647
[7 empty] | 5857 | 145 | 3.0158 | 2.1896
[7 empty] | 5858 | 146 | 2.8097 | 2.0221
[7 empty] | 5859 | 147 | 2.7438 | 1.9685
[7 empty] | 5860 | 148 | 2.7355 | 1.9618
[7 empty] | 5861 | 149 | 2.7355 | 1.9618
[7 empty] | 5862 | 150 | 2.7438 | 1.9685
[7 empty] | 5863 | 151 | 3.8073 | 2.8326
[7 empty] | 5864 | 152 | 5.3079 | 4.0517
[7 empty] | 5865 | 153 | 5.9097 | 4.5407
[7 empty] | 5866 | 154 | 6.4621 | 4.9895
[7 empty] | 5867 | 155 | 6.3137 | 4.869
[7 empty] | 5868 | 156 | 6.4786 | 5.0029
[7 empty] | 5869 | 157 | 7.1794 | 5.5723
[7 empty] | 5870 | 158 | 7.5009 | 5.8335
[7 empty] | 5871 | 159 | 7.7648 | 6.0479
[7 empty] | 5872 | 160 | 7.6411 | 5.9474
[7 empty] | 5873 | 161 | 8.3914 | 6.557
[7 empty] | 5874 | 162 | 7.9049 | 6.1618
[7 empty] | 5875 | 163 | 8.2594 | 6.4498
[7 empty] | 5876 | 164 | 6.9321 | 5.3713
[7 empty] | 5877 | 165 | 10.0073 | 7.8699
[7 empty] | 5878 | 166 | 7.9956 | 6.2354
[7 empty] | 5879 | 167 | 4.4504 | 3.3551
[7 empty] | 5880 | 168 | 3.8156 | 2.8393
[7 empty] | 5881 | 1 | 2.381 | 1.6738
[7 empty] | 5882 | 2 | 2.2738 | 1.5867
[7 empty] | 5883 | 3 | 2.2656 | 1.58
[7 empty] | 5884 | 4 | 2.3975 | 1.6872
[7 empty] | 5885 | 5 | 2.414 | 1.7006
[7 empty] | 5886 | 6 | 2.8345 | 2.0422
[7 empty] | 5887 | 7 | 3.5435 | 2.6183
[7 empty] | 5888 | 8 | 4.2031 | 3.1541
[7 empty] | 5889 | 9 | 4.1783 | 3.134
[7 empty] | 5890 | 10 | 5.6706 | 4.3465
[7 empty] | 5891 | 11 | 7.7153 | 6.0077
[7 empty] | 5892 | 12 | 8.6634 | 6.778
[7 empty] | 5893 | 13 | 9.0344 | 7.0795
[7 empty] | 5894 | 14 | 8.8201 | 6.9053
[7 empty] | 5895 | 15 | 8.7294 | 6.8316
[7 empty] | 5896 | 16 | 9.8919 | 7.7761
[7 empty] | 5897 | 17 | 11.1946 | 8.8345
[7 empty] | 5898 | 18 | 10.9555 | 8.6402
[7 empty] | 5899 | 19 | 11.4749 | 9.0622
[7 empty] | 5900 | 20 | 11.4089 | 9.0086
[7 empty] | 5901 | 21 | 11.9696 | 9.4641
[7 empty] | 5902 | 22 | 8.0781 | 6.3024
[7 empty] | 5903 | 23 | 4.368 | 3.2881
[7 empty] | 5904 | 24 | 2.724 | 1.9525
[7 empty] | 5905 | 25 | 2.6283 | 1.8747
[7 empty] | 5906 | 26 | 2.5212 | 1.7877
[7 empty] | 5907 | 27 | 2.4222 | 1.7073
[7 empty] | 5908 | 28 | 2.5047 | 1.7743
[7 empty] | 5909 | 29 | 2.7438 | 1.9685
[7 empty] | 5910 | 30 | 2.9829 | 2.1628
[7 empty] | 5911 | 31 | 3.8156 | 2.8393
[7 empty] | 5912 | 32 | 4.1618 | 3.1207
[7 empty] | 5913 | 33 | 4.8132 | 3.6498
[7 empty] | 5914 | 34 | 5.6954 | 4.3666
[7 empty] | 5915 | 35 | 7.8307 | 6.1015
[7 empty] | 5916 | 36 | 8.8448 | 6.9254
[7 empty] | 5917 | 37 | 8.919 | 6.9857
[7 empty] | 5918 | 38 | 8.9932 | 7.046
[7 empty] | 5919 | 39 | 8.6717 | 6.7847
[7 empty] | 5920 | 40 | 9.7105 | 7.6287
[7 empty] | 5921 | 41 | 10.2547 | 8.0708
[7 empty] | 5922 | 42 | 10.2711 | 8.0842
[7 empty] | 5923 | 43 | 10.6339 | 8.379
[7 empty] | 5924 | 44 | 11.7717 | 9.3034
[7 empty] | 5925 | 45 | 11.3759 | 8.9818
[7 empty] | 5926 | 46 | 8.6717 | 6.7847
[7 empty] | 5927 | 47 | 5.1265 | 3.9044
[7 empty] | 5928 | 48 | 3.6507 | 2.7053
[7 empty] | 5929 | 49 | 2.9993 | 2.1762
[7 empty] | 5930 | 50 | 2.6943 | 1.9283
[7 empty] | 5931 | 51 | 2.5871 | 1.8412
[7 empty] | 5932 | 52 | 2.6201 | 1.868
[7 empty] | 5933 | 53 | 2.6448 | 1.8881
[7 empty] | 5934 | 54 | 3.2137 | 2.3503
[7 empty] | 5935 | 55 | 4.335 | 3.2613
[7 empty] | 5936 | 56 | 4.5741 | 3.4556
[7 empty] | 5937 | 57 | 5.5057 | 4.2125
[7 empty] | 5938 | 58 | 6.594 | 5.0967
[7 empty] | 5939 | 59 | 7.7813 | 6.0613
[7 empty] | 5940 | 60 | 8.3996 | 6.5637
[7 empty] | 5941 | 61 | 9.0674 | 7.1063
[7 empty] | 5942 | 62 | 8.8696 | 6.9455
[7 empty] | 5943 | 63 | 9.4549 | 7.4211
[7 empty] | 5944 | 64 | 10.3866 | 8.178
[7 empty] | 5945 | 65 | 10.9967 | 8.6737
[7 empty] | 5946 | 66 | 10.8977 | 8.5933
[7 empty] | 5947 | 67 | 11.6233 | 9.1828
[7 empty] | 5948 | 68 | 11.8624 | 9.377
[7 empty] | 5949 | 69 | 11.3594 | 8.9684
[7 empty] | 5950 | 70 | 9.1004 | 7.133
[7 empty] | 5951 | 71 | 4.6565 | 3.5226
[7 empty] | 5952 | 72 | 3.5894 | 2.6556
[7 empty] | 5953 | 73 | 2.8839 | 2.0824
[7 empty] | 5954 | 74 | 2.6613 | 1.9015
[7 empty] | 5955 | 75 | 2.5624 | 1.8211
[7 empty] | 5956 | 76 | 2.5047 | 1.7743
[7 empty] | 5957 | 77 | 2.6778 | 1.9149
[7 empty] | 5958 | 78 | 3.0735 | 2.2365
[7 empty] | 5959 | 79 | 4.1701 | 3.1274
[7 empty] | 5960 | 80 | 4.3432 | 3.268
[7 empty] | 5961 | 81 | 5.5057 | 4.2125
[7 empty] | 5962 | 82 | 6.5775 | 5.0833
[7 empty] | 5963 | 83 | 7.3031 | 5.6728
[7 empty] | 5964 | 84 | 8.5233 | 6.6642
[7 empty] | 5965 | 85 | 8.2265 | 6.423
[7 empty] | 5966 | 86 | 7.7235 | 6.0144
[7 empty] | 5967 | 87 | 8.1605 | 6.3694
[7 empty] | 5968 | 88 | 8.8118 | 6.8986
[7 empty] | 5969 | 89 | 10.1392 | 7.9771
[7 empty] | 5970 | 90 | 9.5621 | 7.5082
[7 empty] | 5971 | 91 | 10.2382 | 8.0574
[7 empty] | 5972 | 92 | 9.6446 | 7.5751
[7 empty] | 5973 | 93 | 7.2701 | 5.646
[7 empty] | 5974 | 94 | 6.3797 | 4.9225
[7 empty] | 5975 | 95 | 4.5493 | 3.4355
[7 empty] | 5976 | 96 | 3.5765 | 2.6451
[7 empty] | 5977 | 97 | 3.527 | 2.6049
[7 empty] | 5978 | 98 | 3.2384 | 2.3704
[7 empty] | 5979 | 99 | 3.1807 | 2.3235
[7 empty] | 5980 | 100 | 2.8345 | 2.0422
[7 empty] | 5981 | 101 | 2.7767 | 1.9953
[7 empty] | 5982 | 102 | 3.0076 | 2.1829
[7 empty] | 5983 | 103 | 3.7414 | 2.779
[7 empty] | 5984 | 104 | 3.9887 | 2.98
[7 empty] | 5985 | 105 | 4.4669 | 3.3685
[7 empty] | 5986 | 106 | 5.9015 | 4.534
[7 empty] | 5987 | 107 | 6.2477 | 4.8154
[7 empty] | 5988 | 108 | 7.7977 | 6.0747
[7 empty] | 5989 | 109 | 7.1464 | 5.5455
[7 empty] | 5990 | 110 | 6.7012 | 5.1838
[7 empty] | 5991 | 111 | 6.5446 | 5.0565
[7 empty] | 5992 | 112 | 6.6105 | 5.1101
[7 empty] | 5993 | 113 | 6.2725 | 4.8355
[7 empty] | 5994 | 114 | 6.4374 | 4.9694
[7 empty] | 5995 | 115 | 5.9922 | 4.6077
[7 empty] | 5996 | 116 | 6.66 | 5.1503
[7 empty] | 5997 | 117 | 6.2477 | 4.8154
[7 empty] | 5998 | 118 | 5.4892 | 4.1991
[7 empty] | 5999 | 119 | 3.9227 | 2.9264
[7 empty] | 6000 | 120 | 3.6106 | 2.6728
[7 empty] | 6001 | 121 | 2.8922 | 2.0891
[7 empty] | 6002 | 122 | 2.4882 | 1.7609
[7 empty] | 6003 | 123 | 2.4057 | 1.6939
[7 empty] | 6004 | 124 | 2.3727 | 1.6671
[7 empty] | 6005 | 125 | 2.3315 | 1.6336
[7 empty] | 6006 | 126 | 2.4717 | 1.7475
[7 empty] | 6007 | 127 | 3.9557 | 2.9532
[7 empty] | 6008 | 128 | 5.4892 | 4.1991
[7 empty] | 6009 | 129 | 6.1571 | 4.7417
[7 empty] | 6010 | 130 | 6.5858 | 5.09
[7 empty] | 6011 | 131 | 6.7424 | 5.2173
[7 empty] | 6012 | 132 | 6.4951 | 5.0163
[7 empty] | 6013 | 133 | 7.1217 | 5.5254
[7 empty] | 6014 | 134 | 7.4185 | 5.7666
[7 empty] | 6015 | 135 | 7.4844 | 5.8201
[7 empty] | 6016 | 136 | 6.6847 | 5.1704
[7 empty] | 6017 | 137 | 6.5858 | 5.09
[7 empty] | 6018 | 138 | 6.5363 | 5.0498
[7 empty] | 6019 | 139 | 6.2065 | 4.7819
[7 empty] | 6020 | 140 | 6.2148 | 4.7886
[7 empty] | 6021 | 141 | 5.5717 | 4.2661
[7 empty] | 6022 | 142 | 4.9451 | 3.757
[7 empty] | 6023 | 143 | 4.0794 | 3.0537
[7 empty] | 6024 | 144 | 3.4775 | 2.5647
[7 empty] | 6025 | 145 | 3.0158 | 2.1896
[7 empty] | 6026 | 146 | 2.8097 | 2.0221
[7 empty] | 6027 | 147 | 2.7438 | 1.9685
[7 empty] | 6028 | 148 | 2.7355 | 1.9618
[7 empty] | 6029 | 149 | 2.7355 | 1.9618
[7 empty] | 6030 | 150 | 2.7438 | 1.9685
[7 empty] | 6031 | 151 | 3.8073 | 2.8326
[7 empty] | 6032 | 152 | 5.3079 | 4.0517
[7 empty] | 6033 | 153 | 5.9097 | 4.5407
[7 empty] | 6034 | 154 | 6.4621 | 4.9895
[7 empty] | 6035 | 155 | 6.3137 | 4.869
[7 empty] | 6036 | 156 | 6.4786 | 5.0029
[7 empty] | 6037 | 157 | 7.1794 | 5.5723
[7 empty] | 6038 | 158 | 7.5009 | 5.8335
[7 empty] | 6039 | 159 | 7.7648 | 6.0479
[7 empty] | 6040 | 160 | 7.6411 | 5.9474
[7 empty] | 6041 | 161 | 8.3914 | 6.557
[7 empty] | 6042 | 162 | 7.9049 | 6.1618
[7 empty] | 6043 | 163 | 8.2594 | 6.4498
[7 empty] | 6044 | 164 | 6.9321 | 5.3713
[7 empty] | 6045 | 165 | 10.0073 | 7.8699
[7 empty] | 6046 | 166 | 7.9956 | 6.2354
[7 empty] | 6047 | 167 | 4.4504 | 3.3551
[7 empty] | 6048 | 168 | 3.8156 | 2.8393
[7 empty] | 6049 | 1 | 2.381 | 1.6738
[7 empty] | 6050 | 2 | 2.2738 | 1.5867
[7 empty] | 6051 | 3 | 2.2656 | 1.58
[7 empty] | 6052 | 4 | 2.3975 | 1.6872
[7 empty] | 6053 | 5 | 2.414 | 1.7006
[7 empty] | 6054 | 6 | 2.8345 | 2.0422
[7 empty] | 6055 | 7 | 3.5435 | 2.6183
[7 empty] | 6056 | 8 | 4.2031 | 3.1541
[7 empty] | 6057 | 9 | 4.1783 | 3.134
[7 empty] | 6058 | 10 | 5.6706 | 4.3465
[7 empty] | 6059 | 11 | 7.7153 | 6.0077
[7 empty] | 6060 | 12 | 8.6634 | 6.778
[7 empty] | 6061 | 13 | 9.0344 | 7.0795
[7 empty] | 6062 | 14 | 8.8201 | 6.9053
[7 empty] | 6063 | 15 | 8.7294 | 6.8316
[7 empty] | 6064 | 16 | 9.8919 | 7.7761
[7 empty] | 6065 | 17 | 11.1946 | 8.8345
[7 empty] | 6066 | 18 | 10.9555 | 8.6402
[7 empty] | 6067 | 19 | 11.4749 | 9.0622
[7 empty] | 6068 | 20 | 11.4089 | 9.0086
[7 empty] | 6069 | 21 | 11.9696 | 9.4641
[7 empty] | 6070 | 22 | 8.0781 | 6.3024
[7 empty] | 6071 | 23 | 4.368 | 3.2881
[7 empty] | 6072 | 24 | 2.724 | 1.9525
[7 empty] | 6073 | 25 | 2.6283 | 1.8747
[7 empty] | 6074 | 26 | 2.5212 | 1.7877
[7 empty] | 6075 | 27 | 2.4222 | 1.7073
[7 empty] | 6076 | 28 | 2.5047 | 1.7743
[7 empty] | 6077 | 29 | 2.7438 | 1.9685
[7 empty] | 6078 | 30 | 2.9829 | 2.1628
[7 empty] | 6079 | 31 | 3.8156 | 2.8393
[7 empty] | 6080 | 32 | 4.1618 | 3.1207
[7 empty] | 6081 | 33 | 4.8132 | 3.6498
[7 empty] | 6082 | 34 | 5.6954 | 4.3666
[7 empty] | 6083 | 35 | 7.8307 | 6.1015
[7 empty] | 6084 | 36 | 8.8448 | 6.9254
[7 empty] | 6085 | 37 | 8.919 | 6.9857
[7 empty] | 6086 | 38 | 8.9932 | 7.046
[7 empty] | 6087 | 39 | 8.6717 | 6.7847
[7 empty] | 6088 | 40 | 9.7105 | 7.6287
[7 empty] | 6089 | 41 | 10.2547 | 8.0708
[7 empty] | 6090 | 42 | 10.2711 | 8.0842
[7 empty] | 6091 | 43 | 10.6339 | 8.379
[7 empty] | 6092 | 44 | 11.7717 | 9.3034
[7 empty] | 6093 | 45 | 11.3759 | 8.9818
[7 empty] | 6094 | 46 | 8.6717 | 6.7847
[7 empty] | 6095 | 47 | 5.1265 | 3.9044
[7 empty] | 6096 | 48 | 3.6507 | 2.7053
[7 empty] | 6097 | 49 | 2.9993 | 2.1762
[7 empty] | 6098 | 50 | 2.6943 | 1.9283
[7 empty] | 6099 | 51 | 2.5871 | 1.8412
[7 empty] | 6100 | 52 | 2.6201 | 1.868
[7 empty] | 6101 | 53 | 2.6448 | 1.8881
[7 empty] | 6102 | 54 | 3.2137 | 2.3503
[7 empty] | 6103 | 55 | 4.335 | 3.2613
[7 empty] | 6104 | 56 | 4.5741 | 3.4556
[7 empty] | 6105 | 57 | 5.5057 | 4.2125
[7 empty] | 6106 | 58 | 6.594 | 5.0967
[7 empty] | 6107 | 59 | 7.7813 | 6.0613
[7 empty] | 6108 | 60 | 8.3996 | 6.5637
[7 empty] | 6109 | 61 | 9.0674 | 7.1063
[7 empty] | 6110 | 62 | 8.8696 | 6.9455
[7 empty] | 6111 | 63 | 9.4549 | 7.4211
[7 empty] | 6112 | 64 | 10.3866 | 8.178
[7 empty] | 6113 | 65 | 10.9967 | 8.6737
[7 empty] | 6114 | 66 | 10.8977 | 8.5933
[7 empty] | 6115 | 67 | 11.6233 | 9.1828
[7 empty] | 6116 | 68 | 11.8624 | 9.377
[7 empty] | 6117 | 69 | 11.3594 | 8.9684
[7 empty] | 6118 | 70 | 9.1004 | 7.133
[7 empty] | 6119 | 71 | 4.6565 | 3.5226
[7 empty] | 6120 | 72 | 3.5894 | 2.6556
[7 empty] | 6121 | 73 | 2.8839 | 2.0824
[7 empty] | 6122 | 74 | 2.6613 | 1.9015
[7 empty] | 6123 | 75 | 2.5624 | 1.8211
[7 empty] | 6124 | 76 | 2.5047 | 1.7743
[7 empty] | 6125 | 77 | 2.6778 | 1.9149
[7 empty] | 6126 | 78 | 3.0735 | 2.2365
[7 empty] | 6127 | 79 | 4.1701 | 3.1274
[7 empty] | 6128 | 80 | 4.3432 | 3.268
[7 empty] | 6129 | 81 | 5.5057 | 4.2125
[7 empty] | 6130 | 82 | 6.5775 | 5.0833
[7 empty] | 6131 | 83 | 7.3031 | 5.6728
[7 empty] | 6132 | 84 | 8.5233 | 6.6642
[7 empty] | 6133 | 85 | 8.2265 | 6.423
[7 empty] | 6134 | 86 | 7.7235 | 6.0144
[7 empty] | 6135 | 87 | 8.1605 | 6.3694
[7 empty] | 6136 | 88 | 8.8118 | 6.8986
[7 empty] | 6137 | 89 | 10.1392 | 7.9771
[7 empty] | 6138 | 90 | 9.5621 | 7.5082
[7 empty] | 6139 | 91 | 10.2382 | 8.0574
[7 empty] | 6140 | 92 | 9.6446 | 7.5751
[7 empty] | 6141 | 93 | 7.2701 | 5.646
[7 empty] | 6142 | 94 | 6.3797 | 4.9225
[7 empty] | 6143 | 95 | 4.5493 | 3.4355
[7 empty] | 6144 | 96 | 3.5765 | 2.6451
[7 empty] | 6145 | 97 | 3.527 | 2.6049
[7 empty] | 6146 | 98 | 3.2384 | 2.3704
[7 empty] | 6147 | 99 | 3.1807 | 2.3235
[7 empty] | 6148 | 100 | 2.8345 | 2.0422
[7 empty] | 6149 | 101 | 2.7767 | 1.9953
[7 empty] | 6150 | 102 | 3.0076 | 2.1829
[7 empty] | 6151 | 103 | 3.7414 | 2.779
[7 empty] | 6152 | 104 | 3.9887 | 2.98
[7 empty] | 6153 | 105 | 4.4669 | 3.3685
[7 empty] | 6154 | 106 | 5.9015 | 4.534
[7 empty] | 6155 | 107 | 6.2477 | 4.8154
[7 empty] | 6156 | 108 | 7.7977 | 6.0747
[7 empty] | 6157 | 109 | 7.1464 | 5.5455
[7 empty] | 6158 | 110 | 6.7012 | 5.1838
[7 empty] | 6159 | 111 | 6.5446 | 5.0565
[7 empty] | 6160 | 112 | 6.6105 | 5.1101
[7 empty] | 6161 | 113 | 6.2725 | 4.8355
[7 empty] | 6162 | 114 | 6.4374 | 4.9694
[7 empty] | 6163 | 115 | 5.9922 | 4.6077
[7 empty] | 6164 | 116 | 6.66 | 5.1503
[7 empty] | 6165 | 117 | 6.2477 | 4.8154
[7 empty] | 6166 | 118 | 5.4892 | 4.1991
[7 empty] | 6167 | 119 | 3.9227 | 2.9264
[7 empty] | 6168 | 120 | 3.6106 | 2.6728
[7 empty] | 6169 | 121 | 2.8922 | 2.0891
[7 empty] | 6170 | 122 | 2.4882 | 1.7609
[7 empty] | 6171 | 123 | 2.4057 | 1.6939
[7 empty] | 6172 | 124 | 2.3727 | 1.6671
[7 empty] | 6173 | 125 | 2.3315 | 1.6336
[7 empty] | 6174 | 126 | 2.4717 | 1.7475
[7 empty] | 6175 | 127 | 3.9557 | 2.9532
[7 empty] | 6176 | 128 | 5.4892 | 4.1991
[7 empty] | 6177 | 129 | 6.1571 | 4.7417
[7 empty] | 6178 | 130 | 6.5858 | 5.09
[7 empty] | 6179 | 131 | 6.7424 | 5.2173
[7 empty] | 6180 | 132 | 6.4951 | 5.0163
[7 empty] | 6181 | 133 | 7.1217 | 5.5254
[7 empty] | 6182 | 134 | 7.4185 | 5.7666
[7 empty] | 6183 | 135 | 7.4844 | 5.8201
[7 empty] | 6184 | 136 | 6.6847 | 5.1704
[7 empty] | 6185 | 137 | 6.5858 | 5.09
[7 empty] | 6186 | 138 | 6.5363 | 5.0498
[7 empty] | 6187 | 139 | 6.2065 | 4.7819
[7 empty] | 6188 | 140 | 6.2148 | 4.7886
[7 empty] | 6189 | 141 | 5.5717 | 4.2661
[7 empty] | 6190 | 142 | 4.9451 | 3.757
[7 empty] | 6191 | 143 | 4.0794 | 3.0537
[7 empty] | 6192 | 144 | 3.4775 | 2.5647
[7 empty] | 6193 | 145 | 3.0158 | 2.1896
[7 empty] | 6194 | 146 | 2.8097 | 2.0221
[7 empty] | 6195 | 147 | 2.7438 | 1.9685
[7 empty] | 6196 | 148 | 2.7355 | 1.9618
[7 empty] | 6197 | 149 | 2.7355 | 1.9618
[7 empty] | 6198 | 150 | 2.7438 | 1.9685
[7 empty] | 6199 | 151 | 3.8073 | 2.8326
[7 empty] | 6200 | 152 | 5.3079 | 4.0517
[7 empty] | 6201 | 153 | 5.9097 | 4.5407
[7 empty] | 6202 | 154 | 6.4621 | 4.9895
[7 empty] | 6203 | 155 | 6.3137 | 4.869
[7 empty] | 6204 | 156 | 6.4786 | 5.0029
[7 empty] | 6205 | 157 | 7.1794 | 5.5723
[7 empty] | 6206 | 158 | 7.5009 | 5.8335
[7 empty] | 6207 | 159 | 7.7648 | 6.0479
[7 empty] | 6208 | 160 | 7.6411 | 5.9474
[7 empty] | 6209 | 161 | 8.3914 | 6.557
[7 empty] | 6210 | 162 | 7.9049 | 6.1618
[7 empty] | 6211 | 163 | 8.2594 | 6.4498
[7 empty] | 6212 | 164 | 6.9321 | 5.3713
[7 empty] | 6213 | 165 | 10.0073 | 7.8699
[7 empty] | 6214 | 166 | 7.9956 | 6.2354
[7 empty] | 6215 | 167 | 4.4504 | 3.3551
[7 empty] | 6216 | 168 | 3.8156 | 2.8393
[7 empty] | 6217 | 1 | 2.381 | 1.6738
[7 empty] | 6218 | 2 | 2.2738 | 1.5867
[7 empty] | 6219 | 3 | 2.2656 | 1.58
[7 empty] | 6220 | 4 | 2.3975 | 1.6872
[7 empty] | 6221 | 5 | 2.414 | 1.7006
[7 empty] | 6222 | 6 | 2.8345 | 2.0422
[7 empty] | 6223 | 7 | 3.5435 | 2.6183
[7 empty] | 6224 | 8 | 4.2031 | 3.1541
[7 empty] | 6225 | 9 | 4.1783 | 3.134
[7 empty] | 6226 | 10 | 5.6706 | 4.3465
[7 empty] | 6227 | 11 | 7.7153 | 6.0077
[7 empty] | 6228 | 12 | 8.6634 | 6.778
[7 empty] | 6229 | 13 | 9.0344 | 7.0795
[7 empty] | 6230 | 14 | 8.8201 | 6.9053
[7 empty] | 6231 | 15 | 8.7294 | 6.8316
[7 empty] | 6232 | 16 | 9.8919 | 7.7761
[7 empty] | 6233 | 17 | 11.1946 | 8.8345
[7 empty] | 6234 | 18 | 10.9555 | 8.6402
[7 empty] | 6235 | 19 | 11.4749 | 9.0622
[7 empty] | 6236 | 20 | 11.4089 | 9.0086
[7 empty] | 6237 | 21 | 11.9696 | 9.4641
[7 empty] | 6238 | 22 | 8.0781 | 6.3024
[7 empty] | 6239 | 23 | 4.368 | 3.2881
[7 empty] | 6240 | 24 | 2.724 | 1.9525
[7 empty] | 6241 | 25 | 2.6283 | 1.8747
[7 empty] | 6242 | 26 | 2.5212 | 1.7877
[7 empty] | 6243 | 27 | 2.4222 | 1.7073
[7 empty] | 6244 | 28 | 2.5047 | 1.7743
[7 empty] | 6245 | 29 | 2.7438 | 1.9685
[7 empty] | 6246 | 30 | 2.9829 | 2.1628
[7 empty] | 6247 | 31 | 3.8156 | 2.8393
[7 empty] | 6248 | 32 | 4.1618 | 3.1207
[7 empty] | 6249 | 33 | 4.8132 | 3.6498
[7 empty] | 6250 | 34 | 5.6954 | 4.3666
[7 empty] | 6251 | 35 | 7.8307 | 6.1015
[7 empty] | 6252 | 36 | 8.8448 | 6.9254
[7 empty] | 6253 | 37 | 8.919 | 6.9857
[7 empty] | 6254 | 38 | 8.9932 | 7.046
[7 empty] | 6255 | 39 | 8.6717 | 6.7847
[7 empty] | 6256 | 40 | 9.7105 | 7.6287
[7 empty] | 6257 | 41 | 10.2547 | 8.0708
[7 empty] | 6258 | 42 | 10.2711 | 8.0842
[7 empty] | 6259 | 43 | 10.6339 | 8.379
[7 empty] | 6260 | 44 | 11.7717 | 9.3034
[7 empty] | 6261 | 45 | 11.3759 | 8.9818
[7 empty] | 6262 | 46 | 8.6717 | 6.7847
[7 empty] | 6263 | 47 | 5.1265 | 3.9044
[7 empty] | 6264 | 48 | 3.6507 | 2.7053
[7 empty] | 6265 | 49 | 2.9993 | 2.1762
[7 empty] | 6266 | 50 | 2.6943 | 1.9283
[7 empty] | 6267 | 51 | 2.5871 | 1.8412
[7 empty] | 6268 | 52 | 2.6201 | 1.868
[7 empty] | 6269 | 53 | 2.6448 | 1.8881
[7 empty] | 6270 | 54 | 3.2137 | 2.3503
[7 empty] | 6271 | 55 | 4.335 | 3.2613
[7 empty] | 6272 | 56 | 4.5741 | 3.4556
[7 empty] | 6273 | 57 | 5.5057 | 4.2125
[7 empty] | 6274 | 58 | 6.594 | 5.0967
[7 empty] | 6275 | 59 | 7.7813 | 6.0613
[7 empty] | 6276 | 60 | 8.3996 | 6.5637
[7 empty] | 6277 | 61 | 9.0674 | 7.1063
[7 empty] | 6278 | 62 | 8.8696 | 6.9455
[7 empty] | 6279 | 63 | 9.4549 | 7.4211
[7 empty] | 6280 | 64 | 10.3866 | 8.178
[7 empty] | 6281 | 65 | 10.9967 | 8.6737
[7 empty] | 6282 | 66 | 10.8977 | 8.5933
[7 empty] | 6283 | 67 | 11.6233 | 9.1828
[7 empty] | 6284 | 68 | 11.8624 | 9.377
[7 empty] | 6285 | 69 | 11.3594 | 8.9684
[7 empty] | 6286 | 70 | 9.1004 | 7.133
[7 empty] | 6287 | 71 | 4.6565 | 3.5226
[7 empty] | 6288 | 72 | 3.5894 | 2.6556
[7 empty] | 6289 | 73 | 2.8839 | 2.0824
[7 empty] | 6290 | 74 | 2.6613 | 1.9015
[7 empty] | 6291 | 75 | 2.5624 | 1.8211
[7 empty] | 6292 | 76 | 2.5047 | 1.7743
[7 empty] | 6293 | 77 | 2.6778 | 1.9149
[7 empty] | 6294 | 78 | 3.0735 | 2.2365
[7 empty] | 6295 | 79 | 4.1701 | 3.1274
[7 empty] | 6296 | 80 | 4.3432 | 3.268
[7 empty] | 6297 | 81 | 5.5057 | 4.2125
[7 empty] | 6298 | 82 | 6.5775 | 5.0833
[7 empty] | 6299 | 83 | 7.3031 | 5.6728
[7 empty] | 6300 | 84 | 8.5233 | 6.6642
[7 empty] | 6301 | 85 | 8.2265 | 6.423
[7 empty] | 6302 | 86 | 7.7235 | 6.0144
[7 empty] | 6303 | 87 | 8.1605 | 6.3694
[7 empty] | 6304 | 88 | 8.8118 | 6.8986
[7 empty] | 6305 | 89 | 10.1392 | 7.9771
[7 empty] | 6306 | 90 | 9.5621 | 7.5082
[7 empty] | 6307 | 91 | 10.2382 | 8.0574
[7 empty] | 6308 | 92 | 9.6446 | 7.5751
[7 empty] | 6309 | 93 | 7.2701 | 5.646
[7 empty] | 6310 | 94 | 6.3797 | 4.9225
[7 empty] | 6311 | 95 | 4.5493 | 3.4355
[7 empty] | 6312 | 96 | 3.5765 | 2.6451
[7 empty] | 6313 | 97 | 3.527 | 2.6049
[7 empty] | 6314 | 98 | 3.2384 | 2.3704
[7 empty] | 6315 | 99 | 3.1807 | 2.3235
[7 empty] | 6316 | 100 | 2.8345 | 2.0422
[7 empty] | 6317 | 101 | 2.7767 | 1.9953
[7 empty] | 6318 | 102 | 3.0076 | 2.1829
[7 empty] | 6319 | 103 | 3.7414 | 2.779
[7 empty] | 6320 | 104 | 3.9887 | 2.98
[7 empty] | 6321 | 105 | 4.4669 | 3.3685
[7 empty] | 6322 | 106 | 5.9015 | 4.534
[7 empty] | 6323 | 107 | 6.2477 | 4.8154
[7 empty] | 6324 | 108 | 7.7977 | 6.0747
[7 empty] | 6325 | 109 | 7.1464 | 5.5455
[7 empty] | 6326 | 110 | 6.7012 | 5.1838
[7 empty] | 6327 | 111 | 6.5446 | 5.0565
[7 empty] | 6328 | 112 | 6.6105 | 5.1101
[7 empty] | 6329 | 113 | 6.2725 | 4.8355
[7 empty] | 6330 | 114 | 6.4374 | 4.9694
[7 empty] | 6331 | 115 | 5.9922 | 4.6077
[7 empty] | 6332 | 116 | 6.66 | 5.1503
[7 empty] | 6333 | 117 | 6.2477 | 4.8154
[7 empty] | 6334 | 118 | 5.4892 | 4.1991
[7 empty] | 6335 | 119 | 3.9227 | 2.9264
[7 empty] | 6336 | 120 | 3.6106 | 2.6728
[7 empty] | 6337 | 121 | 2.8922 | 2.0891
[7 empty] | 6338 | 122 | 2.4882 | 1.7609
[7 empty] | 6339 | 123 | 2.4057 | 1.6939
[7 empty] | 6340 | 124 | 2.3727 | 1.6671
[7 empty] | 6341 | 125 | 2.3315 | 1.6336
[7 empty] | 6342 | 126 | 2.4717 | 1.7475
[7 empty] | 6343 | 127 | 3.9557 | 2.9532
[7 empty] | 6344 | 128 | 5.4892 | 4.1991
[7 empty] | 6345 | 129 | 6.1571 | 4.7417
[7 empty] | 6346 | 130 | 6.5858 | 5.09
[7 empty] | 6347 | 131 | 6.7424 | 5.2173
[7 empty] | 6348 | 132 | 6.4951 | 5.0163
[7 empty] | 6349 | 133 | 7.1217 | 5.5254
[7 empty] | 6350 | 134 | 7.4185 | 5.7666
[7 empty] | 6351 | 135 | 7.4844 | 5.8201
[7 empty] | 6352 | 136 | 6.6847 | 5.1704
[7 empty] | 6353 | 137 | 6.5858 | 5.09
[7 empty] | 6354 | 138 | 6.5363 | 5.0498
[7 empty] | 6355 | 139 | 6.2065 | 4.7819
[7 empty] | 6356 | 140 | 6.2148 | 4.7886
[7 empty] | 6357 | 141 | 5.5717 | 4.2661
[7 empty] | 6358 | 142 | 4.9451 | 3.757
[7 empty] | 6359 | 143 | 4.0794 | 3.0537
[7 empty] | 6360 | 144 | 3.4775 | 2.5647
[7 empty] | 6361 | 145 | 3.0158 | 2.1896
[7 empty] | 6362 | 146 | 2.8097 | 2.0221
[7 empty] | 6363 | 147 | 2.7438 | 1.9685
[7 empty] | 6364 | 148 | 2.7355 | 1.9618
[7 empty] | 6365 | 149 | 2.7355 | 1.9618
[7 empty] | 6366 | 150 | 2.7438 | 1.9685
[7 empty] | 6367 | 151 | 3.8073 | 2.8326
[7 empty] | 6368 | 152 | 5.3079 | 4.0517
[7 empty] | 6369 | 153 | 5.9097 | 4.5407
[7 empty] | 6370 | 154 | 6.4621 | 4.9895
[7 empty] | 6371 | 155 | 6.3137 | 4.869
[7 empty] | 6372 | 156 | 6.4786 | 5.0029
[7 empty] | 6373 | 157 | 7.1794 | 5.5723
[7 empty] | 6374 | 158 | 7.5009 | 5.8335
[7 empty] | 6375 | 159 | 7.7648 | 6.0479
[7 empty] | 6376 | 160 | 7.6411 | 5.9474
[7 empty] | 6377 | 161 | 8.3914 | 6.557
[7 empty] | 6378 | 162 | 7.9049 | 6.1618
[7 empty] | 6379 | 163 | 8.2594 | 6.4498
[7 empty] | 6380 | 164 | 6.9321 | 5.3713
[7 empty] | 6381 | 165 | 10.0073 | 7.8699
[7 empty] | 6382 | 166 | 7.9956 | 6.2354
[7 empty] | 6383 | 167 | 4.4504 | 3.3551
[7 empty] | 6384 | 168 | 3.8156 | 2.8393
[7 empty] | 6385 | 1 | 2.381 | 1.6738
[7 empty] | 6386 | 2 | 2.2738 | 1.5867
[7 empty] | 6387 | 3 | 2.2656 | 1.58
[7 empty] | 6388 | 4 | 2.3975 | 1.6872
[7 empty] | 6389 | 5 | 2.414 | 1.7006
[7 empty] | 6390 | 6 | 2.8345 | 2.0422
[7 empty] | 6391 | 7 | 3.5435 | 2.6183
[7 empty] | 6392 | 8 | 4.2031 | 3.1541
[7 empty] | 6393 | 9 | 4.1783 | 3.134
[7 empty] | 6394 | 10 | 5.6706 | 4.3465
[7 empty] | 6395 | 11 | 7.7153 | 6.0077
[7 empty] | 6396 | 12 | 8.6634 | 6.778
[7 empty] | 6397 | 13 | 9.0344 | 7.0795
[7 empty] | 6398 | 14 | 8.8201 | 6.9053
[7 empty] | 6399 | 15 | 8.7294 | 6.8316
[7 empty] | 6400 | 16 | 9.8919 | 7.7761
[7 empty] | 6401 | 17 | 11.1946 | 8.8345
[7 empty] | 6402 | 18 | 10.9555 | 8.6402
[7 empty] | 6403 | 19 | 11.4749 | 9.0622
[7 empty] | 6404 | 20 | 11.4089 | 9.0086
[7 empty] | 6405 | 21 | 11.9696 | 9.4641
[7 empty] | 6406 | 22 | 8.0781 | 6.3024
[7 empty] | 6407 | 23 | 4.368 | 3.2881
[7 empty] | 6408 | 24 | 2.724 | 1.9525
[7 empty] | 6409 | 25 | 2.6283 | 1.8747
[7 empty] | 6410 | 26 | 2.5212 | 1.7877
[7 empty] | 6411 | 27 | 2.4222 | 1.7073
[7 empty] | 6412 | 28 | 2.5047 | 1.7743
[7 empty] | 6413 | 29 | 2.7438 | 1.9685
[7 empty] | 6414 | 30 | 2.9829 | 2.1628
[7 empty] | 6415 | 31 | 3.8156 | 2.8393
[7 empty] | 6416 | 32 | 4.1618 | 3.1207
[7 empty] | 6417 | 33 | 4.8132 | 3.6498
[7 empty] | 6418 | 34 | 5.6954 | 4.3666
[7 empty] | 6419 | 35 | 7.8307 | 6.1015
[7 empty] | 6420 | 36 | 8.8448 | 6.9254
[7 empty] | 6421 | 37 | 8.919 | 6.9857
[7 empty] | 6422 | 38 | 8.9932 | 7.046
[7 empty] | 6423 | 39 | 8.6717 | 6.7847
[7 empty] | 6424 | 40 | 9.7105 | 7.6287
[7 empty] | 6425 | 41 | 10.2547 | 8.0708
[7 empty] | 6426 | 42 | 10.2711 | 8.0842
[7 empty] | 6427 | 43 | 10.6339 | 8.379
[7 empty] | 6428 | 44 | 11.7717 | 9.3034
[7 empty] | 6429 | 45 | 11.3759 | 8.9818
[7 empty] | 6430 | 46 | 8.6717 | 6.7847
[7 empty] | 6431 | 47 | 5.1265 | 3.9044
[7 empty] | 6432 | 48 | 3.6507 | 2.7053
[7 empty] | 6433 | 49 | 2.9993 | 2.1762
[7 empty] | 6434 | 50 | 2.6943 | 1.9283
[7 empty] | 6435 | 51 | 2.5871 | 1.8412
[7 empty] | 6436 | 52 | 2.6201 | 1.868
[7 empty] | 6437 | 53 | 2.6448 | 1.8881
[7 empty] | 6438 | 54 | 3.2137 | 2.3503
[7 empty] | 6439 | 55 | 4.335 | 3.2613
[7 empty] | 6440 | 56 | 4.5741 | 3.4556
[7 empty] | 6441 | 57 | 5.5057 | 4.2125
[7 empty] | 6442 | 58 | 6.594 | 5.0967
[7 empty] | 6443 | 59 | 7.7813 | 6.0613
[7 empty] | 6444 | 60 | 8.3996 | 6.5637
[7 empty] | 6445 | 61 | 9.0674 | 7.1063
[7 empty] | 6446 | 62 | 8.8696 | 6.9455
[7 empty] | 6447 | 63 | 9.4549 | 7.4211
[7 empty] | 6448 | 64 | 10.3866 | 8.178
[7 empty] | 6449 | 65 | 10.9967 | 8.6737
[7 empty] | 6450 | 66 | 10.8977 | 8.5933
[7 empty] | 6451 | 67 | 11.6233 | 9.1828
[7 empty] | 6452 | 68 | 11.8624 | 9.377
[7 empty] | 6453 | 69 | 11.3594 | 8.9684
[7 empty] | 6454 | 70 | 9.1004 | 7.133
[7 empty] | 6455 | 71 | 4.6565 | 3.5226
[7 empty] | 6456 | 72 | 3.5894 | 2.6556
[7 empty] | 6457 | 73 | 2.8839 | 2.0824
[7 empty] | 6458 | 74 | 2.6613 | 1.9015
[7 empty] | 6459 | 75 | 2.5624 | 1.8211
[7 empty] | 6460 | 76 | 2.5047 | 1.7743
[7 empty] | 6461 | 77 | 2.6778 | 1.9149
[7 empty] | 6462 | 78 | 3.0735 | 2.2365
[7 empty] | 6463 | 79 | 4.1701 | 3.1274
[7 empty] | 6464 | 80 | 4.3432 | 3.268
[7 empty] | 6465 | 81 | 5.5057 | 4.2125
[7 empty] | 6466 | 82 | 6.5775 | 5.0833
[7 empty] | 6467 | 83 | 7.3031 | 5.6728
[7 empty] | 6468 | 84 | 8.5233 | 6.6642
[7 empty] | 6469 | 85 | 8.2265 | 6.423
[7 empty] | 6470 | 86 | 7.7235 | 6.0144
[7 empty] | 6471 | 87 | 8.1605 | 6.3694
[7 empty] | 6472 | 88 | 8.8118 | 6.8986
[7 empty] | 6473 | 89 | 10.1392 | 7.9771
[7 empty] | 6474 | 90 | 9.5621 | 7.5082
[7 empty] | 6475 | 91 | 10.2382 | 8.0574
[7 empty] | 6476 | 92 | 9.6446 | 7.5751
[7 empty] | 6477 | 93 | 7.2701 | 5.646
[7 empty] | 6478 | 94 | 6.3797 | 4.9225
[7 empty] | 6479 | 95 | 4.5493 | 3.4355
[7 empty] | 6480 | 96 | 3.5765 | 2.6451
[7 empty] | 6481 | 97 | 3.527 | 2.6049
[7 empty] | 6482 | 98 | 3.2384 | 2.3704
[7 empty] | 6483 | 99 | 3.1807 | 2.3235
[7 empty] | 6484 | 100 | 2.8345 | 2.0422
[7 empty] | 6485 | 101 | 2.7767 | 1.9953
[7 empty] | 6486 | 102 | 3.0076 | 2.1829
[7 empty] | 6487 | 103 | 3.7414 | 2.779
[7 empty] | 6488 | 104 | 3.9887 | 2.98
[7 empty] | 6489 | 105 | 4.4669 | 3.3685
[7 empty] | 6490 | 106 | 5.9015 | 4.534
[7 empty] | 6491 | 107 | 6.2477 | 4.8154
[7 empty] | 6492 | 108 | 7.7977 | 6.0747
[7 empty] | 6493 | 109 | 7.1464 | 5.5455
[7 empty] | 6494 | 110 | 6.7012 | 5.1838
[7 empty] | 6495 | 111 | 6.5446 | 5.0565
[7 empty] | 6496 | 112 | 6.6105 | 5.1101
[7 empty] | 6497 | 113 | 6.2725 | 4.8355
[7 empty] | 6498 | 114 | 6.4374 | 4.9694
[7 empty] | 6499 | 115 | 5.9922 | 4.6077
[7 empty] | 6500 | 116 | 6.66 | 5.1503
[7 empty] | 6501 | 117 | 6.2477 | 4.8154
[7 empty] | 6502 | 118 | 5.4892 | 4.1991
[7 empty] | 6503 | 119 | 3.9227 | 2.9264
[7 empty] | 6504 | 120 | 3.6106 | 2.6728
[7 empty] | 6505 | 121 | 2.8922 | 2.0891
[7 empty] | 6506 | 122 | 2.4882 | 1.7609
[7 empty] | 6507 | 123 | 2.4057 | 1.6939
[7 empty] | 6508 | 124 | 2.3727 | 1.6671
[7 empty] | 6509 | 125 | 2.3315 | 1.6336
[7 empty] | 6510 | 126 | 2.4717 | 1.7475
[7 empty] | 6511 | 127 | 3.9557 | 2.9532
[7 empty] | 6512 | 128 | 5.4892 | 4.1991
[7 empty] | 6513 | 129 | 6.1571 | 4.7417
[7 empty] | 6514 | 130 | 6.5858 | 5.09
[7 empty] | 6515 | 131 | 6.7424 | 5.2173
[7 empty] | 6516 | 132 | 6.4951 | 5.0163
[7 empty] | 6517 | 133 | 7.1217 | 5.5254
[7 empty] | 6518 | 134 | 7.4185 | 5.7666
[7 empty] | 6519 | 135 | 7.4844 | 5.8201
[7 empty] | 6520 | 136 | 6.6847 | 5.1704
[7 empty] | 6521 | 137 | 6.5858 | 5.09
[7 empty] | 6522 | 138 | 6.5363 | 5.0498
[7 empty] | 6523 | 139 | 6.2065 | 4.7819
[7 empty] | 6524 | 140 | 6.2148 | 4.7886
[7 empty] | 6525 | 141 | 5.5717 | 4.2661
[7 empty] | 6526 | 142 | 4.9451 | 3.757
[7 empty] | 6527 | 143 | 4.0794 | 3.0537
[7 empty] | 6528 | 144 | 3.4775 | 2.5647
[7 empty] | 6529 | 145 | 3.0158 | 2.1896
[7 empty] | 6530 | 146 | 2.8097 | 2.0221
[7 empty] | 6531 | 147 | 2.7438 | 1.9685
[7 empty] | 6532 | 148 | 2.7355 | 1.9618
[7 empty] | 6533 | 149 | 2.7355 | 1.9618
[7 empty] | 6534 | 150 | 2.7438 | 1.9685
[7 empty] | 6535 | 151 | 3.8073 | 2.8326
[7 empty] | 6536 | 152 | 5.3079 | 4.0517
[7 empty] | 6537 | 153 | 5.9097 | 4.5407
[7 empty] | 6538 | 154 | 6.4621 | 4.9895
[7 empty] | 6539 | 155 | 6.3137 | 4.869
[7 empty] | 6540 | 156 | 6.4786 | 5.0029
[7 empty] | 6541 | 157 | 7.1794 | 5.5723
[7 empty] | 6542 | 158 | 7.5009 | 5.8335
[7 empty] | 6543 | 159 | 7.7648 | 6.0479
[7 empty] | 6544 | 160 | 7.6411 | 5.9474
[7 empty] | 6545 | 161 | 8.3914 | 6.557
[7 empty] | 6546 | 162 | 7.9049 | 6.1618
[7 empty] | 6547 | 163 | 8.2594 | 6.4498
[7 empty] | 6548 | 164 | 6.9321 | 5.3713
[7 empty] | 6549 | 165 | 10.0073 | 7.8699
[7 empty] | 6550 | 166 | 7.9956 | 6.2354
[7 empty] | 6551 | 167 | 4.4504 | 3.3551
[7 empty] | 6552 | 168 | 3.8156 | 2.8393
[7 empty] | 6553 | 1 | 2.381 | 1.6738
[7 empty] | 6554 | 2 | 2.2738 | 1.5867
[7 empty] | 6555 | 3 | 2.2656 | 1.58
[7 empty] | 6556 | 4 | 2.3975 | 1.6872
[7 empty] | 6557 | 5 | 2.414 | 1.7006
[7 empty] | 6558 | 6 | 2.8345 | 2.0422
[7 empty] | 6559 | 7 | 3.5435 | 2.6183
[7 empty] | 6560 | 8 | 4.2031 | 3.1541
[7 empty] | 6561 | 9 | 4.1783 | 3.134
[7 empty] | 6562 | 10 | 5.6706 | 4.3465
[7 empty] | 6563 | 11 | 7.7153 | 6.0077
[7 empty] | 6564 | 12 | 8.6634 | 6.778
[7 empty] | 6565 | 13 | 9.0344 | 7.0795
[7 empty] | 6566 | 14 | 8.8201 | 6.9053
[7 empty] | 6567 | 15 | 8.7294 | 6.8316
[7 empty] | 6568 | 16 | 9.8919 | 7.7761
[7 empty] | 6569 | 17 | 11.1946 | 8.8345
[7 empty] | 6570 | 18 | 10.9555 | 8.6402
[7 empty] | 6571 | 19 | 11.4749 | 9.0622
[7 empty] | 6572 | 20 | 11.4089 | 9.0086
[7 empty] | 6573 | 21 | 11.9696 | 9.4641
[7 empty] | 6574 | 22 | 8.0781 | 6.3024
[7 empty] | 6575 | 23 | 4.368 | 3.2881
[7 empty] | 6576 | 24 | 2.724 | 1.9525
[7 empty] | 6577 | 25 | 2.6283 | 1.8747
[7 empty] | 6578 | 26 | 2.5212 | 1.7877
[7 empty] | 6579 | 27 | 2.4222 | 1.7073
[7 empty] | 6580 | 28 | 2.5047 | 1.7743
[7 empty] | 6581 | 29 | 2.7438 | 1.9685
[7 empty] | 6582 | 30 | 2.9829 | 2.1628
[7 empty] | 6583 | 31 | 3.8156 | 2.8393
[7 empty] | 6584 | 32 | 4.1618 | 3.1207
[7 empty] | 6585 | 33 | 4.8132 | 3.6498
[7 empty] | 6586 | 34 | 5.6954 | 4.3666
[7 empty] | 6587 | 35 | 7.8307 | 6.1015
[7 empty] | 6588 | 36 | 8.8448 | 6.9254
[7 empty] | 6589 | 37 | 8.919 | 6.9857
[7 empty] | 6590 | 38 | 8.9932 | 7.046
[7 empty] | 6591 | 39 | 8.6717 | 6.7847
[7 empty] | 6592 | 40 | 9.7105 | 7.6287
[7 empty] | 6593 | 41 | 10.2547 | 8.0708
[7 empty] | 6594 | 42 | 10.2711 | 8.0842
[7 empty] | 6595 | 43 | 10.6339 | 8.379
[7 empty] | 6596 | 44 | 11.7717 | 9.3034
[7 empty] | 6597 | 45 | 11.3759 | 8.9818
[7 empty] | 6598 | 46 | 8.6717 | 6.7847
[7 empty] | 6599 | 47 | 5.1265 | 3.9044
[7 empty] | 6600 | 48 | 3.6507 | 2.7053
[7 empty] | 6601 | 49 | 2.9993 | 2.1762
[7 empty] | 6602 | 50 | 2.6943 | 1.9283
[7 empty] | 6603 | 51 | 2.5871 | 1.8412
[7 empty] | 6604 | 52 | 2.6201 | 1.868
[7 empty] | 6605 | 53 | 2.6448 | 1.8881
[7 empty] | 6606 | 54 | 3.2137 | 2.3503
[7 empty] | 6607 | 55 | 4.335 | 3.2613
[7 empty] | 6608 | 56 | 4.5741 | 3.4556
[7 empty] | 6609 | 57 | 5.5057 | 4.2125
[7 empty] | 6610 | 58 | 6.594 | 5.0967
[7 empty] | 6611 | 59 | 7.7813 | 6.0613
[7 empty] | 6612 | 60 | 8.3996 | 6.5637
[7 empty] | 6613 | 61 | 9.0674 | 7.1063
[7 empty] | 6614 | 62 | 8.8696 | 6.9455
[7 empty] | 6615 | 63 | 9.4549 | 7.4211
[7 empty] | 6616 | 64 | 10.3866 | 8.178
[7 empty] | 6617 | 65 | 10.9967 | 8.6737
[7 empty] | 6618 | 66 | 10.8977 | 8.5933
[7 empty] | 6619 | 67 | 11.6233 | 9.1828
[7 empty] | 6620 | 68 | 11.8624 | 9.377
[7 empty] | 6621 | 69 | 11.3594 | 8.9684
[7 empty] | 6622 | 70 | 9.1004 | 7.133
[7 empty] | 6623 | 71 | 4.6565 | 3.5226
[7 empty] | 6624 | 72 | 3.5894 | 2.6556
[7 empty] | 6625 | 73 | 2.8839 | 2.0824
[7 empty] | 6626 | 74 | 2.6613 | 1.9015
[7 empty] | 6627 | 75 | 2.5624 | 1.8211
[7 empty] | 6628 | 76 | 2.5047 | 1.7743
[7 empty] | 6629 | 77 | 2.6778 | 1.9149
[7 empty] | 6630 | 78 | 3.0735 | 2.2365
[7 empty] | 6631 | 79 | 4.1701 | 3.1274
[7 empty] | 6632 | 80 | 4.3432 | 3.268
[7 empty] | 6633 | 81 | 5.5057 | 4.2125
[7 empty] | 6634 | 82 | 6.5775 | 5.0833
[7 empty] | 6635 | 83 | 7.3031 | 5.6728
[7 empty] | 6636 | 84 | 8.5233 | 6.6642
[7 empty] | 6637 | 85 | 8.2265 | 6.423
[7 empty] | 6638 | 86 | 7.7235 | 6.0144
[7 empty] | 6639 | 87 | 8.1605 | 6.3694
[7 empty] | 6640 | 88 | 8.8118 | 6.8986
[7 empty] | 6641 | 89 | 10.1392 | 7.9771
[7 empty] | 6642 | 90 | 9.5621 | 7.5082
[7 empty] | 6643 | 91 | 10.2382 | 8.0574
[7 empty] | 6644 | 92 | 9.6446 | 7.5751
[7 empty] | 6645 | 93 | 7.2701 | 5.646
[7 empty] | 6646 | 94 | 6.3797 | 4.9225
[7 empty] | 6647 | 95 | 4.5493 | 3.4355
[7 empty] | 6648 | 96 | 3.5765 | 2.6451
[7 empty] | 6649 | 97 | 3.527 | 2.6049
[7 empty] | 6650 | 98 | 3.2384 | 2.3704
[7 empty] | 6651 | 99 | 3.1807 | 2.3235
[7 empty] | 6652 | 100 | 2.8345 | 2.0422
[7 empty] | 6653 | 101 | 2.7767 | 1.9953
[7 empty] | 6654 | 102 | 3.0076 | 2.1829
[7 empty] | 6655 | 103 | 3.7414 | 2.779
[7 empty] | 6656 | 104 | 3.9887 | 2.98
[7 empty] | 6657 | 105 | 4.4669 | 3.3685
[7 empty] | 6658 | 106 | 5.9015 | 4.534
[7 empty] | 6659 | 107 | 6.2477 | 4.8154
[7 empty] | 6660 | 108 | 7.7977 | 6.0747
[7 empty] | 6661 | 109 | 7.1464 | 5.5455
[7 empty] | 6662 | 110 | 6.7012 | 5.1838
[7 empty] | 6663 | 111 | 6.5446 | 5.0565
[7 empty] | 6664 | 112 | 6.6105 | 5.1101
[7 empty] | 6665 | 113 | 6.2725 | 4.8355
[7 empty] | 6666 | 114 | 6.4374 | 4.9694
[7 empty] | 6667 | 115 | 5.9922 | 4.6077
[7 empty] | 6668 | 116 | 6.66 | 5.1503
[7 empty] | 6669 | 117 | 6.2477 | 4.8154
[7 empty] | 6670 | 118 | 5.4892 | 4.1991
[7 empty] | 6671 | 119 | 3.9227 | 2.9264
[7 empty] | 6672 | 120 | 3.6106 | 2.6728
[7 empty] | 6673 | 121 | 2.8922 | 2.0891
[7 empty] | 6674 | 122 | 2.4882 | 1.7609
[7 empty] | 6675 | 123 | 2.4057 | 1.6939
[7 empty] | 6676 | 124 | 2.3727 | 1.6671
[7 empty] | 6677 | 125 | 2.3315 | 1.6336
[7 empty] | 6678 | 126 | 2.4717 | 1.7475
[7 empty] | 6679 | 127 | 3.9557 | 2.9532
[7 empty] | 6680 | 128 | 5.4892 | 4.1991
[7 empty] | 6681 | 129 | 6.1571 | 4.7417
[7 empty] | 6682 | 130 | 6.5858 | 5.09
[7 empty] | 6683 | 131 | 6.7424 | 5.2173
[7 empty] | 6684 | 132 | 6.4951 | 5.0163
[7 empty] | 6685 | 133 | 7.1217 | 5.5254
[7 empty] | 6686 | 134 | 7.4185 | 5.7666
[7 empty] | 6687 | 135 | 7.4844 | 5.8201
[7 empty] | 6688 | 136 | 6.6847 | 5.1704
[7 empty] | 6689 | 137 | 6.5858 | 5.09
[7 empty] | 6690 | 138 | 6.5363 | 5.0498
[7 empty] | 6691 | 139 | 6.2065 | 4.7819
[7 empty] | 6692 | 140 | 6.2148 | 4.7886
[7 empty] | 6693 | 141 | 5.5717 | 4.2661
[7 empty] | 6694 | 142 | 4.9451 | 3.757
[7 empty] | 6695 | 143 | 4.0794 | 3.0537
[7 empty] | 6696 | 144 | 3.4775 | 2.5647
[7 empty] | 6697 | 145 | 3.0158 | 2.1896
[7 empty] | 6698 | 146 | 2.8097 | 2.0221
[7 empty] | 6699 | 147 | 2.7438 | 1.9685
[7 empty] | 6700 | 148 | 2.7355 | 1.9618
[7 empty] | 6701 | 149 | 2.7355 | 1.9618
[7 empty] | 6702 | 150 | 2.7438 | 1.9685
[7 empty] | 6703 | 151 | 3.8073 | 2.8326
[7 empty] | 6704 | 152 | 5.3079 | 4.0517
[7 empty] | 6705 | 153 | 5.9097 | 4.5407
[7 empty] | 6706 | 154 | 6.4621 | 4.9895
[7 empty] | 6707 | 155 | 6.3137 | 4.869
[7 empty] | 6708 | 156 | 6.4786 | 5.0029
[7 empty] | 6709 | 157 | 7.1794 | 5.5723
[7 empty] | 6710 | 158 | 7.5009 | 5.8335
[7 empty] | 6711 | 159 | 7.7648 | 6.0479
[7 empty] | 6712 | 160 | 7.6411 | 5.9474
[7 empty] | 6713 | 161 | 8.3914 | 6.557
[7 empty] | 6714 | 162 | 7.9049 | 6.1618
[7 empty] | 6715 | 163 | 8.2594 | 6.4498
[7 empty] | 6716 | 164 | 6.9321 | 5.3713
[7 empty] | 6717 | 165 | 10.0073 | 7.8699
[7 empty] | 6718 | 166 | 7.9956 | 6.2354
[7 empty] | 6719 | 167 | 4.4504 | 3.3551
[7 empty] | 6720 | 168 | 3.8156 | 2.8393
[7 empty] | 6721 | 1 | 2.381 | 1.6738
[7 empty] | 6722 | 2 | 2.2738 | 1.5867
[7 empty] | 6723 | 3 | 2.2656 | 1.58
[7 empty] | 6724 | 4 | 2.3975 | 1.6872
[7 empty] | 6725 | 5 | 2.414 | 1.7006
[7 empty] | 6726 | 6 | 2.8345 | 2.0422
[7 empty] | 6727 | 7 | 3.5435 | 2.6183
[7 empty] | 6728 | 8 | 4.2031 | 3.1541
[7 empty] | 6729 | 9 | 4.1783 | 3.134
[7 empty] | 6730 | 10 | 5.6706 | 4.3465
[7 empty] | 6731 | 11 | 7.7153 | 6.0077
[7 empty] | 6732 | 12 | 8.6634 | 6.778
[7 empty] | 6733 | 13 | 9.0344 | 7.0795
[7 empty] | 6734 | 14 | 8.8201 | 6.9053
[7 empty] | 6735 | 15 | 8.7294 | 6.8316
[7 empty] | 6736 | 16 | 9.8919 | 7.7761
[7 empty] | 6737 | 17 | 11.1946 | 8.8345
[7 empty] | 6738 | 18 | 10.9555 | 8.6402
[7 empty] | 6739 | 19 | 11.4749 | 9.0622
[7 empty] | 6740 | 20 | 11.4089 | 9.0086
[7 empty] | 6741 | 21 | 11.9696 | 9.4641
[7 empty] | 6742 | 22 | 8.0781 | 6.3024
[7 empty] | 6743 | 23 | 4.368 | 3.2881
[7 empty] | 6744 | 24 | 2.724 | 1.9525
[7 empty] | 6745 | 25 | 2.6283 | 1.8747
[7 empty] | 6746 | 26 | 2.5212 | 1.7877
[7 empty] | 6747 | 27 | 2.4222 | 1.7073
[7 empty] | 6748 | 28 | 2.5047 | 1.7743
[7 empty] | 6749 | 29 | 2.7438 | 1.9685
[7 empty] | 6750 | 30 | 2.9829 | 2.1628
[7 empty] | 6751 | 31 | 3.8156 | 2.8393
[7 empty] | 6752 | 32 | 4.1618 | 3.1207
[7 empty] | 6753 | 33 | 4.8132 | 3.6498
[7 empty] | 6754 | 34 | 5.6954 | 4.3666
[7 empty] | 6755 | 35 | 7.8307 | 6.1015
[7 empty] | 6756 | 36 | 8.8448 | 6.9254
[7 empty] | 6757 | 37 | 8.919 | 6.9857
[7 empty] | 6758 | 38 | 8.9932 | 7.046
[7 empty] | 6759 | 39 | 8.6717 | 6.7847
[7 empty] | 6760 | 40 | 9.7105 | 7.6287
[7 empty] | 6761 | 41 | 10.2547 | 8.0708
[7 empty] | 6762 | 42 | 10.2711 | 8.0842
[7 empty] | 6763 | 43 | 10.6339 | 8.379
[7 empty] | 6764 | 44 | 11.7717 | 9.3034
[7 empty] | 6765 | 45 | 11.3759 | 8.9818
[7 empty] | 6766 | 46 | 8.6717 | 6.7847
[7 empty] | 6767 | 47 | 5.1265 | 3.9044
[7 empty] | 6768 | 48 | 3.6507 | 2.7053
[7 empty] | 6769 | 49 | 2.9993 | 2.1762
[7 empty] | 6770 | 50 | 2.6943 | 1.9283
[7 empty] | 6771 | 51 | 2.5871 | 1.8412
[7 empty] | 6772 | 52 | 2.6201 | 1.868
[7 empty] | 6773 | 53 | 2.6448 | 1.8881
[7 empty] | 6774 | 54 | 3.2137 | 2.3503
[7 empty] | 6775 | 55 | 4.335 | 3.2613
[7 empty] | 6776 | 56 | 4.5741 | 3.4556
[7 empty] | 6777 | 57 | 5.5057 | 4.2125
[7 empty] | 6778 | 58 | 6.594 | 5.0967
[7 empty] | 6779 | 59 | 7.7813 | 6.0613
[7 empty] | 6780 | 60 | 8.3996 | 6.5637
[7 empty] | 6781 | 61 | 9.0674 | 7.1063
[7 empty] | 6782 | 62 | 8.8696 | 6.9455
[7 empty] | 6783 | 63 | 9.4549 | 7.4211
[7 empty] | 6784 | 64 | 10.3866 | 8.178
[7 empty] | 6785 | 65 | 10.9967 | 8.6737
[7 empty] | 6786 | 66 | 10.8977 | 8.5933
[7 empty] | 6787 | 67 | 11.6233 | 9.1828
[7 empty] | 6788 | 68 | 11.8624 | 9.377
[7 empty] | 6789 | 69 | 11.3594 | 8.9684
[7 empty] | 6790 | 70 | 9.1004 | 7.133
[7 empty] | 6791 | 71 | 4.6565 | 3.5226
[7 empty] | 6792 | 72 | 3.5894 | 2.6556
[7 empty] | 6793 | 73 | 2.8839 | 2.0824
[7 empty] | 6794 | 74 | 2.6613 | 1.9015
[7 empty] | 6795 | 75 | 2.5624 | 1.8211
[7 empty] | 6796 | 76 | 2.5047 | 1.7743
[7 empty] | 6797 | 77 | 2.6778 | 1.9149
[7 empty] | 6798 | 78 | 3.0735 | 2.2365
[7 empty] | 6799 | 79 | 4.1701 | 3.1274
[7 empty] | 6800 | 80 | 4.3432 | 3.268
[7 empty] | 6801 | 81 | 5.5057 | 4.2125
[7 empty] | 6802 | 82 | 6.5775 | 5.0833
[7 empty] | 6803 | 83 | 7.3031 | 5.6728
[7 empty] | 6804 | 84 | 8.5233 | 6.6642
[7 empty] | 6805 | 85 | 8.2265 | 6.423
[7 empty] | 6806 | 86 | 7.7235 | 6.0144
[7 empty] | 6807 | 87 | 8.1605 | 6.3694
[7 empty] | 6808 | 88 | 8.8118 | 6.8986
[7 empty] | 6809 | 89 | 10.1392 | 7.9771
[7 empty] | 6810 | 90 | 9.5621 | 7.5082
[7 empty] | 6811 | 91 | 10.2382 | 8.0574
[7 empty] | 6812 | 92 | 9.6446 | 7.5751
[7 empty] | 6813 | 93 | 7.2701 | 5.646
[7 empty] | 6814 | 94 | 6.3797 | 4.9225
[7 empty] | 6815 | 95 | 4.5493 | 3.4355
[7 empty] | 6816 | 96 | 3.5765 | 2.6451
[7 empty] | 6817 | 97 | 3.527 | 2.6049
[7 empty] | 6818 | 98 | 3.2384 | 2.3704
[7 empty] | 6819 | 99 | 3.1807 | 2.3235
[7 empty] | 6820 | 100 | 2.8345 | 2.0422
[7 empty] | 6821 | 101 | 2.7767 | 1.9953
[7 empty] | 6822 | 102 | 3.0076 | 2.1829
[7 empty] | 6823 | 103 | 3.7414 | 2.779
[7 empty] | 6824 | 104 | 3.9887 | 2.98
[7 empty] | 6825 | 105 | 4.4669 | 3.3685
[7 empty] | 6826 | 106 | 5.9015 | 4.534
[7 empty] | 6827 | 107 | 6.2477 | 4.8154
[7 empty] | 6828 | 108 | 7.7977 | 6.0747
[7 empty] | 6829 | 109 | 7.1464 | 5.5455
[7 empty] | 6830 | 110 | 6.7012 | 5.1838
[7 empty] | 6831 | 111 | 6.5446 | 5.0565
[7 empty] | 6832 | 112 | 6.6105 | 5.1101
[7 empty] | 6833 | 113 | 6.2725 | 4.8355
[7 empty] | 6834 | 114 | 6.4374 | 4.9694
[7 empty] | 6835 | 115 | 5.9922 | 4.6077
[7 empty] | 6836 | 116 | 6.66 | 5.1503
[7 empty] | 6837 | 117 | 6.2477 | 4.8154
[7 empty] | 6838 | 118 | 5.4892 | 4.1991
[7 empty] | 6839 | 119 | 3.9227 | 2.9264
[7 empty] | 6840 | 120 | 3.6106 | 2.6728
[7 empty] | 6841 | 121 | 2.8922 | 2.0891
[7 empty] | 6842 | 122 | 2.4882 | 1.7609
[7 empty] | 6843 | 123 | 2.4057 | 1.6939
[7 empty] | 6844 | 124 | 2.3727 | 1.6671
[7 empty] | 6845 | 125 | 2.3315 | 1.6336
[7 empty] | 6846 | 126 | 2.4717 | 1.7475
[7 empty] | 6847 | 127 | 3.9557 | 2.9532
[7 empty] | 6848 | 128 | 5.4892 | 4.1991
[7 empty] | 6849 | 129 | 6.1571 | 4.7417
[7 empty] | 6850 | 130 | 6.5858 | 5.09
[7 empty] | 6851 | 131 | 6.7424 | 5.2173
[7 empty] | 6852 | 132 | 6.4951 | 5.0163
[7 empty] | 6853 | 133 | 7.1217 | 5.5254
[7 empty] | 6854 | 134 | 7.4185 | 5.7666
[7 empty] | 6855 | 135 | 7.4844 | 5.8201
[7 empty] | 6856 | 136 | 6.6847 | 5.1704
[7 empty] | 6857 | 137 | 6.5858 | 5.09
[7 empty] | 6858 | 138 | 6.5363 | 5.0498
[7 empty] | 6859 | 139 | 6.2065 | 4.7819
[7 empty] | 6860 | 140 | 6.2148 | 4.7886
[7 empty] | 6861 | 141 | 5.5717 | 4.2661
[7 empty] | 6862 | 142 | 4.9451 | 3.757
[7 empty] | 6863 | 143 | 4.0794 | 3.0537
[7 empty] | 6864 | 144 | 3.4775 | 2.5647
[7 empty] | 6865 | 145 | 3.0158 | 2.1896
[7 empty] | 6866 | 146 | 2.8097 | 2.0221
[7 empty] | 6867 | 147 | 2.7438 | 1.9685
[7 empty] | 6868 | 148 | 2.7355 | 1.9618
[7 empty] | 6869 | 149 | 2.7355 | 1.9618
[7 empty] | 6870 | 150 | 2.7438 | 1.9685
[7 empty] | 6871 | 151 | 3.8073 | 2.8326
[7 empty] | 6872 | 152 | 5.3079 | 4.0517
[7 empty] | 6873 | 153 | 5.9097 | 4.5407
[7 empty] | 6874 | 154 | 6.4621 | 4.9895
[7 empty] | 6875 | 155 | 6.3137 | 4.869
[7 empty] | 6876 | 156 | 6.4786 | 5.0029
[7 empty] | 6877 | 157 | 7.1794 | 5.5723
[7 empty] | 6878 | 158 | 7.5009 | 5.8335
[7 empty] | 6879 | 159 | 7.7648 | 6.0479
[7 empty] | 6880 | 160 | 7.6411 | 5.9474
[7 empty] | 6881 | 161 | 8.3914 | 6.557
[7 empty] | 6882 | 162 | 7.9049 | 6.1618
[7 empty] | 6883 | 163 | 8.2594 | 6.4498
[7 empty] | 6884 | 164 | 6.9321 | 5.3713
[7 empty] | 6885 | 165 | 10.0073 | 7.8699
[7 empty] | 6886 | 166 | 7.9956 | 6.2354
[7 empty] | 6887 | 167 | 4.4504 | 3.3551
[7 empty] | 6888 | 168 | 3.8156 | 2.8393
[7 empty] | 6889 | 1 | 2.381 | 1.6738
[7 empty] | 6890 | 2 | 2.2738 | 1.5867
[7 empty] | 6891 | 3 | 2.2656 | 1.58
[7 empty] | 6892 | 4 | 2.3975 | 1.6872
[7 empty] | 6893 | 5 | 2.414 | 1.7006
[7 empty] | 6894 | 6 | 2.8345 | 2.0422
[7 empty] | 6895 | 7 | 3.5435 | 2.6183
[7 empty] | 6896 | 8 | 4.2031 | 3.1541
[7 empty] | 6897 | 9 | 4.1783 | 3.134
[7 empty] | 6898 | 10 | 5.6706 | 4.3465
[7 empty] | 6899 | 11 | 7.7153 | 6.0077
[7 empty] | 6900 | 12 | 8.6634 | 6.778
[7 empty] | 6901 | 13 | 9.0344 | 7.0795
[7 empty] | 6902 | 14 | 8.8201 | 6.9053
[7 empty] | 6903 | 15 | 8.7294 | 6.8316
[7 empty] | 6904 | 16 | 9.8919 | 7.7761
[7 empty] | 6905 | 17 | 11.1946 | 8.8345
[7 empty] | 6906 | 18 | 10.9555 | 8.6402
[7 empty] | 6907 | 19 | 11.4749 | 9.0622
[7 empty] | 6908 | 20 | 11.4089 | 9.0086
[7 empty] | 6909 | 21 | 11.9696 | 9.4641
[7 empty] | 6910 | 22 | 8.0781 | 6.3024
[7 empty] | 6911 | 23 | 4.368 | 3.2881
[7 empty] | 6912 | 24 | 2.724 | 1.9525
[7 empty] | 6913 | 25 | 2.6283 | 1.8747
[7 empty] | 6914 | 26 | 2.5212 | 1.7877
[7 empty] | 6915 | 27 | 2.4222 | 1.7073
[7 empty] | 6916 | 28 | 2.5047 | 1.7743
[7 empty] | 6917 | 29 | 2.7438 | 1.9685
[7 empty] | 6918 | 30 | 2.9829 | 2.1628
[7 empty] | 6919 | 31 | 3.8156 | 2.8393
[7 empty] | 6920 | 32 | 4.1618 | 3.1207
[7 empty] | 6921 | 33 | 4.8132 | 3.6498
[7 empty] | 6922 | 34 | 5.6954 | 4.3666
[7 empty] | 6923 | 35 | 7.8307 | 6.1015
[7 empty] | 6924 | 36 | 8.8448 | 6.9254
[7 empty] | 6925 | 37 | 8.919 | 6.9857
[7 empty] | 6926 | 38 | 8.9932 | 7.046
[7 empty] | 6927 | 39 | 8.6717 | 6.7847
[7 empty] | 6928 | 40 | 9.7105 | 7.6287
[7 empty] | 6929 | 41 | 10.2547 | 8.0708
[7 empty] | 6930 | 42 | 10.2711 | 8.0842
[7 empty] | 6931 | 43 | 10.6339 | 8.379
[7 empty] | 6932 | 44 | 11.7717 | 9.3034
[7 empty] | 6933 | 45 | 11.3759 | 8.9818
[7 empty] | 6934 | 46 | 8.6717 | 6.7847
[7 empty] | 6935 | 47 | 5.1265 | 3.9044
[7 empty] | 6936 | 48 | 3.6507 | 2.7053
[7 empty] | 6937 | 49 | 2.9993 | 2.1762
[7 empty] | 6938 | 50 | 2.6943 | 1.9283
[7 empty] | 6939 | 51 | 2.5871 | 1.8412
[7 empty] | 6940 | 52 | 2.6201 | 1.868
[7 empty] | 6941 | 53 | 2.6448 | 1.8881
[7 empty] | 6942 | 54 | 3.2137 | 2.3503
[7 empty] | 6943 | 55 | 4.335 | 3.2613
[7 empty] | 6944 | 56 | 4.5741 | 3.4556
[7 empty] | 6945 | 57 | 5.5057 | 4.2125
[7 empty] | 6946 | 58 | 6.594 | 5.0967
[7 empty] | 6947 | 59 | 7.7813 | 6.0613
[7 empty] | 6948 | 60 | 8.3996 | 6.5637
[7 empty] | 6949 | 61 | 9.0674 | 7.1063
[7 empty] | 6950 | 62 | 8.8696 | 6.9455
[7 empty] | 6951 | 63 | 9.4549 | 7.4211
[7 empty] | 6952 | 64 | 10.3866 | 8.178
[7 empty] | 6953 | 65 | 10.9967 | 8.6737
[7 empty] | 6954 | 66 | 10.8977 | 8.5933
[7 empty] | 6955 | 67 | 11.6233 | 9.1828
[7 empty] | 6956 | 68 | 11.8624 | 9.377
[7 empty] | 6957 | 69 | 11.3594 | 8.9684
[7 empty] | 6958 | 70 | 9.1004 | 7.133
[7 empty] | 6959 | 71 | 4.6565 | 3.5226
[7 empty] | 6960 | 72 | 3.5894 | 2.6556
[7 empty] | 6961 | 73 | 2.8839 | 2.0824
[7 empty] | 6962 | 74 | 2.6613 | 1.9015
[7 empty] | 6963 | 75 | 2.5624 | 1.8211
[7 empty] | 6964 | 76 | 2.5047 | 1.7743
[7 empty] | 6965 | 77 | 2.6778 | 1.9149
[7 empty] | 6966 | 78 | 3.0735 | 2.2365
[7 empty] | 6967 | 79 | 4.1701 | 3.1274
[7 empty] | 6968 | 80 | 4.3432 | 3.268
[7 empty] | 6969 | 81 | 5.5057 | 4.2125
[7 empty] | 6970 | 82 | 6.5775 | 5.0833
[7 empty] | 6971 | 83 | 7.3031 | 5.6728
[7 empty] | 6972 | 84 | 8.5233 | 6.6642
[7 empty] | 6973 | 85 | 8.2265 | 6.423
[7 empty] | 6974 | 86 | 7.7235 | 6.0144
[7 empty] | 6975 | 87 | 8.1605 | 6.3694
[7 empty] | 6976 | 88 | 8.8118 | 6.8986
[7 empty] | 6977 | 89 | 10.1392 | 7.9771
[7 empty] | 6978 | 90 | 9.5621 | 7.5082
[7 empty] | 6979 | 91 | 10.2382 | 8.0574
[7 empty] | 6980 | 92 | 9.6446 | 7.5751
[7 empty] | 6981 | 93 | 7.2701 | 5.646
[7 empty] | 6982 | 94 | 6.3797 | 4.9225
[7 empty] | 6983 | 95 | 4.5493 | 3.4355
[7 empty] | 6984 | 96 | 3.5765 | 2.6451
[7 empty] | 6985 | 97 | 3.527 | 2.6049
[7 empty] | 6986 | 98 | 3.2384 | 2.3704
[7 empty] | 6987 | 99 | 3.1807 | 2.3235
[7 empty] | 6988 | 100 | 2.8345 | 2.0422
[7 empty] | 6989 | 101 | 2.7767 | 1.9953
[7 empty] | 6990 | 102 | 3.0076 | 2.1829
[7 empty] | 6991 | 103 | 3.7414 | 2.779
[7 empty] | 6992 | 104 | 3.9887 | 2.98
[7 empty] | 6993 | 105 | 4.4669 | 3.3685
[7 empty] | 6994 | 106 | 5.9015 | 4.534
[7 empty] | 6995 | 107 | 6.2477 | 4.8154
[7 empty] | 6996 | 108 | 7.7977 | 6.0747
[7 empty] | 6997 | 109 | 7.1464 | 5.5455
[7 empty] | 6998 | 110 | 6.7012 | 5.1838
[7 empty] | 6999 | 111 | 6.5446 | 5.0565
[7 empty] | 7000 | 112 | 6.6105 | 5.1101
[7 empty] | 7001 | 113 | 6.2725 | 4.8355
[7 empty] | 7002 | 114 | 6.4374 | 4.9694
[7 empty] | 7003 | 115 | 5.9922 | 4.6077
[7 empty] | 7004 | 116 | 6.66 | 5.1503
[7 empty] | 7005 | 117 | 6.2477 | 4.8154
[7 empty] | 7006 | 118 | 5.4892 | 4.1991
[7 empty] | 7007 | 119 | 3.9227 | 2.9264
[7 empty] | 7008 | 120 | 3.6106 | 2.6728
[7 empty] | 7009 | 121 | 2.8922 | 2.0891
[7 empty] | 7010 | 122 | 2.4882 | 1.7609
[7 empty] | 7011 | 123 | 2.4057 | 1.6939
[7 empty] | 7012 | 124 | 2.3727 | 1.6671
[7 empty] | 7013 | 125 | 2.3315 | 1.6336
[7 empty] | 7014 | 126 | 2.4717 | 1.7475
[7 empty] | 7015 | 127 | 3.9557 | 2.9532
[7 empty] | 7016 | 128 | 5.4892 | 4.1991
[7 empty] | 7017 | 129 | 6.1571 | 4.7417
[7 empty] | 7018 | 130 | 6.5858 | 5.09
[7 empty] | 7019 | 131 | 6.7424 | 5.2173
[7 empty] | 7020 | 132 | 6.4951 | 5.0163
[7 empty] | 7021 | 133 | 7.1217 | 5.5254
[7 empty] | 7022 | 134 | 7.4185 | 5.7666
[7 empty] | 7023 | 135 | 7.4844 | 5.8201
[7 empty] | 7024 | 136 | 6.6847 | 5.1704
[7 empty] | 7025 | 137 | 6.5858 | 5.09
[7 empty] | 7026 | 138 | 6.5363 | 5.0498
[7 empty] | 7027 | 139 | 6.2065 | 4.7819
[7 empty] | 7028 | 140 | 6.2148 | 4.7886
[7 empty] | 7029 | 141 | 5.5717 | 4.2661
[7 empty] | 7030 | 142 | 4.9451 | 3.757
[7 empty] | 7031 | 143 | 4.0794 | 3.0537
[7 empty] | 7032 | 144 | 3.4775 | 2.5647
[7 empty] | 7033 | 145 | 3.0158 | 2.1896
[7 empty] | 7034 | 146 | 2.8097 | 2.0221
[7 empty] | 7035 | 147 | 2.7438 | 1.9685
[7 empty] | 7036 | 148 | 2.7355 | 1.9618
[7 empty] | 7037 | 149 | 2.7355 | 1.9618
[7 empty] | 7038 | 150 | 2.7438 | 1.9685
[7 empty] | 7039 | 151 | 3.8073 | 2.8326
[7 empty] | 7040 | 152 | 5.3079 | 4.0517
[7 empty] | 7041 | 153 | 5.9097 | 4.5407
[7 empty] | 7042 | 154 | 6.4621 | 4.9895
[7 empty] | 7043 | 155 | 6.3137 | 4.869
[7 empty] | 7044 | 156 | 6.4786 | 5.0029
[7 empty] | 7045 | 157 | 7.1794 | 5.5723
[7 empty] | 7046 | 158 | 7.5009 | 5.8335
[7 empty] | 7047 | 159 | 7.7648 | 6.0479
[7 empty] | 7048 | 160 | 7.6411 | 5.9474
[7 empty] | 7049 | 161 | 8.3914 | 6.557
[7 empty] | 7050 | 162 | 7.9049 | 6.1618
[7 empty] | 7051 | 163 | 8.2594 | 6.4498
[7 empty] | 7052 | 164 | 6.9321 | 5.3713
[7 empty] | 7053 | 165 | 10.0073 | 7.8699
[7 empty] | 7054 | 166 | 7.9956 | 6.2354
[7 empty] | 7055 | 167 | 4.4504 | 3.3551
[7 empty] | 7056 | 168 | 3.8156 | 2.8393
[7 empty] | 7057 | 1 | 2.381 | 1.6738
[7 empty] | 7058 | 2 | 2.2738 | 1.5867
[7 empty] | 7059 | 3 | 2.2656 | 1.58
[7 empty] | 7060 | 4 | 2.3975 | 1.6872
[7 empty] | 7061 | 5 | 2.414 | 1.7006
[7 empty] | 7062 | 6 | 2.8345 | 2.0422
[7 empty] | 7063 | 7 | 3.5435 | 2.6183
[7 empty] | 7064 | 8 | 4.2031 | 3.1541
[7 empty] | 7065 | 9 | 4.1783 | 3.134
[7 empty] | 7066 | 10 | 5.6706 | 4.3465
[7 empty] | 7067 | 11 | 7.7153 | 6.0077
[7 empty] | 7068 | 12 | 8.6634 | 6.778
[7 empty] | 7069 | 13 | 9.0344 | 7.0795
[7 empty] | 7070 | 14 | 8.8201 | 6.9053
[7 empty] | 7071 | 15 | 8.7294 | 6.8316
[7 empty] | 7072 | 16 | 9.8919 | 7.7761
[7 empty] | 7073 | 17 | 11.1946 | 8.8345
[7 empty] | 7074 | 18 | 10.9555 | 8.6402
[7 empty] | 7075 | 19 | 11.4749 | 9.0622
[7 empty] | 7076 | 20 | 11.4089 | 9.0086
[7 empty] | 7077 | 21 | 11.9696 | 9.4641
[7 empty] | 7078 | 22 | 8.0781 | 6.3024
[7 empty] | 7079 | 23 | 4.368 | 3.2881
[7 empty] | 7080 | 24 | 2.724 | 1.9525
[7 empty] | 7081 | 25 | 2.6283 | 1.8747
[7 empty] | 7082 | 26 | 2.5212 | 1.7877
[7 empty] | 7083 | 27 | 2.4222 | 1.7073
[7 empty] | 7084 | 28 | 2.5047 | 1.7743
[7 empty] | 7085 | 29 | 2.7438 | 1.9685
[7 empty] | 7086 | 30 | 2.9829 | 2.1628
[7 empty] | 7087 | 31 | 3.8156 | 2.8393
[7 empty] | 7088 | 32 | 4.1618 | 3.1207
[7 empty] | 7089 | 33 | 4.8132 | 3.6498
[7 empty] | 7090 | 34 | 5.6954 | 4.3666
[7 empty] | 7091 | 35 | 7.8307 | 6.1015
[7 empty] | 7092 | 36 | 8.8448 | 6.9254
[7 empty] | 7093 | 37 | 8.919 | 6.9857
[7 empty] | 7094 | 38 | 8.9932 | 7.046
[7 empty] | 7095 | 39 | 8.6717 | 6.7847
[7 empty] | 7096 | 40 | 9.7105 | 7.6287
[7 empty] | 7097 | 41 | 10.2547 | 8.0708
[7 empty] | 7098 | 42 | 10.2711 | 8.0842
[7 empty] | 7099 | 43 | 10.6339 | 8.379
[7 empty] | 7100 | 44 | 11.7717 | 9.3034
[7 empty] | 7101 | 45 | 11.3759 | 8.9818
[7 empty] | 7102 | 46 | 8.6717 | 6.7847
[7 empty] | 7103 | 47 | 5.1265 | 3.9044
[7 empty] | 7104 | 48 | 3.6507 | 2.7053
[7 empty] | 7105 | 49 | 2.9993 | 2.1762
[7 empty] | 7106 | 50 | 2.6943 | 1.9283
[7 empty] | 7107 | 51 | 2.5871 | 1.8412
[7 empty] | 7108 | 52 | 2.6201 | 1.868
[7 empty] | 7109 | 53 | 2.6448 | 1.8881
[7 empty] | 7110 | 54 | 3.2137 | 2.3503
[7 empty] | 7111 | 55 | 4.335 | 3.2613
[7 empty] | 7112 | 56 | 4.5741 | 3.4556
[7 empty] | 7113 | 57 | 5.5057 | 4.2125
[7 empty] | 7114 | 58 | 6.594 | 5.0967
[7 empty] | 7115 | 59 | 7.7813 | 6.0613
[7 empty] | 7116 | 60 | 8.3996 | 6.5637
[7 empty] | 7117 | 61 | 9.0674 | 7.1063
[7 empty] | 7118 | 62 | 8.8696 | 6.9455
[7 empty] | 7119 | 63 | 9.4549 | 7.4211
[7 empty] | 7120 | 64 | 10.3866 | 8.178
[7 empty] | 7121 | 65 | 10.9967 | 8.6737
[7 empty] | 7122 | 66 | 10.8977 | 8.5933
[7 empty] | 7123 | 67 | 11.6233 | 9.1828
[7 empty] | 7124 | 68 | 11.8624 | 9.377
[7 empty] | 7125 | 69 | 11.3594 | 8.9684
[7 empty] | 7126 | 70 | 9.1004 | 7.133
[7 empty] | 7127 | 71 | 4.6565 | 3.5226
[7 empty] | 7128 | 72 | 3.5894 | 2.6556
[7 empty] | 7129 | 73 | 2.8839 | 2.0824
[7 empty] | 7130 | 74 | 2.6613 | 1.9015
[7 empty] | 7131 | 75 | 2.5624 | 1.8211
[7 empty] | 7132 | 76 | 2.5047 | 1.7743
[7 empty] | 7133 | 77 | 2.6778 | 1.9149
[7 empty] | 7134 | 78 | 3.0735 | 2.2365
[7 empty] | 7135 | 79 | 4.1701 | 3.1274
[7 empty] | 7136 | 80 | 4.3432 | 3.268
[7 empty] | 7137 | 81 | 5.5057 | 4.2125
[7 empty] | 7138 | 82 | 6.5775 | 5.0833
[7 empty] | 7139 | 83 | 7.3031 | 5.6728
[7 empty] | 7140 | 84 | 8.5233 | 6.6642
[7 empty] | 7141 | 85 | 8.2265 | 6.423
[7 empty] | 7142 | 86 | 7.7235 | 6.0144
[7 empty] | 7143 | 87 | 8.1605 | 6.3694
[7 empty] | 7144 | 88 | 8.8118 | 6.8986
[7 empty] | 7145 | 89 | 10.1392 | 7.9771
[7 empty] | 7146 | 90 | 9.5621 | 7.5082
[7 empty] | 7147 | 91 | 10.2382 | 8.0574
[7 empty] | 7148 | 92 | 9.6446 | 7.5751
[7 empty] | 7149 | 93 | 7.2701 | 5.646
[7 empty] | 7150 | 94 | 6.3797 | 4.9225
[7 empty] | 7151 | 95 | 4.5493 | 3.4355
[7 empty] | 7152 | 96 | 3.5765 | 2.6451
[7 empty] | 7153 | 97 | 3.527 | 2.6049
[7 empty] | 7154 | 98 | 3.2384 | 2.3704
[7 empty] | 7155 | 99 | 3.1807 | 2.3235
[7 empty] | 7156 | 100 | 2.8345 | 2.0422
[7 empty] | 7157 | 101 | 2.7767 | 1.9953
[7 empty] | 7158 | 102 | 3.0076 | 2.1829
[7 empty] | 7159 | 103 | 3.7414 | 2.779
[7 empty] | 7160 | 104 | 3.9887 | 2.98
[7 empty] | 7161 | 105 | 4.4669 | 3.3685
[7 empty] | 7162 | 106 | 5.9015 | 4.534
[7 empty] | 7163 | 107 | 6.2477 | 4.8154
[7 empty] | 7164 | 108 | 7.7977 | 6.0747
[7 empty] | 7165 | 109 | 7.1464 | 5.5455
[7 empty] | 7166 | 110 | 6.7012 | 5.1838
[7 empty] | 7167 | 111 | 6.5446 | 5.0565
[7 empty] | 7168 | 112 | 6.6105 | 5.1101
[7 empty] | 7169 | 113 | 6.2725 | 4.8355
[7 empty] | 7170 | 114 | 6.4374 | 4.9694
[7 empty] | 7171 | 115 | 5.9922 | 4.6077
[7 empty] | 7172 | 116 | 6.66 | 5.1503
[7 empty] | 7173 | 117 | 6.2477 | 4.8154
[7 empty] | 7174 | 118 | 5.4892 | 4.1991
[7 empty] | 7175 | 119 | 3.9227 | 2.9264
[7 empty] | 7176 | 120 | 3.6106 | 2.6728
[7 empty] | 7177 | 121 | 2.8922 | 2.0891
[7 empty] | 7178 | 122 | 2.4882 | 1.7609
[7 empty] | 7179 | 123 | 2.4057 | 1.6939
[7 empty] | 7180 | 124 | 2.3727 | 1.6671
[7 empty] | 7181 | 125 | 2.3315 | 1.6336
[7 empty] | 7182 | 126 | 2.4717 | 1.7475
[7 empty] | 7183 | 127 | 3.9557 | 2.9532
[7 empty] | 7184 | 128 | 5.4892 | 4.1991
[7 empty] | 7185 | 129 | 6.1571 | 4.7417
[7 empty] | 7186 | 130 | 6.5858 | 5.09
[7 empty] | 7187 | 131 | 6.7424 | 5.2173
[7 empty] | 7188 | 132 | 6.4951 | 5.0163
[7 empty] | 7189 | 133 | 7.1217 | 5.5254
[7 empty] | 7190 | 134 | 7.4185 | 5.7666
[7 empty] | 7191 | 135 | 7.4844 | 5.8201
[7 empty] | 7192 | 136 | 6.6847 | 5.1704
[7 empty] | 7193 | 137 | 6.5858 | 5.09
[7 empty] | 7194 | 138 | 6.5363 | 5.0498
[7 empty] | 7195 | 139 | 6.2065 | 4.7819
[7 empty] | 7196 | 140 | 6.2148 | 4.7886
[7 empty] | 7197 | 141 | 5.5717 | 4.2661
[7 empty] | 7198 | 142 | 4.9451 | 3.757
[7 empty] | 7199 | 143 | 4.0794 | 3.0537
[7 empty] | 7200 | 144 | 3.4775 | 2.5647
[7 empty] | 7201 | 145 | 3.0158 | 2.1896
[7 empty] | 7202 | 146 | 2.8097 | 2.0221
[7 empty] | 7203 | 147 | 2.7438 | 1.9685
[7 empty] | 7204 | 148 | 2.7355 | 1.9618
[7 empty] | 7205 | 149 | 2.7355 | 1.9618
[7 empty] | 7206 | 150 | 2.7438 | 1.9685
[7 empty] | 7207 | 151 | 3.8073 | 2.8326
[7 empty] | 7208 | 152 | 5.3079 | 4.0517
[7 empty] | 7209 | 153 | 5.9097 | 4.5407
[7 empty] | 7210 | 154 | 6.4621 | 4.9895
[7 empty] | 7211 | 155 | 6.3137 | 4.869
[7 empty] | 7212 | 156 | 6.4786 | 5.0029
[7 empty] | 7213 | 157 | 7.1794 | 5.5723
[7 empty] | 7214 | 158 | 7.5009 | 5.8335
[7 empty] | 7215 | 159 | 7.7648 | 6.0479
[7 empty] | 7216 | 160 | 7.6411 | 5.9474
[7 empty] | 7217 | 161 | 8.3914 | 6.557
[7 empty] | 7218 | 162 | 7.9049 | 6.1618
[7 empty] | 7219 | 163 | 8.2594 | 6.4498
[7 empty] | 7220 | 164 | 6.9321 | 5.3713
[7 empty] | 7221 | 165 | 10.0073 | 7.8699
[7 empty] | 7222 | 166 | 7.9956 | 6.2354
[7 empty] | 7223 | 167 | 4.4504 | 3.3551
[7 empty] | 7224 | 168 | 3.8156 | 2.8393
[7 empty] | 7225 | 1 | 2.381 | 1.6738
[7 empty] | 7226 | 2 | 2.2738 | 1.5867
[7 empty] | 7227 | 3 | 2.2656 | 1.58
[7 empty] | 7228 | 4 | 2.3975 | 1.6872
[7 empty] | 7229 | 5 | 2.414 | 1.7006
[7 empty] | 7230 | 6 | 2.8345 | 2.0422
[7 empty] | 7231 | 7 | 3.5435 | 2.6183
[7 empty] | 7232 | 8 | 4.2031 | 3.1541
[7 empty] | 7233 | 9 | 4.1783 | 3.134
[7 empty] | 7234 | 10 | 5.6706 | 4.3465
[7 empty] | 7235 | 11 | 7.7153 | 6.0077
[7 empty] | 7236 | 12 | 8.6634 | 6.778
[7 empty] | 7237 | 13 | 9.0344 | 7.0795
[7 empty] | 7238 | 14 | 8.8201 | 6.9053
[7 empty] | 7239 | 15 | 8.7294 | 6.8316
[7 empty] | 7240 | 16 | 9.8919 | 7.7761
[7 empty] | 7241 | 17 | 11.1946 | 8.8345
[7 empty] | 7242 | 18 | 10.9555 | 8.6402
[7 empty] | 7243 | 19 | 11.4749 | 9.0622
[7 empty] | 7244 | 20 | 11.4089 | 9.0086
[7 empty] | 7245 | 21 | 11.9696 | 9.4641
[7 empty] | 7246 | 22 | 8.0781 | 6.3024
[7 empty] | 7247 | 23 | 4.368 | 3.2881
[7 empty] | 7248 | 24 | 2.724 | 1.9525
[7 empty] | 7249 | 25 | 2.6283 | 1.8747
[7 empty] | 7250 | 26 | 2.5212 | 1.7877
[7 empty] | 7251 | 27 | 2.4222 | 1.7073
[7 empty] | 7252 | 28 | 2.5047 | 1.7743
[7 empty] | 7253 | 29 | 2.7438 | 1.9685
[7 empty] | 7254 | 30 | 2.9829 | 2.1628
[7 empty] | 7255 | 31 | 3.8156 | 2.8393
[7 empty] | 7256 | 32 | 4.1618 | 3.1207
[7 empty] | 7257 | 33 | 4.8132 | 3.6498
[7 empty] | 7258 | 34 | 5.6954 | 4.3666
[7 empty] | 7259 | 35 | 7.8307 | 6.1015
[7 empty] | 7260 | 36 | 8.8448 | 6.9254
[7 empty] | 7261 | 37 | 8.919 | 6.9857
[7 empty] | 7262 | 38 | 8.9932 | 7.046
[7 empty] | 7263 | 39 | 8.6717 | 6.7847
[7 empty] | 7264 | 40 | 9.7105 | 7.6287
[7 empty] | 7265 | 41 | 10.2547 | 8.0708
[7 empty] | 7266 | 42 | 10.2711 | 8.0842
[7 empty] | 7267 | 43 | 10.6339 | 8.379
[7 empty] | 7268 | 44 | 11.7717 | 9.3034
[7 empty] | 7269 | 45 | 11.3759 | 8.9818
[7 empty] | 7270 | 46 | 8.6717 | 6.7847
[7 empty] | 7271 | 47 | 5.1265 | 3.9044
[7 empty] | 7272 | 48 | 3.6507 | 2.7053
[7 empty] | 7273 | 49 | 2.9993 | 2.1762
[7 empty] | 7274 | 50 | 2.6943 | 1.9283
[7 empty] | 7275 | 51 | 2.5871 | 1.8412
[7 empty] | 7276 | 52 | 2.6201 | 1.868
[7 empty] | 7277 | 53 | 2.6448 | 1.8881
[7 empty] | 7278 | 54 | 3.2137 | 2.3503
[7 empty] | 7279 | 55 | 4.335 | 3.2613
[7 empty] | 7280 | 56 | 4.5741 | 3.4556
[7 empty] | 7281 | 57 | 5.5057 | 4.2125
[7 empty] | 7282 | 58 | 6.594 | 5.0967
[7 empty] | 7283 | 59 | 7.7813 | 6.0613
[7 empty] | 7284 | 60 | 8.3996 | 6.5637
[7 empty] | 7285 | 61 | 9.0674 | 7.1063
[7 empty] | 7286 | 62 | 8.8696 | 6.9455
[7 empty] | 7287 | 63 | 9.4549 | 7.4211
[7 empty] | 7288 | 64 | 10.3866 | 8.178
[7 empty] | 7289 | 65 | 10.9967 | 8.6737
[7 empty] | 7290 | 66 | 10.8977 | 8.5933
[7 empty] | 7291 | 67 | 11.6233 | 9.1828
[7 empty] | 7292 | 68 | 11.8624 | 9.377
[7 empty] | 7293 | 69 | 11.3594 | 8.9684
[7 empty] | 7294 | 70 | 9.1004 | 7.133
[7 empty] | 7295 | 71 | 4.6565 | 3.5226
[7 empty] | 7296 | 72 | 3.5894 | 2.6556
[7 empty] | 7297 | 73 | 2.8839 | 2.0824
[7 empty] | 7298 | 74 | 2.6613 | 1.9015
[7 empty] | 7299 | 75 | 2.5624 | 1.8211
[7 empty] | 7300 | 76 | 2.5047 | 1.7743
[7 empty] | 7301 | 77 | 2.6778 | 1.9149
[7 empty] | 7302 | 78 | 3.0735 | 2.2365
[7 empty] | 7303 | 79 | 4.1701 | 3.1274
[7 empty] | 7304 | 80 | 4.3432 | 3.268
[7 empty] | 7305 | 81 | 5.5057 | 4.2125
[7 empty] | 7306 | 82 | 6.5775 | 5.0833
[7 empty] | 7307 | 83 | 7.3031 | 5.6728
[7 empty] | 7308 | 84 | 8.5233 | 6.6642
[7 empty] | 7309 | 85 | 8.2265 | 6.423
[7 empty] | 7310 | 86 | 7.7235 | 6.0144
[7 empty] | 7311 | 87 | 8.1605 | 6.3694
[7 empty] | 7312 | 88 | 8.8118 | 6.8986
[7 empty] | 7313 | 89 | 10.1392 | 7.9771
[7 empty] | 7314 | 90 | 9.5621 | 7.5082
[7 empty] | 7315 | 91 | 10.2382 | 8.0574
[7 empty] | 7316 | 92 | 9.6446 | 7.5751
[7 empty] | 7317 | 93 | 7.2701 | 5.646
[7 empty] | 7318 | 94 | 6.3797 | 4.9225
[7 empty] | 7319 | 95 | 4.5493 | 3.4355
[7 empty] | 7320 | 96 | 3.5765 | 2.6451
[7 empty] | 7321 | 97 | 3.527 | 2.6049
[7 empty] | 7322 | 98 | 3.2384 | 2.3704
[7 empty] | 7323 | 99 | 3.1807 | 2.3235
[7 empty] | 7324 | 100 | 2.8345 | 2.0422
[7 empty] | 7325 | 101 | 2.7767 | 1.9953
[7 empty] | 7326 | 102 | 3.0076 | 2.1829
[7 empty] | 7327 | 103 | 3.7414 | 2.779
[7 empty] | 7328 | 104 | 3.9887 | 2.98
[7 empty] | 7329 | 105 | 4.4669 | 3.3685
[7 empty] | 7330 | 106 | 5.9015 | 4.534
[7 empty] | 7331 | 107 | 6.2477 | 4.8154
[7 empty] | 7332 | 108 | 7.7977 | 6.0747
[7 empty] | 7333 | 109 | 7.1464 | 5.5455
[7 empty] | 7334 | 110 | 6.7012 | 5.1838
[7 empty] | 7335 | 111 | 6.5446 | 5.0565
[7 empty] | 7336 | 112 | 6.6105 | 5.1101
[7 empty] | 7337 | 113 | 6.2725 | 4.8355
[7 empty] | 7338 | 114 | 6.4374 | 4.9694
[7 empty] | 7339 | 115 | 5.9922 | 4.6077
[7 empty] | 7340 | 116 | 6.66 | 5.1503
[7 empty] | 7341 | 117 | 6.2477 | 4.8154
[7 empty] | 7342 | 118 | 5.4892 | 4.1991
[7 empty] | 7343 | 119 | 3.9227 | 2.9264
[7 empty] | 7344 | 120 | 3.6106 | 2.6728
[7 empty] | 7345 | 121 | 2.8922 | 2.0891
[7 empty] | 7346 | 122 | 2.4882 | 1.7609
[7 empty] | 7347 | 123 | 2.4057 | 1.6939
[7 empty] | 7348 | 124 | 2.3727 | 1.6671
[7 empty] | 7349 | 125 | 2.3315 | 1.6336
[7 empty] | 7350 | 126 | 2.4717 | 1.7475
[7 empty] | 7351 | 127 | 3.9557 | 2.9532
[7 empty] | 7352 | 128 | 5.4892 | 4.1991
[7 empty] | 7353 | 129 | 6.1571 | 4.7417
[7 empty] | 7354 | 130 | 6.5858 | 5.09
[7 empty] | 7355 | 131 | 6.7424 | 5.2173
[7 empty] | 7356 | 132 | 6.4951 | 5.0163
[7 empty] | 7357 | 133 | 7.1217 | 5.5254
[7 empty] | 7358 | 134 | 7.4185 | 5.7666
[7 empty] | 7359 | 135 | 7.4844 | 5.8201
[7 empty] | 7360 | 136 | 6.6847 | 5.1704
[7 empty] | 7361 | 137 | 6.5858 | 5.09
[7 empty] | 7362 | 138 | 6.5363 | 5.0498
[7 empty] | 7363 | 139 | 6.2065 | 4.7819
[7 empty] | 7364 | 140 | 6.2148 | 4.7886
[7 empty] | 7365 | 141 | 5.5717 | 4.2661
[7 empty] | 7366 | 142 | 4.9451 | 3.757
[7 empty] | 7367 | 143 | 4.0794 | 3.0537
[7 empty] | 7368 | 144 | 3.4775 | 2.5647
[7 empty] | 7369 | 145 | 3.0158 | 2.1896
[7 empty] | 7370 | 146 | 2.8097 | 2.0221
[7 empty] | 7371 | 147 | 2.7438 | 1.9685
[7 empty] | 7372 | 148 | 2.7355 | 1.9618
[7 empty] | 7373 | 149 | 2.7355 | 1.9618
[7 empty] | 7374 | 150 | 2.7438 | 1.9685
[7 empty] | 7375 | 151 | 3.8073 | 2.8326
[7 empty] | 7376 | 152 | 5.3079 | 4.0517
[7 empty] | 7377 | 153 | 5.9097 | 4.5407
[7 empty] | 7378 | 154 | 6.4621 | 4.9895
[7 empty] | 7379 | 155 | 6.3137 | 4.869
[7 empty] | 7380 | 156 | 6.4786 | 5.0029
[7 empty] | 7381 | 157 | 7.1794 | 5.5723
[7 empty] | 7382 | 158 | 7.5009 | 5.8335
[7 empty] | 7383 | 159 | 7.7648 | 6.0479
[7 empty] | 7384 | 160 | 7.6411 | 5.9474
[7 empty] | 7385 | 161 | 8.3914 | 6.557
[7 empty] | 7386 | 162 | 7.9049 | 6.1618
[7 empty] | 7387 | 163 | 8.2594 | 6.4498
[7 empty] | 7388 | 164 | 6.9321 | 5.3713
[7 empty] | 7389 | 165 | 10.0073 | 7.8699
[7 empty] | 7390 | 166 | 7.9956 | 6.2354
[7 empty] | 7391 | 167 | 4.4504 | 3.3551
[7 empty] | 7392 | 168 | 3.8156 | 2.8393
[7 empty] | 7393 | 1 | 2.381 | 1.6738
[7 empty] | 7394 | 2 | 2.2738 | 1.5867
[7 empty] | 7395 | 3 | 2.2656 | 1.58
[7 empty] | 7396 | 4 | 2.3975 | 1.6872
[7 empty] | 7397 | 5 | 2.414 | 1.7006
[7 empty] | 7398 | 6 | 2.8345 | 2.0422
[7 empty] | 7399 | 7 | 3.5435 | 2.6183
[7 empty] | 7400 | 8 | 4.2031 | 3.1541
[7 empty] | 7401 | 9 | 4.1783 | 3.134
[7 empty] | 7402 | 10 | 5.6706 | 4.3465
[7 empty] | 7403 | 11 | 7.7153 | 6.0077
[7 empty] | 7404 | 12 | 8.6634 | 6.778
[7 empty] | 7405 | 13 | 9.0344 | 7.0795
[7 empty] | 7406 | 14 | 8.8201 | 6.9053
[7 empty] | 7407 | 15 | 8.7294 | 6.8316
[7 empty] | 7408 | 16 | 9.8919 | 7.7761
[7 empty] | 7409 | 17 | 11.1946 | 8.8345
[7 empty] | 7410 | 18 | 10.9555 | 8.6402
[7 empty] | 7411 | 19 | 11.4749 | 9.0622
[7 empty] | 7412 | 20 | 11.4089 | 9.0086
[7 empty] | 7413 | 21 | 11.9696 | 9.4641
[7 empty] | 7414 | 22 | 8.0781 | 6.3024
[7 empty] | 7415 | 23 | 4.368 | 3.2881
[7 empty] | 7416 | 24 | 2.724 | 1.9525
[7 empty] | 7417 | 25 | 2.6283 | 1.8747
[7 empty] | 7418 | 26 | 2.5212 | 1.7877
[7 empty] | 7419 | 27 | 2.4222 | 1.7073
[7 empty] | 7420 | 28 | 2.5047 | 1.7743
[7 empty] | 7421 | 29 | 2.7438 | 1.9685
[7 empty] | 7422 | 30 | 2.9829 | 2.1628
[7 empty] | 7423 | 31 | 3.8156 | 2.8393
[7 empty] | 7424 | 32 | 4.1618 | 3.1207
[7 empty] | 7425 | 33 | 4.8132 | 3.6498
[7 empty] | 7426 | 34 | 5.6954 | 4.3666
[7 empty] | 7427 | 35 | 7.8307 | 6.1015
[7 empty] | 7428 | 36 | 8.8448 | 6.9254
[7 empty] | 7429 | 37 | 8.919 | 6.9857
[7 empty] | 7430 | 38 | 8.9932 | 7.046
[7 empty] | 7431 | 39 | 8.6717 | 6.7847
[7 empty] | 7432 | 40 | 9.7105 | 7.6287
[7 empty] | 7433 | 41 | 10.2547 | 8.0708
[7 empty] | 7434 | 42 | 10.2711 | 8.0842
[7 empty] | 7435 | 43 | 10.6339 | 8.379
[7 empty] | 7436 | 44 | 11.7717 | 9.3034
[7 empty] | 7437 | 45 | 11.3759 | 8.9818
[7 empty] | 7438 | 46 | 8.6717 | 6.7847
[7 empty] | 7439 | 47 | 5.1265 | 3.9044
[7 empty] | 7440 | 48 | 3.6507 | 2.7053
[7 empty] | 7441 | 49 | 2.9993 | 2.1762
[7 empty] | 7442 | 50 | 2.6943 | 1.9283
[7 empty] | 7443 | 51 | 2.5871 | 1.8412
[7 empty] | 7444 | 52 | 2.6201 | 1.868
[7 empty] | 7445 | 53 | 2.6448 | 1.8881
[7 empty] | 7446 | 54 | 3.2137 | 2.3503
[7 empty] | 7447 | 55 | 4.335 | 3.2613
[7 empty] | 7448 | 56 | 4.5741 | 3.4556
[7 empty] | 7449 | 57 | 5.5057 | 4.2125
[7 empty] | 7450 | 58 | 6.594 | 5.0967
[7 empty] | 7451 | 59 | 7.7813 | 6.0613
[7 empty] | 7452 | 60 | 8.3996 | 6.5637
[7 empty] | 7453 | 61 | 9.0674 | 7.1063
[7 empty] | 7454 | 62 | 8.8696 | 6.9455
[7 empty] | 7455 | 63 | 9.4549 | 7.4211
[7 empty] | 7456 | 64 | 10.3866 | 8.178
[7 empty] | 7457 | 65 | 10.9967 | 8.6737
[7 empty] | 7458 | 66 | 10.8977 | 8.5933
[7 empty] | 7459 | 67 | 11.6233 | 9.1828
[7 empty] | 7460 | 68 | 11.8624 | 9.377
[7 empty] | 7461 | 69 | 11.3594 | 8.9684
[7 empty] | 7462 | 70 | 9.1004 | 7.133
[7 empty] | 7463 | 71 | 4.6565 | 3.5226
[7 empty] | 7464 | 72 | 3.5894 | 2.6556
[7 empty] | 7465 | 73 | 2.8839 | 2.0824
[7 empty] | 7466 | 74 | 2.6613 | 1.9015
[7 empty] | 7467 | 75 | 2.5624 | 1.8211
[7 empty] | 7468 | 76 | 2.5047 | 1.7743
[7 empty] | 7469 | 77 | 2.6778 | 1.9149
[7 empty] | 7470 | 78 | 3.0735 | 2.2365
[7 empty] | 7471 | 79 | 4.1701 | 3.1274
[7 empty] | 7472 | 80 | 4.3432 | 3.268
[7 empty] | 7473 | 81 | 5.5057 | 4.2125
[7 empty] | 7474 | 82 | 6.5775 | 5.0833
[7 empty] | 7475 | 83 | 7.3031 | 5.6728
[7 empty] | 7476 | 84 | 8.5233 | 6.6642
[7 empty] | 7477 | 85 | 8.2265 | 6.423
[7 empty] | 7478 | 86 | 7.7235 | 6.0144
[7 empty] | 7479 | 87 | 8.1605 | 6.3694
[7 empty] | 7480 | 88 | 8.8118 | 6.8986
[7 empty] | 7481 | 89 | 10.1392 | 7.9771
[7 empty] | 7482 | 90 | 9.5621 | 7.5082
[7 empty] | 7483 | 91 | 10.2382 | 8.0574
[7 empty] | 7484 | 92 | 9.6446 | 7.5751
[7 empty] | 7485 | 93 | 7.2701 | 5.646
[7 empty] | 7486 | 94 | 6.3797 | 4.9225
[7 empty] | 7487 | 95 | 4.5493 | 3.4355
[7 empty] | 7488 | 96 | 3.5765 | 2.6451
[7 empty] | 7489 | 97 | 3.527 | 2.6049
[7 empty] | 7490 | 98 | 3.2384 | 2.3704
[7 empty] | 7491 | 99 | 3.1807 | 2.3235
[7 empty] | 7492 | 100 | 2.8345 | 2.0422
[7 empty] | 7493 | 101 | 2.7767 | 1.9953
[7 empty] | 7494 | 102 | 3.0076 | 2.1829
[7 empty] | 7495 | 103 | 3.7414 | 2.779
[7 empty] | 7496 | 104 | 3.9887 | 2.98
[7 empty] | 7497 | 105 | 4.4669 | 3.3685
[7 empty] | 7498 | 106 | 5.9015 | 4.534
[7 empty] | 7499 | 107 | 6.2477 | 4.8154
[7 empty] | 7500 | 108 | 7.7977 | 6.0747
[7 empty] | 7501 | 109 | 7.1464 | 5.5455
[7 empty] | 7502 | 110 | 6.7012 | 5.1838
[7 empty] | 7503 | 111 | 6.5446 | 5.0565
[7 empty] | 7504 | 112 | 6.6105 | 5.1101
[7 empty] | 7505 | 113 | 6.2725 | 4.8355
[7 empty] | 7506 | 114 | 6.4374 | 4.9694
[7 empty] | 7507 | 115 | 5.9922 | 4.6077
[7 empty] | 7508 | 116 | 6.66 | 5.1503
[7 empty] | 7509 | 117 | 6.2477 | 4.8154
[7 empty] | 7510 | 118 | 5.4892 | 4.1991
[7 empty] | 7511 | 119 | 3.9227 | 2.9264
[7 empty] | 7512 | 120 | 3.6106 | 2.6728
[7 empty] | 7513 | 121 | 2.8922 | 2.0891
[7 empty] | 7514 | 122 | 2.4882 | 1.7609
[7 empty] | 7515 | 123 | 2.4057 | 1.6939
[7 empty] | 7516 | 124 | 2.3727 | 1.6671
[7 empty] | 7517 | 125 | 2.3315 | 1.6336
[7 empty] | 7518 | 126 | 2.4717 | 1.7475
[7 empty] | 7519 | 127 | 3.9557 | 2.9532
[7 empty] | 7520 | 128 | 5.4892 | 4.1991
[7 empty] | 7521 | 129 | 6.1571 | 4.7417
[7 empty] | 7522 | 130 | 6.5858 | 5.09
[7 empty] | 7523 | 131 | 6.7424 | 5.2173
[7 empty] | 7524 | 132 | 6.4951 | 5.0163
[7 empty] | 7525 | 133 | 7.1217 | 5.5254
[7 empty] | 7526 | 134 | 7.4185 | 5.7666
[7 empty] | 7527 | 135 | 7.4844 | 5.8201
[7 empty] | 7528 | 136 | 6.6847 | 5.1704
[7 empty] | 7529 | 137 | 6.5858 | 5.09
[7 empty] | 7530 | 138 | 6.5363 | 5.0498
[7 empty] | 7531 | 139 | 6.2065 | 4.7819
[7 empty] | 7532 | 140 | 6.2148 | 4.7886
[7 empty] | 7533 | 141 | 5.5717 | 4.2661
[7 empty] | 7534 | 142 | 4.9451 | 3.757
[7 empty] | 7535 | 143 | 4.0794 | 3.0537
[7 empty] | 7536 | 144 | 3.4775 | 2.5647
[7 empty] | 7537 | 145 | 3.0158 | 2.1896
[7 empty] | 7538 | 146 | 2.8097 | 2.0221
[7 empty] | 7539 | 147 | 2.7438 | 1.9685
[7 empty] | 7540 | 148 | 2.7355 | 1.9618
[7 empty] | 7541 | 149 | 2.7355 | 1.9618
[7 empty] | 7542 | 150 | 2.7438 | 1.9685
[7 empty] | 7543 | 151 | 3.8073 | 2.8326
[7 empty] | 7544 | 152 | 5.3079 | 4.0517
[7 empty] | 7545 | 153 | 5.9097 | 4.5407
[7 empty] | 7546 | 154 | 6.4621 | 4.9895
[7 empty] | 7547 | 155 | 6.3137 | 4.869
[7 empty] | 7548 | 156 | 6.4786 | 5.0029
[7 empty] | 7549 | 157 | 7.1794 | 5.5723
[7 empty] | 7550 | 158 | 7.5009 | 5.8335
[7 empty] | 7551 | 159 | 7.7648 | 6.0479
[7 empty] | 7552 | 160 | 7.6411 | 5.9474
[7 empty] | 7553 | 161 | 8.3914 | 6.557
[7 empty] | 7554 | 162 | 7.9049 | 6.1618
[7 empty] | 7555 | 163 | 8.2594 | 6.4498
[7 empty] | 7556 | 164 | 6.9321 | 5.3713
[7 empty] | 7557 | 165 | 10.0073 | 7.8699
[7 empty] | 7558 | 166 | 7.9956 | 6.2354
[7 empty] | 7559 | 167 | 4.4504 | 3.3551
[7 empty] | 7560 | 168 | 3.8156 | 2.8393
[7 empty] | 7561 | 1 | 2.381 | 1.6738
[7 empty] | 7562 | 2 | 2.2738 | 1.5867
[7 empty] | 7563 | 3 | 2.2656 | 1.58
[7 empty] | 7564 | 4 | 2.3975 | 1.6872
[7 empty] | 7565 | 5 | 2.414 | 1.7006
[7 empty] | 7566 | 6 | 2.8345 | 2.0422
[7 empty] | 7567 | 7 | 3.5435 | 2.6183
[7 empty] | 7568 | 8 | 4.2031 | 3.1541
[7 empty] | 7569 | 9 | 4.1783 | 3.134
[7 empty] | 7570 | 10 | 5.6706 | 4.3465
[7 empty] | 7571 | 11 | 7.7153 | 6.0077
[7 empty] | 7572 | 12 | 8.6634 | 6.778
[7 empty] | 7573 | 13 | 9.0344 | 7.0795
[7 empty] | 7574 | 14 | 8.8201 | 6.9053
[7 empty] | 7575 | 15 | 8.7294 | 6.8316
[7 empty] | 7576 | 16 | 9.8919 | 7.7761
[7 empty] | 7577 | 17 | 11.1946 | 8.8345
[7 empty] | 7578 | 18 | 10.9555 | 8.6402
[7 empty] | 7579 | 19 | 11.4749 | 9.0622
[7 empty] | 7580 | 20 | 11.4089 | 9.0086
[7 empty] | 7581 | 21 | 11.9696 | 9.4641
[7 empty] | 7582 | 22 | 8.0781 | 6.3024
[7 empty] | 7583 | 23 | 4.368 | 3.2881
[7 empty] | 7584 | 24 | 2.724 | 1.9525
[7 empty] | 7585 | 25 | 2.6283 | 1.8747
[7 empty] | 7586 | 26 | 2.5212 | 1.7877
[7 empty] | 7587 | 27 | 2.4222 | 1.7073
[7 empty] | 7588 | 28 | 2.5047 | 1.7743
[7 empty] | 7589 | 29 | 2.7438 | 1.9685
[7 empty] | 7590 | 30 | 2.9829 | 2.1628
[7 empty] | 7591 | 31 | 3.8156 | 2.8393
[7 empty] | 7592 | 32 | 4.1618 | 3.1207
[7 empty] | 7593 | 33 | 4.8132 | 3.6498
[7 empty] | 7594 | 34 | 5.6954 | 4.3666
[7 empty] | 7595 | 35 | 7.8307 | 6.1015
[7 empty] | 7596 | 36 | 8.8448 | 6.9254
[7 empty] | 7597 | 37 | 8.919 | 6.9857
[7 empty] | 7598 | 38 | 8.9932 | 7.046
[7 empty] | 7599 | 39 | 8.6717 | 6.7847
[7 empty] | 7600 | 40 | 9.7105 | 7.6287
[7 empty] | 7601 | 41 | 10.2547 | 8.0708
[7 empty] | 7602 | 42 | 10.2711 | 8.0842
[7 empty] | 7603 | 43 | 10.6339 | 8.379
[7 empty] | 7604 | 44 | 11.7717 | 9.3034
[7 empty] | 7605 | 45 | 11.3759 | 8.9818
[7 empty] | 7606 | 46 | 8.6717 | 6.7847
[7 empty] | 7607 | 47 | 5.1265 | 3.9044
[7 empty] | 7608 | 48 | 3.6507 | 2.7053
[7 empty] | 7609 | 49 | 2.9993 | 2.1762
[7 empty] | 7610 | 50 | 2.6943 | 1.9283
[7 empty] | 7611 | 51 | 2.5871 | 1.8412
[7 empty] | 7612 | 52 | 2.6201 | 1.868
[7 empty] | 7613 | 53 | 2.6448 | 1.8881
[7 empty] | 7614 | 54 | 3.2137 | 2.3503
[7 empty] | 7615 | 55 | 4.335 | 3.2613
[7 empty] | 7616 | 56 | 4.5741 | 3.4556
[7 empty] | 7617 | 57 | 5.5057 | 4.2125
[7 empty] | 7618 | 58 | 6.594 | 5.0967
[7 empty] | 7619 | 59 | 7.7813 | 6.0613
[7 empty] | 7620 | 60 | 8.3996 | 6.5637
[7 empty] | 7621 | 61 | 9.0674 | 7.1063
[7 empty] | 7622 | 62 | 8.8696 | 6.9455
[7 empty] | 7623 | 63 | 9.4549 | 7.4211
[7 empty] | 7624 | 64 | 10.3866 | 8.178
[7 empty] | 7625 | 65 | 10.9967 | 8.6737
[7 empty] | 7626 | 66 | 10.8977 | 8.5933
[7 empty] | 7627 | 67 | 11.6233 | 9.1828
[7 empty] | 7628 | 68 | 11.8624 | 9.377
[7 empty] | 7629 | 69 | 11.3594 | 8.9684
[7 empty] | 7630 | 70 | 9.1004 | 7.133
[7 empty] | 7631 | 71 | 4.6565 | 3.5226
[7 empty] | 7632 | 72 | 3.5894 | 2.6556
[7 empty] | 7633 | 73 | 2.8839 | 2.0824
[7 empty] | 7634 | 74 | 2.6613 | 1.9015
[7 empty] | 7635 | 75 | 2.5624 | 1.8211
[7 empty] | 7636 | 76 | 2.5047 | 1.7743
[7 empty] | 7637 | 77 | 2.6778 | 1.9149
[7 empty] | 7638 | 78 | 3.0735 | 2.2365
[7 empty] | 7639 | 79 | 4.1701 | 3.1274
[7 empty] | 7640 | 80 | 4.3432 | 3.268
[7 empty] | 7641 | 81 | 5.5057 | 4.2125
[7 empty] | 7642 | 82 | 6.5775 | 5.0833
[7 empty] | 7643 | 83 | 7.3031 | 5.6728
[7 empty] | 7644 | 84 | 8.5233 | 6.6642
[7 empty] | 7645 | 85 | 8.2265 | 6.423
[7 empty] | 7646 | 86 | 7.7235 | 6.0144
[7 empty] | 7647 | 87 | 8.1605 | 6.3694
[7 empty] | 7648 | 88 | 8.8118 | 6.8986
[7 empty] | 7649 | 89 | 10.1392 | 7.9771
[7 empty] | 7650 | 90 | 9.5621 | 7.5082
[7 empty] | 7651 | 91 | 10.2382 | 8.0574
[7 empty] | 7652 | 92 | 9.6446 | 7.5751
[7 empty] | 7653 | 93 | 7.2701 | 5.646
[7 empty] | 7654 | 94 | 6.3797 | 4.9225
[7 empty] | 7655 | 95 | 4.5493 | 3.4355
[7 empty] | 7656 | 96 | 3.5765 | 2.6451
[7 empty] | 7657 | 97 | 3.527 | 2.6049
[7 empty] | 7658 | 98 | 3.2384 | 2.3704
[7 empty] | 7659 | 99 | 3.1807 | 2.3235
[7 empty] | 7660 | 100 | 2.8345 | 2.0422
[7 empty] | 7661 | 101 | 2.7767 | 1.9953
[7 empty] | 7662 | 102 | 3.0076 | 2.1829
[7 empty] | 7663 | 103 | 3.7414 | 2.779
[7 empty] | 7664 | 104 | 3.9887 | 2.98
[7 empty] | 7665 | 105 | 4.4669 | 3.3685
[7 empty] | 7666 | 106 | 5.9015 | 4.534
[7 empty] | 7667 | 107 | 6.2477 | 4.8154
[7 empty] | 7668 | 108 | 7.7977 | 6.0747
[7 empty] | 7669 | 109 | 7.1464 | 5.5455
[7 empty] | 7670 | 110 | 6.7012 | 5.1838
[7 empty] | 7671 | 111 | 6.5446 | 5.0565
[7 empty] | 7672 | 112 | 6.6105 | 5.1101
[7 empty] | 7673 | 113 | 6.2725 | 4.8355
[7 empty] | 7674 | 114 | 6.4374 | 4.9694
[7 empty] | 7675 | 115 | 5.9922 | 4.6077
[7 empty] | 7676 | 116 | 6.66 | 5.1503
[7 empty] | 7677 | 117 | 6.2477 | 4.8154
[7 empty] | 7678 | 118 | 5.4892 | 4.1991
[7 empty] | 7679 | 119 | 3.9227 | 2.9264
[7 empty] | 7680 | 120 | 3.6106 | 2.6728
[7 empty] | 7681 | 121 | 2.8922 | 2.0891
[7 empty] | 7682 | 122 | 2.4882 | 1.7609
[7 empty] | 7683 | 123 | 2.4057 | 1.6939
[7 empty] | 7684 | 124 | 2.3727 | 1.6671
[7 empty] | 7685 | 125 | 2.3315 | 1.6336
[7 empty] | 7686 | 126 | 2.4717 | 1.7475
[7 empty] | 7687 | 127 | 3.9557 | 2.9532
[7 empty] | 7688 | 128 | 5.4892 | 4.1991
[7 empty] | 7689 | 129 | 6.1571 | 4.7417
[7 empty] | 7690 | 130 | 6.5858 | 5.09
[7 empty] | 7691 | 131 | 6.7424 | 5.2173
[7 empty] | 7692 | 132 | 6.4951 | 5.0163
[7 empty] | 7693 | 133 | 7.1217 | 5.5254
[7 empty] | 7694 | 134 | 7.4185 | 5.7666
[7 empty] | 7695 | 135 | 7.4844 | 5.8201
[7 empty] | 7696 | 136 | 6.6847 | 5.1704
[7 empty] | 7697 | 137 | 6.5858 | 5.09
[7 empty] | 7698 | 138 | 6.5363 | 5.0498
[7 empty] | 7699 | 139 | 6.2065 | 4.7819
[7 empty] | 7700 | 140 | 6.2148 | 4.7886
[7 empty] | 7701 | 141 | 5.5717 | 4.2661
[7 empty] | 7702 | 142 | 4.9451 | 3.757
[7 empty] | 7703 | 143 | 4.0794 | 3.0537
[7 empty] | 7704 | 144 | 3.4775 | 2.5647
[7 empty] | 7705 | 145 | 3.0158 | 2.1896
[7 empty] | 7706 | 146 | 2.8097 | 2.0221
[7 empty] | 7707 | 147 | 2.7438 | 1.9685
[7 empty] | 7708 | 148 | 2.7355 | 1.9618
[7 empty] | 7709 | 149 | 2.7355 | 1.9618
[7 empty] | 7710 | 150 | 2.7438 | 1.9685
[7 empty] | 7711 | 151 | 3.8073 | 2.8326
[7 empty] | 7712 | 152 | 5.3079 | 4.0517
[7 empty] | 7713 | 153 | 5.9097 | 4.5407
[7 empty] | 7714 | 154 | 6.4621 | 4.9895
[7 empty] | 7715 | 155 | 6.3137 | 4.869
[7 empty] | 7716 | 156 | 6.4786 | 5.0029
[7 empty] | 7717 | 157 | 7.1794 | 5.5723
[7 empty] | 7718 | 158 | 7.5009 | 5.8335
[7 empty] | 7719 | 159 | 7.7648 | 6.0479
[7 empty] | 7720 | 160 | 7.6411 | 5.9474
[7 empty] | 7721 | 161 | 8.3914 | 6.557
[7 empty] | 7722 | 162 | 7.9049 | 6.1618
[7 empty] | 7723 | 163 | 8.2594 | 6.4498
[7 empty] | 7724 | 164 | 6.9321 | 5.3713
[7 empty] | 7725 | 165 | 10.0073 | 7.8699
[7 empty] | 7726 | 166 | 7.9956 | 6.2354
[7 empty] | 7727 | 167 | 4.4504 | 3.3551
[7 empty] | 7728 | 168 | 3.8156 | 2.8393
[7 empty] | 7729 | 1 | 2.381 | 1.6738
[7 empty] | 7730 | 2 | 2.2738 | 1.5867
[7 empty] | 7731 | 3 | 2.2656 | 1.58
[7 empty] | 7732 | 4 | 2.3975 | 1.6872
[7 empty] | 7733 | 5 | 2.414 | 1.7006
[7 empty] | 7734 | 6 | 2.8345 | 2.0422
[7 empty] | 7735 | 7 | 3.5435 | 2.6183
[7 empty] | 7736 | 8 | 4.2031 | 3.1541
[7 empty] | 7737 | 9 | 4.1783 | 3.134
[7 empty] | 7738 | 10 | 5.6706 | 4.3465
[7 empty] | 7739 | 11 | 7.7153 | 6.0077
[7 empty] | 7740 | 12 | 8.6634 | 6.778
[7 empty] | 7741 | 13 | 9.0344 | 7.0795
[7 empty] | 7742 | 14 | 8.8201 | 6.9053
[7 empty] | 7743 | 15 | 8.7294 | 6.8316
[7 empty] | 7744 | 16 | 9.8919 | 7.7761
[7 empty] | 7745 | 17 | 11.1946 | 8.8345
[7 empty] | 7746 | 18 | 10.9555 | 8.6402
[7 empty] | 7747 | 19 | 11.4749 | 9.0622
[7 empty] | 7748 | 20 | 11.4089 | 9.0086
[7 empty] | 7749 | 21 | 11.9696 | 9.4641
[7 empty] | 7750 | 22 | 8.0781 | 6.3024
[7 empty] | 7751 | 23 | 4.368 | 3.2881
[7 empty] | 7752 | 24 | 2.724 | 1.9525
[7 empty] | 7753 | 25 | 2.6283 | 1.8747
[7 empty] | 7754 | 26 | 2.5212 | 1.7877
[7 empty] | 7755 | 27 | 2.4222 | 1.7073
[7 empty] | 7756 | 28 | 2.5047 | 1.7743
[7 empty] | 7757 | 29 | 2.7438 | 1.9685
[7 empty] | 7758 | 30 | 2.9829 | 2.1628
[7 empty] | 7759 | 31 | 3.8156 | 2.8393
[7 empty] | 7760 | 32 | 4.1618 | 3.1207
[7 empty] | 7761 | 33 | 4.8132 | 3.6498
[7 empty] | 7762 | 34 | 5.6954 | 4.3666
[7 empty] | 7763 | 35 | 7.8307 | 6.1015
[7 empty] | 7764 | 36 | 8.8448 | 6.9254
[7 empty] | 7765 | 37 | 8.919 | 6.9857
[7 empty] | 7766 | 38 | 8.9932 | 7.046
[7 empty] | 7767 | 39 | 8.6717 | 6.7847
[7 empty] | 7768 | 40 | 9.7105 | 7.6287
[7 empty] | 7769 | 41 | 10.2547 | 8.0708
[7 empty] | 7770 | 42 | 10.2711 | 8.0842
[7 empty] | 7771 | 43 | 10.6339 | 8.379
[7 empty] | 7772 | 44 | 11.7717 | 9.3034
[7 empty] | 7773 | 45 | 11.3759 | 8.9818
[7 empty] | 7774 | 46 | 8.6717 | 6.7847
[7 empty] | 7775 | 47 | 5.1265 | 3.9044
[7 empty] | 7776 | 48 | 3.6507 | 2.7053
[7 empty] | 7777 | 49 | 2.9993 | 2.1762
[7 empty] | 7778 | 50 | 2.6943 | 1.9283
[7 empty] | 7779 | 51 | 2.5871 | 1.8412
[7 empty] | 7780 | 52 | 2.6201 | 1.868
[7 empty] | 7781 | 53 | 2.6448 | 1.8881
[7 empty] | 7782 | 54 | 3.2137 | 2.3503
[7 empty] | 7783 | 55 | 4.335 | 3.2613
[7 empty] | 7784 | 56 | 4.5741 | 3.4556
[7 empty] | 7785 | 57 | 5.5057 | 4.2125
[7 empty] | 7786 | 58 | 6.594 | 5.0967
[7 empty] | 7787 | 59 | 7.7813 | 6.0613
[7 empty] | 7788 | 60 | 8.3996 | 6.5637
[7 empty] | 7789 | 61 | 9.0674 | 7.1063
[7 empty] | 7790 | 62 | 8.8696 | 6.9455
[7 empty] | 7791 | 63 | 9.4549 | 7.4211
[7 empty] | 7792 | 64 | 10.3866 | 8.178
[7 empty] | 7793 | 65 | 10.9967 | 8.6737
[7 empty] | 7794 | 66 | 10.8977 | 8.5933
[7 empty] | 7795 | 67 | 11.6233 | 9.1828
[7 empty] | 7796 | 68 | 11.8624 | 9.377
[7 empty] | 7797 | 69 | 11.3594 | 8.9684
[7 empty] | 7798 | 70 | 9.1004 | 7.133
[7 empty] | 7799 | 71 | 4.6565 | 3.5226
[7 empty] | 7800 | 72 | 3.5894 | 2.6556
[7 empty] | 7801 | 73 | 2.8839 | 2.0824
[7 empty] | 7802 | 74 | 2.6613 | 1.9015
[7 empty] | 7803 | 75 | 2.5624 | 1.8211
[7 empty] | 7804 | 76 | 2.5047 | 1.7743
[7 empty] | 7805 | 77 | 2.6778 | 1.9149
[7 empty] | 7806 | 78 | 3.0735 | 2.2365
[7 empty] | 7807 | 79 | 4.1701 | 3.1274
[7 empty] | 7808 | 80 | 4.3432 | 3.268
[7 empty] | 7809 | 81 | 5.5057 | 4.2125
[7 empty] | 7810 | 82 | 6.5775 | 5.0833
[7 empty] | 7811 | 83 | 7.3031 | 5.6728
[7 empty] | 7812 | 84 | 8.5233 | 6.6642
[7 empty] | 7813 | 85 | 8.2265 | 6.423
[7 empty] | 7814 | 86 | 7.7235 | 6.0144
[7 empty] | 7815 | 87 | 8.1605 | 6.3694
[7 empty] | 7816 | 88 | 8.8118 | 6.8986
[7 empty] | 7817 | 89 | 10.1392 | 7.9771
[7 empty] | 7818 | 90 | 9.5621 | 7.5082
[7 empty] | 7819 | 91 | 10.2382 | 8.0574
[7 empty] | 7820 | 92 | 9.6446 | 7.5751
[7 empty] | 7821 | 93 | 7.2701 | 5.646
[7 empty] | 7822 | 94 | 6.3797 | 4.9225
[7 empty] | 7823 | 95 | 4.5493 | 3.4355
[7 empty] | 7824 | 96 | 3.5765 | 2.6451
[7 empty] | 7825 | 97 | 3.527 | 2.6049
[7 empty] | 7826 | 98 | 3.2384 | 2.3704
[7 empty] | 7827 | 99 | 3.1807 | 2.3235
[7 empty] | 7828 | 100 | 2.8345 | 2.0422
[7 empty] | 7829 | 101 | 2.7767 | 1.9953
[7 empty] | 7830 | 102 | 3.0076 | 2.1829
[7 empty] | 7831 | 103 | 3.7414 | 2.779
[7 empty] | 7832 | 104 | 3.9887 | 2.98
[7 empty] | 7833 | 105 | 4.4669 | 3.3685
[7 empty] | 7834 | 106 | 5.9015 | 4.534
[7 empty] | 7835 | 107 | 6.2477 | 4.8154
[7 empty] | 7836 | 108 | 7.7977 | 6.0747
[7 empty] | 7837 | 109 | 7.1464 | 5.5455
[7 empty] | 7838 | 110 | 6.7012 | 5.1838
[7 empty] | 7839 | 111 | 6.5446 | 5.0565
[7 empty] | 7840 | 112 | 6.6105 | 5.1101
[7 empty] | 7841 | 113 | 6.2725 | 4.8355
[7 empty] | 7842 | 114 | 6.4374 | 4.9694
[7 empty] | 7843 | 115 | 5.9922 | 4.6077
[7 empty] | 7844 | 116 | 6.66 | 5.1503
[7 empty] | 7845 | 117 | 6.2477 | 4.8154
[7 empty] | 7846 | 118 | 5.4892 | 4.1991
[7 empty] | 7847 | 119 | 3.9227 | 2.9264
[7 empty] | 7848 | 120 | 3.6106 | 2.6728
[7 empty] | 7849 | 121 | 2.8922 | 2.0891
[7 empty] | 7850 | 122 | 2.4882 | 1.7609
[7 empty] | 7851 | 123 | 2.4057 | 1.6939
[7 empty] | 7852 | 124 | 2.3727 | 1.6671
[7 empty] | 7853 | 125 | 2.3315 | 1.6336
[7 empty] | 7854 | 126 | 2.4717 | 1.7475
[7 empty] | 7855 | 127 | 3.9557 | 2.9532
[7 empty] | 7856 | 128 | 5.4892 | 4.1991
[7 empty] | 7857 | 129 | 6.1571 | 4.7417
[7 empty] | 7858 | 130 | 6.5858 | 5.09
[7 empty] | 7859 | 131 | 6.7424 | 5.2173
[7 empty] | 7860 | 132 | 6.4951 | 5.0163
[7 empty] | 7861 | 133 | 7.1217 | 5.5254
[7 empty] | 7862 | 134 | 7.4185 | 5.7666
[7 empty] | 7863 | 135 | 7.4844 | 5.8201
[7 empty] | 7864 | 136 | 6.6847 | 5.1704
[7 empty] | 7865 | 137 | 6.5858 | 5.09
[7 empty] | 7866 | 138 | 6.5363 | 5.0498
[7 empty] | 7867 | 139 | 6.2065 | 4.7819
[7 empty] | 7868 | 140 | 6.2148 | 4.7886
[7 empty] | 7869 | 141 | 5.5717 | 4.2661
[7 empty] | 7870 | 142 | 4.9451 | 3.757
[7 empty] | 7871 | 143 | 4.0794 | 3.0537
[7 empty] | 7872 | 144 | 3.4775 | 2.5647
[7 empty] | 7873 | 145 | 3.0158 | 2.1896
[7 empty] | 7874 | 146 | 2.8097 | 2.0221
[7 empty] | 7875 | 147 | 2.7438 | 1.9685
[7 empty] | 7876 | 148 | 2.7355 | 1.9618
[7 empty] | 7877 | 149 | 2.7355 | 1.9618
[7 empty] | 7878 | 150 | 2.7438 | 1.9685
[7 empty] | 7879 | 151 | 3.8073 | 2.8326
[7 empty] | 7880 | 152 | 5.3079 | 4.0517
[7 empty] | 7881 | 153 | 5.9097 | 4.5407
[7 empty] | 7882 | 154 | 6.4621 | 4.9895
[7 empty] | 7883 | 155 | 6.3137 | 4.869
[7 empty] | 7884 | 156 | 6.4786 | 5.0029
[7 empty] | 7885 | 157 | 7.1794 | 5.5723
[7 empty] | 7886 | 158 | 7.5009 | 5.8335
[7 empty] | 7887 | 159 | 7.7648 | 6.0479
[7 empty] | 7888 | 160 | 7.6411 | 5.9474
[7 empty] | 7889 | 161 | 8.3914 | 6.557
[7 empty] | 7890 | 162 | 7.9049 | 6.1618
[7 empty] | 7891 | 163 | 8.2594 | 6.4498
[7 empty] | 7892 | 164 | 6.9321 | 5.3713
[7 empty] | 7893 | 165 | 10.0073 | 7.8699
[7 empty] | 7894 | 166 | 7.9956 | 6.2354
[7 empty] | 7895 | 167 | 4.4504 | 3.3551
[7 empty] | 7896 | 168 | 3.8156 | 2.8393
[7 empty] | 7897 | 1 | 2.381 | 1.6738
[7 empty] | 7898 | 2 | 2.2738 | 1.5867
[7 empty] | 7899 | 3 | 2.2656 | 1.58
[7 empty] | 7900 | 4 | 2.3975 | 1.6872
[7 empty] | 7901 | 5 | 2.414 | 1.7006
[7 empty] | 7902 | 6 | 2.8345 | 2.0422
[7 empty] | 7903 | 7 | 3.5435 | 2.6183
[7 empty] | 7904 | 8 | 4.2031 | 3.1541
[7 empty] | 7905 | 9 | 4.1783 | 3.134
[7 empty] | 7906 | 10 | 5.6706 | 4.3465
[7 empty] | 7907 | 11 | 7.7153 | 6.0077
[7 empty] | 7908 | 12 | 8.6634 | 6.778
[7 empty] | 7909 | 13 | 9.0344 | 7.0795
[7 empty] | 7910 | 14 | 8.8201 | 6.9053
[7 empty] | 7911 | 15 | 8.7294 | 6.8316
[7 empty] | 7912 | 16 | 9.8919 | 7.7761
[7 empty] | 7913 | 17 | 11.1946 | 8.8345
[7 empty] | 7914 | 18 | 10.9555 | 8.6402
[7 empty] | 7915 | 19 | 11.4749 | 9.0622
[7 empty] | 7916 | 20 | 11.4089 | 9.0086
[7 empty] | 7917 | 21 | 11.9696 | 9.4641
[7 empty] | 7918 | 22 | 8.0781 | 6.3024
[7 empty] | 7919 | 23 | 4.368 | 3.2881
[7 empty] | 7920 | 24 | 2.724 | 1.9525
[7 empty] | 7921 | 25 | 2.6283 | 1.8747
[7 empty] | 7922 | 26 | 2.5212 | 1.7877
[7 empty] | 7923 | 27 | 2.4222 | 1.7073
[7 empty] | 7924 | 28 | 2.5047 | 1.7743
[7 empty] | 7925 | 29 | 2.7438 | 1.9685
[7 empty] | 7926 | 30 | 2.9829 | 2.1628
[7 empty] | 7927 | 31 | 3.8156 | 2.8393
[7 empty] | 7928 | 32 | 4.1618 | 3.1207
[7 empty] | 7929 | 33 | 4.8132 | 3.6498
[7 empty] | 7930 | 34 | 5.6954 | 4.3666
[7 empty] | 7931 | 35 | 7.8307 | 6.1015
[7 empty] | 7932 | 36 | 8.8448 | 6.9254
[7 empty] | 7933 | 37 | 8.919 | 6.9857
[7 empty] | 7934 | 38 | 8.9932 | 7.046
[7 empty] | 7935 | 39 | 8.6717 | 6.7847
[7 empty] | 7936 | 40 | 9.7105 | 7.6287
[7 empty] | 7937 | 41 | 10.2547 | 8.0708
[7 empty] | 7938 | 42 | 10.2711 | 8.0842
[7 empty] | 7939 | 43 | 10.6339 | 8.379
[7 empty] | 7940 | 44 | 11.7717 | 9.3034
[7 empty] | 7941 | 45 | 11.3759 | 8.9818
[7 empty] | 7942 | 46 | 8.6717 | 6.7847
[7 empty] | 7943 | 47 | 5.1265 | 3.9044
[7 empty] | 7944 | 48 | 3.6507 | 2.7053
[7 empty] | 7945 | 49 | 2.9993 | 2.1762
[7 empty] | 7946 | 50 | 2.6943 | 1.9283
[7 empty] | 7947 | 51 | 2.5871 | 1.8412
[7 empty] | 7948 | 52 | 2.6201 | 1.868
[7 empty] | 7949 | 53 | 2.6448 | 1.8881
[7 empty] | 7950 | 54 | 3.2137 | 2.3503
[7 empty] | 7951 | 55 | 4.335 | 3.2613
[7 empty] | 7952 | 56 | 4.5741 | 3.4556
[7 empty] | 7953 | 57 | 5.5057 | 4.2125
[7 empty] | 7954 | 58 | 6.594 | 5.0967
[7 empty] | 7955 | 59 | 7.7813 | 6.0613
[7 empty] | 7956 | 60 | 8.3996 | 6.5637
[7 empty] | 7957 | 61 | 9.0674 | 7.1063
[7 empty] | 7958 | 62 | 8.8696 | 6.9455
[7 empty] | 7959 | 63 | 9.4549 | 7.4211
[7 empty] | 7960 | 64 | 10.3866 | 8.178
[7 empty] | 7961 | 65 | 10.9967 | 8.6737
[7 empty] | 7962 | 66 | 10.8977 | 8.5933
[7 empty] | 7963 | 67 | 11.6233 | 9.1828
[7 empty] | 7964 | 68 | 11.8624 | 9.377
[7 empty] | 7965 | 69 | 11.3594 | 8.9684
[7 empty] | 7966 | 70 | 9.1004 | 7.133
[7 empty] | 7967 | 71 | 4.6565 | 3.5226
[7 empty] | 7968 | 72 | 3.5894 | 2.6556
[7 empty] | 7969 | 73 | 2.8839 | 2.0824
[7 empty] | 7970 | 74 | 2.6613 | 1.9015
[7 empty] | 7971 | 75 | 2.5624 | 1.8211
[7 empty] | 7972 | 76 | 2.5047 | 1.7743
[7 empty] | 7973 | 77 | 2.6778 | 1.9149
[7 empty] | 7974 | 78 | 3.0735 | 2.2365
[7 empty] | 7975 | 79 | 4.1701 | 3.1274
[7 empty] | 7976 | 80 | 4.3432 | 3.268
[7 empty] | 7977 | 81 | 5.5057 | 4.2125
[7 empty] | 7978 | 82 | 6.5775 | 5.0833
[7 empty] | 7979 | 83 | 7.3031 | 5.6728
[7 empty] | 7980 | 84 | 8.5233 | 6.6642
[7 empty] | 7981 | 85 | 8.2265 | 6.423
[7 empty] | 7982 | 86 | 7.7235 | 6.0144
[7 empty] | 7983 | 87 | 8.1605 | 6.3694
[7 empty] | 7984 | 88 | 8.8118 | 6.8986
[7 empty] | 7985 | 89 | 10.1392 | 7.9771
[7 empty] | 7986 | 90 | 9.5621 | 7.5082
[7 empty] | 7987 | 91 | 10.2382 | 8.0574
[7 empty] | 7988 | 92 | 9.6446 | 7.5751
[7 empty] | 7989 | 93 | 7.2701 | 5.646
[7 empty] | 7990 | 94 | 6.3797 | 4.9225
[7 empty] | 7991 | 95 | 4.5493 | 3.4355
[7 empty] | 7992 | 96 | 3.5765 | 2.6451
[7 empty] | 7993 | 97 | 3.527 | 2.6049
[7 empty] | 7994 | 98 | 3.2384 | 2.3704
[7 empty] | 7995 | 99 | 3.1807 | 2.3235
[7 empty] | 7996 | 100 | 2.8345 | 2.0422
[7 empty] | 7997 | 101 | 2.7767 | 1.9953
[7 empty] | 7998 | 102 | 3.0076 | 2.1829
[7 empty] | 7999 | 103 | 3.7414 | 2.779
[7 empty] | 8000 | 104 | 3.9887 | 2.98
[7 empty] | 8001 | 105 | 4.4669 | 3.3685
[7 empty] | 8002 | 106 | 5.9015 | 4.534
[7 empty] | 8003 | 107 | 6.2477 | 4.8154
[7 empty] | 8004 | 108 | 7.7977 | 6.0747
[7 empty] | 8005 | 109 | 7.1464 | 5.5455
[7 empty] | 8006 | 110 | 6.7012 | 5.1838
[7 empty] | 8007 | 111 | 6.5446 | 5.0565
[7 empty] | 8008 | 112 | 6.6105 | 5.1101
[7 empty] | 8009 | 113 | 6.2725 | 4.8355
[7 empty] | 8010 | 114 | 6.4374 | 4.9694
[7 empty] | 8011 | 115 | 5.9922 | 4.6077
[7 empty] | 8012 | 116 | 6.66 | 5.1503
[7 empty] | 8013 | 117 | 6.2477 | 4.8154
[7 empty] | 8014 | 118 | 5.4892 | 4.1991
[7 empty] | 8015 | 119 | 3.9227 | 2.9264
[7 empty] | 8016 | 120 | 3.6106 | 2.6728
[7 empty] | 8017 | 121 | 2.8922 | 2.0891
[7 empty] | 8018 | 122 | 2.4882 | 1.7609
[7 empty] | 8019 | 123 | 2.4057 | 1.6939
[7 empty] | 8020 | 124 | 2.3727 | 1.6671
[7 empty] | 8021 | 125 | 2.3315 | 1.6336
[7 empty] | 8022 | 126 | 2.4717 | 1.7475
[7 empty] | 8023 | 127 | 3.9557 | 2.9532
[7 empty] | 8024 | 128 | 5.4892 | 4.1991
[7 empty] | 8025 | 129 | 6.1571 | 4.7417
[7 empty] | 8026 | 130 | 6.5858 | 5.09
[7 empty] | 8027 | 131 | 6.7424 | 5.2173
[7 empty] | 8028 | 132 | 6.4951 | 5.0163
[7 empty] | 8029 | 133 | 7.1217 | 5.5254
[7 empty] | 8030 | 134 | 7.4185 | 5.7666
[7 empty] | 8031 | 135 | 7.4844 | 5.8201
[7 empty] | 8032 | 136 | 6.6847 | 5.1704
[7 empty] | 8033 | 137 | 6.5858 | 5.09
[7 empty] | 8034 | 138 | 6.5363 | 5.0498
[7 empty] | 8035 | 139 | 6.2065 | 4.7819
[7 empty] | 8036 | 140 | 6.2148 | 4.7886
[7 empty] | 8037 | 141 | 5.5717 | 4.2661
[7 empty] | 8038 | 142 | 4.9451 | 3.757
[7 empty] | 8039 | 143 | 4.0794 | 3.0537
[7 empty] | 8040 | 144 | 3.4775 | 2.5647
[7 empty] | 8041 | 145 | 3.0158 | 2.1896
[7 empty] | 8042 | 146 | 2.8097 | 2.0221
[7 empty] | 8043 | 147 | 2.7438 | 1.9685
[7 empty] | 8044 | 148 | 2.7355 | 1.9618
[7 empty] | 8045 | 149 | 2.7355 | 1.9618
[7 empty] | 8046 | 150 | 2.7438 | 1.9685
[7 empty] | 8047 | 151 | 3.8073 | 2.8326
[7 empty] | 8048 | 152 | 5.3079 | 4.0517
[7 empty] | 8049 | 153 | 5.9097 | 4.5407
[7 empty] | 8050 | 154 | 6.4621 | 4.9895
[7 empty] | 8051 | 155 | 6.3137 | 4.869
[7 empty] | 8052 | 156 | 6.4786 | 5.0029
[7 empty] | 8053 | 157 | 7.1794 | 5.5723
[7 empty] | 8054 | 158 | 7.5009 | 5.8335
[7 empty] | 8055 | 159 | 7.7648 | 6.0479
[7 empty] | 8056 | 160 | 7.6411 | 5.9474
[7 empty] | 8057 | 161 | 8.3914 | 6.557
[7 empty] | 8058 | 162 | 7.9049 | 6.1618
[7 empty] | 8059 | 163 | 8.2594 | 6.4498
[7 empty] | 8060 | 164 | 6.9321 | 5.3713
[7 empty] | 8061 | 165 | 10.0073 | 7.8699
[7 empty] | 8062 | 166 | 7.9956 | 6.2354
[7 empty] | 8063 | 167 | 4.4504 | 3.3551
[7 empty] | 8064 | 168 | 3.8156 | 2.8393
[7 empty] | 8065 | 1 | 2.381 | 1.6738
[7 empty] | 8066 | 2 | 2.2738 | 1.5867
[7 empty] | 8067 | 3 | 2.2656 | 1.58
[7 empty] | 8068 | 4 | 2.3975 | 1.6872
[7 empty] | 8069 | 5 | 2.414 | 1.7006
[7 empty] | 8070 | 6 | 2.8345 | 2.0422
[7 empty] | 8071 | 7 | 3.5435 | 2.6183
[7 empty] | 8072 | 8 | 4.2031 | 3.1541
[7 empty] | 8073 | 9 | 4.1783 | 3.134
[7 empty] | 8074 | 10 | 5.6706 | 4.3465
[7 empty] | 8075 | 11 | 7.7153 | 6.0077
[7 empty] | 8076 | 12 | 8.6634 | 6.778
[7 empty] | 8077 | 13 | 9.0344 | 7.0795
[7 empty] | 8078 | 14 | 8.8201 | 6.9053
[7 empty] | 8079 | 15 | 8.7294 | 6.8316
[7 empty] | 8080 | 16 | 9.8919 | 7.7761
[7 empty] | 8081 | 17 | 11.1946 | 8.8345
[7 empty] | 8082 | 18 | 10.9555 | 8.6402
[7 empty] | 8083 | 19 | 11.4749 | 9.0622
[7 empty] | 8084 | 20 | 11.4089 | 9.0086
[7 empty] | 8085 | 21 | 11.9696 | 9.4641
[7 empty] | 8086 | 22 | 8.0781 | 6.3024
[7 empty] | 8087 | 23 | 4.368 | 3.2881
[7 empty] | 8088 | 24 | 2.724 | 1.9525
[7 empty] | 8089 | 25 | 2.6283 | 1.8747
[7 empty] | 8090 | 26 | 2.5212 | 1.7877
[7 empty] | 8091 | 27 | 2.4222 | 1.7073
[7 empty] | 8092 | 28 | 2.5047 | 1.7743
[7 empty] | 8093 | 29 | 2.7438 | 1.9685
[7 empty] | 8094 | 30 | 2.9829 | 2.1628
[7 empty] | 8095 | 31 | 3.8156 | 2.8393
[7 empty] | 8096 | 32 | 4.1618 | 3.1207
[7 empty] | 8097 | 33 | 4.8132 | 3.6498
[7 empty] | 8098 | 34 | 5.6954 | 4.3666
[7 empty] | 8099 | 35 | 7.8307 | 6.1015
[7 empty] | 8100 | 36 | 8.8448 | 6.9254
[7 empty] | 8101 | 37 | 8.919 | 6.9857
[7 empty] | 8102 | 38 | 8.9932 | 7.046
[7 empty] | 8103 | 39 | 8.6717 | 6.7847
[7 empty] | 8104 | 40 | 9.7105 | 7.6287
[7 empty] | 8105 | 41 | 10.2547 | 8.0708
[7 empty] | 8106 | 42 | 10.2711 | 8.0842
[7 empty] | 8107 | 43 | 10.6339 | 8.379
[7 empty] | 8108 | 44 | 11.7717 | 9.3034
[7 empty] | 8109 | 45 | 11.3759 | 8.9818
[7 empty] | 8110 | 46 | 8.6717 | 6.7847
[7 empty] | 8111 | 47 | 5.1265 | 3.9044
[7 empty] | 8112 | 48 | 3.6507 | 2.7053
[7 empty] | 8113 | 49 | 2.9993 | 2.1762
[7 empty] | 8114 | 50 | 2.6943 | 1.9283
[7 empty] | 8115 | 51 | 2.5871 | 1.8412
[7 empty] | 8116 | 52 | 2.6201 | 1.868
[7 empty] | 8117 | 53 | 2.6448 | 1.8881
[7 empty] | 8118 | 54 | 3.2137 | 2.3503
[7 empty] | 8119 | 55 | 4.335 | 3.2613
[7 empty] | 8120 | 56 | 4.5741 | 3.4556
[7 empty] | 8121 | 57 | 5.5057 | 4.2125
[7 empty] | 8122 | 58 | 6.594 | 5.0967
[7 empty] | 8123 | 59 | 7.7813 | 6.0613
[7 empty] | 8124 | 60 | 8.3996 | 6.5637
[7 empty] | 8125 | 61 | 9.0674 | 7.1063
[7 empty] | 8126 | 62 | 8.8696 | 6.9455
[7 empty] | 8127 | 63 | 9.4549 | 7.4211
[7 empty] | 8128 | 64 | 10.3866 | 8.178
[7 empty] | 8129 | 65 | 10.9967 | 8.6737
[7 empty] | 8130 | 66 | 10.8977 | 8.5933
[7 empty] | 8131 | 67 | 11.6233 | 9.1828
[7 empty] | 8132 | 68 | 11.8624 | 9.377
[7 empty] | 8133 | 69 | 11.3594 | 8.9684
[7 empty] | 8134 | 70 | 9.1004 | 7.133
[7 empty] | 8135 | 71 | 4.6565 | 3.5226
[7 empty] | 8136 | 72 | 3.5894 | 2.6556
[7 empty] | 8137 | 73 | 2.8839 | 2.0824
[7 empty] | 8138 | 74 | 2.6613 | 1.9015
[7 empty] | 8139 | 75 | 2.5624 | 1.8211
[7 empty] | 8140 | 76 | 2.5047 | 1.7743
[7 empty] | 8141 | 77 | 2.6778 | 1.9149
[7 empty] | 8142 | 78 | 3.0735 | 2.2365
[7 empty] | 8143 | 79 | 4.1701 | 3.1274
[7 empty] | 8144 | 80 | 4.3432 | 3.268
[7 empty] | 8145 | 81 | 5.5057 | 4.2125
[7 empty] | 8146 | 82 | 6.5775 | 5.0833
[7 empty] | 8147 | 83 | 7.3031 | 5.6728
[7 empty] | 8148 | 84 | 8.5233 | 6.6642
[7 empty] | 8149 | 85 | 8.2265 | 6.423
[7 empty] | 8150 | 86 | 7.7235 | 6.0144
[7 empty] | 8151 | 87 | 8.1605 | 6.3694
[7 empty] | 8152 | 88 | 8.8118 | 6.8986
[7 empty] | 8153 | 89 | 10.1392 | 7.9771
[7 empty] | 8154 | 90 | 9.5621 | 7.5082
[7 empty] | 8155 | 91 | 10.2382 | 8.0574
[7 empty] | 8156 | 92 | 9.6446 | 7.5751
[7 empty] | 8157 | 93 | 7.2701 | 5.646
[7 empty] | 8158 | 94 | 6.3797 | 4.9225
[7 empty] | 8159 | 95 | 4.5493 | 3.4355
[7 empty] | 8160 | 96 | 3.5765 | 2.6451
[7 empty] | 8161 | 97 | 3.527 | 2.6049
[7 empty] | 8162 | 98 | 3.2384 | 2.3704
[7 empty] | 8163 | 99 | 3.1807 | 2.3235
[7 empty] | 8164 | 100 | 2.8345 | 2.0422
[7 empty] | 8165 | 101 | 2.7767 | 1.9953
[7 empty] | 8166 | 102 | 3.0076 | 2.1829
[7 empty] | 8167 | 103 | 3.7414 | 2.779
[7 empty] | 8168 | 104 | 3.9887 | 2.98
[7 empty] | 8169 | 105 | 4.4669 | 3.3685
[7 empty] | 8170 | 106 | 5.9015 | 4.534
[7 empty] | 8171 | 107 | 6.2477 | 4.8154
[7 empty] | 8172 | 108 | 7.7977 | 6.0747
[7 empty] | 8173 | 109 | 7.1464 | 5.5455
[7 empty] | 8174 | 110 | 6.7012 | 5.1838
[7 empty] | 8175 | 111 | 6.5446 | 5.0565
[7 empty] | 8176 | 112 | 6.6105 | 5.1101
[7 empty] | 8177 | 113 | 6.2725 | 4.8355
[7 empty] | 8178 | 114 | 6.4374 | 4.9694
[7 empty] | 8179 | 115 | 5.9922 | 4.6077
[7 empty] | 8180 | 116 | 6.66 | 5.1503
[7 empty] | 8181 | 117 | 6.2477 | 4.8154
[7 empty] | 8182 | 118 | 5.4892 | 4.1991
[7 empty] | 8183 | 119 | 3.9227 | 2.9264
[7 empty] | 8184 | 120 | 3.6106 | 2.6728
[7 empty] | 8185 | 121 | 2.8922 | 2.0891
[7 empty] | 8186 | 122 | 2.4882 | 1.7609
[7 empty] | 8187 | 123 | 2.4057 | 1.6939
[7 empty] | 8188 | 124 | 2.3727 | 1.6671
[7 empty] | 8189 | 125 | 2.3315 | 1.6336
[7 empty] | 8190 | 126 | 2.4717 | 1.7475
[7 empty] | 8191 | 127 | 3.9557 | 2.9532
[7 empty] | 8192 | 128 | 5.4892 | 4.1991
[7 empty] | 8193 | 129 | 6.1571 | 4.7417
[7 empty] | 8194 | 130 | 6.5858 | 5.09
[7 empty] | 8195 | 131 | 6.7424 | 5.2173
[7 empty] | 8196 | 132 | 6.4951 | 5.0163
[7 empty] | 8197 | 133 | 7.1217 | 5.5254
[7 empty] | 8198 | 134 | 7.4185 | 5.7666
[7 empty] | 8199 | 135 | 7.4844 | 5.8201
[7 empty] | 8200 | 136 | 6.6847 | 5.1704
[7 empty] | 8201 | 137 | 6.5858 | 5.09
[7 empty] | 8202 | 138 | 6.5363 | 5.0498
[7 empty] | 8203 | 139 | 6.2065 | 4.7819
[7 empty] | 8204 | 140 | 6.2148 | 4.7886
[7 empty] | 8205 | 141 | 5.5717 | 4.2661
[7 empty] | 8206 | 142 | 4.9451 | 3.757
[7 empty] | 8207 | 143 | 4.0794 | 3.0537
[7 empty] | 8208 | 144 | 3.4775 | 2.5647
[7 empty] | 8209 | 145 | 3.0158 | 2.1896
[7 empty] | 8210 | 146 | 2.8097 | 2.0221
[7 empty] | 8211 | 147 | 2.7438 | 1.9685
[7 empty] | 8212 | 148 | 2.7355 | 1.9618
[7 empty] | 8213 | 149 | 2.7355 | 1.9618
[7 empty] | 8214 | 150 | 2.7438 | 1.9685
[7 empty] | 8215 | 151 | 3.8073 | 2.8326
[7 empty] | 8216 | 152 | 5.3079 | 4.0517
[7 empty] | 8217 | 153 | 5.9097 | 4.5407
[7 empty] | 8218 | 154 | 6.4621 | 4.9895
[7 empty] | 8219 | 155 | 6.3137 | 4.869
[7 empty] | 8220 | 156 | 6.4786 | 5.0029
[7 empty] | 8221 | 157 | 7.1794 | 5.5723
[7 empty] | 8222 | 158 | 7.5009 | 5.8335
[7 empty] | 8223 | 159 | 7.7648 | 6.0479
[7 empty] | 8224 | 160 | 7.6411 | 5.9474
[7 empty] | 8225 | 161 | 8.3914 | 6.557
[7 empty] | 8226 | 162 | 7.9049 | 6.1618
[7 empty] | 8227 | 163 | 8.2594 | 6.4498
[7 empty] | 8228 | 164 | 6.9321 | 5.3713
[7 empty] | 8229 | 165 | 10.0073 | 7.8699
[7 empty] | 8230 | 166 | 7.9956 | 6.2354
[7 empty] | 8231 | 167 | 4.4504 | 3.3551
[7 empty] | 8232 | 168 | 3.8156 | 2.8393
[7 empty] | 8233 | 1 | 2.381 | 1.6738
[7 empty] | 8234 | 2 | 2.2738 | 1.5867
[7 empty] | 8235 | 3 | 2.2656 | 1.58
[7 empty] | 8236 | 4 | 2.3975 | 1.6872
[7 empty] | 8237 | 5 | 2.414 | 1.7006
[7 empty] | 8238 | 6 | 2.8345 | 2.0422
[7 empty] | 8239 | 7 | 3.5435 | 2.6183
[7 empty] | 8240 | 8 | 4.2031 | 3.1541
[7 empty] | 8241 | 9 | 4.1783 | 3.134
[7 empty] | 8242 | 10 | 5.6706 | 4.3465
[7 empty] | 8243 | 11 | 7.7153 | 6.0077
[7 empty] | 8244 | 12 | 8.6634 | 6.778
[7 empty] | 8245 | 13 | 9.0344 | 7.0795
[7 empty] | 8246 | 14 | 8.8201 | 6.9053
[7 empty] | 8247 | 15 | 8.7294 | 6.8316
[7 empty] | 8248 | 16 | 9.8919 | 7.7761
[7 empty] | 8249 | 17 | 11.1946 | 8.8345
[7 empty] | 8250 | 18 | 10.9555 | 8.6402
[7 empty] | 8251 | 19 | 11.4749 | 9.0622
[7 empty] | 8252 | 20 | 11.4089 | 9.0086
[7 empty] | 8253 | 21 | 11.9696 | 9.4641
[7 empty] | 8254 | 22 | 8.0781 | 6.3024
[7 empty] | 8255 | 23 | 4.368 | 3.2881
[7 empty] | 8256 | 24 | 2.724 | 1.9525
[7 empty] | 8257 | 25 | 2.6283 | 1.8747
[7 empty] | 8258 | 26 | 2.5212 | 1.7877
[7 empty] | 8259 | 27 | 2.4222 | 1.7073
[7 empty] | 8260 | 28 | 2.5047 | 1.7743
[7 empty] | 8261 | 29 | 2.7438 | 1.9685
[7 empty] | 8262 | 30 | 2.9829 | 2.1628
[7 empty] | 8263 | 31 | 3.8156 | 2.8393
[7 empty] | 8264 | 32 | 4.1618 | 3.1207
[7 empty] | 8265 | 33 | 4.8132 | 3.6498
[7 empty] | 8266 | 34 | 5.6954 | 4.3666
[7 empty] | 8267 | 35 | 7.8307 | 6.1015
[7 empty] | 8268 | 36 | 8.8448 | 6.9254
[7 empty] | 8269 | 37 | 8.919 | 6.9857
[7 empty] | 8270 | 38 | 8.9932 | 7.046
[7 empty] | 8271 | 39 | 8.6717 | 6.7847
[7 empty] | 8272 | 40 | 9.7105 | 7.6287
[7 empty] | 8273 | 41 | 10.2547 | 8.0708
[7 empty] | 8274 | 42 | 10.2711 | 8.0842
[7 empty] | 8275 | 43 | 10.6339 | 8.379
[7 empty] | 8276 | 44 | 11.7717 | 9.3034
[7 empty] | 8277 | 45 | 11.3759 | 8.9818
[7 empty] | 8278 | 46 | 8.6717 | 6.7847
[7 empty] | 8279 | 47 | 5.1265 | 3.9044
[7 empty] | 8280 | 48 | 3.6507 | 2.7053
[7 empty] | 8281 | 49 | 2.9993 | 2.1762
[7 empty] | 8282 | 50 | 2.6943 | 1.9283
[7 empty] | 8283 | 51 | 2.5871 | 1.8412
[7 empty] | 8284 | 52 | 2.6201 | 1.868
[7 empty] | 8285 | 53 | 2.6448 | 1.8881
[7 empty] | 8286 | 54 | 3.2137 | 2.3503
[7 empty] | 8287 | 55 | 4.335 | 3.2613
[7 empty] | 8288 | 56 | 4.5741 | 3.4556
[7 empty] | 8289 | 57 | 5.5057 | 4.2125
[7 empty] | 8290 | 58 | 6.594 | 5.0967
[7 empty] | 8291 | 59 | 7.7813 | 6.0613
[7 empty] | 8292 | 60 | 8.3996 | 6.5637
[7 empty] | 8293 | 61 | 9.0674 | 7.1063
[7 empty] | 8294 | 62 | 8.8696 | 6.9455
[7 empty] | 8295 | 63 | 9.4549 | 7.4211
[7 empty] | 8296 | 64 | 10.3866 | 8.178
[7 empty] | 8297 | 65 | 10.9967 | 8.6737
[7 empty] | 8298 | 66 | 10.8977 | 8.5933
[7 empty] | 8299 | 67 | 11.6233 | 9.1828
[7 empty] | 8300 | 68 | 11.8624 | 9.377
[7 empty] | 8301 | 69 | 11.3594 | 8.9684
[7 empty] | 8302 | 70 | 9.1004 | 7.133
[7 empty] | 8303 | 71 | 4.6565 | 3.5226
[7 empty] | 8304 | 72 | 3.5894 | 2.6556
[7 empty] | 8305 | 73 | 2.8839 | 2.0824
[7 empty] | 8306 | 74 | 2.6613 | 1.9015
[7 empty] | 8307 | 75 | 2.5624 | 1.8211
[7 empty] | 8308 | 76 | 2.5047 | 1.7743
[7 empty] | 8309 | 77 | 2.6778 | 1.9149
[7 empty] | 8310 | 78 | 3.0735 | 2.2365
[7 empty] | 8311 | 79 | 4.1701 | 3.1274
[7 empty] | 8312 | 80 | 4.3432 | 3.268
[7 empty] | 8313 | 81 | 5.5057 | 4.2125
[7 empty] | 8314 | 82 | 6.5775 | 5.0833
[7 empty] | 8315 | 83 | 7.3031 | 5.6728
[7 empty] | 8316 | 84 | 8.5233 | 6.6642
[7 empty] | 8317 | 85 | 8.2265 | 6.423
[7 empty] | 8318 | 86 | 7.7235 | 6.0144
[7 empty] | 8319 | 87 | 8.1605 | 6.3694
[7 empty] | 8320 | 88 | 8.8118 | 6.8986
[7 empty] | 8321 | 89 | 10.1392 | 7.9771
[7 empty] | 8322 | 90 | 9.5621 | 7.5082
[7 empty] | 8323 | 91 | 10.2382 | 8.0574
[7 empty] | 8324 | 92 | 9.6446 | 7.5751
[7 empty] | 8325 | 93 | 7.2701 | 5.646
[7 empty] | 8326 | 94 | 6.3797 | 4.9225
[7 empty] | 8327 | 95 | 4.5493 | 3.4355
[7 empty] | 8328 | 96 | 3.5765 | 2.6451
[7 empty] | 8329 | 97 | 3.527 | 2.6049
[7 empty] | 8330 | 98 | 3.2384 | 2.3704
[7 empty] | 8331 | 99 | 3.1807 | 2.3235
[7 empty] | 8332 | 100 | 2.8345 | 2.0422
[7 empty] | 8333 | 101 | 2.7767 | 1.9953
[7 empty] | 8334 | 102 | 3.0076 | 2.1829
[7 empty] | 8335 | 103 | 3.7414 | 2.779
[7 empty] | 8336 | 104 | 3.9887 | 2.98
[7 empty] | 8337 | 105 | 4.4669 | 3.3685
[7 empty] | 8338 | 106 | 5.9015 | 4.534
[7 empty] | 8339 | 107 | 6.2477 | 4.8154
[7 empty] | 8340 | 108 | 7.7977 | 6.0747
[7 empty] | 8341 | 109 | 7.1464 | 5.5455
[7 empty] | 8342 | 110 | 6.7012 | 5.1838
[7 empty] | 8343 | 111 | 6.5446 | 5.0565
[7 empty] | 8344 | 112 | 6.6105 | 5.1101
[7 empty] | 8345 | 113 | 6.2725 | 4.8355
[7 empty] | 8346 | 114 | 6.4374 | 4.9694
[7 empty] | 8347 | 115 | 5.9922 | 4.6077
[7 empty] | 8348 | 116 | 6.66 | 5.1503
[7 empty] | 8349 | 117 | 6.2477 | 4.8154
[7 empty] | 8350 | 118 | 5.4892 | 4.1991
[7 empty] | 8351 | 119 | 3.9227 | 2.9264
[7 empty] | 8352 | 120 | 3.6106 | 2.6728
[7 empty] | 8353 | 121 | 2.8922 | 2.0891
[7 empty] | 8354 | 122 | 2.4882 | 1.7609
[7 empty] | 8355 | 123 | 2.4057 | 1.6939
[7 empty] | 8356 | 124 | 2.3727 | 1.6671
[7 empty] | 8357 | 125 | 2.3315 | 1.6336
[7 empty] | 8358 | 126 | 2.4717 | 1.7475
[7 empty] | 8359 | 127 | 3.9557 | 2.9532
[7 empty] | 8360 | 128 | 5.4892 | 4.1991
[7 empty] | 8361 | 129 | 6.1571 | 4.7417
[7 empty] | 8362 | 130 | 6.5858 | 5.09
[7 empty] | 8363 | 131 | 6.7424 | 5.2173
[7 empty] | 8364 | 132 | 6.4951 | 5.0163
[7 empty] | 8365 | 133 | 7.1217 | 5.5254
[7 empty] | 8366 | 134 | 7.4185 | 5.7666
[7 empty] | 8367 | 135 | 7.4844 | 5.8201
[7 empty] | 8368 | 136 | 6.6847 | 5.1704
[7 empty] | 8369 | 137 | 6.5858 | 5.09
[7 empty] | 8370 | 138 | 6.5363 | 5.0498
[7 empty] | 8371 | 139 | 6.2065 | 4.7819
[7 empty] | 8372 | 140 | 6.2148 | 4.7886
[7 empty] | 8373 | 141 | 5.5717 | 4.2661
[7 empty] | 8374 | 142 | 4.9451 | 3.757
[7 empty] | 8375 | 143 | 4.0794 | 3.0537
[7 empty] | 8376 | 144 | 3.4775 | 2.5647
[7 empty] | 8377 | 145 | 3.0158 | 2.1896
[7 empty] | 8378 | 146 | 2.8097 | 2.0221
[7 empty] | 8379 | 147 | 2.7438 | 1.9685
[7 empty] | 8380 | 148 | 2.7355 | 1.9618
[7 empty] | 8381 | 149 | 2.7355 | 1.9618
[7 empty] | 8382 | 150 | 2.7438 | 1.9685
[7 empty] | 8383 | 151 | 3.8073 | 2.8326
[7 empty] | 8384 | 152 | 5.3079 | 4.0517
[7 empty] | 8385 | 153 | 5.9097 | 4.5407
[7 empty] | 8386 | 154 | 6.4621 | 4.9895
[7 empty] | 8387 | 155 | 6.3137 | 4.869
[7 empty] | 8388 | 156 | 6.4786 | 5.0029
[7 empty] | 8389 | 157 | 7.1794 | 5.5723
[7 empty] | 8390 | 158 | 7.5009 | 5.8335
[7 empty] | 8391 | 159 | 7.7648 | 6.0479
[7 empty] | 8392 | 160 | 7.6411 | 5.9474
[7 empty] | 8393 | 161 | 8.3914 | 6.557
[7 empty] | 8394 | 162 | 7.9049 | 6.1618
[7 empty] | 8395 | 163 | 8.2594 | 6.4498
[7 empty] | 8396 | 164 | 6.9321 | 5.3713
[7 empty] | 8397 | 165 | 10.0073 | 7.8699
[7 empty] | 8398 | 166 | 7.9956 | 6.2354
[7 empty] | 8399 | 167 | 4.4504 | 3.3551
[7 empty] | 8400 | 168 | 3.8156 | 2.8393
[7 empty] | 8401 | 1 | 2.381 | 1.6738
[7 empty] | 8402 | 2 | 2.2738 | 1.5867
[7 empty] | 8403 | 3 | 2.2656 | 1.58
[7 empty] | 8404 | 4 | 2.3975 | 1.6872
[7 empty] | 8405 | 5 | 2.414 | 1.7006
[7 empty] | 8406 | 6 | 2.8345 | 2.0422
[7 empty] | 8407 | 7 | 3.5435 | 2.6183
[7 empty] | 8408 | 8 | 4.2031 | 3.1541
[7 empty] | 8409 | 9 | 4.1783 | 3.134
[7 empty] | 8410 | 10 | 5.6706 | 4.3465
[7 empty] | 8411 | 11 | 7.7153 | 6.0077
[7 empty] | 8412 | 12 | 8.6634 | 6.778
[7 empty] | 8413 | 13 | 9.0344 | 7.0795
[7 empty] | 8414 | 14 | 8.8201 | 6.9053
[7 empty] | 8415 | 15 | 8.7294 | 6.8316
[7 empty] | 8416 | 16 | 9.8919 | 7.7761
[7 empty] | 8417 | 17 | 11.1946 | 8.8345
[7 empty] | 8418 | 18 | 10.9555 | 8.6402
[7 empty] | 8419 | 19 | 11.4749 | 9.0622
[7 empty] | 8420 | 20 | 11.4089 | 9.0086
[7 empty] | 8421 | 21 | 11.9696 | 9.4641
[7 empty] | 8422 | 22 | 8.0781 | 6.3024
[7 empty] | 8423 | 23 | 4.368 | 3.2881
[7 empty] | 8424 | 24 | 2.724 | 1.9525
[7 empty] | 8425 | 25 | 2.6283 | 1.8747
[7 empty] | 8426 | 26 | 2.5212 | 1.7877
[7 empty] | 8427 | 27 | 2.4222 | 1.7073
[7 empty] | 8428 | 28 | 2.5047 | 1.7743
[7 empty] | 8429 | 29 | 2.7438 | 1.9685
[7 empty] | 8430 | 30 | 2.9829 | 2.1628
[7 empty] | 8431 | 31 | 3.8156 | 2.8393
[7 empty] | 8432 | 32 | 4.1618 | 3.1207
[7 empty] | 8433 | 33 | 4.8132 | 3.6498
[7 empty] | 8434 | 34 | 5.6954 | 4.3666
[7 empty] | 8435 | 35 | 7.8307 | 6.1015
[7 empty] | 8436 | 36 | 8.8448 | 6.9254
[7 empty] | 8437 | 37 | 8.919 | 6.9857
[7 empty] | 8438 | 38 | 8.9932 | 7.046
[7 empty] | 8439 | 39 | 8.6717 | 6.7847
[7 empty] | 8440 | 40 | 9.7105 | 7.6287
[7 empty] | 8441 | 41 | 10.2547 | 8.0708
[7 empty] | 8442 | 42 | 10.2711 | 8.0842
[7 empty] | 8443 | 43 | 10.6339 | 8.379
[7 empty] | 8444 | 44 | 11.7717 | 9.3034
[7 empty] | 8445 | 45 | 11.3759 | 8.9818
[7 empty] | 8446 | 46 | 8.6717 | 6.7847
[7 empty] | 8447 | 47 | 5.1265 | 3.9044
[7 empty] | 8448 | 48 | 3.6507 | 2.7053
[7 empty] | 8449 | 49 | 2.9993 | 2.1762
[7 empty] | 8450 | 50 | 2.6943 | 1.9283
[7 empty] | 8451 | 51 | 2.5871 | 1.8412
[7 empty] | 8452 | 52 | 2.6201 | 1.868
[7 empty] | 8453 | 53 | 2.6448 | 1.8881
[7 empty] | 8454 | 54 | 3.2137 | 2.3503
[7 empty] | 8455 | 55 | 4.335 | 3.2613
[7 empty] | 8456 | 56 | 4.5741 | 3.4556
[7 empty] | 8457 | 57 | 5.5057 | 4.2125
[7 empty] | 8458 | 58 | 6.594 | 5.0967
[7 empty] | 8459 | 59 | 7.7813 | 6.0613
[7 empty] | 8460 | 60 | 8.3996 | 6.5637
[7 empty] | 8461 | 61 | 9.0674 | 7.1063
[7 empty] | 8462 | 62 | 8.8696 | 6.9455
[7 empty] | 8463 | 63 | 9.4549 | 7.4211
[7 empty] | 8464 | 64 | 10.3866 | 8.178
[7 empty] | 8465 | 65 | 10.9967 | 8.6737
[7 empty] | 8466 | 66 | 10.8977 | 8.5933
[7 empty] | 8467 | 67 | 11.6233 | 9.1828
[7 empty] | 8468 | 68 | 11.8624 | 9.377
[7 empty] | 8469 | 69 | 11.3594 | 8.9684
[7 empty] | 8470 | 70 | 9.1004 | 7.133
[7 empty] | 8471 | 71 | 4.6565 | 3.5226
[7 empty] | 8472 | 72 | 3.5894 | 2.6556
[7 empty] | 8473 | 73 | 2.8839 | 2.0824
[7 empty] | 8474 | 74 | 2.6613 | 1.9015
[7 empty] | 8475 | 75 | 2.5624 | 1.8211
[7 empty] | 8476 | 76 | 2.5047 | 1.7743
[7 empty] | 8477 | 77 | 2.6778 | 1.9149
[7 empty] | 8478 | 78 | 3.0735 | 2.2365
[7 empty] | 8479 | 79 | 4.1701 | 3.1274
[7 empty] | 8480 | 80 | 4.3432 | 3.268
[7 empty] | 8481 | 81 | 5.5057 | 4.2125
[7 empty] | 8482 | 82 | 6.5775 | 5.0833
[7 empty] | 8483 | 83 | 7.3031 | 5.6728
[7 empty] | 8484 | 84 | 8.5233 | 6.6642
[7 empty] | 8485 | 85 | 8.2265 | 6.423
[7 empty] | 8486 | 86 | 7.7235 | 6.0144
[7 empty] | 8487 | 87 | 8.1605 | 6.3694
[7 empty] | 8488 | 88 | 8.8118 | 6.8986
[7 empty] | 8489 | 89 | 10.1392 | 7.9771
[7 empty] | 8490 | 90 | 9.5621 | 7.5082
[7 empty] | 8491 | 91 | 10.2382 | 8.0574
[7 empty] | 8492 | 92 | 9.6446 | 7.5751
[7 empty] | 8493 | 93 | 7.2701 | 5.646
[7 empty] | 8494 | 94 | 6.3797 | 4.9225
[7 empty] | 8495 | 95 | 4.5493 | 3.4355
[7 empty] | 8496 | 96 | 3.5765 | 2.6451
[7 empty] | 8497 | 97 | 3.527 | 2.6049
[7 empty] | 8498 | 98 | 3.2384 | 2.3704
[7 empty] | 8499 | 99 | 3.1807 | 2.3235
[7 empty] | 8500 | 100 | 2.8345 | 2.0422
[7 empty] | 8501 | 101 | 2.7767 | 1.9953
[7 empty] | 8502 | 102 | 3.0076 | 2.1829
[7 empty] | 8503 | 103 | 3.7414 | 2.779
[7 empty] | 8504 | 104 | 3.9887 | 2.98
[7 empty] | 8505 | 105 | 4.4669 | 3.3685
[7 empty] | 8506 | 106 | 5.9015 | 4.534
[7 empty] | 8507 | 107 | 6.2477 | 4.8154
[7 empty] | 8508 | 108 | 7.7977 | 6.0747
[7 empty] | 8509 | 109 | 7.1464 | 5.5455
[7 empty] | 8510 | 110 | 6.7012 | 5.1838
[7 empty] | 8511 | 111 | 6.5446 | 5.0565
[7 empty] | 8512 | 112 | 6.6105 | 5.1101
[7 empty] | 8513 | 113 | 6.2725 | 4.8355
[7 empty] | 8514 | 114 | 6.4374 | 4.9694
[7 empty] | 8515 | 115 | 5.9922 | 4.6077
[7 empty] | 8516 | 116 | 6.66 | 5.1503
[7 empty] | 8517 | 117 | 6.2477 | 4.8154
[7 empty] | 8518 | 118 | 5.4892 | 4.1991
[7 empty] | 8519 | 119 | 3.9227 | 2.9264
[7 empty] | 8520 | 120 | 3.6106 | 2.6728
[7 empty] | 8521 | 121 | 2.8922 | 2.0891
[7 empty] | 8522 | 122 | 2.4882 | 1.7609
[7 empty] | 8523 | 123 | 2.4057 | 1.6939
[7 empty] | 8524 | 124 | 2.3727 | 1.6671
[7 empty] | 8525 | 125 | 2.3315 | 1.6336
[7 empty] | 8526 | 126 | 2.4717 | 1.7475
[7 empty] | 8527 | 127 | 3.9557 | 2.9532
[7 empty] | 8528 | 128 | 5.4892 | 4.1991
[7 empty] | 8529 | 129 | 6.1571 | 4.7417
[7 empty] | 8530 | 130 | 6.5858 | 5.09
[7 empty] | 8531 | 131 | 6.7424 | 5.2173
[7 empty] | 8532 | 132 | 6.4951 | 5.0163
[7 empty] | 8533 | 133 | 7.1217 | 5.5254
[7 empty] | 8534 | 134 | 7.4185 | 5.7666
[7 empty] | 8535 | 135 | 7.4844 | 5.8201
[7 empty] | 8536 | 136 | 6.6847 | 5.1704
[7 empty] | 8537 | 137 | 6.5858 | 5.09
[7 empty] | 8538 | 138 | 6.5363 | 5.0498
[7 empty] | 8539 | 139 | 6.2065 | 4.7819
[7 empty] | 8540 | 140 | 6.2148 | 4.7886
[7 empty] | 8541 | 141 | 5.5717 | 4.2661
[7 empty] | 8542 | 142 | 4.9451 | 3.757
[7 empty] | 8543 | 143 | 4.0794 | 3.0537
[7 empty] | 8544 | 144 | 3.4775 | 2.5647
[7 empty] | 8545 | 145 | 3.0158 | 2.1896
[7 empty] | 8546 | 146 | 2.8097 | 2.0221
[7 empty] | 8547 | 147 | 2.7438 | 1.9685
[7 empty] | 8548 | 148 | 2.7355 | 1.9618
[7 empty] | 8549 | 149 | 2.7355 | 1.9618
[7 empty] | 8550 | 150 | 2.7438 | 1.9685
[7 empty] | 8551 | 151 | 3.8073 | 2.8326
[7 empty] | 8552 | 152 | 5.3079 | 4.0517
[7 empty] | 8553 | 153 | 5.9097 | 4.5407
[7 empty] | 8554 | 154 | 6.4621 | 4.9895
[7 empty] | 8555 | 155 | 6.3137 | 4.869
[7 empty] | 8556 | 156 | 6.4786 | 5.0029
[7 empty] | 8557 | 157 | 7.1794 | 5.5723
[7 empty] | 8558 | 158 | 7.5009 | 5.8335
[7 empty] | 8559 | 159 | 7.7648 | 6.0479
[7 empty] | 8560 | 160 | 7.6411 | 5.9474
[7 empty] | 8561 | 161 | 8.3914 | 6.557
[7 empty] | 8562 | 162 | 7.9049 | 6.1618
[7 empty] | 8563 | 163 | 8.2594 | 6.4498
[7 empty] | 8564 | 164 | 6.9321 | 5.3713
[7 empty] | 8565 | 165 | 10.0073 | 7.8699
[7 empty] | 8566 | 166 | 7.9956 | 6.2354
[7 empty] | 8567 | 167 | 4.4504 | 3.3551
[7 empty] | 8568 | 168 | 3.8156 | 2.8393
[7 empty] | 8569 | 1 | 2.381 | 1.6738
[7 empty] | 8570 | 2 | 2.2738 | 1.5867
[7 empty] | 8571 | 3 | 2.2656 | 1.58
[7 empty] | 8572 | 4 | 2.3975 | 1.6872
[7 empty] | 8573 | 5 | 2.414 | 1.7006
[7 empty] | 8574 | 6 | 2.8345 | 2.0422
[7 empty] | 8575 | 7 | 3.5435 | 2.6183
[7 empty] | 8576 | 8 | 4.2031 | 3.1541
[7 empty] | 8577 | 9 | 4.1783 | 3.134
[7 empty] | 8578 | 10 | 5.6706 | 4.3465
[7 empty] | 8579 | 11 | 7.7153 | 6.0077
[7 empty] | 8580 | 12 | 8.6634 | 6.778
[7 empty] | 8581 | 13 | 9.0344 | 7.0795
[7 empty] | 8582 | 14 | 8.8201 | 6.9053
[7 empty] | 8583 | 15 | 8.7294 | 6.8316
[7 empty] | 8584 | 16 | 9.8919 | 7.7761
[7 empty] | 8585 | 17 | 11.1946 | 8.8345
[7 empty] | 8586 | 18 | 10.9555 | 8.6402
[7 empty] | 8587 | 19 | 11.4749 | 9.0622
[7 empty] | 8588 | 20 | 11.4089 | 9.0086
[7 empty] | 8589 | 21 | 11.9696 | 9.4641
[7 empty] | 8590 | 22 | 8.0781 | 6.3024
[7 empty] | 8591 | 23 | 4.368 | 3.2881
[7 empty] | 8592 | 24 | 2.724 | 1.9525
[7 empty] | 8593 | 25 | 2.6283 | 1.8747
[7 empty] | 8594 | 26 | 2.5212 | 1.7877
[7 empty] | 8595 | 27 | 2.4222 | 1.7073
[7 empty] | 8596 | 28 | 2.5047 | 1.7743
[7 empty] | 8597 | 29 | 2.7438 | 1.9685
[7 empty] | 8598 | 30 | 2.9829 | 2.1628
[7 empty] | 8599 | 31 | 3.8156 | 2.8393
[7 empty] | 8600 | 32 | 4.1618 | 3.1207
[7 empty] | 8601 | 33 | 4.8132 | 3.6498
[7 empty] | 8602 | 34 | 5.6954 | 4.3666
[7 empty] | 8603 | 35 | 7.8307 | 6.1015
[7 empty] | 8604 | 36 | 8.8448 | 6.9254
[7 empty] | 8605 | 37 | 8.919 | 6.9857
[7 empty] | 8606 | 38 | 8.9932 | 7.046
[7 empty] | 8607 | 39 | 8.6717 | 6.7847
[7 empty] | 8608 | 40 | 9.7105 | 7.6287
[7 empty] | 8609 | 41 | 10.2547 | 8.0708
[7 empty] | 8610 | 42 | 10.2711 | 8.0842
[7 empty] | 8611 | 43 | 10.6339 | 8.379
[7 empty] | 8612 | 44 | 11.7717 | 9.3034
[7 empty] | 8613 | 45 | 11.3759 | 8.9818
[7 empty] | 8614 | 46 | 8.6717 | 6.7847
[7 empty] | 8615 | 47 | 5.1265 | 3.9044
[7 empty] | 8616 | 48 | 3.6507 | 2.7053
[7 empty] | 8617 | 49 | 2.9993 | 2.1762
[7 empty] | 8618 | 50 | 2.6943 | 1.9283
[7 empty] | 8619 | 51 | 2.5871 | 1.8412
[7 empty] | 8620 | 52 | 2.6201 | 1.868
[7 empty] | 8621 | 53 | 2.6448 | 1.8881
[7 empty] | 8622 | 54 | 3.2137 | 2.3503
[7 empty] | 8623 | 55 | 4.335 | 3.2613
[7 empty] | 8624 | 56 | 4.5741 | 3.4556
[7 empty] | 8625 | 57 | 5.5057 | 4.2125
[7 empty] | 8626 | 58 | 6.594 | 5.0967
[7 empty] | 8627 | 59 | 7.7813 | 6.0613
[7 empty] | 8628 | 60 | 8.3996 | 6.5637
[7 empty] | 8629 | 61 | 9.0674 | 7.1063
[7 empty] | 8630 | 62 | 8.8696 | 6.9455
[7 empty] | 8631 | 63 | 9.4549 | 7.4211
[7 empty] | 8632 | 64 | 10.3866 | 8.178
[7 empty] | 8633 | 65 | 10.9967 | 8.6737
[7 empty] | 8634 | 66 | 10.8977 | 8.5933
[7 empty] | 8635 | 67 | 11.6233 | 9.1828
[7 empty] | 8636 | 68 | 11.8624 | 9.377
[7 empty] | 8637 | 69 | 11.3594 | 8.9684
[7 empty] | 8638 | 70 | 9.1004 | 7.133
[7 empty] | 8639 | 71 | 4.6565 | 3.5226
[7 empty] | 8640 | 72 | 3.5894 | 2.6556
[7 empty] | 8641 | 73 | 2.8839 | 2.0824
[7 empty] | 8642 | 74 | 2.6613 | 1.9015
[7 empty] | 8643 | 75 | 2.5624 | 1.8211
[7 empty] | 8644 | 76 | 2.5047 | 1.7743
[7 empty] | 8645 | 77 | 2.6778 | 1.9149
[7 empty] | 8646 | 78 | 3.0735 | 2.2365
[7 empty] | 8647 | 79 | 4.1701 | 3.1274
[7 empty] | 8648 | 80 | 4.3432 | 3.268
[7 empty] | 8649 | 81 | 5.5057 | 4.2125
[7 empty] | 8650 | 82 | 6.5775 | 5.0833
[7 empty] | 8651 | 83 | 7.3031 | 5.6728
[7 empty] | 8652 | 84 | 8.5233 | 6.6642
[7 empty] | 8653 | 85 | 8.2265 | 6.423
[7 empty] | 8654 | 86 | 7.7235 | 6.0144
[7 empty] | 8655 | 87 | 8.1605 | 6.3694
[7 empty] | 8656 | 88 | 8.8118 | 6.8986
[7 empty] | 8657 | 89 | 10.1392 | 7.9771
[7 empty] | 8658 | 90 | 9.5621 | 7.5082
[7 empty] | 8659 | 91 | 10.2382 | 8.0574
[7 empty] | 8660 | 92 | 9.6446 | 7.5751
[7 empty] | 8661 | 93 | 7.2701 | 5.646
[7 empty] | 8662 | 94 | 6.3797 | 4.9225
[7 empty] | 8663 | 95 | 4.5493 | 3.4355
[7 empty] | 8664 | 96 | 3.5765 | 2.6451
[7 empty] | 8665 | 97 | 3.527 | 2.6049
[7 empty] | 8666 | 98 | 3.2384 | 2.3704
[7 empty] | 8667 | 99 | 3.1807 | 2.3235
[7 empty] | 8668 | 100 | 2.8345 | 2.0422
[7 empty] | 8669 | 101 | 2.7767 | 1.9953
[7 empty] | 8670 | 102 | 3.0076 | 2.1829
[7 empty] | 8671 | 103 | 3.7414 | 2.779
[7 empty] | 8672 | 104 | 3.9887 | 2.98
[7 empty] | 8673 | 105 | 4.4669 | 3.3685
[7 empty] | 8674 | 106 | 5.9015 | 4.534
[7 empty] | 8675 | 107 | 6.2477 | 4.8154
[7 empty] | 8676 | 108 | 7.7977 | 6.0747
[7 empty] | 8677 | 109 | 7.1464 | 5.5455
[7 empty] | 8678 | 110 | 6.7012 | 5.1838
[7 empty] | 8679 | 111 | 6.5446 | 5.0565
[7 empty] | 8680 | 112 | 6.6105 | 5.1101
[7 empty] | 8681 | 113 | 6.2725 | 4.8355
[7 empty] | 8682 | 114 | 6.4374 | 4.9694
[7 empty] | 8683 | 115 | 5.9922 | 4.6077
[7 empty] | 8684 | 116 | 6.66 | 5.1503
[7 empty] | 8685 | 117 | 6.2477 | 4.8154
[7 empty] | 8686 | 118 | 5.4892 | 4.1991
[7 empty] | 8687 | 119 | 3.9227 | 2.9264
[7 empty] | 8688 | 120 | 3.6106 | 2.6728
[7 empty] | 8689 | 121 | 2.8922 | 2.0891
[7 empty] | 8690 | 122 | 2.4882 | 1.7609
[7 empty] | 8691 | 123 | 2.4057 | 1.6939
[7 empty] | 8692 | 124 | 2.3727 | 1.6671
[7 empty] | 8693 | 125 | 2.3315 | 1.6336
[7 empty] | 8694 | 126 | 2.4717 | 1.7475
[7 empty] | 8695 | 127 | 3.9557 | 2.9532
[7 empty] | 8696 | 128 | 5.4892 | 4.1991
[7 empty] | 8697 | 129 | 6.1571 | 4.7417
[7 empty] | 8698 | 130 | 6.5858 | 5.09
[7 empty] | 8699 | 131 | 6.7424 | 5.2173
[7 empty] | 8700 | 132 | 6.4951 | 5.0163
[7 empty] | 8701 | 133 | 7.1217 | 5.5254
[7 empty] | 8702 | 134 | 7.4185 | 5.7666
[7 empty] | 8703 | 135 | 7.4844 | 5.8201
[7 empty] | 8704 | 136 | 6.6847 | 5.1704
[7 empty] | 8705 | 137 | 6.5858 | 5.09
[7 empty] | 8706 | 138 | 6.5363 | 5.0498
[7 empty] | 8707 | 139 | 6.2065 | 4.7819
[7 empty] | 8708 | 140 | 6.2148 | 4.7886
[7 empty] | 8709 | 141 | 5.5717 | 4.2661
[7 empty] | 8710 | 142 | 4.9451 | 3.757
[7 empty] | 8711 | 143 | 4.0794 | 3.0537
[7 empty] | 8712 | 144 | 3.4775 | 2.5647
[7 empty] | 8713 | 145 | 3.0158 | 2.1896
[7 empty] | 8714 | 146 | 2.8097 | 2.0221
[7 empty] | 8715 | 147 | 2.7438 | 1.9685
[7 empty] | 8716 | 148 | 2.7355 | 1.9618
[7 empty] | 8717 | 149 | 2.7355 | 1.9618
[7 empty] | 8718 | 150 | 2.7438 | 1.9685
[7 empty] | 8719 | 151 | 3.8073 | 2.8326
[7 empty] | 8720 | 152 | 5.3079 | 4.0517
[7 empty] | 8721 | 153 | 5.9097 | 4.5407
[7 empty] | 8722 | 154 | 6.4621 | 4.9895
[7 empty] | 8723 | 155 | 6.3137 | 4.869
[7 empty] | 8724 | 156 | 6.4786 | 5.0029
[7 empty] | 8725 | 157 | 7.1794 | 5.5723
[7 empty] | 8726 | 158 | 7.5009 | 5.8335
[7 empty] | 8727 | 159 | 7.7648 | 6.0479
[7 empty] | 8728 | 160 | 7.6411 | 5.9474
[7 empty] | 8729 | 161 | 8.3914 | 6.557
[7 empty] | 8730 | 162 | 7.9049 | 6.1618
[7 empty] | 8731 | 163 | 8.2594 | 6.4498
[7 empty] | 8732 | 164 | 6.9321 | 5.3713
[7 empty] | 8733 | 165 | 10.0073 | 7.8699
[7 empty] | 8734 | 166 | 7.9956 | 6.2354
[7 empty] | 8735 | 167 | 4.4504 | 3.3551
[7 empty] | 8736 | 168 | 3.8156 | 2.8393
[7 empty] | 8737 | 1 | 2.381 | 1.6738
[7 empty] | 8738 | 2 | 2.2738 | 1.5867
[7 empty] | 8739 | 3 | 2.2656 | 1.58
[7 empty] | 8740 | 4 | 2.3975 | 1.6872
[7 empty] | 8741 | 5 | 2.414 | 1.7006
[7 empty] | 8742 | 6 | 2.8345 | 2.0422
[7 empty] | 8743 | 7 | 3.5435 | 2.6183
[7 empty] | 8744 | 8 | 4.2031 | 3.1541
[7 empty] | 8745 | 9 | 4.1783 | 3.134
[7 empty] | 8746 | 10 | 5.6706 | 4.3465
[7 empty] | 8747 | 11 | 7.7153 | 6.0077
[7 empty] | 8748 | 12 | 8.6634 | 6.778
[7 empty] | 8749 | 13 | 9.0344 | 7.0795
[7 empty] | 8750 | 14 | 8.8201 | 6.9053
[7 empty] | 8751 | 15 | 8.7294 | 6.8316
[7 empty] | 8752 | 16 | 9.8919 | 7.7761
[7 empty] | 8753 | 17 | 11.1946 | 8.8345
[7 empty] | 8754 | 18 | 10.9555 | 8.6402
[7 empty] | 8755 | 19 | 11.4749 | 9.0622
[7 empty] | 8756 | 20 | 11.4089 | 9.0086
[7 empty] | 8757 | 21 | 11.9696 | 9.4641
[7 empty] | 8758 | 22 | 8.0781 | 6.3024
[7 empty] | 8759 | 23 | 4.368 | 3.2881
[7 empty] | 8760 | 24 | 2.724 | 1.9525

## 2016
Month | Day | Hour (PDT) | Wind_curtail (MWh) | Solar_curtail (MWh) | Total_curtail (MWh) | GHG_intensity (kgCO2e/MWh) | CA_DC_load (MW) | #_ExistingDCs_needed | #_ExistingDCs_allowed | PJM_intensity (kgCO2e/MWh) | ExistingDCs_absorption (MWh) | Remaining_curtailment (MWh) | ExistingDCs_GHG_reduction (kgCO2e) | #_NewDCs_needed | #_NewDCs_allowed | NewDCs_absorption (MWh) | Total_absorption (MWh) | Final_curtailment (MWh) | NewDCs_GHG_reduction (kgCO2e) | Total_GHG_reduction (kgCO2e)
1 | 1 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 346.3366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 344.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 345.3139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 345.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 347.7527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 350.8257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 354.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 358.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 361.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 363.0794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 364.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 11 | 0.98917 | 24.1151 | 25.1043 | 46.5421 | 9.8676 | 381.6867 | 288 | 360.0098 | 18.9423 | 6.162 | 5937.8134 | 0.61589 | 0 | 0 | 18.9423 | 6.162 | 0 | 5937.8134
1 | 1 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 356.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 359.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 376.5819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 393.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 398.6766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 397.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 396.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 385.4364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 369.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 360.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 352.4722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 348.9532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 353.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 355.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 364.5487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 378.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 388.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 402.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 404.1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 403.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 391.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 384.3472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 373.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 369.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 364.6082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 365.8952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 370.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 390.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 391.9932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 392.2085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 391.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 388.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 379.9104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 377.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 372.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 365.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 360.9741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 364.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 373.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 380.3598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 388.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 396.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 6 | 11.4455 | 0 | 11.4455 | 11 | 5.3513 | 5.1371 | 5.1371 | 398.6475 | 11.4455 | 0 | 4436.8181 | 0 | 0 | 0 | 11.4455 | 0 | 0 | 4436.8181
1 | 3 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 393.0125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 393.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 9 | 0.54829 | 0 | 0.54829 | 11 | 7.7084 | 0.49866 | 0.49866 | 393.0773 | 0.54829 | 0 | 209.4898 | 0 | 0 | 0 | 0.54829 | 0 | 0 | 209.4898
1 | 3 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 394.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 395.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 12 | 0 | 0.02575 | 0.02575 | 48 | 10.2891 | 0 | 0 | 393.3987 | 0 | 0.02575 | 0 | 0.0025737 | 0 | 0 | 0 | 0.02575 | 0 | 0
1 | 3 | 13 | 0 | 0.0024583 | 0.0024583 | 48 | 10.0827 | 0 | 0 | 391.9566 | 0 | 0.0024583 | 0 | 0.00024571 | 0 | 0 | 0 | 0.0024583 | 0 | 0
1 | 3 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 398.8448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 423.3587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 432.9069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 433.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 431.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 415.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 404.7844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 395.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 393.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 393.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 393.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 397.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 405.3718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 426.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 436.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 443.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 450.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 461.8996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 8 | 0 | 8.0691 | 8.0691 | 48 | 6.5729 | 4.9107 | 4.9107 | 459.6076 | 8.0691 | 0 | 3321.3131 | 0 | 0 | 0 | 8.0691 | 0 | 0 | 3321.3131
1 | 4 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 458.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 459.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 459.4046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 458.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 13 | 0 | 3.3616 | 3.3616 | 48 | 8.8869 | 6.2799 | 6.2799 | 467.7599 | 3.3616 | 0 | 1411.0497 | 0 | 0 | 0 | 3.3616 | 0 | 0 | 1411.0497
1 | 4 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 472.2547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 484.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 487.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 489.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 496.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 491.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 480.7002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 485.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 487.4367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 488.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 489.7541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 498.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 494.7134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 496.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 503.6101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 505.1878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 504.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 506.7772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 8 | 0 | 9.1367 | 9.1367 | 48 | 5.4889 | 4.2258 | 4.2258 | 506.976 | 9.1367 | 0 | 4193.5108 | 0 | 0 | 0 | 9.1367 | 0 | 0 | 4193.5108
1 | 5 | 9 | 0 | 8.9773 | 8.9773 | 48 | 6.9858 | 6.2106 | 6.2106 | 508.0547 | 8.9773 | 0 | 4130.0556 | 0 | 0 | 0 | 8.9773 | 0 | 0 | 4130.0556
1 | 5 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 503.543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 500.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 12 | 15.5135 | 0 | 15.5135 | 11 | 8.2847 | 18.8365 | 18.8365 | 495.2102 | 15.5135 | 0 | 7511.8001 | 0 | 0 | 0 | 15.5135 | 0 | 0 | 7511.8001
1 | 5 | 13 | 21.0292 | 0 | 21.0292 | 11 | 7.8202 | 20.1046 | 20.1046 | 500.198 | 21.0292 | 0 | 10287.4254 | 0 | 0 | 0 | 21.0292 | 0 | 0 | 10287.4254
1 | 5 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 494.7802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 507.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 501.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 505.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 500.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 491.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 493.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 481.5067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 471.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 470.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 473.9128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 480.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 489.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 493.6297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 497.7856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 502.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 502.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 499.3396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 497.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 490.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 486.1987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 479.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 12 | 8.6933 | 5.6644 | 14.3577 | 25.5972 | 8.2589 | 17.1754 | 17.1754 | 478.4134 | 14.3577 | 0 | 6501.3858 | 0 | 0 | 0 | 14.3577 | 0 | 0 | 6501.3858
1 | 6 | 13 | 0 | 14.0304 | 14.0304 | 48 | 8.5686 | 20.4027 | 20.4027 | 478.2927 | 14.0304 | 0 | 6037.1939 | 0 | 0 | 0 | 14.0304 | 0 | 0 | 6037.1939
1 | 6 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 478.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 493.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 16 | 2.4966 | 0 | 2.4966 | 11 | 7.6998 | 2.2622 | 2.2622 | 490.7485 | 2.4966 | 0 | 1197.7617 | 0 | 0 | 0 | 2.4966 | 0 | 0 | 1197.7617
1 | 6 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 484.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 481.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 472.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 462.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 448.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 435.5399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 434.9093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 436.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 441.1648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 445.3037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 458.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 473.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 479.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 482.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 488.1045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 481.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 9 | 0 | 4.7621 | 4.7621 | 48 | 7.5707 | 4.0862 | 4.0862 | 477.6128 | 4.7621 | 0 | 2045.8734 | 0 | 0 | 0 | 4.7621 | 0 | 0 | 2045.8734
1 | 7 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 469.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 11 | 0.31057 | 0 | 0.31057 | 11 | 7.5879 | 0.26839 | 0.26839 | 461.9555 | 0.31057 | 0 | 140.0546 | 0 | 0 | 0 | 0.31057 | 0 | 0 | 140.0546
1 | 7 | 12 | 0 | 0.41346 | 0.41346 | 48 | 8.3192 | 0.51227 | 0.51227 | 462.3644 | 0.41346 | 0 | 171.3232 | 0 | 0 | 0 | 0.41346 | 0 | 0 | 171.3232
1 | 7 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 458.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 452.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 465.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 466.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 467.4575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 458.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 446.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 423.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 412.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 402.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 399.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 401.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 400.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 402.4838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 416.6097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 4 | 1.525 | 0 | 1.525 | 11 | 3.3469 | 0.4784 | 0.4784 | 440.5662 | 1.525 | 0 | 655.0705 | 0 | 0 | 0 | 1.525 | 0 | 0 | 655.0705
1 | 8 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 451.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 459.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 466.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 8 | 0 | 0.3911 | 0.3911 | 48 | 5.1879 | 0.16958 | 0.16958 | 462.171 | 0.3911 | 0 | 161.9833 | 0 | 0 | 0 | 0.3911 | 0 | 0 | 161.9833
1 | 8 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 458.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 457.3964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 452.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 449.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 448.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 450.3425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 456.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 451.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 439.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 428.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 411.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 394.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 391.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 393.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 390.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 385.5645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 383.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 385.9309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 390.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 400.9775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 417.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 432.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 437.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 434.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 432.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 422.1171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 415.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 408.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 409.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 423.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 420.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 16 | 1.6182 | 0 | 1.6182 | 11 | 11.5279 | 0 | 0 | 410.2331 | 0 | 1.6182 | 0 | 0.16174 | 0 | 0 | 0 | 1.6182 | 0 | 0
1 | 9 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 400.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 395.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 389.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 386.4105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 378.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 377.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 377.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 367.5659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 368.5511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 369.2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 372.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 377.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 380.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 384.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 389.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 393.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 397.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 401.9704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 402.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 12 | 0.44369 | 0 | 0.44369 | 11 | 10.2891 | 0 | 0 | 408.2773 | 0 | 0.44369 | 0 | 0.044347 | 0 | 0 | 0 | 0.44369 | 0 | 0
1 | 10 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 419.4259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 436.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 454.9492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 462.1853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 466.2967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 459.5151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 448.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 426.9024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 419.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 419.1536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 429.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 433.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 448.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 465.1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 480.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 501.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 504.7592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 511.4957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 506.4225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 502.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 9 | 0 | 0.0525 | 0.0525 | 48 | 7.6912 | 0.047393 | 0.047393 | 500.6726 | 0.0525 | 0 | 23.7653 | 0 | 0 | 0 | 0.0525 | 0 | 0 | 23.7653
1 | 11 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 496.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 11 | 0 | 29.6852 | 29.6852 | 48 | 9.7214 | 218.615 | 218.615 | 486.7154 | 29.6852 | 0 | 13023.3476 | 0 | 0 | 0 | 29.6852 | 0 | 0 | 13023.3476
1 | 11 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 478.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 13 | 0 | 18.9749 | 18.9749 | 48 | 8.8869 | 35.4481 | 35.4481 | 478.0836 | 18.9749 | 0 | 8160.8055 | 0 | 0 | 0 | 18.9749 | 0 | 0 | 8160.8055
1 | 11 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 482.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 497.8473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 500.3207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 503.4542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 501.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 494.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 465.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 451.6668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 446.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 439.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 441.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 443.7111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 460.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 473.8767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 482.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 484.6587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 486.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 488.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 486.7359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 9 | 1.3833 | 0 | 1.3833 | 11 | 6.9858 | 0.95697 | 0.95697 | 486.2135 | 1.3833 | 0 | 657.3589 | 0 | 0 | 0 | 1.3833 | 0 | 0 | 657.3589
1 | 12 | 10 | 1.7434 | 29.4912 | 31.2346 | 45.9348 | 7.3471 | 24.5457 | 24.5457 | 487.4943 | 31.2346 | 0 | 13791.9415 | 0 | 0 | 0 | 31.2346 | 0 | 0 | 13791.9415
1 | 12 | 11 | 0.099167 | 193.0424 | 193.1416 | 47.981 | 8.9643 | 387.6628 | 288 | 487.5042 | 143.4875 | 49.6541 | 63066.0859 | 4.9629 | 0 | 0 | 143.4875 | 49.6541 | 0 | 63066.0859
1 | 12 | 12 | 0 | 190.5595 | 190.5595 | 48 | 8.2847 | 231.3776 | 231.3776 | 474.8031 | 190.5595 | 0 | 81331.3783 | 0 | 0 | 0 | 190.5595 | 0 | 0 | 81331.3783
1 | 12 | 13 | 0 | 206.8736 | 206.8736 | 48 | 7.8202 | 197.7781 | 197.7781 | 476.0228 | 206.8736 | 0 | 88546.6172 | 0 | 0 | 0 | 206.8736 | 0 | 0 | 88546.6172
1 | 12 | 14 | 0 | 24.7533 | 24.7533 | 48 | 7.6568 | 22.0178 | 22.0178 | 474.3423 | 24.7533 | 0 | 10553.3743 | 0 | 0 | 0 | 24.7533 | 0 | 0 | 10553.3743
1 | 12 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 489.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 490.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 494.9573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 495.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 487.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 20 | 146.8614 | 0 | 146.8614 | 11 | 7.3471 | 115.4108 | 115.4108 | 475.7616 | 146.8614 | 0 | 68255.518 | 0 | 0 | 0 | 146.8614 | 0 | 0 | 68255.518
1 | 12 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 472.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 472.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 472.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 478.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 487.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 492.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 503.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 517.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 520.8903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 517.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 520.1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 518.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 9 | 2.8752 | 54.1328 | 57.008 | 46.1339 | 7.6998 | 51.6541 | 51.6541 | 514.8496 | 57.008 | 0 | 26720.5227 | 0 | 0 | 0 | 57.008 | 0 | 0 | 26720.5227
1 | 13 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 509.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 11 | 0.65583 | 0.34337 | 0.99921 | 23.7149 | 7.6051 | 0.86967 | 0.86967 | 507.4343 | 0.99921 | 0 | 483.3364 | 0 | 0 | 0 | 0.99921 | 0 | 0 | 483.3364
1 | 13 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 506.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 13 | 8.18 | 0 | 8.18 | 11 | 8.5686 | 11.8951 | 11.8951 | 509.4961 | 8.18 | 0 | 4077.6777 | 0 | 0 | 0 | 8.18 | 0 | 0 | 4077.6777
1 | 13 | 14 | 1 | 0 | 1 | 11 | 8.6374 | 1.5274 | 1.5274 | 508.3379 | 1 | 0 | 497.3379 | 0 | 0 | 0 | 1 | 0 | 0 | 497.3379
1 | 13 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 507.8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 16 | 0 | 0.965 | 0.965 | 48 | 7.6998 | 0.87437 | 0.87437 | 505.7567 | 0.965 | 0 | 441.7352 | 0 | 0 | 0 | 0.965 | 0 | 0 | 441.7352
1 | 13 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 505.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 501.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 493.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 480.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 461.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 442.6953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 435.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 427.8176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 426.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 434.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 458.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 482.9325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 484.4674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 486.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 476.3156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 8 | 25.941 | 55.8877 | 81.8286 | 36.2704 | 6.9944 | 56.7714 | 56.7714 | 465.338 | 81.8286 | 0 | 35110.0194 | 0 | 0 | 0 | 81.8286 | 0 | 0 | 35110.0194
1 | 14 | 9 | 14.3314 | 260.2238 | 274.5552 | 46.0687 | 7.5707 | 235.5834 | 235.5834 | 460.9086 | 274.5552 | 0 | 113896.4714 | 0 | 0 | 0 | 274.5552 | 0 | 0 | 113896.4714
1 | 14 | 10 | 1.67 | 0 | 1.67 | 11 | 7.4159 | 1.3472 | 1.3472 | 447.1741 | 1.67 | 0 | 728.3926 | 0 | 0 | 0 | 1.67 | 0 | 0 | 728.3926
1 | 14 | 11 | 16.481 | 341.0422 | 357.5232 | 46.2944 | 7.5879 | 308.9582 | 288 | 441.2836 | 333.2706 | 24.2526 | 131638.3164 | 2.4241 | 0 | 0 | 333.2706 | 24.2526 | 0 | 131638.3164
1 | 14 | 12 | 0 | 99.0664 | 99.0664 | 48 | 8.3192 | 122.7417 | 122.7417 | 440.783 | 99.0664 | 0 | 38911.5918 | 0 | 0 | 0 | 99.0664 | 0 | 0 | 38911.5918
1 | 14 | 13 | 3.6974 | 8.2781 | 11.9755 | 36.5763 | 8.6546 | 18.5239 | 18.5239 | 447.2196 | 11.9755 | 0 | 4917.6589 | 0 | 0 | 0 | 11.9755 | 0 | 0 | 4917.6589
1 | 14 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 445.7579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 464.761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 458.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 17 | 7.215 | 0 | 7.215 | 11 | 9.0762 | 16.2252 | 16.2252 | 453.7139 | 7.215 | 0 | 3194.1807 | 0 | 0 | 0 | 7.215 | 0 | 0 | 3194.1807
1 | 14 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 450.0129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 430.4528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 409.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 399.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 393.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 392.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 389.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 390.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 408.1652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 432.9227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 467.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 474.5595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 471.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 463.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 456.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 449.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 448.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 11 | 0.78094 | 0 | 0.78094 | 11 | 9.8676 | 11.8734 | 11.8734 | 453.1877 | 0.78094 | 0 | 345.3213 | 0 | 0 | 0 | 0.78094 | 0 | 0 | 345.3213
1 | 15 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 455.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 454.6057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 463.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 464.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 452.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 450.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 435.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 418.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 414.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 404.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 403.7439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 396.7454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 390.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 387.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 390.7482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 3 | 0.7901 | 0 | 0.7901 | 11 | 3.4416 | 0.25144 | 0.25144 | 397.8112 | 0.7901 | 0 | 305.6214 | 0 | 0 | 0 | 0.7901 | 0 | 0 | 305.6214
1 | 16 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 415.3645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 428.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 438.4869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 444.0528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 446.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 9 | 0.083292 | 0 | 0.083292 | 11 | 6.7707 | 0.05379 | 0.05379 | 446.6785 | 0.083292 | 0 | 36.2884 | 0 | 0 | 0 | 0.083292 | 0 | 0 | 36.2884
1 | 16 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 441.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 441.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 12 | 0 | 1.8312 | 1.8312 | 48 | 10.1343 | 0 | 0 | 440.4575 | 0 | 1.8312 | 0 | 0.18302 | 0 | 0 | 0 | 1.8312 | 0 | 0
1 | 16 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 449.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 462.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 479.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 475.372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 468.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 460.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 443.5394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 434.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 417.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 416.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 413.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 414.5415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 412.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 412.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 3 | 0.099958 | 0 | 0.099958 | 11 | 3.562 | 0.032405 | 0.032405 | 418.5319 | 0.099958 | 0 | 40.7362 | 0 | 0 | 0 | 0.099958 | 0 | 0 | 40.7362
1 | 17 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 424.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 446.436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 464.306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 7 | 2.0754 | 0 | 2.0754 | 11 | 5.6008 | 0.98425 | 0.98425 | 476.9683 | 2.0754 | 0 | 967.0518 | 0 | 0 | 0 | 2.0754 | 0 | 0 | 967.0518
1 | 17 | 8 | 0.71312 | 0 | 0.71312 | 11 | 6.5729 | 0.43399 | 0.43399 | 484.7211 | 0.71312 | 0 | 337.8178 | 0 | 0 | 0 | 0.71312 | 0 | 0 | 337.8178
1 | 17 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 481.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 479.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 475.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 468.8274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 469.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 483.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 503.7205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 16 | 0.37496 | 0 | 0.37496 | 11 | 12.3021 | 0 | 0 | 508.9465 | 0 | 0.37496 | 0 | 0.037477 | 0 | 0 | 0 | 0.37496 | 0 | 0
1 | 17 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 510.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 502.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 494.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 487.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 469.4576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 472.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 475.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 0 | 16.8058 | 0 | 16.8058 | 11 | 3.8373 | 5.6913 | 5.6913 | 474.4061 | 16.8058 | 0 | 7787.906 | 0 | 0 | 0 | 16.8058 | 0 | 0 | 7787.906
1 | 18 | 1 | 8.4775 | 0 | 8.4775 | 11 | 3.605 | 2.7667 | 2.7667 | 486.6762 | 8.4775 | 0 | 4032.5452 | 0 | 0 | 0 | 8.4775 | 0 | 0 | 4032.5452
1 | 18 | 2 | 4.725 | 0 | 4.725 | 11 | 3.5018 | 1.5176 | 1.5176 | 501.4567 | 4.725 | 0 | 2317.4079 | 0 | 0 | 0 | 4.725 | 0 | 0 | 2317.4079
1 | 18 | 3 | 5.0708 | 0 | 5.0708 | 11 | 3.4416 | 1.6137 | 1.6137 | 510.7349 | 5.0708 | 0 | 2534.0725 | 0 | 0 | 0 | 5.0708 | 0 | 0 | 2534.0725
1 | 18 | 4 | 33.9292 | 0 | 33.9292 | 11 | 3.6222 | 11.103 | 11.103 | 519.2221 | 33.9292 | 0 | 17243.5534 | 0 | 0 | 0 | 33.9292 | 0 | 0 | 17243.5534
1 | 18 | 5 | 1.8492 | 0 | 1.8492 | 11 | 4.0351 | 0.64698 | 0.64698 | 530.1637 | 1.8492 | 0 | 960.0203 | 0 | 0 | 0 | 1.8492 | 0 | 0 | 960.0203
1 | 18 | 6 | 3.4858 | 0 | 3.4858 | 11 | 5.1793 | 1.5088 | 1.5088 | 538.3754 | 3.4858 | 0 | 1838.3426 | 0 | 0 | 0 | 3.4858 | 0 | 0 | 1838.3426
1 | 18 | 7 | 6.975 | 0 | 6.975 | 11 | 5.3599 | 3.1364 | 3.1364 | 541.821 | 6.975 | 0 | 3702.4545 | 0 | 0 | 0 | 6.975 | 0 | 0 | 3702.4545
1 | 18 | 8 | 1.1742 | 0 | 1.1742 | 11 | 6.5729 | 0.71457 | 0.71457 | 539.5195 | 1.1742 | 0 | 620.5699 | 0 | 0 | 0 | 1.1742 | 0 | 0 | 620.5699
1 | 18 | 9 | 0.895 | 0 | 0.895 | 11 | 7.6912 | 0.80793 | 0.80793 | 541.1549 | 0.895 | 0 | 474.4886 | 0 | 0 | 0 | 0.895 | 0 | 0 | 474.4886
1 | 18 | 10 | 0.86667 | 0 | 0.86667 | 11 | 8.4482 | 1.1628 | 1.1628 | 541.0411 | 0.86667 | 0 | 459.369 | 0 | 0 | 0 | 0.86667 | 0 | 0 | 459.369
1 | 18 | 11 | 2.6217 | 0 | 2.6217 | 11 | 9.7214 | 19.3071 | 19.3071 | 540.4989 | 2.6217 | 0 | 1388.1697 | 0 | 0 | 0 | 2.6217 | 0 | 0 | 1388.1697
1 | 18 | 12 | 4.2392 | 0 | 4.2392 | 11 | 9.4117 | 14.9237 | 14.9237 | 540.025 | 4.2392 | 0 | 2242.625 | 0 | 0 | 0 | 4.2392 | 0 | 0 | 2242.625
1 | 18 | 13 | 11.4375 | 0 | 11.4375 | 11 | 8.8869 | 21.367 | 21.367 | 540.3284 | 11.4375 | 0 | 6054.1938 | 0 | 0 | 0 | 11.4375 | 0 | 0 | 6054.1938
1 | 18 | 14 | 12.5125 | 0 | 12.5125 | 11 | 9.3428 | 39.4711 | 39.4711 | 533.5493 | 12.5125 | 0 | 6538.3981 | 0 | 0 | 0 | 12.5125 | 0 | 0 | 6538.3981
1 | 18 | 15 | 3.4225 | 0 | 3.4225 | 11 | 10.0224 | 0 | 0 | 535.182 | 0 | 3.4225 | 0 | 0.34208 | 0 | 0 | 0 | 3.4225 | 0 | 0
1 | 18 | 16 | 1.355 | 0 | 1.355 | 11 | 11.4074 | 0 | 0 | 536.2734 | 0 | 1.355 | 0 | 0.13543 | 0 | 0 | 0 | 1.355 | 0 | 0
1 | 18 | 17 | 1.35 | 0 | 1.35 | 11 | 10.8053 | 0 | 0 | 538.0034 | 0 | 1.35 | 0 | 0.13493 | 0 | 0 | 0 | 1.35 | 0 | 0
1 | 18 | 18 | 1.6092 | 0 | 1.6092 | 11 | 11.5107 | 0 | 0 | 543.2002 | 0 | 1.6092 | 0 | 0.16084 | 0 | 0 | 0 | 1.6092 | 0 | 0
1 | 18 | 19 | 3.6333 | 0 | 3.6333 | 11 | 10.8913 | 0 | 0 | 547.6299 | 0 | 3.6333 | 0 | 0.36315 | 0 | 0 | 0 | 3.6333 | 0 | 0
1 | 18 | 20 | 2.6108 | 0 | 2.6108 | 11 | 8.4138 | 3.4272 | 3.4272 | 546.7773 | 2.6108 | 0 | 1398.8252 | 0 | 0 | 0 | 2.6108 | 0 | 0 | 1398.8252
1 | 18 | 21 | 1.0083 | 0 | 1.0083 | 11 | 7.4847 | 0.83567 | 0.83567 | 547.8089 | 1.0083 | 0 | 541.2823 | 0 | 0 | 0 | 1.0083 | 0 | 0 | 541.2823
1 | 18 | 22 | 0.985 | 0 | 0.985 | 11 | 5.575 | 0.46442 | 0.46442 | 549.5852 | 0.985 | 0 | 530.5064 | 0 | 0 | 0 | 0.985 | 0 | 0 | 530.5064
1 | 18 | 23 | 0.99333 | 0 | 0.99333 | 11 | 4.5599 | 0.38104 | 0.38104 | 552.0046 | 0.99333 | 0 | 537.3979 | 0 | 0 | 0 | 0.99333 | 0 | 0 | 537.3979
1 | 19 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 551.1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 550.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 545.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 544.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 543.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 542.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 540.4505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 7 | 57.777 | 4.1645 | 61.9415 | 13.4876 | 4.99 | 25.7983 | 25.7983 | 541.4256 | 61.9415 | 0 | 32701.2873 | 0 | 0 | 0 | 61.9415 | 0 | 0 | 32701.2873
1 | 19 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 550.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 9 | 0 | 64.1822 | 64.1822 | 48 | 6.9858 | 44.4017 | 44.4017 | 554.4229 | 64.1822 | 0 | 32503.3255 | 0 | 0 | 0 | 64.1822 | 0 | 0 | 32503.3255
1 | 19 | 10 | 5.8518 | 60.4464 | 66.2982 | 44.7342 | 7.3471 | 52.1003 | 52.1003 | 555.6172 | 66.2982 | 0 | 33870.6065 | 0 | 0 | 0 | 66.2982 | 0 | 0 | 33870.6065
1 | 19 | 11 | 92.1016 | 195.2441 | 287.3457 | 36.1406 | 8.9643 | 576.744 | 288 | 550.0197 | 143.4875 | 143.8582 | 73735.2415 | 14.3787 | 0 | 0 | 143.4875 | 143.8582 | 0 | 73735.2415
1 | 19 | 12 | 0 | 59.4218 | 59.4218 | 48 | 8.2847 | 72.15 | 72.15 | 547.1638 | 59.4218 | 0 | 29661.2054 | 0 | 0 | 0 | 59.4218 | 0 | 0 | 29661.2054
1 | 19 | 13 | 0 | 24.0675 | 24.0675 | 48 | 7.8202 | 23.0093 | 23.0093 | 545.6754 | 24.0675 | 0 | 11977.7839 | 0 | 0 | 0 | 24.0675 | 0 | 0 | 11977.7839
1 | 19 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 542.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 543.8251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 544.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 17 | 86.1664 | 0 | 86.1664 | 11 | 7.5449 | 73.1599 | 73.1599 | 544.5643 | 86.1664 | 0 | 45975.3271 | 0 | 0 | 0 | 86.1664 | 0 | 0 | 45975.3271
1 | 19 | 18 | 2.6812 | 0 | 2.6812 | 11 | 7.0804 | 1.9149 | 1.9149 | 544.4591 | 2.6812 | 0 | 1430.322 | 0 | 0 | 0 | 2.6812 | 0 | 0 | 1430.322
1 | 19 | 19 | 33.5651 | 0 | 33.5651 | 11 | 7.7772 | 31.4698 | 31.4698 | 546.277 | 33.5651 | 0 | 17966.6207 | 0 | 0 | 0 | 33.5651 | 0 | 0 | 17966.6207
1 | 19 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 546.1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 541.9367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 545.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 541.6653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 0 | 31.392 | 0 | 31.392 | 11 | 3.8459 | 10.6458 | 10.6458 | 544.1416 | 31.392 | 0 | 16736.3691 | 0 | 0 | 0 | 31.392 | 0 | 0 | 16736.3691
1 | 20 | 1 | 28.3301 | 0 | 28.3301 | 11 | 3.4243 | 8.9921 | 8.9921 | 546.3812 | 28.3301 | 0 | 15167.4148 | 0 | 0 | 0 | 28.3301 | 0 | 0 | 15167.4148
1 | 20 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 544.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 3 | 1.2567 | 0 | 1.2567 | 11 | 3.3039 | 0.39171 | 0.39171 | 542.5324 | 1.2567 | 0 | 667.9783 | 0 | 0 | 0 | 1.2567 | 0 | 0 | 667.9783
1 | 20 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 540.8651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 543.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 6 | 11.8243 | 0 | 11.8243 | 11 | 4.9556 | 4.8912 | 4.8912 | 544.5605 | 11.8243 | 0 | 6309.005 | 0 | 0 | 0 | 11.8243 | 0 | 0 | 6309.005
1 | 20 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 549.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 8 | 0.2225 | 17.3572 | 17.5797 | 47.5317 | 7.2524 | 13.3401 | 13.3401 | 551.2617 | 17.5797 | 0 | 8855.4383 | 0 | 0 | 0 | 17.5797 | 0 | 0 | 8855.4383
1 | 20 | 9 | 0 | 157.6355 | 157.6355 | 48 | 7.6998 | 142.8313 | 142.8313 | 546.9482 | 157.6355 | 0 | 78651.9626 | 0 | 0 | 0 | 157.6355 | 0 | 0 | 78651.9626
1 | 20 | 10 | 0 | 97.2385 | 97.2385 | 48 | 7.8632 | 94.8302 | 94.8302 | 549.2612 | 97.2385 | 0 | 48741.91 | 0 | 0 | 0 | 97.2385 | 0 | 0 | 48741.91
1 | 20 | 11 | 0 | 8.2003 | 8.2003 | 48 | 7.6051 | 7.1372 | 7.1372 | 548.9718 | 8.2003 | 0 | 4108.1136 | 0 | 0 | 0 | 8.2003 | 0 | 0 | 4108.1136
1 | 20 | 12 | 0 | 80.5995 | 80.5995 | 48 | 8.2589 | 96.4175 | 96.4175 | 541.5815 | 80.5995 | 0 | 39782.4132 | 0 | 0 | 0 | 80.5995 | 0 | 0 | 39782.4132
1 | 20 | 13 | 0 | 35.6348 | 35.6348 | 48 | 8.5686 | 51.8193 | 51.8193 | 542.9275 | 35.6348 | 0 | 17636.6371 | 0 | 0 | 0 | 35.6348 | 0 | 0 | 17636.6371
1 | 20 | 14 | 0 | 1.1718 | 1.1718 | 48 | 8.6374 | 1.7898 | 1.7898 | 539.4509 | 1.1718 | 0 | 575.8911 | 0 | 0 | 0 | 1.1718 | 0 | 0 | 575.8911
1 | 20 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 547.8666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 550.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 17 | 177.508 | 0 | 177.508 | 11 | 7.6482 | 157.3151 | 157.3151 | 548.4903 | 177.508 | 0 | 95408.8219 | 0 | 0 | 0 | 177.508 | 0 | 0 | 95408.8219
1 | 20 | 18 | 15.095 | 0 | 15.095 | 11 | 7.3041 | 11.6734 | 11.6734 | 545.283 | 15.095 | 0 | 8064.9808 | 0 | 0 | 0 | 15.095 | 0 | 0 | 8064.9808
1 | 20 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 538.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 20 | 15.1619 | 0 | 15.1619 | 11 | 6.6417 | 9.416 | 9.416 | 520.684 | 15.1619 | 0 | 7727.7879 | 0 | 0 | 0 | 15.1619 | 0 | 0 | 7727.7879
1 | 20 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 502.9673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 494.7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 491.9943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 493.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 501.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 503.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 507.1689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 525.9531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 533.5934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 533.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 7 | 2.7891 | 0 | 2.7891 | 11 | 6.3664 | 1.6011 | 1.6011 | 536.5756 | 2.7891 | 0 | 1465.8996 | 0 | 0 | 0 | 2.7891 | 0 | 0 | 1465.8996
1 | 21 | 8 | 0 | 21.8743 | 21.8743 | 48 | 6.9944 | 15.176 | 15.176 | 531.7044 | 21.8743 | 0 | 10580.6885 | 0 | 0 | 0 | 21.8743 | 0 | 0 | 10580.6885
1 | 21 | 9 | 2.8967 | 185.5892 | 188.4859 | 47.4314 | 7.5707 | 161.7312 | 161.7312 | 526.1576 | 188.4859 | 0 | 90233.1262 | 0 | 0 | 0 | 188.4859 | 0 | 0 | 90233.1262
1 | 21 | 10 | 5.2337 | 78.2268 | 83.4605 | 45.6798 | 7.4159 | 67.3307 | 67.3307 | 521.0653 | 83.4605 | 0 | 39675.905 | 0 | 0 | 0 | 83.4605 | 0 | 0 | 39675.905
1 | 21 | 11 | 4.1658 | 469.1266 | 473.2925 | 47.6743 | 7.5879 | 409.0016 | 288 | 518.8375 | 333.2706 | 140.0218 | 157024.8495 | 13.9952 | 0 | 0 | 333.2706 | 140.0218 | 0 | 157024.8495
1 | 21 | 12 | 0 | 78.3939 | 78.3939 | 48 | 8.3192 | 97.1289 | 97.1289 | 516.329 | 78.3939 | 0 | 36714.1527 | 0 | 0 | 0 | 78.3939 | 0 | 0 | 36714.1527
1 | 21 | 13 | 0 | 11.7789 | 11.7789 | 48 | 8.6546 | 18.2198 | 18.2198 | 514.3643 | 11.7789 | 0 | 5493.2466 | 0 | 0 | 0 | 11.7789 | 0 | 0 | 5493.2466
1 | 21 | 14 | 0 | 24.4542 | 24.4542 | 48 | 8.9299 | 47.512 | 47.512 | 514.0387 | 24.4542 | 0 | 11396.5937 | 0 | 0 | 0 | 24.4542 | 0 | 0 | 11396.5937
1 | 21 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 530.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 16 | 15.2229 | 0 | 15.2229 | 11 | 9.5837 | 75.4791 | 75.4791 | 536.4684 | 15.2229 | 0 | 7999.1792 | 0 | 0 | 0 | 15.2229 | 0 | 0 | 7999.1792
1 | 21 | 17 | 0.13221 | 0 | 0.13221 | 11 | 9.0762 | 0.29732 | 0.29732 | 539.2719 | 0.13221 | 0 | 69.845 | 0 | 0 | 0 | 0.13221 | 0 | 0 | 69.845
1 | 21 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 539.3088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 530.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 523.9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 513.8823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 511.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 505.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 500.5752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 511.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 2 | 0.44162 | 0 | 0.44162 | 11 | 3.1921 | 0.13539 | 0.13539 | 518.8864 | 0.44163 | 0 | 224.2953 | 0 | 0 | 0 | 0.44163 | 0 | 0 | 224.2953
1 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 518.8145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 518.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 521.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 6 | 17.4286 | 0 | 17.4286 | 11 | 4.5255 | 6.6435 | 6.6435 | 525.2219 | 17.4286 | 0 | 8962.1477 | 0 | 0 | 0 | 17.4286 | 0 | 0 | 8962.1477
1 | 22 | 7 | 6.5274 | 0 | 6.5274 | 11 | 5.2137 | 2.8455 | 2.8455 | 531.7255 | 6.5274 | 0 | 3398.9953 | 0 | 0 | 0 | 6.5274 | 0 | 0 | 3398.9953
1 | 22 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 532.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 9 | 0.21662 | 0 | 0.21662 | 11 | 6.7449 | 0.13879 | 0.13879 | 533.1117 | 0.21663 | 0 | 113.1024 | 0 | 0 | 0 | 0.21663 | 0 | 0 | 113.1024
1 | 22 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 529.7946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 11 | 0.42357 | 0 | 0.42357 | 11 | 9.8676 | 6.44 | 6.44 | 527.4072 | 0.42357 | 0 | 218.7343 | 0 | 0 | 0 | 0.42357 | 0 | 0 | 218.7343
1 | 22 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 529.7583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 526.8394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 519.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 523.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 524.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 523.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 18 | 11.9 | 0 | 11.9 | 11 | 12.801 | 0 | 0 | 518.9684 | 0 | 11.9 | 0 | 1.1894 | 0 | 0 | 0 | 11.9 | 0 | 0
1 | 22 | 19 | 5.4 | 0 | 5.4 | 11 | 12.7322 | 0 | 0 | 515.1265 | 0 | 5.4 | 0 | 0.53973 | 0 | 0 | 0 | 5.4 | 0 | 0
1 | 22 | 20 | 13.6 | 0 | 13.6 | 11 | 13.3172 | 0 | 0 | 507.9083 | 0 | 13.6 | 0 | 1.3593 | 0 | 0 | 0 | 13.6 | 0 | 0
1 | 22 | 21 | 4.9 | 0 | 4.9 | 11 | 9.2568 | 13.6799 | 13.6799 | 495.1011 | 4.9 | 0 | 2372.0953 | 0 | 0 | 0 | 4.9 | 0 | 0 | 2372.0953
1 | 22 | 22 | 8.4516 | 0 | 8.4516 | 11 | 5.3857 | 3.8216 | 3.8216 | 487.5272 | 8.4516 | 0 | 4027.4073 | 0 | 0 | 0 | 8.4516 | 0 | 0 | 4027.4073
1 | 22 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 481.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 484.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 492.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 502.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 508.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 511.4774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 518.3916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 520.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 521.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 527.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 528.9191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 530.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 526.6893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 526.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 13 | 26.6255 | 10.4957 | 37.1212 | 21.4614 | 10.2117 | 0 | 0 | 526.8794 | 0 | 37.1212 | 0 | 3.7103 | 0 | 0 | 0 | 37.1212 | 0 | 0
1 | 23 | 14 | 71.364 | 436.7865 | 508.1505 | 42.8038 | 9.8762 | 8242.0427 | 288 | 522.0349 | 17.7562 | 490.3943 | 8509.3231 | 49.015 | 0 | 0 | 17.7562 | 490.3943 | 0 | 8509.3231
1 | 23 | 15 | 81.8117 | 195.89 | 277.7017 | 37.0997 | 10.9601 | 0 | 0 | 525.2252 | 0 | 277.7017 | 0 | 27.7564 | 0 | 0 | 0 | 277.7017 | 0 | 0
1 | 23 | 16 | 3.225 | 0.16667 | 3.3917 | 12.8182 | 11.5279 | 0 | 0 | 524.3186 | 0 | 3.3917 | 0 | 0.339 | 0 | 0 | 0 | 3.3917 | 0 | 0
1 | 23 | 17 | 41.0137 | 0.0041667 | 41.0179 | 11.0038 | 11.5451 | 0 | 0 | 523.3701 | 0 | 41.0179 | 0 | 4.0997 | 0 | 0 | 0 | 41.0179 | 0 | 0
1 | 23 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 522.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 520.2516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 506.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 497.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 22 | 8.0672 | 0 | 8.0672 | 11 | 6.1771 | 4.4019 | 4.4019 | 494.6241 | 8.0672 | 0 | 3901.4711 | 0 | 0 | 0 | 8.0672 | 0 | 0 | 3901.4711
1 | 23 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 494.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 0 | 2.7633 | 0 | 2.7633 | 11 | 3.9577 | 0.95445 | 0.95445 | 496.6896 | 2.7633 | 0 | 1342.1222 | 0 | 0 | 0 | 2.7633 | 0 | 0 | 1342.1222
1 | 24 | 1 | 3.8708 | 0 | 3.8708 | 11 | 3.6394 | 1.2701 | 1.2701 | 497.3316 | 3.8708 | 0 | 1882.5087 | 0 | 0 | 0 | 3.8708 | 0 | 0 | 1882.5087
1 | 24 | 2 | 4.8917 | 0 | 4.8917 | 11 | 3.5276 | 1.5774 | 1.5774 | 497.8559 | 4.8917 | 0 | 2381.5368 | 0 | 0 | 0 | 4.8917 | 0 | 0 | 2381.5368
1 | 24 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 499.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 498.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 507.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 513.5834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 518.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 8 | 23.59 | 31.4382 | 55.0282 | 32.1385 | 6.5729 | 33.4889 | 33.4889 | 511.6684 | 55.0282 | 0 | 26387.6724 | 0 | 0 | 0 | 55.0282 | 0 | 0 | 26387.6724
1 | 24 | 9 | 50.8512 | 233.1706 | 284.0217 | 41.3755 | 7.7084 | 258.312 | 258.312 | 513.3689 | 284.0217 | 0 | 134056.3807 | 0 | 0 | 0 | 284.0217 | 0 | 0 | 134056.3807
1 | 24 | 10 | 33.0901 | 642.805 | 675.8951 | 46.1886 | 8.9471 | 1334.5541 | 288 | 506.4036 | 145.8598 | 530.0353 | 67126.8725 | 52.9772 | 0 | 0 | 145.8598 | 530.0353 | 0 | 67126.8725
1 | 24 | 11 | 0.88529 | 586.1491 | 587.0344 | 47.9442 | 9.5923 | 2971.3354 | 288 | 495.2457 | 56.899 | 530.1354 | 25450.9929 | 52.9872 | 0 | 0 | 56.899 | 530.1354 | 0 | 25450.9929
1 | 24 | 12 | 15.8189 | 209.8002 | 225.6191 | 45.4058 | 10.2891 | 0 | 0 | 496.5687 | 0 | 225.6191 | 0 | 22.5507 | 0 | 0 | 0 | 225.6191 | 0 | 0
1 | 24 | 13 | 5.1241 | 21.266 | 26.3901 | 40.8158 | 10.0827 | 0 | 0 | 502.6573 | 0 | 26.3901 | 0 | 2.6377 | 0 | 0 | 0 | 26.3901 | 0 | 0
1 | 24 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 515.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 530.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 526.8106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 526.4102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 519.0173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 511.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 508.1386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 495.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 490.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 491.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 493.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 505.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 512.0931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 517.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 523.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 530.3693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 532.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 531.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 528.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 514.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 10 | 0.068333 | 0.57519 | 0.64352 | 44.0711 | 8.4482 | 0.8634 | 0.8634 | 507.0494 | 0.64352 | 0 | 297.9351 | 0 | 0 | 0 | 0.64352 | 0 | 0 | 297.9351
1 | 25 | 11 | 0.75083 | 3.2201 | 3.9709 | 41.004 | 9.7214 | 29.2438 | 29.2438 | 501.8482 | 3.9709 | 0 | 1829.9848 | 0 | 0 | 0 | 3.9709 | 0 | 0 | 1829.9848
1 | 25 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 502.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 495.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 495.2654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 511.0964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 506.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 508.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 495.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 475.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 458.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 438.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 427.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 422.5754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 419.7398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 420.0042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 431.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 452.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 466.6059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 473.4064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 477.3004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 7 | 6.5927 | 0 | 6.5927 | 11 | 4.99 | 2.7458 | 2.7458 | 474.1197 | 6.5927 | 0 | 3053.196 | 0 | 0 | 0 | 6.5927 | 0 | 0 | 3053.196
1 | 26 | 8 | 0.081609 | 57.2778 | 57.3594 | 47.9474 | 5.4889 | 26.5293 | 26.5293 | 465.9954 | 57.3594 | 0 | 23978.9794 | 0 | 0 | 0 | 57.3594 | 0 | 0 | 23978.9794
1 | 26 | 9 | 0 | 2.7111 | 2.7111 | 48 | 6.9858 | 1.8756 | 1.8756 | 456.9509 | 2.7111 | 0 | 1108.7099 | 0 | 0 | 0 | 2.7111 | 0 | 0 | 1108.7099
1 | 26 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 452.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 448.7914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 447.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 445.6929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 446.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 15 | 1.2508 | 8.2507 | 9.5016 | 43.1291 | 7.7256 | 8.7067 | 8.7067 | 471.6472 | 9.5016 | 0 | 4071.5911 | 0 | 0 | 0 | 9.5016 | 0 | 0 | 4071.5911
1 | 26 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 472.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 474.7141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 461.1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 442.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 432.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 427.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 424.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 421.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 418.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 420.4234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 436.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 460.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 493.9609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 495.5756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 500.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 7 | 10.5936 | 7.8817 | 18.4753 | 26.7844 | 6.5556 | 11.1875 | 11.1875 | 497.3521 | 18.4753 | 0 | 8693.8664 | 0 | 0 | 0 | 18.4753 | 0 | 0 | 8693.8664
1 | 27 | 8 | 0 | 14.0108 | 14.0108 | 48 | 7.2524 | 10.6319 | 10.6319 | 500.7534 | 14.0108 | 0 | 6343.4471 | 0 | 0 | 0 | 14.0108 | 0 | 0 | 6343.4471
1 | 27 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 495.2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 497.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 11 | 0 | 1.1667 | 1.1667 | 48 | 7.6051 | 1.0155 | 1.0155 | 492.5271 | 1.1667 | 0 | 518.6471 | 0 | 0 | 0 | 1.1667 | 0 | 0 | 518.6471
1 | 27 | 12 | 0 | 0.87387 | 0.87387 | 48 | 8.2589 | 1.0454 | 1.0454 | 487.3147 | 0.87387 | 0 | 383.9028 | 0 | 0 | 0 | 0.87387 | 0 | 0 | 383.9028
1 | 27 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 483.3763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 482.7039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 496.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 498.6391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 505.1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 495.7899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 478.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 468.6967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 455.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 444.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 440.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 446.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 449.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 458.7884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 473.8859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 491.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 491.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 6 | 10.1364 | 0 | 10.1364 | 11 | 4.8007 | 4.0682 | 4.0682 | 491.8662 | 10.1364 | 0 | 4874.2305 | 0 | 0 | 0 | 10.1364 | 0 | 0 | 4874.2305
1 | 28 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 486.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 478.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 9 | 19.0997 | 26.3384 | 45.4381 | 32.4472 | 7.5707 | 38.9884 | 38.9884 | 476.9208 | 45.4381 | 0 | 20196.0203 | 0 | 0 | 0 | 45.4381 | 0 | 0 | 20196.0203
1 | 28 | 10 | 12.7361 | 46.5801 | 59.3162 | 40.0555 | 7.4159 | 47.8526 | 47.8526 | 469.8495 | 59.3162 | 0 | 25493.7239 | 0 | 0 | 0 | 59.3162 | 0 | 0 | 25493.7239
1 | 28 | 11 | 27.2519 | 2.8612 | 30.1131 | 14.5156 | 7.5879 | 26.0226 | 26.0226 | 459.7747 | 30.1131 | 0 | 13408.1486 | 0 | 0 | 0 | 30.1131 | 0 | 0 | 13408.1486
1 | 28 | 12 | 16.877 | 1.6279 | 18.5049 | 14.255 | 8.3192 | 22.9273 | 22.9273 | 459.9706 | 18.5049 | 0 | 8247.9311 | 0 | 0 | 0 | 18.5049 | 0 | 0 | 8247.9311
1 | 28 | 13 | 0.040327 | 0 | 0.040327 | 11 | 8.6546 | 0.062378 | 0.062378 | 459.3813 | 0.040327 | 0 | 18.0818 | 0 | 0 | 0 | 0.040327 | 0 | 0 | 18.0818
1 | 28 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 457.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 477.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 16 | 3.5605 | 0.091667 | 3.6521 | 11.9287 | 9.5837 | 18.1082 | 18.1082 | 479.377 | 3.6521 | 0 | 1707.1873 | 0 | 0 | 0 | 3.6521 | 0 | 0 | 1707.1873
1 | 28 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 482.8823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 478.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 462.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 449.1738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 430.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 428.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 420.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 423.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 429.8138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 450.3231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 472.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 500.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 501.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 6 | 0.016625 | 0 | 0.016625 | 11 | 4.5255 | 0.0063372 | 0.0063372 | 500.2834 | 0.016625 | 0 | 8.1343 | 0 | 0 | 0 | 0.016625 | 0 | 0 | 8.1343
1 | 29 | 7 | 1.1136 | 0 | 1.1136 | 11 | 5.2137 | 0.48544 | 0.48544 | 497.3006 | 1.1136 | 0 | 541.5268 | 0 | 0 | 0 | 1.1136 | 0 | 0 | 541.5268
1 | 29 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 495.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 496.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 488.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 11 | 27.3817 | 0 | 27.3817 | 11 | 9.8676 | 416.3116 | 288 | 487.4095 | 18.9423 | 8.4393 | 9024.3121 | 0.84351 | 0 | 0 | 18.9423 | 8.4393 | 0 | 9024.3121
1 | 29 | 12 | 3.0203 | 4.6753 | 7.6956 | 33.4785 | 10.2547 | 0 | 0 | 480.7354 | 0 | 7.6956 | 0 | 0.76918 | 0 | 0 | 0 | 7.6956 | 0 | 0
1 | 29 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 480.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 484.6983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 498.9778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 493.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 484.8749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 484.2277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 476.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 476.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 446.4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 439.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 432.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 432.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 434.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 442.7122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 455.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 471.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 476.7685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 473.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 470.0832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 456.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 442.9961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 10 | 0.2425 | 0.31833 | 0.56083 | 32.0015 | 8.9987 | 1.1642 | 1.1642 | 427.8551 | 0.56083 | 0 | 222.0079 | 0 | 0 | 0 | 0.56083 | 0 | 0 | 222.0079
1 | 30 | 11 | 27.0131 | 17.1961 | 44.2092 | 25.3919 | 10.0569 | 0 | 0 | 419.5017 | 0 | 44.2092 | 0 | 4.4187 | 0 | 0 | 0 | 44.2092 | 0 | 0
1 | 30 | 12 | 8.0133 | 1.3358 | 9.3491 | 16.2867 | 10.1343 | 0 | 0 | 419.285 | 0 | 9.3491 | 0 | 0.93445 | 0 | 0 | 0 | 9.3491 | 0 | 0
1 | 30 | 13 | 81.7898 | 238.9659 | 320.7557 | 38.5653 | 10.2117 | 0 | 0 | 422.6213 | 0 | 320.7557 | 0 | 32.0596 | 0 | 0 | 0 | 320.7557 | 0 | 0
1 | 30 | 14 | 12.9284 | 0.265 | 13.1934 | 11.7432 | 9.8762 | 213.9933 | 213.9933 | 426.4862 | 13.1934 | 0 | 5471.8825 | 0 | 0 | 0 | 13.1934 | 0 | 0 | 5471.8825
1 | 30 | 15 | 2.3987 | 0.07 | 2.4687 | 12.0491 | 10.9601 | 0 | 0 | 455.2265 | 0 | 2.4687 | 0 | 0.24674 | 0 | 0 | 0 | 2.4687 | 0 | 0
1 | 30 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 456.4478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 450.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 441.7069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 430.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 416.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 396.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 385.4562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 383.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 382.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 381.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 383.231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 388.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 391.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 403.3583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 410.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 398.8161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 391.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 390.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 388.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 386.8221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 385.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 13 | 0.40833 | 0.061667 | 0.47 | 15.8546 | 10.0827 | 0 | 0 | 388.4475 | 0 | 0.47 | 0 | 0.046977 | 0 | 0 | 0 | 0.47 | 0 | 0
1 | 31 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 390.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 423.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 423.2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 415.4069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 403.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 390.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 381.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 381.0142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 381.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 382.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 383.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 386.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 400.8599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 437.4397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 4 | 0.87872 | 0 | 0.87872 | 11 | 3.6222 | 0.28755 | 0.28755 | 462.7431 | 0.87872 | 0 | 396.956 | 0 | 0 | 0 | 0.87872 | 0 | 0 | 396.956
2 | 1 | 5 | 1.4584 | 0 | 1.4584 | 11 | 4.0351 | 0.51027 | 0.51027 | 468.7027 | 1.4584 | 0 | 667.5319 | 0 | 0 | 0 | 1.4584 | 0 | 0 | 667.5319
2 | 1 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 471.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 7 | 1.1133 | 0 | 1.1133 | 11 | 5.3599 | 0.5006 | 0.5006 | 468.7992 | 1.1133 | 0 | 509.6641 | 0 | 0 | 0 | 1.1133 | 0 | 0 | 509.6641
2 | 1 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 468.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 9 | 6.4314 | 7.6506 | 14.082 | 31.1018 | 7.6912 | 12.7121 | 12.7121 | 469.9912 | 14.082 | 0 | 6180.4404 | 0 | 0 | 0 | 14.082 | 0 | 0 | 6180.4404
2 | 1 | 10 | 22.8434 | 0 | 22.8434 | 11 | 8.4482 | 30.6485 | 30.6485 | 472.26 | 22.8434 | 0 | 10536.7367 | 0 | 0 | 0 | 22.8434 | 0 | 0 | 10536.7367
2 | 1 | 11 | 9.8477 | 0 | 9.8477 | 11 | 9.7214 | 72.523 | 72.523 | 468.2006 | 9.8477 | 0 | 4502.3808 | 0 | 0 | 0 | 9.8477 | 0 | 0 | 4502.3808
2 | 1 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 454.2526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 13 | 20.9508 | 0 | 20.9508 | 11 | 8.8869 | 39.1393 | 39.1393 | 457.9856 | 20.9508 | 0 | 9364.6954 | 0 | 0 | 0 | 20.9508 | 0 | 0 | 9364.6954
2 | 1 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 450.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 15 | 15.0775 | 0.50258 | 15.5801 | 12.1935 | 10.0224 | 0 | 0 | 467.2746 | 0 | 15.5801 | 0 | 1.5572 | 0 | 0 | 0 | 15.5801 | 0 | 0
2 | 1 | 16 | 87.0765 | 119.3163 | 206.3928 | 32.3898 | 11.4074 | 0 | 0 | 484.9863 | 0 | 206.3928 | 0 | 20.629 | 0 | 0 | 0 | 206.3928 | 0 | 0
2 | 1 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 485.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 470.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 450.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 424.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 449.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 435.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 430.7232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 429.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 430.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 432.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 443.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 468.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 473.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 461.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 7 | 0 | 0.16435 | 0.16435 | 48 | 4.99 | 0.068452 | 0.068452 | 453.2861 | 0.16435 | 0 | 66.6095 | 0 | 0 | 0 | 0.16435 | 0 | 0 | 66.6095
2 | 2 | 8 | 0 | 209.8766 | 209.8766 | 48 | 5.4889 | 97.0699 | 97.0699 | 457.5173 | 209.8766 | 0 | 85948.108 | 0 | 0 | 0 | 209.8766 | 0 | 0 | 85948.108
2 | 2 | 9 | 0 | 147.2717 | 147.2717 | 48 | 6.9858 | 101.8837 | 101.8837 | 446.2798 | 147.2717 | 0 | 58655.3508 | 0 | 0 | 0 | 147.2717 | 0 | 0 | 58655.3508
2 | 2 | 10 | 0 | 246.2525 | 246.2525 | 48 | 7.3471 | 193.5173 | 193.5173 | 439.5209 | 246.2525 | 0 | 96413.0154 | 0 | 0 | 0 | 246.2525 | 0 | 0 | 96413.0154
2 | 2 | 11 | 0 | 93.0048 | 93.0048 | 48 | 8.9643 | 186.674 | 186.674 | 431.4031 | 93.0048 | 0 | 35658.3421 | 0 | 0 | 0 | 93.0048 | 0 | 0 | 35658.3421
2 | 2 | 12 | 0 | 87.7425 | 87.7425 | 48 | 8.2847 | 106.5371 | 106.5371 | 428.2351 | 87.7425 | 0 | 33362.7952 | 0 | 0 | 0 | 87.7425 | 0 | 0 | 33362.7952
2 | 2 | 13 | 0 | 63.2678 | 63.2678 | 48 | 7.8202 | 60.4861 | 60.4861 | 426.3954 | 63.2678 | 0 | 23940.2522 | 0 | 0 | 0 | 63.2678 | 0 | 0 | 23940.2522
2 | 2 | 14 | 0 | 154.6443 | 154.6443 | 48 | 7.6568 | 137.5544 | 137.5544 | 436.4882 | 154.6443 | 0 | 60077.4895 | 0 | 0 | 0 | 154.6443 | 0 | 0 | 60077.4895
2 | 2 | 15 | 7.4242 | 18.6167 | 26.0409 | 37.4514 | 7.7256 | 23.8624 | 23.8624 | 457.9489 | 26.0409 | 0 | 10950.1204 | 0 | 0 | 0 | 26.0409 | 0 | 0 | 10950.1204
2 | 2 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 469.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 471.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 465.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 456.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 456.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 449.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 435.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 430.7232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 429.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 430.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 432.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 443.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 468.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 473.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 405.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 411.1981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 8 | 0 | 174.4002 | 174.4002 | 48 | 7.2524 | 132.3406 | 132.3406 | 408.148 | 174.4002 | 0 | 62809.8731 | 0 | 0 | 0 | 174.4002 | 0 | 0 | 62809.8731
2 | 3 | 9 | 0 | 291.8209 | 291.8209 | 48 | 7.6998 | 264.4148 | 264.4148 | 405.6849 | 291.8209 | 0 | 104379.9392 | 0 | 0 | 0 | 291.8209 | 0 | 0 | 104379.9392
2 | 3 | 10 | 0 | 234.4535 | 234.4535 | 48 | 7.8632 | 228.6468 | 228.6468 | 407.7598 | 234.4535 | 0 | 84346.938 | 0 | 0 | 0 | 234.4535 | 0 | 0 | 84346.938
2 | 3 | 11 | 0 | 50.8002 | 50.8002 | 48 | 7.6051 | 44.2143 | 44.2143 | 401.8212 | 50.8002 | 0 | 17974.179 | 0 | 0 | 0 | 50.8002 | 0 | 0 | 17974.179
2 | 3 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 391.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 418.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 402.1992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 15 | 0.085 | 0.12667 | 0.21167 | 33.1417 | 7.803 | 0.20078 | 0.20078 | 422.2082 | 0.21167 | 0 | 82.3524 | 0 | 0 | 0 | 0.21167 | 0 | 0 | 82.3524
2 | 3 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 421.0231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 420.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 420.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 420.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 420.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 365.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 359.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 358.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 360.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 362.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 374.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 401.8457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 4 | 0.022478 | 0 | 0.022478 | 11 | 3.6824 | 0.0074257 | 0.0074257 | 438.4877 | 0.022478 | 0 | 9.609 | 0 | 0 | 0 | 0.022478 | 0 | 0 | 9.609
2 | 4 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 441.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 442.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 445.9577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 8 | 0 | 104.5033 | 104.5033 | 48 | 6.9944 | 72.5028 | 72.5028 | 455.2897 | 104.5033 | 0 | 42563.1162 | 0 | 0 | 0 | 104.5033 | 0 | 0 | 42563.1162
2 | 4 | 9 | 0 | 184.7224 | 184.7224 | 48 | 7.5707 | 158.502 | 158.502 | 457.2025 | 184.7224 | 0 | 75588.895 | 0 | 0 | 0 | 184.7224 | 0 | 0 | 75588.895
2 | 4 | 10 | 2.4075 | 73.6253 | 76.0328 | 46.8284 | 7.4159 | 61.3385 | 61.3385 | 454.5687 | 76.0328 | 0 | 31001.6544 | 0 | 0 | 0 | 76.0328 | 0 | 0 | 31001.6544
2 | 4 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 452.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 12 | 0 | 5.8561 | 5.8561 | 48 | 8.3192 | 7.2557 | 7.2557 | 457.1954 | 5.8561 | 0 | 2396.3068 | 0 | 0 | 0 | 5.8561 | 0 | 0 | 2396.3068
2 | 4 | 13 | 0 | 25.3368 | 25.3368 | 48 | 8.6546 | 39.1914 | 39.1914 | 460.5143 | 25.3368 | 0 | 10451.7898 | 0 | 0 | 0 | 25.3368 | 0 | 0 | 10451.7898
2 | 4 | 14 | 0.18917 | 5.9536 | 6.1428 | 46.8606 | 8.9299 | 11.9349 | 11.9349 | 451.6771 | 6.1428 | 0 | 2486.7097 | 0 | 0 | 0 | 6.1428 | 0 | 0 | 2486.7097
2 | 4 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 462.2444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 461.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 463.4347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 467.1794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 452.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 431.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 410.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 397.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 392.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 394.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 397.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 416.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 428.4869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 455.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 462.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 469.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 7 | 0 | 64.1686 | 64.1686 | 48 | 5.2137 | 27.9735 | 27.9735 | 470.5683 | 64.1686 | 0 | 27115.6319 | 0 | 0 | 0 | 64.1686 | 0 | 0 | 27115.6319
2 | 5 | 8 | 0 | 0.11629 | 0.11629 | 48 | 5.1879 | 0.050425 | 0.050425 | 466.1119 | 0.11629 | 0 | 48.6234 | 0 | 0 | 0 | 0.11629 | 0 | 0 | 48.6234
2 | 5 | 9 | 0 | 173.4308 | 173.4308 | 48 | 6.7449 | 111.116 | 111.116 | 456.3584 | 173.4308 | 0 | 70821.9077 | 0 | 0 | 0 | 173.4308 | 0 | 0 | 70821.9077
2 | 5 | 10 | 0 | 59.811 | 59.811 | 48 | 8.8783 | 110.883 | 110.883 | 450.3911 | 59.811 | 0 | 24067.4106 | 0 | 0 | 0 | 59.811 | 0 | 0 | 24067.4106
2 | 5 | 11 | 3.2683 | 5.1624 | 8.4307 | 33.6562 | 9.8676 | 128.1807 | 128.1807 | 445.6958 | 8.4307 | 0 | 3473.785 | 0 | 0 | 0 | 8.4307 | 0 | 0 | 3473.785
2 | 5 | 12 | 6.18 | 46.0844 | 52.2644 | 43.6249 | 10.2547 | 0 | 0 | 432.0148 | 0 | 52.2644 | 0 | 5.2238 | 0 | 0 | 0 | 52.2644 | 0 | 0
2 | 5 | 13 | 0 | 38.9335 | 38.9335 | 48 | 10.031 | 0 | 0 | 435.4029 | 0 | 38.9335 | 0 | 3.8914 | 0 | 0 | 0 | 38.9335 | 0 | 0
2 | 5 | 14 | 0 | 71.2366 | 71.2366 | 48 | 9.9364 | 2170.2877 | 288 | 438.2012 | 9.4532 | 61.7834 | 3688.6453 | 6.1753 | 0 | 0 | 9.4532 | 61.7834 | 0 | 3688.6453
2 | 5 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 454.6973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 462.1987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 464.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 471.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 19 | 0.71267 | 0 | 0.71267 | 11 | 12.7322 | 0 | 0 | 466.7996 | 0 | 0.71267 | 0 | 0.071232 | 0 | 0 | 0 | 0.71267 | 0 | 0
2 | 5 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 444.2606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 431.1652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 423.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 425.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 421.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 421.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 429.7864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 437.6419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 4 | 1.8082 | 0 | 1.8082 | 11 | 3.691 | 0.59817 | 0.59817 | 448.0025 | 1.8082 | 0 | 790.1958 | 0 | 0 | 0 | 1.8082 | 0 | 0 | 790.1958
2 | 6 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 453.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 457.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 449.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 440.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 9 | 0 | 5.6621 | 5.6621 | 48 | 6.7707 | 3.6566 | 3.6566 | 423.4703 | 5.6621 | 0 | 2125.9418 | 0 | 0 | 0 | 5.6621 | 0 | 0 | 2125.9418
2 | 6 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 406.7348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 399.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 391.2585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 13 | 0 | 0.024546 | 0.024546 | 48 | 10.2117 | 0 | 0 | 393.9298 | 0 | 0.024546 | 0 | 0.0024534 | 0 | 0 | 0 | 0.024546 | 0 | 0
2 | 6 | 14 | 0 | 31.2381 | 31.2381 | 48 | 9.8762 | 506.672 | 288 | 394.8477 | 17.7562 | 13.4819 | 6158.6976 | 1.3475 | 0 | 0 | 17.7562 | 13.4819 | 0 | 6158.6976
2 | 6 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 432.8574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 439.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 445.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 445.5027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 438.4959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 416.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 399.9071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 394.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 391.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 388.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 390.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 398.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 400.7377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 417.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 424.7665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 431.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 426.6576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 416.1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 9 | 1.7833 | 34.1645 | 35.9479 | 46.1645 | 7.7084 | 32.6939 | 32.6939 | 404.132 | 35.9479 | 0 | 12868.1695 | 0 | 0 | 0 | 35.9479 | 0 | 0 | 12868.1695
2 | 7 | 10 | 1.0792 | 11.2034 | 12.2826 | 44.7491 | 8.9471 | 24.2519 | 24.2519 | 398.413 | 12.2826 | 0 | 4343.9059 | 0 | 0 | 0 | 12.2826 | 0 | 0 | 4343.9059
2 | 7 | 11 | 2.0492 | 22.0806 | 24.1298 | 44.8579 | 9.5923 | 122.1354 | 122.1354 | 394.4402 | 24.1298 | 0 | 8435.3419 | 0 | 0 | 0 | 24.1298 | 0 | 0 | 8435.3419
2 | 7 | 12 | 0 | 0.064776 | 0.064776 | 48 | 10.2891 | 0 | 0 | 395.8362 | 0 | 0.064776 | 0 | 0.0064744 | 0 | 0 | 0 | 0.064776 | 0 | 0
2 | 7 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 401.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 412.8859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 432.5279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 428.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 427.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 432.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 423.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 424.2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 453.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 450.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 449.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 451.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 458.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 463.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 481.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 500.9364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 498.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 494.5934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 496.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 8 | 2.24 | 88.4633 | 90.7033 | 47.0863 | 6.5729 | 55.1999 | 55.1999 | 490.2294 | 90.7033 | 0 | 40194.5521 | 0 | 0 | 0 | 90.7033 | 0 | 0 | 40194.5521
2 | 8 | 9 | 3.9467 | 213.7675 | 217.7142 | 47.3293 | 7.6912 | 196.5343 | 196.5343 | 490.2193 | 217.7142 | 0 | 96423.4539 | 0 | 0 | 0 | 217.7142 | 0 | 0 | 96423.4539
2 | 8 | 10 | 0 | 211.9981 | 211.9981 | 48 | 8.4482 | 284.4338 | 284.4338 | 488.9144 | 211.9981 | 0 | 93473.0308 | 0 | 0 | 0 | 211.9981 | 0 | 0 | 93473.0308
2 | 8 | 11 | 0 | 306.3615 | 306.3615 | 48 | 9.7214 | 2256.1835 | 288 | 483.0579 | 39.1068 | 267.2547 | 17013.7235 | 26.7122 | 0 | 0 | 39.1068 | 267.2547 | 0 | 17013.7235
2 | 8 | 12 | 0 | 330.4717 | 330.4717 | 48 | 9.4117 | 1163.4054 | 288 | 501.8422 | 81.808 | 248.6638 | 37127.9237 | 24.854 | 0 | 0 | 81.808 | 248.6638 | 0 | 37127.9237
2 | 8 | 13 | 0 | 331.261 | 331.261 | 48 | 8.8869 | 618.8469 | 288 | 511.7024 | 154.1628 | 177.0982 | 71485.662 | 17.701 | 0 | 0 | 154.1628 | 177.0982 | 0 | 71485.662
2 | 8 | 14 | 0 | 350.1235 | 350.1235 | 48 | 9.3428 | 1104.4766 | 288 | 511.2667 | 91.2972 | 258.8264 | 42294.9304 | 25.8698 | 0 | 0 | 91.2972 | 258.8264 | 0 | 42294.9304
2 | 8 | 15 | 8.6358 | 272.1082 | 280.7441 | 46.8619 | 10.0224 | 0 | 0 | 522.4491 | 0 | 280.7441 | 0 | 28.0604 | 0 | 0 | 0 | 280.7441 | 0 | 0
2 | 8 | 16 | 0 | 21.5085 | 21.5085 | 48 | 11.4074 | 0 | 0 | 521.9316 | 0 | 21.5085 | 0 | 2.1498 | 0 | 0 | 0 | 21.5085 | 0 | 0
2 | 8 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 527.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 519.7061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 502.4296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 488.6405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 485.3034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 22 | 2.9901 | 0 | 2.9901 | 11 | 5.575 | 1.4098 | 1.4098 | 440.7622 | 2.9901 | 0 | 1285.0511 | 0 | 0 | 0 | 2.9901 | 0 | 0 | 1285.0511
2 | 8 | 23 | 68.55 | 0 | 68.55 | 11 | 4.5599 | 26.2954 | 26.2954 | 435.1744 | 68.55 | 0 | 29077.172 | 0 | 0 | 0 | 68.55 | 0 | 0 | 29077.172
2 | 9 | 0 | 110.1451 | 0 | 110.1451 | 11 | 4.5083 | 41.8543 | 41.8543 | 436.2249 | 110.1451 | 0 | 46836.4419 | 0 | 0 | 0 | 110.1451 | 0 | 0 | 46836.4419
2 | 9 | 1 | 76.4157 | 0 | 76.4157 | 11 | 4.2072 | 27.5294 | 27.5294 | 446.4962 | 76.4157 | 0 | 33278.7574 | 0 | 0 | 0 | 76.4157 | 0 | 0 | 33278.7574
2 | 9 | 2 | 3.835 | 0 | 3.835 | 11 | 4.147 | 1.3674 | 1.3674 | 455.8614 | 3.835 | 0 | 1706.0622 | 0 | 0 | 0 | 3.835 | 0 | 0 | 1706.0622
2 | 9 | 3 | 102.1584 | 0 | 102.1584 | 11 | 3.7857 | 34.3091 | 34.3091 | 475.6484 | 102.1584 | 0 | 47467.7517 | 0 | 0 | 0 | 102.1584 | 0 | 0 | 47467.7517
2 | 9 | 4 | 64.4063 | 0 | 64.4063 | 11 | 3.7254 | 21.4229 | 21.4229 | 491.17 | 64.4063 | 0 | 30925.9751 | 0 | 0 | 0 | 64.4063 | 0 | 0 | 30925.9751
2 | 9 | 5 | 17.5364 | 0 | 17.5364 | 11 | 3.9663 | 6.0656 | 6.0656 | 501.3776 | 17.5364 | 0 | 8599.4511 | 0 | 0 | 0 | 17.5364 | 0 | 0 | 8599.4511
2 | 9 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 499.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 501.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 8 | 80.4993 | 9.9856 | 90.4849 | 15.0832 | 5.4889 | 41.8501 | 41.8501 | 495.8442 | 90.4849 | 0 | 43501.6004 | 0 | 0 | 0 | 90.4849 | 0 | 0 | 43501.6004
2 | 9 | 9 | 75.4959 | 61.3634 | 136.8593 | 27.5896 | 6.9858 | 94.6803 | 94.6803 | 495.071 | 136.8593 | 0 | 63979.1595 | 0 | 0 | 0 | 136.8593 | 0 | 0 | 63979.1595
2 | 9 | 10 | 72.3034 | 9.1991 | 81.5025 | 15.1762 | 7.3471 | 64.0487 | 64.0487 | 495.0066 | 81.5025 | 0 | 39107.3834 | 0 | 0 | 0 | 81.5025 | 0 | 0 | 39107.3834
2 | 9 | 11 | 58.4139 | 0.32777 | 58.7417 | 11.2065 | 8.9643 | 117.903 | 117.903 | 492.3673 | 58.7417 | 0 | 28264.2028 | 0 | 0 | 0 | 58.7417 | 0 | 0 | 28264.2028
2 | 9 | 12 | 78.5079 | 5.3634 | 83.8713 | 13.3661 | 8.2847 | 101.8366 | 101.8366 | 494.9051 | 83.8713 | 0 | 40387.2966 | 0 | 0 | 0 | 83.8713 | 0 | 0 | 40387.2966
2 | 9 | 13 | 128.9652 | 22.6209 | 151.5861 | 16.5214 | 7.8202 | 144.9214 | 144.9214 | 497.0598 | 151.5861 | 0 | 72842.9354 | 0 | 0 | 0 | 151.5861 | 0 | 0 | 72842.9354
2 | 9 | 14 | 170.0142 | 146.8456 | 316.8599 | 28.1473 | 7.6568 | 281.8433 | 281.8433 | 499.4197 | 316.8599 | 0 | 149327.3084 | 0 | 0 | 0 | 316.8599 | 0 | 0 | 149327.3084
2 | 9 | 15 | 98.7673 | 201.7029 | 300.4702 | 35.8378 | 7.7256 | 275.3342 | 275.3342 | 506.5944 | 300.4702 | 0 | 141448.3542 | 0 | 0 | 0 | 300.4702 | 0 | 0 | 141448.3542
2 | 9 | 16 | 40.8332 | 0 | 40.8332 | 11 | 7.3729 | 32.4033 | 32.4033 | 509.8797 | 40.8332 | 0 | 20370.8329 | 0 | 0 | 0 | 40.8332 | 0 | 0 | 20370.8329
2 | 9 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 515.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 511.3417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 19 | 0.90248 | 0 | 0.90248 | 11 | 7.7772 | 0.84615 | 0.84615 | 495.9094 | 0.90248 | 0 | 437.623 | 0 | 0 | 0 | 0.90248 | 0 | 0 | 437.623
2 | 9 | 20 | 8.5346 | 0 | 8.5346 | 11 | 7.3471 | 6.7069 | 6.7069 | 482.0364 | 8.5346 | 0 | 4020.107 | 0 | 0 | 0 | 8.5346 | 0 | 0 | 4020.107
2 | 9 | 21 | 81.894 | 0 | 81.894 | 11 | 6.5556 | 49.5902 | 49.5902 | 517.0787 | 81.894 | 0 | 41444.8327 | 0 | 0 | 0 | 81.894 | 0 | 0 | 41444.8327
2 | 9 | 22 | 78.2167 | 0 | 78.2167 | 11 | 4.9212 | 32.1358 | 32.1358 | 514.5822 | 78.2167 | 0 | 39388.5277 | 0 | 0 | 0 | 78.2167 | 0 | 0 | 39388.5277
2 | 9 | 23 | 93.7821 | 0 | 93.7821 | 11 | 4.5954 | 36.2108 | 36.2108 | 511.0577 | 93.7821 | 0 | 46896.4522 | 0 | 0 | 0 | 93.7821 | 0 | 0 | 46896.4522
2 | 10 | 0 | 139.0657 | 0 | 139.0657 | 11 | 3.8459 | 47.1607 | 47.1607 | 511.5995 | 139.0657 | 0 | 69616.2025 | 0 | 0 | 0 | 139.0657 | 0 | 0 | 69616.2025
2 | 10 | 1 | 171.7679 | 0 | 171.7679 | 11 | 3.4243 | 54.5196 | 54.5196 | 518.2123 | 171.7679 | 0 | 87122.8116 | 0 | 0 | 0 | 171.7679 | 0 | 0 | 87122.8116
2 | 10 | 2 | 123.9299 | 0 | 123.9299 | 11 | 3.3383 | 38.8281 | 38.8281 | 526.6664 | 123.9299 | 0 | 63906.4651 | 0 | 0 | 0 | 123.9299 | 0 | 0 | 63906.4651
2 | 10 | 3 | 121.7395 | 0 | 121.7395 | 11 | 3.3039 | 37.946 | 37.946 | 536.7815 | 121.7395 | 0 | 64008.38 | 0 | 0 | 0 | 121.7395 | 0 | 0 | 64008.38
2 | 10 | 4 | 96.0914 | 0 | 96.0914 | 11 | 3.2609 | 29.7605 | 29.7605 | 552.0051 | 96.0914 | 0 | 51985.9178 | 0 | 0 | 0 | 96.0914 | 0 | 0 | 51985.9178
2 | 10 | 5 | 57.7168 | 0 | 57.7168 | 11 | 3.4071 | 18.2717 | 18.2717 | 551.7287 | 57.7168 | 0 | 31209.1203 | 0 | 0 | 0 | 57.7168 | 0 | 0 | 31209.1203
2 | 10 | 6 | 76.1496 | 0 | 76.1496 | 11 | 4.9556 | 31.4997 | 31.4997 | 557.1623 | 76.1496 | 0 | 41590.0463 | 0 | 0 | 0 | 76.1496 | 0 | 0 | 41590.0463
2 | 10 | 7 | 90.4428 | 0 | 90.4428 | 11 | 6.5556 | 54.7668 | 54.7668 | 560.6902 | 90.4428 | 0 | 49715.5105 | 0 | 0 | 0 | 90.4428 | 0 | 0 | 49715.5105
2 | 10 | 8 | 75.114 | 68.6085 | 143.7225 | 28.6626 | 7.2524 | 109.0614 | 109.0614 | 558.7629 | 143.7225 | 0 | 76187.3637 | 0 | 0 | 0 | 143.7225 | 0 | 0 | 76187.3637
2 | 10 | 9 | 101.6097 | 76.3774 | 177.9871 | 26.8774 | 7.6998 | 161.2716 | 161.2716 | 552.2433 | 177.9871 | 0 | 93508.3689 | 0 | 0 | 0 | 177.9871 | 0 | 0 | 93508.3689
2 | 10 | 10 | 105.1458 | 10.7545 | 115.9003 | 14.4333 | 7.8632 | 113.0298 | 113.0298 | 557.7716 | 115.9003 | 0 | 62973.0594 | 0 | 0 | 0 | 115.9003 | 0 | 0 | 62973.0594
2 | 10 | 11 | 73.8676 | 69.77 | 143.6375 | 28.9722 | 7.6051 | 125.0161 | 125.0161 | 555.4179 | 143.6375 | 0 | 75617.3537 | 0 | 0 | 0 | 143.6375 | 0 | 0 | 75617.3537
2 | 10 | 12 | 47.0709 | 0.40799 | 47.4789 | 11.3179 | 8.2589 | 56.7969 | 56.7969 | 556.4675 | 47.4789 | 0 | 25883.1186 | 0 | 0 | 0 | 47.4789 | 0 | 0 | 25883.1186
2 | 10 | 13 | 17.8304 | 4.9502 | 22.7805 | 19.04 | 8.5686 | 33.1269 | 33.1269 | 557.3139 | 22.7805 | 0 | 12262.1646 | 0 | 0 | 0 | 22.7805 | 0 | 0 | 12262.1646
2 | 10 | 14 | 0 | 0.42666 | 0.42666 | 48 | 8.6374 | 0.65166 | 0.65166 | 554.7151 | 0.42666 | 0 | 216.1946 | 0 | 0 | 0 | 0.42666 | 0 | 0 | 216.1946
2 | 10 | 15 | 0 | 0.23864 | 0.23864 | 48 | 7.803 | 0.22636 | 0.22636 | 561.0374 | 0.23864 | 0 | 122.431 | 0 | 0 | 0 | 0.23864 | 0 | 0 | 122.431
2 | 10 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 564.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 568.2916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 576.1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 571.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 569.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 566.6565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 565.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 562.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 560.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 557.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 560.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 556.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 562.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 558.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 6 | 5.6999 | 0 | 5.6999 | 11 | 4.8007 | 2.2877 | 2.2877 | 571.9901 | 5.6999 | 0 | 3197.6131 | 0 | 0 | 0 | 5.6999 | 0 | 0 | 3197.6131
2 | 11 | 7 | 57.0045 | 0 | 57.0045 | 11 | 6.3664 | 32.7231 | 32.7231 | 580.3226 | 57.0045 | 0 | 32453.9549 | 0 | 0 | 0 | 57.0045 | 0 | 0 | 32453.9549
2 | 11 | 8 | 111.3124 | 47.7225 | 159.0349 | 22.1028 | 6.9944 | 110.3359 | 110.3359 | 586.4278 | 159.0349 | 0 | 89747.3943 | 0 | 0 | 0 | 159.0349 | 0 | 0 | 89747.3943
2 | 11 | 9 | 22.3271 | 20.882 | 43.2091 | 28.8813 | 7.5707 | 37.0757 | 37.0757 | 589.015 | 43.2091 | 0 | 24202.8496 | 0 | 0 | 0 | 43.2091 | 0 | 0 | 24202.8496
2 | 11 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 588.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 585.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 580.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 575.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 564.6953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 565.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 571.8315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 579.1769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 587.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 592.8095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 600.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 590.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 588.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 587.7289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 582.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 580.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 578.6617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 572.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 565.1511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 563.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 571.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 577.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 579.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 567.6686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 556.9408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 558.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 555.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 558.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 548.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 549.0148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 545.5033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 543.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 542.8271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 538.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 534.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 531.1423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 525.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 527.6459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 522.6146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 534.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 535.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 539.8551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 551.5562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 5 | 13.072 | 0 | 13.072 | 11 | 3.9405 | 4.5022 | 4.5022 | 554.7539 | 13.072 | 0 | 7107.9633 | 0 | 0 | 0 | 13.072 | 0 | 0 | 7107.9633
2 | 13 | 6 | 66.6091 | 0 | 66.6091 | 11 | 4.8093 | 26.7777 | 26.7777 | 551.3108 | 66.6091 | 0 | 35989.6407 | 0 | 0 | 0 | 66.6091 | 0 | 0 | 35989.6407
2 | 13 | 7 | 142.4443 | 0 | 142.4443 | 11 | 5.1706 | 61.5442 | 61.5442 | 550.0276 | 142.4443 | 0 | 76781.3874 | 0 | 0 | 0 | 142.4443 | 0 | 0 | 76781.3874
2 | 13 | 8 | 118.0978 | 94.1787 | 212.2765 | 27.4154 | 5.8502 | 106.7178 | 106.7178 | 555.8269 | 212.2765 | 0 | 112169.3191 | 0 | 0 | 0 | 212.2765 | 0 | 0 | 112169.3191
2 | 13 | 9 | 66.0926 | 5.3108 | 71.4034 | 13.752 | 6.7707 | 46.1127 | 46.1127 | 561.8615 | 71.4034 | 0 | 39136.8876 | 0 | 0 | 0 | 71.4034 | 0 | 0 | 39136.8876
2 | 13 | 10 | 53.9201 | 0 | 53.9201 | 11 | 8.9987 | 111.9263 | 111.9263 | 557.2395 | 53.9201 | 0 | 29453.2721 | 0 | 0 | 0 | 53.9201 | 0 | 0 | 29453.2721
2 | 13 | 11 | 28.6832 | 0 | 28.6832 | 11 | 10.0569 | 0 | 0 | 561.7035 | 0 | 28.6832 | 0 | 2.8669 | 0 | 0 | 0 | 28.6832 | 0 | 0
2 | 13 | 12 | 63.0466 | 0 | 63.0466 | 11 | 10.1343 | 0 | 0 | 557.0334 | 0 | 63.0466 | 0 | 6.3015 | 0 | 0 | 0 | 63.0466 | 0 | 0
2 | 13 | 13 | 56.5719 | 176.6353 | 233.2072 | 39.0245 | 10.2117 | 0 | 0 | 560.7402 | 0 | 233.2072 | 0 | 23.3091 | 0 | 0 | 0 | 233.2072 | 0 | 0
2 | 13 | 14 | 3.2913 | 18.2709 | 21.5621 | 42.3523 | 9.8762 | 349.7308 | 288 | 553.0814 | 17.7562 | 3.8059 | 9068.6074 | 0.3804 | 0 | 0 | 17.7562 | 3.8059 | 0 | 9068.6074
2 | 13 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 555.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 557.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 559.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 567.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 579.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 588.7845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 584.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 579.4412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 578.776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 0 | 39.7508 | 0 | 39.7508 | 11 | 3.9577 | 13.7298 | 13.7298 | 579.2625 | 39.7508 | 0 | 22588.8868 | 0 | 0 | 0 | 39.7508 | 0 | 0 | 22588.8868
2 | 14 | 1 | 97.6504 | 0 | 97.6504 | 11 | 3.6394 | 32.0417 | 32.0417 | 579.0339 | 97.6504 | 0 | 55468.7558 | 0 | 0 | 0 | 97.6504 | 0 | 0 | 55468.7558
2 | 14 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 573.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 568.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 4 | 38.2752 | 0 | 38.2752 | 11 | 3.5878 | 12.4581 | 12.4581 | 562.2425 | 38.2752 | 0 | 21098.8991 | 0 | 0 | 0 | 38.2752 | 0 | 0 | 21098.8991
2 | 14 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 557.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 6 | 35.9618 | 0 | 35.9618 | 11 | 5.3513 | 16.1407 | 16.1407 | 550.0047 | 35.9618 | 0 | 19383.5655 | 0 | 0 | 0 | 35.9618 | 0 | 0 | 19383.5655
2 | 14 | 7 | 10.6049 | 23.575 | 34.1798 | 36.5201 | 5.6008 | 16.2099 | 16.2099 | 549.1091 | 34.1798 | 0 | 17520.2131 | 0 | 0 | 0 | 34.1798 | 0 | 0 | 17520.2131
2 | 14 | 8 | 4.4581 | 11.2481 | 15.7062 | 37.4977 | 6.5729 | 9.5584 | 9.5584 | 561.7669 | 15.7062 | 0 | 8234.2838 | 0 | 0 | 0 | 15.7062 | 0 | 0 | 8234.2838
2 | 14 | 9 | 11.2667 | 61.3611 | 72.6278 | 42.2602 | 7.7084 | 66.0535 | 66.0535 | 561.2953 | 72.6278 | 0 | 37696.3658 | 0 | 0 | 0 | 72.6278 | 0 | 0 | 37696.3658
2 | 14 | 10 | 0.24434 | 1.2893 | 1.5336 | 42.105 | 8.9471 | 3.0281 | 3.0281 | 562.182 | 1.5336 | 0 | 797.5932 | 0 | 0 | 0 | 1.5336 | 0 | 0 | 797.5932
2 | 14 | 11 | 0.25083 | 2.9405 | 3.1913 | 45.0919 | 9.5923 | 16.1532 | 16.1532 | 554.8944 | 3.1913 | 0 | 1626.9438 | 0 | 0 | 0 | 3.1913 | 0 | 0 | 1626.9438
2 | 14 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 554.9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 557.6657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 560.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 15 | 5.0099 | 0 | 5.0099 | 11 | 11.6655 | 0 | 0 | 573.804 | 0 | 5.0099 | 0 | 0.50074 | 0 | 0 | 0 | 5.0099 | 0 | 0
2 | 14 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 572.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 575.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 592.1564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 601.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 605.2706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 604.5954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 602.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 602.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 598.1877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 1 | 16.5769 | 0 | 16.5769 | 11 | 3.605 | 5.4101 | 5.4101 | 600.0793 | 16.5769 | 0 | 9765.1004 | 0 | 0 | 0 | 16.5769 | 0 | 0 | 9765.1004
2 | 15 | 2 | 23.2939 | 0 | 23.2939 | 11 | 3.5018 | 7.4816 | 7.4816 | 596.6494 | 23.2939 | 0 | 13642.0756 | 0 | 0 | 0 | 23.2939 | 0 | 0 | 13642.0756
2 | 15 | 3 | 8.5332 | 0 | 8.5332 | 11 | 3.4416 | 2.7156 | 2.7156 | 590.2025 | 8.5332 | 0 | 4942.4545 | 0 | 0 | 0 | 8.5332 | 0 | 0 | 4942.4545
2 | 15 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 591.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 593.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 590.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 589.4262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 8 | 0 | 4.1197 | 4.1197 | 48 | 6.5729 | 2.5072 | 2.5072 | 597.7299 | 4.1197 | 0 | 2264.7482 | 0 | 0 | 0 | 4.1197 | 0 | 0 | 2264.7482
2 | 15 | 9 | 0.1725 | 35.3385 | 35.511 | 47.8203 | 7.6912 | 32.0563 | 32.0563 | 604.9633 | 35.511 | 0 | 19784.684 | 0 | 0 | 0 | 35.511 | 0 | 0 | 19784.684
2 | 15 | 10 | 1.34 | 35.0217 | 36.3617 | 46.6365 | 8.4482 | 48.7858 | 48.7858 | 607.4994 | 36.3617 | 0 | 20393.9508 | 0 | 0 | 0 | 36.3617 | 0 | 0 | 20393.9508
2 | 15 | 11 | 0 | 14.2562 | 14.2562 | 48 | 9.7214 | 104.989 | 104.989 | 610.1631 | 14.2562 | 0 | 8014.3098 | 0 | 0 | 0 | 14.2562 | 0 | 0 | 8014.3098
2 | 15 | 12 | 0 | 4.5959 | 4.5959 | 48 | 9.4117 | 16.1796 | 16.1796 | 609.3677 | 4.5959 | 0 | 2579.9947 | 0 | 0 | 0 | 4.5959 | 0 | 0 | 2579.9947
2 | 15 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 606.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 601.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 598.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 601.4867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 605.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 599.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 594.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 591.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 580.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 576.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 570.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 567.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 568.4777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 571.9071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 578.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 579.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 580.4538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 579.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 7 | 1.3182 | 0 | 1.3182 | 11 | 4.99 | 0.54904 | 0.54904 | 581.2711 | 1.3182 | 0 | 751.7571 | 0 | 0 | 0 | 1.3182 | 0 | 0 | 751.7571
2 | 16 | 8 | 3.3915 | 1.3341 | 4.7256 | 21.4458 | 5.4889 | 2.1856 | 2.1856 | 581.9802 | 4.7256 | 0 | 2648.8646 | 0 | 0 | 0 | 4.7256 | 0 | 0 | 2648.8646
2 | 16 | 9 | 0 | 4.3442 | 4.3442 | 48 | 6.9858 | 3.0054 | 3.0054 | 583.7576 | 4.3442 | 0 | 2327.449 | 0 | 0 | 0 | 4.3442 | 0 | 0 | 2327.449
2 | 16 | 10 | 0 | 8.2579 | 8.2579 | 48 | 7.3471 | 6.4895 | 6.4895 | 572.7551 | 8.2579 | 0 | 4333.3991 | 0 | 0 | 0 | 8.2579 | 0 | 0 | 4333.3991
2 | 16 | 11 | 0 | 1.0508 | 1.0508 | 48 | 8.9643 | 2.1091 | 2.1091 | 567.1532 | 1.0508 | 0 | 545.5266 | 0 | 0 | 0 | 1.0508 | 0 | 0 | 545.5266
2 | 16 | 12 | 0 | 1.0475 | 1.0475 | 48 | 8.2847 | 1.2718 | 1.2718 | 561.0866 | 1.0475 | 0 | 537.4351 | 0 | 0 | 0 | 1.0475 | 0 | 0 | 537.4351
2 | 16 | 13 | 0 | 28.3703 | 28.3703 | 48 | 7.8202 | 27.1229 | 27.1229 | 560.6206 | 28.3703 | 0 | 14543.1897 | 0 | 0 | 0 | 28.3703 | 0 | 0 | 14543.1897
2 | 16 | 14 | 0 | 20.5304 | 20.5304 | 48 | 7.6568 | 18.2615 | 18.2615 | 561.9973 | 20.5304 | 0 | 10552.5615 | 0 | 0 | 0 | 20.5304 | 0 | 0 | 10552.5615
2 | 16 | 15 | 0 | 17.5555 | 17.5555 | 48 | 7.7256 | 16.0868 | 16.0868 | 569.9518 | 17.5555 | 0 | 9163.1008 | 0 | 0 | 0 | 17.5555 | 0 | 0 | 9163.1008
2 | 16 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 569.7237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 566.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 560.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 544.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 536.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 522.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 507.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 502.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 501.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 504.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 511.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 525.7618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 544.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 550.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 548.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 553.9644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 549.5697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 541.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 538.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 532.1579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 533.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 534.2183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 544.6316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 549.6156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 553.9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 552.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 551.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 542.8278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 527.6319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 522.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 511.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 23 | 20.3852 | 0 | 20.3852 | 11 | 4.4566 | 7.6742 | 7.6742 | 502.6268 | 20.3852 | 0 | 10021.9169 | 0 | 0 | 0 | 20.3852 | 0 | 0 | 10021.9169
2 | 18 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 504.9299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 507.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 511.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 517.5802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 534.532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 539.5155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 534.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 531.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 528.2362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 9 | 1.1828 | 1.7141 | 2.897 | 32.8929 | 7.5707 | 2.4857 | 2.4857 | 513.6969 | 2.897 | 0 | 1392.8664 | 0 | 0 | 0 | 2.897 | 0 | 0 | 1392.8664
2 | 18 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 504.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 11 | 0 | 0.36713 | 0.36713 | 48 | 7.5879 | 0.31726 | 0.31726 | 496.9466 | 0.36713 | 0 | 164.8227 | 0 | 0 | 0 | 0.36713 | 0 | 0 | 164.8227
2 | 18 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 489.4846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 13 | 19.3806 | 74.6842 | 94.0648 | 40.3767 | 8.6546 | 145.5011 | 145.5011 | 493.1038 | 94.0648 | 0 | 42585.6719 | 0 | 0 | 0 | 94.0648 | 0 | 0 | 42585.6719
2 | 18 | 14 | 16.8234 | 626.7267 | 643.5501 | 47.0328 | 8.9299 | 1250.3529 | 288 | 490.9367 | 148.2321 | 495.318 | 65800.8123 | 49.5072 | 0 | 0 | 148.2321 | 495.318 | 0 | 65800.8123
2 | 18 | 15 | 28.0988 | 240.9272 | 269.026 | 44.1355 | 8.8009 | 466.6757 | 288 | 507.858 | 166.0243 | 103.0018 | 76989.1853 | 10.2951 | 0 | 0 | 166.0243 | 103.0018 | 0 | 76989.1853
2 | 18 | 16 | 10.8539 | 57.3983 | 68.2522 | 42.116 | 9.5837 | 338.4108 | 288 | 521.9318 | 58.0851 | 10.1671 | 27870.1502 | 1.0162 | 0 | 0 | 58.0851 | 10.1671 | 0 | 27870.1502
2 | 18 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 525.8919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 526.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 518.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 497.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 478.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 472.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 470.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 470.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 475.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 476.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 495.9685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 514.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 508.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 506.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 510.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 8 | 11.6029 | 30.0123 | 41.6152 | 37.6839 | 5.1879 | 18.0444 | 18.0444 | 507.4887 | 41.6152 | 0 | 19551.022 | 0 | 0 | 0 | 41.6152 | 0 | 0 | 19551.022
2 | 19 | 9 | 22.1425 | 223.2992 | 245.4417 | 44.662 | 6.7449 | 157.2529 | 157.2529 | 496.5754 | 245.4417 | 0 | 110918.3825 | 0 | 0 | 0 | 245.4417 | 0 | 0 | 110918.3825
2 | 19 | 10 | 29.2733 | 408.6866 | 437.9599 | 45.5269 | 8.8783 | 811.9299 | 288 | 489.0456 | 155.349 | 282.611 | 68900.1559 | 28.247 | 0 | 0 | 155.349 | 282.611 | 0 | 68900.1559
2 | 19 | 11 | 2.08 | 12.5243 | 14.6043 | 42.7303 | 9.8676 | 222.045 | 222.045 | 482.0618 | 14.6043 | 0 | 6416.1494 | 0 | 0 | 0 | 14.6043 | 0 | 0 | 6416.1494
2 | 19 | 12 | 16.3669 | 77.7513 | 94.1181 | 41.5658 | 10.2547 | 0 | 0 | 475.1749 | 0 | 94.1181 | 0 | 9.4071 | 0 | 0 | 0 | 94.1181 | 0 | 0
2 | 19 | 13 | 40.3866 | 58.6249 | 99.0115 | 32.9078 | 10.031 | 0 | 0 | 471.9787 | 0 | 99.0115 | 0 | 9.8962 | 0 | 0 | 0 | 99.0115 | 0 | 0
2 | 19 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 467.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 15 | 18.3695 | 59.1183 | 77.4878 | 39.2287 | 11.1494 | 0 | 0 | 483.5227 | 0 | 77.4878 | 0 | 7.7449 | 0 | 0 | 0 | 77.4878 | 0 | 0
2 | 19 | 16 | 2.1858 | 2.3517 | 4.5375 | 30.1761 | 12.5086 | 0 | 0 | 481.5476 | 0 | 4.5375 | 0 | 0.45352 | 0 | 0 | 0 | 4.5375 | 0 | 0
2 | 19 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 474.4975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 470.8848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 459.0757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 442.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 425.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 416.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 23 | 28.9655 | 0 | 28.9655 | 11 | 3.6704 | 9.5509 | 9.5509 | 410.5301 | 28.9655 | 0 | 11572.6051 | 0 | 0 | 0 | 28.9655 | 0 | 0 | 11572.6051
2 | 20 | 0 | 2.1858 | 0 | 2.1858 | 11 | 3.5706 | 0.70954 | 0.70954 | 410.6133 | 2.1858 | 0 | 873.4715 | 0 | 0 | 0 | 2.1858 | 0 | 0 | 873.4715
2 | 20 | 1 | 6.2191 | 0 | 6.2191 | 11 | 3.4588 | 1.9843 | 1.9843 | 410.3353 | 6.2191 | 0 | 2483.516 | 0 | 0 | 0 | 6.2191 | 0 | 0 | 2483.516
2 | 20 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 406.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 408.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 408.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 413.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 422.4599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 429.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 8 | 3.9092 | 108.9734 | 112.8825 | 46.7187 | 5.8502 | 56.7495 | 56.7495 | 427.4336 | 112.8825 | 0 | 42976.065 | 0 | 0 | 0 | 112.8825 | 0 | 0 | 42976.065
2 | 20 | 9 | 3.5533 | 175.9007 | 179.454 | 47.2674 | 6.7707 | 115.8925 | 115.8925 | 425.8094 | 179.454 | 0 | 67930.8914 | 0 | 0 | 0 | 179.454 | 0 | 0 | 67930.8914
2 | 20 | 10 | 10.5791 | 473.967 | 484.5461 | 47.1922 | 8.9987 | 1005.8117 | 288 | 423.2954 | 138.7429 | 345.8031 | 52181.6603 | 34.5631 | 0 | 0 | 138.7429 | 345.8031 | 0 | 52181.6603
2 | 20 | 11 | 14.3597 | 475.7161 | 490.0758 | 46.9159 | 10.0569 | 0 | 0 | 416.3719 | 0 | 490.0758 | 0 | 48.9832 | 0 | 0 | 0 | 490.0758 | 0 | 0
2 | 20 | 12 | 1.0353 | 305.7413 | 306.7766 | 47.8751 | 10.1343 | 0 | 0 | 410.6464 | 0 | 306.7766 | 0 | 30.6624 | 0 | 0 | 0 | 306.7766 | 0 | 0
2 | 20 | 13 | 1.4181 | 193.6562 | 195.0743 | 47.731 | 10.2117 | 0 | 0 | 412.7627 | 0 | 195.0743 | 0 | 19.4977 | 0 | 0 | 0 | 195.0743 | 0 | 0
2 | 20 | 14 | 0.53667 | 200.1791 | 200.7158 | 47.9011 | 9.8762 | 3255.5474 | 288 | 414.027 | 17.7562 | 182.9596 | 6501.0047 | 18.2869 | 0 | 0 | 17.7562 | 182.9596 | 0 | 6501.0047
2 | 20 | 15 | 0.32667 | 107.247 | 107.5736 | 47.8876 | 10.9601 | 0 | 0 | 424.9923 | 0 | 107.5736 | 0 | 10.752 | 0 | 0 | 0 | 107.5736 | 0 | 0
2 | 20 | 16 | 0.14917 | 21.9791 | 22.1283 | 47.7506 | 11.5279 | 0 | 0 | 439.7007 | 0 | 22.1283 | 0 | 2.2117 | 0 | 0 | 0 | 22.1283 | 0 | 0
2 | 20 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 435.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 430.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 424.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 417.1822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 407.1554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 405.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 399.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 403.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 414.4826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 2 | 0.8525 | 0 | 0.8525 | 11 | 3.5276 | 0.2749 | 0.2749 | 414.1838 | 0.8525 | 0 | 343.7142 | 0 | 0 | 0 | 0.8525 | 0 | 0 | 343.7142
2 | 21 | 3 | 1.7125 | 0 | 1.7125 | 11 | 3.562 | 0.55516 | 0.55516 | 421.9526 | 1.7125 | 0 | 703.7564 | 0 | 0 | 0 | 1.7125 | 0 | 0 | 703.7564
2 | 21 | 4 | 1.7675 | 0 | 1.7675 | 11 | 3.5878 | 0.5753 | 0.5753 | 425.3981 | 1.7675 | 0 | 732.4486 | 0 | 0 | 0 | 1.7675 | 0 | 0 | 732.4486
2 | 21 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 430.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 442.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 7 | 1.2508 | 0 | 1.2508 | 11 | 5.6008 | 0.59321 | 0.59321 | 455.9108 | 1.2508 | 0 | 556.5092 | 0 | 0 | 0 | 1.2508 | 0 | 0 | 556.5092
2 | 21 | 8 | 1.6619 | 403.1462 | 404.8081 | 47.8481 | 6.5729 | 246.3566 | 246.3566 | 455.6041 | 404.8081 | 0 | 165062.9547 | 0 | 0 | 0 | 404.8081 | 0 | 0 | 165062.9547
2 | 21 | 9 | 1.9242 | 620.8427 | 622.7668 | 47.8857 | 7.7084 | 566.3938 | 288 | 452.0988 | 316.6646 | 306.1023 | 127999.9804 | 30.595 | 0 | 0 | 316.6646 | 306.1023 | 0 | 127999.9804
2 | 21 | 10 | 0.4625 | 269.0836 | 269.5461 | 47.9365 | 8.9471 | 532.2185 | 288 | 445.1057 | 145.8598 | 123.6863 | 57931.0226 | 12.3625 | 0 | 0 | 145.8598 | 123.6863 | 0 | 57931.0226
2 | 21 | 11 | 0.13417 | 0.80379 | 0.93796 | 42.7075 | 9.5923 | 4.7476 | 4.7476 | 442.0645 | 0.93796 | 0 | 374.5804 | 0 | 0 | 0 | 0.93796 | 0 | 0 | 374.5804
2 | 21 | 12 | 1.1692 | 87.4724 | 88.6415 | 47.512 | 10.2891 | 0 | 0 | 438.6271 | 0 | 88.6415 | 0 | 8.8597 | 0 | 0 | 0 | 88.6415 | 0 | 0
2 | 21 | 13 | 0.37667 | 67.5452 | 67.9218 | 47.7948 | 10.0827 | 0 | 0 | 440.5569 | 0 | 67.9218 | 0 | 6.7888 | 0 | 0 | 0 | 67.9218 | 0 | 0
2 | 21 | 14 | 6.1342 | 361.2225 | 367.3567 | 47.3822 | 10.6934 | 0 | 0 | 441.4251 | 0 | 367.3567 | 0 | 36.7174 | 0 | 0 | 0 | 367.3567 | 0 | 0
2 | 21 | 15 | 14.4782 | 556.0795 | 570.5577 | 47.0611 | 11.6655 | 0 | 0 | 445.981 | 0 | 570.5577 | 0 | 57.0274 | 0 | 0 | 0 | 570.5577 | 0 | 0
2 | 21 | 16 | 59.6144 | 168.717 | 228.3314 | 38.3398 | 12.3021 | 0 | 0 | 464.1417 | 0 | 228.3314 | 0 | 22.8218 | 0 | 0 | 0 | 228.3314 | 0 | 0
2 | 21 | 17 | 2.9491 | 0 | 2.9491 | 11 | 12.1989 | 0 | 0 | 466.5716 | 0 | 2.9491 | 0 | 0.29477 | 0 | 0 | 0 | 2.9491 | 0 | 0
2 | 21 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 465.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 458.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 449.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 21 | 0.61083 | 0 | 0.61083 | 11 | 10.3235 | 0 | 0 | 438.4885 | 0 | 0.61083 | 0 | 0.061053 | 0 | 0 | 0 | 0.61083 | 0 | 0
2 | 21 | 22 | 38.0871 | 0 | 38.0871 | 11 | 5.6868 | 18.4228 | 18.4228 | 433.3447 | 38.0871 | 0 | 16085.891 | 0 | 0 | 0 | 38.0871 | 0 | 0 | 16085.891
2 | 21 | 23 | 18.9033 | 0 | 18.9033 | 11 | 4.5734 | 7.2693 | 7.2693 | 431.8243 | 18.9033 | 0 | 7954.9535 | 0 | 0 | 0 | 18.9033 | 0 | 0 | 7954.9535
2 | 22 | 0 | 5.1948 | 0 | 5.1948 | 11 | 3.8373 | 1.7592 | 1.7592 | 435.5077 | 5.1948 | 0 | 2205.2367 | 0 | 0 | 0 | 5.1948 | 0 | 0 | 2205.2367
2 | 22 | 1 | 0.2975 | 0 | 0.2975 | 11 | 3.605 | 0.097093 | 0.097093 | 442.0947 | 0.2975 | 0 | 128.2507 | 0 | 0 | 0 | 0.2975 | 0 | 0 | 128.2507
2 | 22 | 2 | 24.813 | 0 | 24.813 | 11 | 3.5018 | 7.9695 | 7.9695 | 458.9845 | 24.813 | 0 | 11115.8536 | 0 | 0 | 0 | 24.813 | 0 | 0 | 11115.8536
2 | 22 | 3 | 8.9755 | 0 | 8.9755 | 11 | 3.4416 | 2.8563 | 2.8563 | 483.2874 | 8.9755 | 0 | 4238.9936 | 0 | 0 | 0 | 8.9755 | 0 | 0 | 4238.9936
2 | 22 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 509.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 506.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 6 | 0.76583 | 0 | 0.76583 | 11 | 5.1793 | 0.33147 | 0.33147 | 513.6555 | 0.76583 | 0 | 384.9503 | 0 | 0 | 0 | 0.76583 | 0 | 0 | 384.9503
2 | 22 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 499.0457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 8 | 4.2392 | 207.6574 | 211.8966 | 47.2598 | 6.5729 | 128.9552 | 128.9552 | 494.3738 | 211.8966 | 0 | 94741.9348 | 0 | 0 | 0 | 211.8966 | 0 | 0 | 94741.9348
2 | 22 | 9 | 0 | 0.020199 | 0.020199 | 48 | 7.6912 | 0.018234 | 0.018234 | 493.9954 | 0.020199 | 0 | 9.0088 | 0 | 0 | 0 | 0.020199 | 0 | 0 | 9.0088
2 | 22 | 10 | 0 | 5.0457 | 5.0457 | 48 | 8.4482 | 6.7697 | 6.7697 | 486.609 | 5.0457 | 0 | 2213.0865 | 0 | 0 | 0 | 5.0457 | 0 | 0 | 2213.0865
2 | 22 | 11 | 6.475 | 41.306 | 47.781 | 42.986 | 9.7214 | 351.8807 | 288 | 479.5059 | 39.1068 | 8.6742 | 17070.8949 | 0.86699 | 0 | 0 | 39.1068 | 8.6742 | 0 | 17070.8949
2 | 22 | 12 | 0 | 23.9984 | 23.9984 | 48 | 9.4117 | 84.4847 | 84.4847 | 478.196 | 23.9984 | 0 | 10323.9954 | 0 | 0 | 0 | 23.9984 | 0 | 0 | 10323.9954
2 | 22 | 13 | 0.53731 | 32.2309 | 32.7682 | 47.3933 | 8.8869 | 61.2161 | 61.2161 | 477.2409 | 32.7682 | 0 | 14085.3439 | 0 | 0 | 0 | 32.7682 | 0 | 0 | 14085.3439
2 | 22 | 14 | 0 | 24.3967 | 24.3967 | 48 | 9.3428 | 76.9601 | 76.9601 | 471.7736 | 24.3967 | 0 | 10338.6639 | 0 | 0 | 0 | 24.3967 | 0 | 0 | 10338.6639
2 | 22 | 15 | 0 | 11.0308 | 11.0308 | 48 | 10.0224 | 0 | 0 | 470.836 | 0 | 11.0308 | 0 | 1.1025 | 0 | 0 | 0 | 11.0308 | 0 | 0
2 | 22 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 493.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 485.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 484.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 469.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 452.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 434.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 429.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 428.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 430.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 434.9532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 438.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 446.0346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 474.058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 490.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 497.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 497.8288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 8 | 0 | 0.40925 | 0.40925 | 48 | 5.4889 | 0.18928 | 0.18928 | 495.8898 | 0.40925 | 0 | 183.2997 | 0 | 0 | 0 | 0.40925 | 0 | 0 | 183.2997
2 | 23 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 490.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 483.4448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 485.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 478.6014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 13 | 0.17167 | 0 | 0.17167 | 11 | 7.8202 | 0.16412 | 0.16412 | 479.2993 | 0.17167 | 0 | 80.3914 | 0 | 0 | 0 | 0.17167 | 0 | 0 | 80.3914
2 | 23 | 14 | 0.15 | 0 | 0.15 | 11 | 7.6568 | 0.13342 | 0.13342 | 482.9664 | 0.15 | 0 | 70.795 | 0 | 0 | 0 | 0.15 | 0 | 0 | 70.795
2 | 23 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 483.5183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 484.5603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 474.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 472.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 451.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 439.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 424.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 412.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 408.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 407.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 410.6393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 416.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 432.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 462.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 468.5618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 472.8399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 470.2932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 8 | 1.8717 | 71.0865 | 72.9582 | 47.0508 | 7.2524 | 55.363 | 55.363 | 472.8696 | 72.9582 | 0 | 31066.9586 | 0 | 0 | 0 | 72.9582 | 0 | 0 | 31066.9586
2 | 24 | 9 | 0 | 0.68642 | 0.68642 | 48 | 7.6998 | 0.62195 | 0.62195 | 469.2164 | 0.68642 | 0 | 289.13 | 0 | 0 | 0 | 0.68642 | 0 | 0 | 289.13
2 | 24 | 10 | 0.79881 | 0.66493 | 1.4637 | 27.808 | 7.8632 | 1.4275 | 1.4275 | 469.6264 | 1.4637 | 0 | 646.7067 | 0 | 0 | 0 | 1.4637 | 0 | 0 | 646.7067
2 | 24 | 11 | 0 | 0.11405 | 0.11405 | 48 | 7.6051 | 0.099264 | 0.099264 | 462.5311 | 0.11405 | 0 | 47.277 | 0 | 0 | 0 | 0.11405 | 0 | 0 | 47.277
2 | 24 | 12 | 0.72083 | 14.3412 | 15.062 | 46.2293 | 8.2589 | 18.018 | 18.018 | 459.9943 | 15.062 | 0 | 6232.1239 | 0 | 0 | 0 | 15.062 | 0 | 0 | 6232.1239
2 | 24 | 13 | 0 | 11.7858 | 11.7858 | 48 | 8.5686 | 17.1387 | 17.1387 | 463.3449 | 11.7858 | 0 | 4895.1853 | 0 | 0 | 0 | 11.7858 | 0 | 0 | 4895.1853
2 | 24 | 14 | 0 | 46.3928 | 46.3928 | 48 | 8.6374 | 70.8584 | 70.8584 | 452.8949 | 46.3928 | 0 | 18784.2226 | 0 | 0 | 0 | 46.3928 | 0 | 0 | 18784.2226
2 | 24 | 15 | 0 | 147.7591 | 147.7591 | 48 | 7.803 | 140.1588 | 140.1588 | 461.5651 | 147.7591 | 0 | 61107.9923 | 0 | 0 | 0 | 147.7591 | 0 | 0 | 61107.9923
2 | 24 | 16 | 0 | 8.5827 | 8.5827 | 48 | 7.6998 | 7.7767 | 7.7767 | 467.5578 | 8.5827 | 0 | 3600.9494 | 0 | 0 | 0 | 8.5827 | 0 | 0 | 3600.9494
2 | 24 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 471.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 458.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 443.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 425.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 408.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 406.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 404.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 408.7834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 410.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 428.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 449.7117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 473.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 467.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 472.8274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 475.9687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 471.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 9 | 0.18 | 0.34917 | 0.52917 | 35.4142 | 7.5707 | 0.45405 | 0.45405 | 470.5115 | 0.52917 | 0 | 230.239 | 0 | 0 | 0 | 0.52917 | 0 | 0 | 230.239
2 | 25 | 10 | 2.0758 | 13.2465 | 15.3224 | 42.9873 | 7.4159 | 12.3611 | 12.3611 | 473.4183 | 15.3224 | 0 | 6595.2233 | 0 | 0 | 0 | 15.3224 | 0 | 0 | 6595.2233
2 | 25 | 11 | 0 | 7.4375 | 7.4375 | 48 | 7.5879 | 6.4272 | 6.4272 | 475.0898 | 7.4375 | 0 | 3176.4807 | 0 | 0 | 0 | 7.4375 | 0 | 0 | 3176.4807
2 | 25 | 12 | 0 | 25.0429 | 25.0429 | 48 | 8.3192 | 31.0278 | 31.0278 | 473.8699 | 25.0429 | 0 | 10665.0123 | 0 | 0 | 0 | 25.0429 | 0 | 0 | 10665.0123
2 | 25 | 13 | 0 | 236.6515 | 236.6515 | 48 | 8.6546 | 366.0568 | 288 | 475.9895 | 186.1887 | 50.4628 | 79686.8139 | 5.0438 | 0 | 0 | 186.1887 | 50.4628 | 0 | 79686.8139
2 | 25 | 14 | 0 | 3.7833 | 3.7833 | 48 | 8.9299 | 7.3506 | 7.3506 | 480.1433 | 3.7833 | 0 | 1634.9422 | 0 | 0 | 0 | 3.7833 | 0 | 0 | 1634.9422
2 | 25 | 15 | 0 | 0.34 | 0.34 | 48 | 8.8009 | 0.58979 | 0.58979 | 476.5979 | 0.34 | 0 | 145.7233 | 0 | 0 | 0 | 0.34 | 0 | 0 | 145.7233
2 | 25 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 478.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 483.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 497.7757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 491.8628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 485.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 457.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 446.6173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 438.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 440.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 445.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 451.8773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 451.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 470.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 476.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 483.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 487.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 8 | 1.0942 | 78.7434 | 79.8376 | 47.4929 | 5.1879 | 34.6177 | 34.6177 | 503.0756 | 79.8376 | 0 | 36372.6072 | 0 | 0 | 0 | 79.8376 | 0 | 0 | 36372.6072
2 | 26 | 9 | 0.90417 | 20.7804 | 21.6845 | 46.4572 | 6.7449 | 13.8931 | 13.8931 | 502.0092 | 21.6845 | 0 | 9878.4256 | 0 | 0 | 0 | 21.6845 | 0 | 0 | 9878.4256
2 | 26 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 491.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 481.8971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 476.5986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 474.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 472.7521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 469.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 483.5891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 486.2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 488.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 492.9485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 20 | 12.3633 | 0 | 12.3633 | 11 | 13.3172 | 0 | 0 | 479.4862 | 0 | 12.3633 | 0 | 1.2357 | 0 | 0 | 0 | 12.3633 | 0 | 0
2 | 26 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 469.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 462.642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 455.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 452.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 453.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 459.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 3 | 0.81083 | 0 | 0.81083 | 11 | 3.4416 | 0.25804 | 0.25804 | 462.0757 | 0.81083 | 0 | 365.7473 | 0 | 0 | 0 | 0.81083 | 0 | 0 | 365.7473
2 | 27 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 461.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 466.2509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 6 | 31.1693 | 0 | 31.1693 | 11 | 4.8093 | 12.5304 | 12.5304 | 466.004 | 31.1693 | 0 | 14182.1388 | 0 | 0 | 0 | 31.1693 | 0 | 0 | 14182.1388
2 | 27 | 7 | 34.3783 | 130.3198 | 164.6982 | 40.2768 | 5.1706 | 71.1592 | 71.1592 | 457.2096 | 164.6982 | 0 | 68668.0689 | 0 | 0 | 0 | 164.6982 | 0 | 0 | 68668.0689
2 | 27 | 8 | 19.4797 | 278.0327 | 297.5124 | 45.5774 | 5.8502 | 149.5685 | 149.5685 | 449.7483 | 297.5124 | 0 | 120245.8249 | 0 | 0 | 0 | 297.5124 | 0 | 0 | 120245.8249
2 | 27 | 9 | 98.4966 | 563.5238 | 662.0203 | 42.4951 | 6.7707 | 427.5367 | 288 | 435.6155 | 445.9543 | 216.066 | 175313.7751 | 21.5959 | 0 | 0 | 445.9543 | 216.066 | 0 | 175313.7751
2 | 27 | 10 | 0.31917 | 478.9104 | 479.2295 | 47.9754 | 8.9987 | 994.7758 | 288 | 426.1251 | 138.7429 | 340.4866 | 52465.6026 | 34.0317 | 0 | 0 | 138.7429 | 340.4866 | 0 | 52465.6026
2 | 27 | 11 | 4.2864 | 0 | 4.2864 | 11 | 10.0569 | 0 | 0 | 419.3243 | 0 | 4.2864 | 0 | 0.42843 | 0 | 0 | 0 | 4.2864 | 0 | 0
2 | 27 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 410.8879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 13 | 19.57 | 57.9345 | 77.5045 | 38.6575 | 10.2117 | 0 | 0 | 410.1279 | 0 | 77.5045 | 0 | 7.7466 | 0 | 0 | 0 | 77.5045 | 0 | 0
2 | 27 | 14 | 25.5765 | 96.0348 | 121.6113 | 40.2184 | 9.8762 | 1972.4976 | 288 | 407.1646 | 17.7562 | 103.8551 | 6515.5699 | 10.3803 | 0 | 0 | 17.7562 | 103.8551 | 0 | 6515.5699
2 | 27 | 15 | 13.7958 | 244.668 | 258.4638 | 46.0251 | 10.9601 | 0 | 0 | 424.9251 | 0 | 258.4638 | 0 | 25.8335 | 0 | 0 | 0 | 258.4638 | 0 | 0
2 | 27 | 16 | 0.42996 | 86.7936 | 87.2236 | 47.8176 | 11.5279 | 0 | 0 | 438.1321 | 0 | 87.2236 | 0 | 8.718 | 0 | 0 | 0 | 87.2236 | 0 | 0
2 | 27 | 17 | 65.0321 | 12.0817 | 77.1138 | 16.7969 | 11.5451 | 0 | 0 | 428.6112 | 0 | 77.1138 | 0 | 7.7075 | 0 | 0 | 0 | 77.1138 | 0 | 0
2 | 27 | 18 | 1.4754 | 0 | 1.4754 | 11 | 11.9236 | 0 | 0 | 431.1839 | 0 | 1.4754 | 0 | 0.14747 | 0 | 0 | 0 | 1.4754 | 0 | 0
2 | 27 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 424.1095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 414.0726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 405.7899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 400.1648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 397.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 394.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 393.3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 397.0975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 396.7317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 396.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 398.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 392.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 387.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 383.5309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 380.1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 378.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 381.7154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 383.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 385.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 382.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 385.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 16 | 7.4057 | 0 | 7.4057 | 11 | 12.3021 | 0 | 0 | 405.2186 | 0 | 7.4057 | 0 | 0.7402 | 0 | 0 | 0 | 7.4057 | 0 | 0
2 | 28 | 17 | 1.9505 | 0 | 1.9505 | 11 | 12.1989 | 0 | 0 | 403.9772 | 0 | 1.9505 | 0 | 0.19495 | 0 | 0 | 0 | 1.9505 | 0 | 0
2 | 28 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 393.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 382.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 379.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 422.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 414.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 419.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 416.4793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 423.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 416.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 3 | 10.4428 | 0 | 10.4428 | 11 | 3.4416 | 3.3233 | 3.3233 | 431.0519 | 10.4428 | 0 | 4386.5358 | 0 | 0 | 0 | 10.4428 | 0 | 0 | 4386.5358
3 | 1 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 452.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 453.8222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 456.8152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 441.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 8 | 0 | 51.6673 | 51.6673 | 48 | 6.5729 | 31.4435 | 31.4435 | 441.4586 | 51.6673 | 0 | 20328.9467 | 0 | 0 | 0 | 51.6673 | 0 | 0 | 20328.9467
3 | 1 | 9 | 14.0565 | 138.8644 | 152.9209 | 44.599 | 7.6912 | 138.0443 | 138.0443 | 435.7014 | 152.9209 | 0 | 59807.7414 | 0 | 0 | 0 | 152.9209 | 0 | 0 | 59807.7414
3 | 1 | 10 | 0 | 700.5787 | 700.5787 | 48 | 8.4482 | 939.9528 | 288 | 431.3123 | 214.6562 | 485.9225 | 82280.3599 | 48.5681 | 0 | 0 | 214.6562 | 485.9225 | 0 | 82280.3599
3 | 1 | 11 | 0 | 1667.9383 | 1667.9383 | 48 | 9.7214 | 12283.4454 | 288 | 423.9946 | 39.1068 | 1628.8315 | 14703.9444 | 162.8022 | 0 | 0 | 39.1068 | 1628.8315 | 0 | 14703.9444
3 | 1 | 12 | 1.1077 | 2735.6901 | 2736.7978 | 47.985 | 9.4117 | 9634.7276 | 288 | 418.3156 | 81.808 | 2654.9898 | 30296.0024 | 265.367 | 0 | 0 | 81.808 | 2654.9898 | 0 | 30296.0024
3 | 1 | 13 | 0 | 1144.7189 | 1144.7189 | 48 | 8.8869 | 2138.5122 | 288 | 418.0444 | 154.1628 | 990.5561 | 57047.0874 | 99.0064 | 0 | 0 | 154.1628 | 990.5561 | 0 | 57047.0874
3 | 1 | 14 | 0 | 201.56 | 201.56 | 48 | 9.3428 | 635.8279 | 288 | 415.221 | 91.2972 | 110.2628 | 33526.2275 | 11.0208 | 0 | 0 | 91.2972 | 110.2628 | 0 | 33526.2275
3 | 1 | 15 | 0 | 181.66 | 181.66 | 48 | 10.0224 | 0 | 0 | 434.8834 | 0 | 181.66 | 0 | 18.157 | 0 | 0 | 0 | 181.66 | 0 | 0
3 | 1 | 16 | 4.2919 | 6.13 | 10.4219 | 32.7629 | 11.4074 | 0 | 0 | 445.4921 | 0 | 10.4219 | 0 | 1.0417 | 0 | 0 | 0 | 10.4219 | 0 | 0
3 | 1 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 454.8826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 447.5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 422.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 422.7255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 412.8401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 400.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 397.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 396.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 405.338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 418.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 431.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 462.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 477.4188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 6 | 0 | 2.8458 | 2.8458 | 48 | 4.7319 | 1.1273 | 1.1273 | 475.2705 | 2.8458 | 0 | 1215.9406 | 0 | 0 | 0 | 2.8458 | 0 | 0 | 1215.9406
3 | 2 | 7 | 0 | 47.9633 | 47.9633 | 48 | 4.99 | 19.9764 | 19.9764 | 472.3257 | 47.9633 | 0 | 20352.0756 | 0 | 0 | 0 | 47.9633 | 0 | 0 | 20352.0756
3 | 2 | 8 | 0 | 73.9358 | 73.9358 | 48 | 5.4889 | 34.196 | 34.196 | 470.9349 | 73.9358 | 0 | 31270.045 | 0 | 0 | 0 | 73.9358 | 0 | 0 | 31270.045
3 | 2 | 9 | 0 | 75 | 75 | 48 | 6.9858 | 51.8856 | 51.8856 | 463.8029 | 75 | 0 | 31185.2178 | 0 | 0 | 0 | 75 | 0 | 0 | 31185.2178
3 | 2 | 10 | 0 | 75 | 75 | 48 | 7.3471 | 58.9387 | 58.9387 | 462.1058 | 75 | 0 | 31057.9371 | 0 | 0 | 0 | 75 | 0 | 0 | 31057.9371
3 | 2 | 11 | 0 | 75 | 75 | 48 | 8.9643 | 150.5358 | 150.5358 | 456.8979 | 75 | 0 | 30667.3407 | 0 | 0 | 0 | 75 | 0 | 0 | 30667.3407
3 | 2 | 12 | 0 | 75 | 75 | 48 | 8.2847 | 91.0651 | 91.0651 | 454.7622 | 75 | 0 | 30507.1625 | 0 | 0 | 0 | 75 | 0 | 0 | 30507.1625
3 | 2 | 13 | 0 | 75 | 75 | 48 | 7.8202 | 71.7025 | 71.7025 | 454.4327 | 75 | 0 | 30482.4505 | 0 | 0 | 0 | 75 | 0 | 0 | 30482.4505
3 | 2 | 14 | 12.8783 | 53.3831 | 66.2614 | 40.8088 | 7.6568 | 58.9388 | 58.9388 | 450.1523 | 66.2614 | 0 | 27123.6676 | 0 | 0 | 0 | 66.2614 | 0 | 0 | 27123.6676
3 | 2 | 15 | 95.8651 | 573.8267 | 669.6917 | 42.7035 | 7.7256 | 613.6683 | 288 | 454.1815 | 314.2923 | 355.3994 | 129324.3635 | 35.5223 | 0 | 0 | 314.2923 | 355.3994 | 0 | 129324.3635
3 | 2 | 16 | 34.7163 | 189.7687 | 224.485 | 42.278 | 7.3729 | 178.141 | 178.141 | 475.365 | 224.485 | 0 | 97221.5317 | 0 | 0 | 0 | 224.485 | 0 | 0 | 97221.5317
3 | 2 | 17 | 0.86648 | 0.070833 | 0.93731 | 13.7961 | 7.5449 | 0.79583 | 0.79583 | 485.2233 | 0.93731 | 0 | 441.8741 | 0 | 0 | 0 | 0.93731 | 0 | 0 | 441.8741
3 | 2 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 495.6194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 494.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 485.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 472.4636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 22 | 0.73333 | 0 | 0.73333 | 11 | 4.9212 | 0.30129 | 0.30129 | 461.6139 | 0.73333 | 0 | 330.4502 | 0 | 0 | 0 | 0.73333 | 0 | 0 | 330.4502
3 | 2 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 450.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 0 | 7.5913 | 0 | 7.5913 | 11 | 3.8459 | 2.5744 | 2.5744 | 449.9403 | 7.5913 | 0 | 3332.1494 | 0 | 0 | 0 | 7.5913 | 0 | 0 | 3332.1494
3 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 459.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 2 | 2.6758 | 0 | 2.6758 | 11 | 3.3383 | 0.83836 | 0.83836 | 465.1222 | 2.6758 | 0 | 1215.1553 | 0 | 0 | 0 | 2.6758 | 0 | 0 | 1215.1553
3 | 3 | 3 | 1.0425 | 0 | 1.0425 | 11 | 3.3039 | 0.32495 | 0.32495 | 466.0595 | 1.0425 | 0 | 474.3995 | 0 | 0 | 0 | 1.0425 | 0 | 0 | 474.3995
3 | 3 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 484.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 481.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 490.668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 7 | 0 | 43.9317 | 43.9317 | 48 | 6.5556 | 26.6024 | 26.6024 | 490.877 | 43.9317 | 0 | 19456.324 | 0 | 0 | 0 | 43.9317 | 0 | 0 | 19456.324
3 | 3 | 8 | 0.97917 | 68.6167 | 69.5958 | 47.4794 | 7.2524 | 52.8116 | 52.8116 | 492.1926 | 69.5958 | 0 | 30950.1865 | 0 | 0 | 0 | 69.5958 | 0 | 0 | 30950.1865
3 | 3 | 9 | 0 | 75 | 75 | 48 | 7.6998 | 67.9564 | 67.9564 | 484.2926 | 75 | 0 | 32721.9419 | 0 | 0 | 0 | 75 | 0 | 0 | 32721.9419
3 | 3 | 10 | 9.7759 | 96.2157 | 105.9916 | 44.5874 | 7.8632 | 103.3665 | 103.3665 | 484.5718 | 105.9916 | 0 | 46634.6533 | 0 | 0 | 0 | 105.9916 | 0 | 0 | 46634.6533
3 | 3 | 11 | 1.2458 | 75 | 76.2458 | 47.3954 | 7.6051 | 66.3612 | 66.3612 | 482.616 | 76.2458 | 0 | 33183.7567 | 0 | 0 | 0 | 76.2458 | 0 | 0 | 33183.7567
3 | 3 | 12 | 8.0108 | 94.3996 | 102.4104 | 45.1058 | 8.2589 | 122.509 | 122.509 | 481.6269 | 102.4104 | 0 | 44704.3219 | 0 | 0 | 0 | 102.4104 | 0 | 0 | 44704.3219
3 | 3 | 13 | 0 | 75 | 75 | 48 | 8.5686 | 109.0633 | 109.0633 | 490.8654 | 75 | 0 | 33214.9039 | 0 | 0 | 0 | 75 | 0 | 0 | 33214.9039
3 | 3 | 14 | 0 | 75 | 75 | 48 | 8.6374 | 114.5518 | 114.5518 | 482.6716 | 75 | 0 | 32600.3705 | 0 | 0 | 0 | 75 | 0 | 0 | 32600.3705
3 | 3 | 15 | 4.3933 | 75 | 79.3933 | 45.9526 | 7.803 | 75.3096 | 75.3096 | 482.9281 | 79.3933 | 0 | 34692.9488 | 0 | 0 | 0 | 79.3933 | 0 | 0 | 34692.9488
3 | 3 | 16 | 0.70083 | 54.5883 | 55.2892 | 47.531 | 7.6998 | 50.0967 | 50.0967 | 486.2663 | 55.2892 | 0 | 24257.3116 | 0 | 0 | 0 | 55.2892 | 0 | 0 | 24257.3116
3 | 3 | 17 | 0 | 0.81 | 0.81 | 48 | 7.6482 | 0.71786 | 0.71786 | 492.0864 | 0.81 | 0 | 359.71 | 0 | 0 | 0 | 0.81 | 0 | 0 | 359.71
3 | 3 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 504.1994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 488.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 473.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 466.4401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 461.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 23 | 0.98873 | 0 | 0.98873 | 11 | 4.4566 | 0.37221 | 0.37221 | 457.5063 | 0.98873 | 0 | 441.4745 | 0 | 0 | 0 | 0.98873 | 0 | 0 | 441.4745
3 | 4 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 456.2483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 455.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 463.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 463.9302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 486.1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 491.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 6 | 0 | 1.0558 | 1.0558 | 48 | 4.8007 | 0.42376 | 0.42376 | 492.3287 | 1.0558 | 0 | 469.1371 | 0 | 0 | 0 | 1.0558 | 0 | 0 | 469.1371
3 | 4 | 7 | 0 | 46.0967 | 46.0967 | 48 | 6.3664 | 26.4615 | 26.4615 | 503.3147 | 46.0967 | 0 | 20988.4907 | 0 | 0 | 0 | 46.0967 | 0 | 0 | 20988.4907
3 | 4 | 8 | 0 | 74.31 | 74.31 | 48 | 6.9944 | 51.5551 | 51.5551 | 505.4215 | 74.31 | 0 | 33991.0074 | 0 | 0 | 0 | 74.31 | 0 | 0 | 33991.0074
3 | 4 | 9 | 0 | 75.69 | 75.69 | 48 | 7.5707 | 64.9462 | 64.9462 | 502.6558 | 75.69 | 0 | 34412.8962 | 0 | 0 | 0 | 75.69 | 0 | 0 | 34412.8962
3 | 4 | 10 | 0 | 75 | 75 | 48 | 7.4159 | 60.5053 | 60.5053 | 496.0681 | 75 | 0 | 33605.1096 | 0 | 0 | 0 | 75 | 0 | 0 | 33605.1096
3 | 4 | 11 | 0 | 75 | 75 | 48 | 7.5879 | 64.8122 | 64.8122 | 489.5358 | 75 | 0 | 33115.1848 | 0 | 0 | 0 | 75 | 0 | 0 | 33115.1848
3 | 4 | 12 | 0 | 20.8886 | 20.8886 | 48 | 8.3192 | 25.8807 | 25.8807 | 487.6388 | 20.8886 | 0 | 9183.4393 | 0 | 0 | 0 | 20.8886 | 0 | 0 | 9183.4393
3 | 4 | 13 | 1.3143 | 19.45 | 20.7643 | 45.6581 | 8.6546 | 32.1185 | 32.1185 | 486.6655 | 20.7643 | 0 | 9157.1908 | 0 | 0 | 0 | 20.7643 | 0 | 0 | 9157.1908
3 | 4 | 14 | 0 | 45.7249 | 45.7249 | 48 | 8.9299 | 88.8389 | 88.8389 | 483.8563 | 45.7249 | 0 | 19929.4821 | 0 | 0 | 0 | 45.7249 | 0 | 0 | 19929.4821
3 | 4 | 15 | 0 | 23.4281 | 23.4281 | 48 | 8.8009 | 40.6405 | 40.6405 | 469.7935 | 23.4281 | 0 | 9881.8397 | 0 | 0 | 0 | 23.4281 | 0 | 0 | 9881.8397
3 | 4 | 16 | 0 | 30.6592 | 30.6592 | 48 | 9.5837 | 152.0155 | 152.0155 | 485.2714 | 30.6592 | 0 | 13406.3755 | 0 | 0 | 0 | 30.6592 | 0 | 0 | 13406.3755
3 | 4 | 17 | 0 | 0.53083 | 0.53083 | 48 | 9.0762 | 1.1937 | 1.1937 | 488.708 | 0.53083 | 0 | 233.9425 | 0 | 0 | 0 | 0.53083 | 0 | 0 | 233.9425
3 | 4 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 490.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 477.7829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 458.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 461.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 454.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 451.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 446.8096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 446.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 453.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 464.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 458.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 472.4579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 6 | 0 | 1.755 | 1.755 | 48 | 4.5255 | 0.66898 | 0.66898 | 479.1788 | 1.755 | 0 | 756.7188 | 0 | 0 | 0 | 1.755 | 0 | 0 | 756.7188
3 | 5 | 7 | 0 | 49.3767 | 49.3767 | 48 | 5.2137 | 21.5251 | 21.5251 | 480.5489 | 49.3767 | 0 | 21357.8238 | 0 | 0 | 0 | 49.3767 | 0 | 0 | 21357.8238
3 | 5 | 8 | 0.96333 | 75 | 75.9633 | 47.5308 | 5.1879 | 32.9378 | 32.9378 | 475.4165 | 75.9633 | 0 | 32503.6218 | 0 | 0 | 0 | 75.9633 | 0 | 0 | 32503.6218
3 | 5 | 9 | 1.6808 | 75 | 76.6808 | 47.189 | 6.7449 | 49.1289 | 49.1289 | 466.7224 | 76.6808 | 0 | 32170.1705 | 0 | 0 | 0 | 76.6808 | 0 | 0 | 32170.1705
3 | 5 | 10 | 0.37583 | 40.9333 | 41.3091 | 47.6634 | 8.8783 | 76.5826 | 76.5826 | 456.0433 | 41.3091 | 0 | 16869.8157 | 0 | 0 | 0 | 41.3091 | 0 | 0 | 16869.8157
3 | 5 | 11 | 0 | 78.9925 | 78.9925 | 48 | 9.8676 | 1201.0044 | 288 | 457.9601 | 18.9423 | 60.0502 | 7765.6047 | 6.002 | 0 | 0 | 18.9423 | 60.0502 | 0 | 7765.6047
3 | 5 | 12 | 0 | 75.7967 | 75.7967 | 48 | 10.2547 | 0 | 0 | 458.0959 | 0 | 75.7967 | 0 | 7.5759 | 0 | 0 | 0 | 75.7967 | 0 | 0
3 | 5 | 13 | 0 | 75.7208 | 75.7208 | 48 | 10.031 | 0 | 0 | 464.0183 | 0 | 75.7208 | 0 | 7.5683 | 0 | 0 | 0 | 75.7208 | 0 | 0
3 | 5 | 14 | 0 | 75 | 75 | 48 | 9.9364 | 2284.9433 | 288 | 462.119 | 9.4532 | 65.5468 | 3914.745 | 6.5514 | 0 | 0 | 9.4532 | 65.5468 | 0 | 3914.745
3 | 5 | 15 | 0 | 69.5317 | 69.5317 | 48 | 11.1494 | 0 | 0 | 463.7263 | 0 | 69.5317 | 0 | 6.9497 | 0 | 0 | 0 | 69.5317 | 0 | 0
3 | 5 | 16 | 0 | 42.5383 | 42.5383 | 48 | 12.5086 | 0 | 0 | 476.5273 | 0 | 42.5383 | 0 | 4.2517 | 0 | 0 | 0 | 42.5383 | 0 | 0
3 | 5 | 17 | 0 | 0.0575 | 0.0575 | 48 | 12.2591 | 0 | 0 | 483.8134 | 0 | 0.0575 | 0 | 0.0057471 | 0 | 0 | 0 | 0.0575 | 0 | 0
3 | 5 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 484.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 485.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 475.5197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 462.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 22 | 0.68083 | 0 | 0.68083 | 11 | 5.3857 | 0.30785 | 0.30785 | 447.266 | 0.68083 | 0 | 297.0245 | 0 | 0 | 0 | 0.68083 | 0 | 0 | 297.0245
3 | 5 | 23 | 0.43917 | 0 | 0.43917 | 11 | 3.6704 | 0.14481 | 0.14481 | 444.5446 | 0.43917 | 0 | 190.3983 | 0 | 0 | 0 | 0.43917 | 0 | 0 | 190.3983
3 | 6 | 0 | 0.41333 | 0 | 0.41333 | 11 | 3.5706 | 0.13417 | 0.13417 | 442.0659 | 0.41333 | 0 | 178.1739 | 0 | 0 | 0 | 0.41333 | 0 | 0 | 178.1739
3 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 445.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 443.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 446.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 444.5835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 5 | 0.56667 | 0 | 0.56667 | 11 | 3.9405 | 0.19517 | 0.19517 | 455.2077 | 0.56667 | 0 | 251.7177 | 0 | 0 | 0 | 0.56667 | 0 | 0 | 251.7177
3 | 6 | 6 | 0.805 | 1.66 | 2.465 | 35.9168 | 4.8093 | 0.99096 | 0.99096 | 457.7402 | 2.465 | 0 | 1039.7946 | 0 | 0 | 0 | 2.465 | 0 | 0 | 1039.7946
3 | 6 | 7 | 0 | 23.465 | 23.465 | 48 | 5.1706 | 10.1382 | 10.1382 | 449.3796 | 23.465 | 0 | 9418.373 | 0 | 0 | 0 | 23.465 | 0 | 0 | 9418.373
3 | 6 | 8 | 0 | 23.24 | 23.24 | 48 | 5.8502 | 11.6835 | 11.6835 | 435.4787 | 23.24 | 0 | 9005.0039 | 0 | 0 | 0 | 23.24 | 0 | 0 | 9005.0039
3 | 6 | 9 | 0 | 67.2782 | 67.2782 | 48 | 6.7707 | 43.4487 | 43.4487 | 435.639 | 67.2782 | 0 | 26079.6523 | 0 | 0 | 0 | 67.2782 | 0 | 0 | 26079.6523
3 | 6 | 10 | 0 | 68.75 | 68.75 | 48 | 8.9987 | 142.71 | 142.71 | 428.4491 | 68.75 | 0 | 26155.8742 | 0 | 0 | 0 | 68.75 | 0 | 0 | 26155.8742
3 | 6 | 11 | 0 | 10.3201 | 10.3201 | 48 | 10.0569 | 0 | 0 | 425.9213 | 0 | 10.3201 | 0 | 1.0315 | 0 | 0 | 0 | 10.3201 | 0 | 0
3 | 6 | 12 | 0 | 68.3983 | 68.3983 | 48 | 10.1343 | 0 | 0 | 420.8391 | 0 | 68.3983 | 0 | 6.8364 | 0 | 0 | 0 | 68.3983 | 0 | 0
3 | 6 | 13 | 0 | 49.7867 | 49.7867 | 48 | 10.2117 | 0 | 0 | 421.9638 | 0 | 49.7867 | 0 | 4.9762 | 0 | 0 | 0 | 49.7867 | 0 | 0
3 | 6 | 14 | 0 | 26.1592 | 26.1592 | 48 | 9.8762 | 424.2935 | 288 | 422.558 | 17.7562 | 8.403 | 6650.7271 | 0.83988 | 0 | 0 | 17.7562 | 8.403 | 0 | 6650.7271
3 | 6 | 15 | 0 | 43.0292 | 43.0292 | 48 | 10.9601 | 0 | 0 | 418.7969 | 0 | 43.0292 | 0 | 4.3008 | 0 | 0 | 0 | 43.0292 | 0 | 0
3 | 6 | 16 | 0 | 30.52 | 30.52 | 48 | 11.5279 | 0 | 0 | 424.2159 | 0 | 30.52 | 0 | 3.0505 | 0 | 0 | 0 | 30.52 | 0 | 0
3 | 6 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 438.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 440.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 431.9006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 423.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 418.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 414.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 23 | 2.7075 | 0 | 2.7075 | 11 | 4.6373 | 1.0536 | 1.0536 | 410.1163 | 2.7075 | 0 | 1080.6073 | 0 | 0 | 0 | 2.7075 | 0 | 0 | 1080.6073
3 | 7 | 0 | 301.8301 | 0 | 301.8301 | 11 | 3.9577 | 104.2511 | 104.2511 | 417.62 | 301.8301 | 0 | 122730.1325 | 0 | 0 | 0 | 301.8301 | 0 | 0 | 122730.1325
3 | 7 | 1 | 59.4497 | 0 | 59.4497 | 11 | 3.6394 | 19.507 | 19.507 | 420.8604 | 59.4497 | 0 | 24366.0681 | 0 | 0 | 0 | 59.4497 | 0 | 0 | 24366.0681
3 | 7 | 2 | 1.8511 | 0 | 1.8511 | 11 | 3.5276 | 0.59691 | 0.59691 | 429.4476 | 1.8511 | 0 | 774.594 | 0 | 0 | 0 | 1.8511 | 0 | 0 | 774.594
3 | 7 | 3 | 3.6308 | 0 | 3.6308 | 11 | 3.562 | 1.1771 | 1.1771 | 436.0419 | 3.6308 | 0 | 1543.2563 | 0 | 0 | 0 | 3.6308 | 0 | 0 | 1543.2563
3 | 7 | 4 | 144.9905 | 0 | 144.9905 | 11 | 3.5878 | 47.1925 | 47.1925 | 444.2795 | 144.9905 | 0 | 62821.4149 | 0 | 0 | 0 | 144.9905 | 0 | 0 | 62821.4149
3 | 7 | 5 | 8.2249 | 0 | 8.2249 | 11 | 4.1814 | 2.95 | 2.95 | 430.1782 | 8.2249 | 0 | 3447.7047 | 0 | 0 | 0 | 8.2249 | 0 | 0 | 3447.7047
3 | 7 | 6 | 193.4237 | 27.9858 | 221.4095 | 15.6767 | 5.3513 | 99.3753 | 99.3753 | 430.8104 | 221.4095 | 0 | 91914.5416 | 0 | 0 | 0 | 221.4095 | 0 | 0 | 91914.5416
3 | 7 | 7 | 22.7187 | 103.5632 | 126.2819 | 41.3435 | 5.6008 | 59.8897 | 59.8897 | 432.1403 | 126.2819 | 0 | 49350.5629 | 0 | 0 | 0 | 126.2819 | 0 | 0 | 49350.5629
3 | 7 | 8 | 20.8342 | 145.4861 | 166.3202 | 43.3652 | 6.5729 | 101.2185 | 101.2185 | 420.7118 | 166.3202 | 0 | 62760.3817 | 0 | 0 | 0 | 166.3202 | 0 | 0 | 62760.3817
3 | 7 | 9 | 22.6501 | 81.0989 | 103.7489 | 39.9223 | 7.7084 | 94.3575 | 94.3575 | 418.2523 | 103.7489 | 0 | 39251.3313 | 0 | 0 | 0 | 103.7489 | 0 | 0 | 39251.3313
3 | 7 | 10 | 5.8099 | 75 | 80.8099 | 45.3399 | 8.9471 | 159.5591 | 159.5591 | 416.8896 | 80.8099 | 0 | 30024.8958 | 0 | 0 | 0 | 80.8099 | 0 | 0 | 30024.8958
3 | 7 | 11 | 11.5905 | 75.6088 | 87.1993 | 43.082 | 9.5923 | 441.3684 | 288 | 414.2617 | 56.899 | 30.3004 | 21119.7429 | 3.0285 | 0 | 0 | 56.899 | 30.3004 | 0 | 21119.7429
3 | 7 | 12 | 6.0725 | 114.5627 | 120.6352 | 46.1375 | 10.2891 | 0 | 0 | 411.0421 | 0 | 120.6352 | 0 | 12.0575 | 0 | 0 | 0 | 120.6352 | 0 | 0
3 | 7 | 13 | 3.4717 | 90.3606 | 93.8323 | 46.6311 | 10.0827 | 0 | 0 | 419.4606 | 0 | 93.8323 | 0 | 9.3786 | 0 | 0 | 0 | 93.8323 | 0 | 0
3 | 7 | 14 | 14.6892 | 121.2491 | 135.9382 | 44.0019 | 10.6934 | 0 | 0 | 429.5845 | 0 | 135.9382 | 0 | 13.5871 | 0 | 0 | 0 | 135.9382 | 0 | 0
3 | 7 | 15 | 14.3555 | 75 | 89.3555 | 42.0557 | 11.6655 | 0 | 0 | 416.4151 | 0 | 89.3555 | 0 | 8.9311 | 0 | 0 | 0 | 89.3555 | 0 | 0
3 | 7 | 16 | 7.8601 | 95.9293 | 103.7894 | 45.1979 | 12.3021 | 0 | 0 | 436.4472 | 0 | 103.7894 | 0 | 10.3738 | 0 | 0 | 0 | 103.7894 | 0 | 0
3 | 7 | 17 | 0 | 0.19833 | 0.19833 | 48 | 12.1989 | 0 | 0 | 440.2802 | 0 | 0.19833 | 0 | 0.019823 | 0 | 0 | 0 | 0.19833 | 0 | 0
3 | 7 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 425.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 403.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 392.1526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 381.602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 374.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 23 | 2.0565 | 0 | 2.0565 | 11 | 4.5734 | 0.79082 | 0.79082 | 367.4877 | 2.0565 | 0 | 733.1112 | 0 | 0 | 0 | 2.0565 | 0 | 0 | 733.1112
3 | 8 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 367.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 371.8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 376.3812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 380.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 411.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 5 | 0.15833 | 0 | 0.15833 | 11 | 4.0351 | 0.055397 | 0.055397 | 411.8999 | 0.15833 | 0 | 63.4758 | 0 | 0 | 0 | 0.15833 | 0 | 0 | 63.4758
3 | 8 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 422.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 7 | 0 | 21.1608 | 21.1608 | 48 | 5.3599 | 9.5152 | 9.5152 | 422.4605 | 21.1608 | 0 | 7923.8959 | 0 | 0 | 0 | 21.1608 | 0 | 0 | 7923.8959
3 | 8 | 8 | 0 | 40.4797 | 40.4797 | 48 | 6.5729 | 24.635 | 24.635 | 412.8067 | 40.4797 | 0 | 14767.2795 | 0 | 0 | 0 | 40.4797 | 0 | 0 | 14767.2795
3 | 8 | 9 | 0 | 36.4564 | 36.4564 | 48 | 7.6912 | 32.9098 | 32.9098 | 420.916 | 36.4564 | 0 | 13595.1892 | 0 | 0 | 0 | 36.4564 | 0 | 0 | 13595.1892
3 | 8 | 10 | 0.26917 | 17.1717 | 17.4408 | 47.429 | 8.4482 | 23.4 | 23.4 | 414.6288 | 17.4408 | 0 | 6404.2716 | 0 | 0 | 0 | 17.4408 | 0 | 0 | 6404.2716
3 | 8 | 11 | 0.21333 | 27.775 | 27.9883 | 47.718 | 9.7214 | 206.1186 | 206.1186 | 414.8809 | 27.9883 | 0 | 10276.279 | 0 | 0 | 0 | 27.9883 | 0 | 0 | 10276.279
3 | 8 | 12 | 0 | 36.3058 | 36.3058 | 48 | 9.4117 | 127.8124 | 127.8124 | 413.518 | 36.3058 | 0 | 13270.4339 | 0 | 0 | 0 | 36.3058 | 0 | 0 | 13270.4339
3 | 8 | 13 | 0 | 18.1775 | 18.1775 | 48 | 8.8869 | 33.9584 | 33.9584 | 414.8343 | 18.1775 | 0 | 6668.1305 | 0 | 0 | 0 | 18.1775 | 0 | 0 | 6668.1305
3 | 8 | 14 | 0 | 14.94 | 14.94 | 48 | 9.3428 | 47.1287 | 47.1287 | 419.6935 | 14.94 | 0 | 5553.1012 | 0 | 0 | 0 | 14.94 | 0 | 0 | 5553.1012
3 | 8 | 15 | 0 | 28.2742 | 28.2742 | 48 | 10.0224 | 0 | 0 | 408.9574 | 0 | 28.2742 | 0 | 2.826 | 0 | 0 | 0 | 28.2742 | 0 | 0
3 | 8 | 16 | 0 | 20.2158 | 20.2158 | 48 | 11.4074 | 0 | 0 | 423.3742 | 0 | 20.2158 | 0 | 2.0206 | 0 | 0 | 0 | 20.2158 | 0 | 0
3 | 8 | 17 | 0 | 0.1875 | 0.1875 | 48 | 10.8053 | 0 | 0 | 428.281 | 0 | 0.1875 | 0 | 0.018741 | 0 | 0 | 0 | 0.1875 | 0 | 0
3 | 8 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 429.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 407.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 397.9335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 386.8992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 369.8761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 364.7402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 364.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 366.9112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 372.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 3 | 0.50667 | 0 | 0.50667 | 11 | 3.7857 | 0.17016 | 0.17016 | 395.3617 | 0.50667 | 0 | 194.7432 | 0 | 0 | 0 | 0.50667 | 0 | 0 | 194.7432
3 | 9 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 417.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 418.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 423.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 7 | 11.1067 | 73.7019 | 84.8086 | 43.1544 | 4.99 | 35.3223 | 35.3223 | 412.373 | 84.8086 | 0 | 31312.905 | 0 | 0 | 0 | 84.8086 | 0 | 0 | 31312.905
3 | 9 | 8 | 28.5533 | 579.093 | 607.6463 | 46.2614 | 5.4889 | 281.0422 | 281.0422 | 412.5983 | 607.6463 | 0 | 222603.2878 | 0 | 0 | 0 | 607.6463 | 0 | 0 | 222603.2878
3 | 9 | 9 | 0.82583 | 481.3546 | 482.1804 | 47.9366 | 6.9858 | 333.5761 | 288 | 422.6069 | 416.3007 | 65.8797 | 155975.5235 | 6.5847 | 0 | 0 | 416.3007 | 65.8797 | 0 | 155975.5235
3 | 9 | 10 | 9.1817 | 77.1131 | 86.2947 | 44.0632 | 7.3471 | 67.8146 | 67.8146 | 427.1216 | 86.2947 | 0 | 33055.9193 | 0 | 0 | 0 | 86.2947 | 0 | 0 | 33055.9193
3 | 9 | 11 | 1.5091 | 75 | 76.5091 | 47.2702 | 8.9643 | 153.5648 | 153.5648 | 436.6704 | 76.5091 | 0 | 29792.6661 | 0 | 0 | 0 | 76.5091 | 0 | 0 | 29792.6661
3 | 9 | 12 | 0 | 75 | 75 | 48 | 8.2847 | 91.0651 | 91.0651 | 434.6647 | 75 | 0 | 28999.8522 | 0 | 0 | 0 | 75 | 0 | 0 | 28999.8522
3 | 9 | 13 | 5.2392 | 51.9137 | 57.1529 | 44.6082 | 7.8202 | 54.64 | 54.64 | 445.1847 | 57.1529 | 0 | 22894.0855 | 0 | 0 | 0 | 57.1529 | 0 | 0 | 22894.0855
3 | 9 | 14 | 0 | 41.24 | 41.24 | 48 | 7.6568 | 36.6825 | 36.6825 | 438.1609 | 41.24 | 0 | 16090.2454 | 0 | 0 | 0 | 41.24 | 0 | 0 | 16090.2454
3 | 9 | 15 | 17.6825 | 280.3182 | 298.0007 | 45.8045 | 7.7256 | 273.0713 | 273.0713 | 432.0276 | 298.0007 | 0 | 115094.7551 | 0 | 0 | 0 | 298.0007 | 0 | 0 | 115094.7551
3 | 9 | 16 | 9.5512 | 55.5908 | 65.1421 | 42.575 | 7.3729 | 51.6937 | 51.6937 | 445.351 | 65.1421 | 0 | 26237.6603 | 0 | 0 | 0 | 65.1421 | 0 | 0 | 26237.6603
3 | 9 | 17 | 0 | 0.074167 | 0.074167 | 48 | 7.5449 | 0.062971 | 0.062971 | 450.052 | 0.074167 | 0 | 29.8189 | 0 | 0 | 0 | 0.074167 | 0 | 0 | 29.8189
3 | 9 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 456.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 435.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 430.5175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 412.4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 400.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 393.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 390.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 389.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 398.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 3 | 0.64068 | 0 | 0.64068 | 11 | 3.3039 | 0.1997 | 0.1997 | 422.6469 | 0.64068 | 0 | 263.7328 | 0 | 0 | 0 | 0.64068 | 0 | 0 | 263.7328
3 | 10 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 436.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 441.2943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 6 | 0 | 3.7692 | 3.7692 | 48 | 4.9556 | 1.5591 | 1.5591 | 444.2123 | 3.7692 | 0 | 1493.3903 | 0 | 0 | 0 | 3.7692 | 0 | 0 | 1493.3903
3 | 10 | 7 | 0 | 54.97 | 54.97 | 48 | 6.5556 | 33.2866 | 33.2866 | 452.6389 | 54.97 | 0 | 22243.0021 | 0 | 0 | 0 | 54.97 | 0 | 0 | 22243.0021
3 | 10 | 8 | 0.053333 | 79.7256 | 79.7789 | 47.9753 | 7.2524 | 60.5389 | 60.5389 | 454.3742 | 79.7789 | 0 | 32422.0687 | 0 | 0 | 0 | 79.7789 | 0 | 0 | 32422.0687
3 | 10 | 9 | 0 | 82.4566 | 82.4566 | 48 | 7.6998 | 74.7127 | 74.7127 | 451.366 | 82.4566 | 0 | 33260.1856 | 0 | 0 | 0 | 82.4566 | 0 | 0 | 33260.1856
3 | 10 | 10 | 0 | 75 | 75 | 48 | 7.8632 | 73.1425 | 73.1425 | 455.1281 | 75 | 0 | 30534.6108 | 0 | 0 | 0 | 75 | 0 | 0 | 30534.6108
3 | 10 | 11 | 0 | 68.75 | 68.75 | 48 | 7.6051 | 59.8371 | 59.8371 | 457.1988 | 68.75 | 0 | 28132.416 | 0 | 0 | 0 | 68.75 | 0 | 0 | 28132.416
3 | 10 | 12 | 0 | 2.3833 | 2.3833 | 48 | 8.2589 | 2.851 | 2.851 | 454.0906 | 2.3833 | 0 | 967.8324 | 0 | 0 | 0 | 2.3833 | 0 | 0 | 967.8324
3 | 10 | 13 | 0 | 78.2658 | 78.2658 | 48 | 8.5686 | 113.8124 | 113.8124 | 454.8828 | 78.2658 | 0 | 31845.0202 | 0 | 0 | 0 | 78.2658 | 0 | 0 | 31845.0202
3 | 10 | 14 | 0 | 75 | 75 | 48 | 8.6374 | 114.5518 | 114.5518 | 451.6697 | 75 | 0 | 30275.2304 | 0 | 0 | 0 | 75 | 0 | 0 | 30275.2304
3 | 10 | 15 | 0 | 74.4592 | 74.4592 | 48 | 7.803 | 70.6292 | 70.6292 | 449.8306 | 74.4592 | 0 | 29919.9742 | 0 | 0 | 0 | 74.4592 | 0 | 0 | 29919.9742
3 | 10 | 16 | 3.5908 | 49.3833 | 52.9742 | 45.492 | 7.6998 | 47.9991 | 47.9991 | 455.2784 | 52.9742 | 0 | 21708.0929 | 0 | 0 | 0 | 52.9742 | 0 | 0 | 21708.0929
3 | 10 | 17 | 0 | 0.031667 | 0.031667 | 48 | 7.6482 | 0.028064 | 0.028064 | 457.3051 | 0.031667 | 0 | 12.9613 | 0 | 0 | 0 | 0.031667 | 0 | 0 | 12.9613
3 | 10 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 462.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 435.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 425.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 403.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 390.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 379.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 0 | 0.15917 | 0 | 0.15917 | 11 | 3.9749 | 0.055133 | 0.055133 | 377.2369 | 0.15917 | 0 | 58.2927 | 0 | 0 | 0 | 0.15917 | 0 | 0 | 58.2927
3 | 11 | 1 | 0.25333 | 0 | 0.25333 | 11 | 3.7598 | 0.084728 | 0.084728 | 375.7776 | 0.25333 | 0 | 92.4103 | 0 | 0 | 0 | 0.25333 | 0 | 0 | 92.4103
3 | 11 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 391.2162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 404.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 428.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 435.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 6 | 0 | 0.84667 | 0.84667 | 48 | 4.8007 | 0.33981 | 0.33981 | 434.3381 | 0.84667 | 0 | 327.0996 | 0 | 0 | 0 | 0.84667 | 0 | 0 | 327.0996
3 | 11 | 7 | 1.5183 | 97.2912 | 98.8095 | 47.4314 | 6.3664 | 56.7211 | 56.7211 | 439.6748 | 98.8095 | 0 | 38757.3819 | 0 | 0 | 0 | 98.8095 | 0 | 0 | 38757.3819
3 | 11 | 8 | 1.7358 | 237.7161 | 239.4519 | 47.7318 | 6.9944 | 166.128 | 166.128 | 449.7808 | 239.4519 | 0 | 96271.3955 | 0 | 0 | 0 | 239.4519 | 0 | 0 | 96271.3955
3 | 11 | 9 | 2.2046 | 277.6939 | 279.8984 | 47.7086 | 7.5707 | 240.1682 | 240.1682 | 452.5255 | 279.8984 | 0 | 113307.6343 | 0 | 0 | 0 | 279.8984 | 0 | 0 | 113307.6343
3 | 11 | 10 | 0.6125 | 97.5674 | 98.1799 | 47.7692 | 7.4159 | 79.2054 | 79.2054 | 450.7624 | 98.1799 | 0 | 39565.8176 | 0 | 0 | 0 | 98.1799 | 0 | 0 | 39565.8176
3 | 11 | 11 | 0 | 75 | 75 | 48 | 7.5879 | 64.8122 | 64.8122 | 446.7897 | 75 | 0 | 29909.2304 | 0 | 0 | 0 | 75 | 0 | 0 | 29909.2304
3 | 11 | 12 | 0 | 75 | 75 | 48 | 8.3192 | 92.9239 | 92.9239 | 440.6406 | 75 | 0 | 29448.0449 | 0 | 0 | 0 | 75 | 0 | 0 | 29448.0449
3 | 11 | 13 | 0 | 75 | 75 | 48 | 8.6546 | 116.0113 | 116.0113 | 435.1581 | 75 | 0 | 29036.8552 | 0 | 0 | 0 | 75 | 0 | 0 | 29036.8552
3 | 11 | 14 | 0 | 75.3668 | 75.3668 | 48 | 8.9299 | 146.4301 | 146.4301 | 428.8584 | 75.3668 | 0 | 28704.0771 | 0 | 0 | 0 | 75.3668 | 0 | 0 | 28704.0771
3 | 11 | 15 | 0 | 68.3183 | 68.3183 | 48 | 8.8009 | 118.5109 | 118.5109 | 417.0902 | 68.3183 | 0 | 25215.6252 | 0 | 0 | 0 | 68.3183 | 0 | 0 | 25215.6252
3 | 11 | 16 | 0 | 48.1525 | 48.1525 | 48 | 9.5837 | 238.7517 | 238.7517 | 432.8293 | 48.1525 | 0 | 18530.4942 | 0 | 0 | 0 | 48.1525 | 0 | 0 | 18530.4942
3 | 11 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 434.1528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 435.5849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 428.9436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 410.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 388.4642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 375.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 370.3592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 364.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 370.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 379.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 389.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 4 | 0.046667 | 0 | 0.046667 | 11 | 3.3469 | 0.01464 | 0.01464 | 384.6417 | 0.046667 | 0 | 17.4366 | 0 | 0 | 0 | 0.046667 | 0 | 0 | 17.4366
3 | 12 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 405.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 407.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 7 | 0 | 0.0175 | 0.0175 | 48 | 5.2137 | 0.0076289 | 0.0076289 | 420.6821 | 0.0175 | 0 | 6.5219 | 0 | 0 | 0 | 0.0175 | 0 | 0 | 6.5219
3 | 12 | 8 | 0 | 0.098333 | 0.098333 | 48 | 5.1879 | 0.042637 | 0.042637 | 428.0475 | 0.098333 | 0 | 37.3713 | 0 | 0 | 0 | 0.098333 | 0 | 0 | 37.3713
3 | 12 | 9 | 0 | 59.524 | 59.524 | 48 | 6.7449 | 38.1367 | 38.1367 | 435.5089 | 59.524 | 0 | 23066.086 | 0 | 0 | 0 | 59.524 | 0 | 0 | 23066.086
3 | 12 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 427.7219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 11 | 0.18913 | 0.0016667 | 0.19079 | 11.3232 | 9.8676 | 2.9008 | 2.9008 | 427.0909 | 0.19079 | 0 | 79.325 | 0 | 0 | 0 | 0.19079 | 0 | 0 | 79.325
3 | 12 | 12 | 0.11083 | 0.67413 | 0.78496 | 42.7757 | 10.2547 | 0 | 0 | 419.1505 | 0 | 0.78496 | 0 | 0.078457 | 0 | 0 | 0 | 0.78496 | 0 | 0
3 | 12 | 13 | 0 | 1.3516 | 1.3516 | 48 | 10.031 | 0 | 0 | 420.6882 | 0 | 1.3516 | 0 | 0.13509 | 0 | 0 | 0 | 1.3516 | 0 | 0
3 | 12 | 14 | 0.19583 | 0.015 | 0.21083 | 13.6324 | 9.9364 | 6.4232 | 6.4232 | 417.4209 | 0.21083 | 0 | 85.1321 | 0 | 0 | 0 | 0.21083 | 0 | 0 | 85.1321
3 | 12 | 15 | 11.87 | 127.2493 | 139.1193 | 44.8431 | 11.1494 | 0 | 0 | 413.7347 | 0 | 139.1193 | 0 | 13.905 | 0 | 0 | 0 | 139.1193 | 0 | 0
3 | 12 | 16 | 21.7681 | 218.5859 | 240.354 | 44.649 | 12.5086 | 0 | 0 | 429.1349 | 0 | 240.354 | 0 | 24.0234 | 0 | 0 | 0 | 240.354 | 0 | 0
3 | 12 | 17 | 16.0486 | 3.52 | 19.5686 | 17.6555 | 12.2591 | 0 | 0 | 423.3423 | 0 | 19.5686 | 0 | 1.9559 | 0 | 0 | 0 | 19.5686 | 0 | 0
3 | 12 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 416.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 407.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 391.8559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 377.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 366.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 362.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 357.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 352.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 350.6454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 348.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 4 | 0.37583 | 0 | 0.37583 | 11 | 3.691 | 0.12433 | 0.12433 | 346.0528 | 0.37583 | 0 | 125.924 | 0 | 0 | 0 | 0.37583 | 0 | 0 | 125.924
3 | 13 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 351.1233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 6 | 0 | 0.73 | 0.73 | 48 | 4.8093 | 0.29347 | 0.29347 | 355.925 | 0.73 | 0 | 224.7852 | 0 | 0 | 0 | 0.73 | 0 | 0 | 224.7852
3 | 13 | 7 | 0 | 48.32 | 48.32 | 48 | 5.1706 | 20.877 | 20.877 | 362.4179 | 48.32 | 0 | 15192.6738 | 0 | 0 | 0 | 48.32 | 0 | 0 | 15192.6738
3 | 13 | 8 | 9.9583 | 456.6209 | 466.5793 | 47.2103 | 5.8502 | 234.5635 | 234.5635 | 367.619 | 466.5793 | 0 | 149496.0674 | 0 | 0 | 0 | 466.5793 | 0 | 0 | 149496.0674
3 | 13 | 9 | 0.77333 | 158.3469 | 159.1202 | 47.8202 | 6.7707 | 102.7608 | 102.7608 | 386.6153 | 159.1202 | 0 | 53909.1412 | 0 | 0 | 0 | 159.1202 | 0 | 0 | 53909.1412
3 | 13 | 10 | 6.0566 | 496.0305 | 502.0871 | 47.5537 | 8.9987 | 1042.2231 | 288 | 400.5589 | 138.7429 | 363.3442 | 48976.9858 | 36.3164 | 0 | 0 | 138.7429 | 363.3442 | 0 | 48976.9858
3 | 13 | 11 | 17.5808 | 767.6569 | 785.2378 | 47.1716 | 10.0569 | 0 | 0 | 402.1364 | 0 | 785.2378 | 0 | 78.4847 | 0 | 0 | 0 | 785.2378 | 0 | 0
3 | 13 | 12 | 69.595 | 919.2033 | 988.7983 | 45.3958 | 10.1343 | 0 | 0 | 406.9233 | 0 | 988.7983 | 0 | 98.8307 | 0 | 0 | 0 | 988.7983 | 0 | 0
3 | 13 | 13 | 79.0201 | 960.4628 | 1039.4829 | 45.1873 | 10.2117 | 0 | 0 | 410.482 | 0 | 1039.4829 | 0 | 103.8966 | 0 | 0 | 0 | 1039.4829 | 0 | 0
3 | 13 | 14 | 27.7975 | 710.2785 | 738.076 | 46.6065 | 9.8762 | 11971.3624 | 288 | 410.6399 | 17.7562 | 720.3198 | 6463.8496 | 71.9962 | 0 | 0 | 17.7562 | 720.3198 | 0 | 6463.8496
3 | 13 | 15 | 147.7817 | 588.1631 | 735.9447 | 40.5702 | 10.9601 | 0 | 0 | 403.7242 | 0 | 735.9447 | 0 | 73.5579 | 0 | 0 | 0 | 735.9447 | 0 | 0
3 | 13 | 16 | 3.5672 | 65.3798 | 68.947 | 46.0857 | 11.5279 | 0 | 0 | 404.6485 | 0 | 68.947 | 0 | 6.8913 | 0 | 0 | 0 | 68.947 | 0 | 0
3 | 13 | 17 | 0 | 0.175 | 0.175 | 48 | 11.5451 | 0 | 0 | 418.8647 | 0 | 0.175 | 0 | 0.017491 | 0 | 0 | 0 | 0.175 | 0 | 0
3 | 13 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 424.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 19 | 2.0805 | 0 | 2.0805 | 11 | 13.1107 | 0 | 0 | 404.4315 | 0 | 2.0805 | 0 | 0.20794 | 0 | 0 | 0 | 2.0805 | 0 | 0
3 | 13 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 392.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 379.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 364.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 360.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 362.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 365.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 377.0771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 400.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 4 | 80.4538 | 0 | 80.4538 | 11 | 3.5878 | 26.1867 | 26.1867 | 422.643 | 80.4538 | 0 | 33118.2519 | 0 | 0 | 0 | 80.4538 | 0 | 0 | 33118.2519
3 | 14 | 5 | 23.3802 | 0 | 23.3802 | 11 | 4.1814 | 8.3856 | 8.3856 | 429.8975 | 23.3802 | 0 | 9793.922 | 0 | 0 | 0 | 23.3802 | 0 | 0 | 9793.922
3 | 14 | 6 | 24.7064 | 0 | 24.7064 | 11 | 5.3513 | 11.089 | 11.089 | 440.301 | 24.7064 | 0 | 10606.4734 | 0 | 0 | 0 | 24.7064 | 0 | 0 | 10606.4734
3 | 14 | 7 | 60.9029 | 2.7358 | 63.6388 | 12.5906 | 5.6008 | 30.1809 | 30.1809 | 438.6724 | 63.6388 | 0 | 27115.3183 | 0 | 0 | 0 | 63.6388 | 0 | 0 | 27115.3183
3 | 14 | 8 | 17.8323 | 50.2097 | 68.0419 | 38.3031 | 6.5729 | 41.4087 | 41.4087 | 438.3261 | 68.0419 | 0 | 27218.3358 | 0 | 0 | 0 | 68.0419 | 0 | 0 | 27218.3358
3 | 14 | 9 | 34.9139 | 288.7444 | 323.6582 | 44.0087 | 7.7084 | 294.3606 | 288 | 434.8067 | 316.6646 | 6.9936 | 123751.8891 | 0.69902 | 0 | 0 | 316.6646 | 6.9936 | 0 | 123751.8891
3 | 14 | 10 | 30.122 | 75 | 105.122 | 37.3979 | 8.9471 | 207.5633 | 207.5633 | 437.5275 | 105.122 | 0 | 42062.4307 | 0 | 0 | 0 | 105.122 | 0 | 0 | 42062.4307
3 | 14 | 11 | 45.5745 | 75 | 120.5745 | 34.0148 | 9.5923 | 610.3005 | 288 | 445.8418 | 56.899 | 63.6756 | 23432.5309 | 6.3644 | 0 | 0 | 56.899 | 63.6756 | 0 | 23432.5309
3 | 14 | 12 | 4.5548 | 75 | 79.5548 | 45.8816 | 10.2891 | 0 | 0 | 443.4767 | 0 | 79.5548 | 0 | 7.9515 | 0 | 0 | 0 | 79.5548 | 0 | 0
3 | 14 | 13 | 2.8708 | 75 | 77.8708 | 46.6359 | 10.0827 | 0 | 0 | 445.2318 | 0 | 77.8708 | 0 | 7.7832 | 0 | 0 | 0 | 77.8708 | 0 | 0
3 | 14 | 14 | 0 | 75 | 75 | 48 | 10.6934 | 0 | 0 | 440.7118 | 0 | 75 | 0 | 7.4963 | 0 | 0 | 0 | 75 | 0 | 0
3 | 14 | 15 | 0 | 75 | 75 | 48 | 11.6655 | 0 | 0 | 429.7822 | 0 | 75 | 0 | 7.4963 | 0 | 0 | 0 | 75 | 0 | 0
3 | 14 | 16 | 12.0833 | 67.8619 | 79.9452 | 42.4076 | 12.3021 | 0 | 0 | 412.8599 | 0 | 79.9452 | 0 | 7.9905 | 0 | 0 | 0 | 79.9452 | 0 | 0
3 | 14 | 17 | 1.9466 | 38.8825 | 40.8291 | 46.2359 | 12.1989 | 0 | 0 | 431.1452 | 0 | 40.8291 | 0 | 4.0809 | 0 | 0 | 0 | 40.8291 | 0 | 0
3 | 14 | 18 | 0 | 0.06 | 0.06 | 48 | 12.9559 | 0 | 0 | 437.7247 | 0 | 0.06 | 0 | 0.005997 | 0 | 0 | 0 | 0.06 | 0 | 0
3 | 14 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 442.4001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 438.2199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 422.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 401.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 389.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 384.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 384.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 399.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 402.4558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 4 | 8.4476 | 0 | 8.4476 | 11 | 3.6222 | 2.7644 | 2.7644 | 424.9415 | 8.4476 | 0 | 3496.8149 | 0 | 0 | 0 | 8.4476 | 0 | 0 | 3496.8149
3 | 15 | 5 | 4.8867 | 0 | 4.8867 | 11 | 4.0351 | 1.7097 | 1.7097 | 425.653 | 4.8867 | 0 | 2026.2664 | 0 | 0 | 0 | 4.8867 | 0 | 0 | 2026.2664
3 | 15 | 6 | 45.1291 | 0 | 45.1291 | 11 | 5.1793 | 19.5331 | 19.5331 | 425.4708 | 45.1291 | 0 | 18704.6816 | 0 | 0 | 0 | 45.1291 | 0 | 0 | 18704.6816
3 | 15 | 7 | 0 | 9.4 | 9.4 | 48 | 5.3599 | 4.2268 | 4.2268 | 429.3319 | 9.4 | 0 | 3584.5195 | 0 | 0 | 0 | 9.4 | 0 | 0 | 3584.5195
3 | 15 | 8 | 5.4909 | 77.3189 | 82.8099 | 45.5466 | 6.5729 | 50.3961 | 50.3961 | 431.7837 | 82.8099 | 0 | 31984.2367 | 0 | 0 | 0 | 82.8099 | 0 | 0 | 31984.2367
3 | 15 | 9 | 10.7445 | 364.6608 | 375.4054 | 46.941 | 7.6912 | 338.8848 | 288 | 434.7015 | 319.0369 | 56.3685 | 123709.8934 | 5.634 | 0 | 0 | 319.0369 | 56.3685 | 0 | 123709.8934
3 | 15 | 10 | 13.695 | 399.7801 | 413.4751 | 46.7745 | 8.4482 | 554.7515 | 288 | 434.2129 | 214.6562 | 198.8189 | 83166.0481 | 19.872 | 0 | 0 | 214.6562 | 198.8189 | 0 | 83166.0481
3 | 15 | 11 | 0 | 285.0873 | 285.0873 | 48 | 9.7214 | 2099.5106 | 288 | 430.5479 | 39.1068 | 245.9805 | 14960.2228 | 24.5858 | 0 | 0 | 39.1068 | 245.9805 | 0 | 14960.2228
3 | 15 | 12 | 64.608 | 382.1845 | 446.7925 | 42.6496 | 9.4117 | 1572.9054 | 288 | 424.074 | 81.808 | 364.9845 | 31203.5631 | 36.4803 | 0 | 0 | 81.808 | 364.9845 | 0 | 31203.5631
3 | 15 | 13 | 16.8625 | 290.1634 | 307.0259 | 45.9679 | 8.8869 | 573.572 | 288 | 423.3456 | 154.1628 | 152.8631 | 58177.6064 | 15.2787 | 0 | 0 | 154.1628 | 152.8631 | 0 | 58177.6064
3 | 15 | 14 | 8.29 | 164.4355 | 172.7255 | 46.2242 | 9.3428 | 544.8684 | 288 | 421.6984 | 91.2972 | 81.4283 | 34279.724 | 8.1388 | 0 | 0 | 91.2972 | 81.4283 | 0 | 34279.724
3 | 15 | 15 | 14.7326 | 428.8539 | 443.5865 | 46.7711 | 10.0224 | 0 | 0 | 410.619 | 0 | 443.5865 | 0 | 44.3366 | 0 | 0 | 0 | 443.5865 | 0 | 0
3 | 15 | 16 | 131.0094 | 305.8387 | 436.8481 | 36.9038 | 11.4074 | 0 | 0 | 394.4651 | 0 | 436.8481 | 0 | 43.6631 | 0 | 0 | 0 | 436.8481 | 0 | 0
3 | 15 | 17 | 92.3746 | 190.5196 | 282.8942 | 35.9182 | 10.8053 | 0 | 0 | 406.6874 | 0 | 282.8942 | 0 | 28.2754 | 0 | 0 | 0 | 282.8942 | 0 | 0
3 | 15 | 18 | 4.9822 | 0.23333 | 5.2156 | 12.6553 | 11.5107 | 0 | 0 | 413.0961 | 0 | 5.2156 | 0 | 0.5213 | 0 | 0 | 0 | 5.2156 | 0 | 0
3 | 15 | 19 | 0.79888 | 0 | 0.79888 | 11 | 10.8913 | 0 | 0 | 413.3474 | 0 | 0.79888 | 0 | 0.079848 | 0 | 0 | 0 | 0.79888 | 0 | 0
3 | 15 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 399.0341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 380.5461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 368.8857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 363.2779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 0 | 0.165 | 0 | 0.165 | 11 | 4.5083 | 0.062699 | 0.062699 | 361.6263 | 0.165 | 0 | 57.8533 | 0 | 0 | 0 | 0.165 | 0 | 0 | 57.8533
3 | 16 | 1 | 1.6733 | 0 | 1.6733 | 11 | 4.2072 | 0.60283 | 0.60283 | 365.6861 | 1.6733 | 0 | 593.5081 | 0 | 0 | 0 | 1.6733 | 0 | 0 | 593.5081
3 | 16 | 2 | 18.2681 | 0 | 18.2681 | 11 | 4.147 | 6.5136 | 6.5136 | 374.7364 | 18.2681 | 0 | 6644.7836 | 0 | 0 | 0 | 18.2681 | 0 | 0 | 6644.7836
3 | 16 | 3 | 6.3566 | 0 | 6.3566 | 11 | 3.7857 | 2.1348 | 2.1348 | 382.4694 | 6.3566 | 0 | 2361.2915 | 0 | 0 | 0 | 6.3566 | 0 | 0 | 2361.2915
3 | 16 | 4 | 17.7368 | 0 | 17.7368 | 11 | 3.7254 | 5.8996 | 5.8996 | 403.6014 | 17.7368 | 0 | 6963.4772 | 0 | 0 | 0 | 17.7368 | 0 | 0 | 6963.4772
3 | 16 | 5 | 6.3965 | 0 | 6.3965 | 11 | 3.9663 | 2.2125 | 2.2125 | 417.5829 | 6.3965 | 0 | 2600.6945 | 0 | 0 | 0 | 6.3965 | 0 | 0 | 2600.6945
3 | 16 | 6 | 13.2921 | 0 | 13.2921 | 11 | 4.7319 | 5.2651 | 5.2651 | 424.127 | 13.2921 | 0 | 5491.3169 | 0 | 0 | 0 | 13.2921 | 0 | 0 | 5491.3169
3 | 16 | 7 | 0 | 2.1117 | 2.1117 | 48 | 4.99 | 0.8795 | 0.8795 | 422.7456 | 2.1117 | 0 | 791.3378 | 0 | 0 | 0 | 2.1117 | 0 | 0 | 791.3378
3 | 16 | 8 | 0 | 61.7608 | 61.7608 | 48 | 5.4889 | 28.565 | 28.565 | 418.2851 | 61.7608 | 0 | 22869.1181 | 0 | 0 | 0 | 61.7608 | 0 | 0 | 22869.1181
3 | 16 | 9 | 0.58 | 90.4977 | 91.0777 | 47.7644 | 6.9858 | 63.0082 | 63.0082 | 416.6322 | 91.0777 | 0 | 33595.6325 | 0 | 0 | 0 | 91.0777 | 0 | 0 | 33595.6325
3 | 16 | 10 | 0.795 | 139.508 | 140.303 | 47.7903 | 7.3471 | 110.2569 | 110.2569 | 419.4692 | 140.303 | 0 | 52147.648 | 0 | 0 | 0 | 140.303 | 0 | 0 | 52147.648
3 | 16 | 11 | 0.83167 | 129.73 | 130.5616 | 47.7643 | 8.9643 | 262.0559 | 262.0559 | 421.9175 | 130.5616 | 0 | 48850.0547 | 0 | 0 | 0 | 130.5616 | 0 | 0 | 48850.0547
3 | 16 | 12 | 0.28278 | 77.8811 | 78.1639 | 47.8661 | 8.2847 | 94.9067 | 94.9067 | 417.5753 | 78.1639 | 0 | 28897.8923 | 0 | 0 | 0 | 78.1639 | 0 | 0 | 28897.8923
3 | 16 | 13 | 1.5686 | 75 | 76.5686 | 47.242 | 7.8202 | 73.2021 | 73.2021 | 414.0789 | 76.5686 | 0 | 28088.1897 | 0 | 0 | 0 | 76.5686 | 0 | 0 | 28088.1897
3 | 16 | 14 | 0.77083 | 85.0061 | 85.777 | 47.6675 | 7.6568 | 76.2976 | 76.2976 | 411.9033 | 85.777 | 0 | 31243.041 | 0 | 0 | 0 | 85.777 | 0 | 0 | 31243.041
3 | 16 | 15 | 0.41083 | 75 | 75.4108 | 47.7984 | 7.7256 | 69.1023 | 69.1023 | 400.3061 | 75.4108 | 0 | 26582.9012 | 0 | 0 | 0 | 75.4108 | 0 | 0 | 26582.9012
3 | 16 | 16 | 1.3508 | 123.5228 | 124.8736 | 47.5997 | 7.3729 | 99.094 | 99.094 | 382.9747 | 124.8736 | 0 | 41879.4889 | 0 | 0 | 0 | 124.8736 | 0 | 0 | 41879.4889
3 | 16 | 17 | 0.56667 | 48.5117 | 49.0783 | 47.5728 | 7.5449 | 41.6701 | 41.6701 | 408.5121 | 49.0783 | 0 | 17714.2991 | 0 | 0 | 0 | 49.0783 | 0 | 0 | 17714.2991
3 | 16 | 18 | 0 | 0.27667 | 0.27667 | 48 | 7.0804 | 0.19759 | 0.19759 | 420.4427 | 0.27667 | 0 | 103.0425 | 0 | 0 | 0 | 0.27667 | 0 | 0 | 103.0425
3 | 16 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 410.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 384.1226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 370.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 22 | 0.11713 | 0 | 0.11713 | 11 | 4.9212 | 0.048126 | 0.048126 | 360.5624 | 0.11713 | 0 | 40.946 | 0 | 0 | 0 | 0.11713 | 0 | 0 | 40.946
3 | 16 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 356.9347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 358.8999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 365.1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 370.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 382.9518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 408.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 5 | 0.14667 | 0 | 0.14667 | 11 | 3.4071 | 0.046431 | 0.046431 | 418.6974 | 0.14667 | 0 | 59.7956 | 0 | 0 | 0 | 0.14667 | 0 | 0 | 59.7956
3 | 17 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 423.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 7 | 0 | 6.5442 | 6.5442 | 48 | 6.5556 | 3.9628 | 3.9628 | 428.8556 | 6.5442 | 0 | 2492.3828 | 0 | 0 | 0 | 6.5442 | 0 | 0 | 2492.3828
3 | 17 | 8 | 1.0967 | 67.52 | 68.6167 | 47.4086 | 7.2524 | 52.0686 | 52.0686 | 423.96 | 68.6167 | 0 | 25837.6957 | 0 | 0 | 0 | 68.6167 | 0 | 0 | 25837.6957
3 | 17 | 9 | 10.2767 | 301.5134 | 311.7901 | 46.7805 | 7.6998 | 282.5085 | 282.5085 | 417.6519 | 311.7901 | 0 | 115634.0319 | 0 | 0 | 0 | 311.7901 | 0 | 0 | 115634.0319
3 | 17 | 10 | 2.8525 | 266.8815 | 269.734 | 47.6087 | 7.8632 | 263.0536 | 263.0536 | 415.0811 | 269.734 | 0 | 99119.7964 | 0 | 0 | 0 | 269.734 | 0 | 0 | 99119.7964
3 | 17 | 11 | 6.5137 | 334.0452 | 340.5589 | 47.2923 | 7.6051 | 296.4082 | 288 | 417.1123 | 330.8983 | 9.6606 | 122372.7986 | 0.96558 | 0 | 0 | 330.8983 | 9.6606 | 0 | 122372.7986
3 | 17 | 12 | 5.7725 | 216.6153 | 222.3878 | 47.0396 | 8.2589 | 266.0325 | 266.0325 | 414.5071 | 222.3878 | 0 | 81720.2723 | 0 | 0 | 0 | 222.3878 | 0 | 0 | 81720.2723
3 | 17 | 13 | 3.3433 | 165.5967 | 168.9401 | 47.2678 | 8.5686 | 245.6688 | 245.6688 | 409.2969 | 168.9401 | 0 | 61161.2275 | 0 | 0 | 0 | 168.9401 | 0 | 0 | 61161.2275
3 | 17 | 14 | 1.6792 | 75 | 76.6792 | 47.1898 | 8.6374 | 117.1165 | 117.1165 | 407.7077 | 76.6792 | 0 | 27644.2183 | 0 | 0 | 0 | 76.6792 | 0 | 0 | 27644.2183
3 | 17 | 15 | 0.18 | 75 | 75.18 | 47.9114 | 7.803 | 71.313 | 71.313 | 402.865 | 75.18 | 0 | 26685.4081 | 0 | 0 | 0 | 75.18 | 0 | 0 | 26685.4081
3 | 17 | 16 | 1.1292 | 135.3245 | 136.4536 | 47.6938 | 7.6998 | 123.6387 | 123.6387 | 390.2761 | 136.4536 | 0 | 46746.5921 | 0 | 0 | 0 | 136.4536 | 0 | 0 | 46746.5921
3 | 17 | 17 | 0 | 52.64 | 52.64 | 48 | 7.6482 | 46.6518 | 46.6518 | 423.4812 | 52.64 | 0 | 19765.3289 | 0 | 0 | 0 | 52.64 | 0 | 0 | 19765.3289
3 | 17 | 18 | 0 | 0.3175 | 0.3175 | 48 | 7.3041 | 0.24553 | 0.24553 | 446.5522 | 0.3175 | 0 | 126.5403 | 0 | 0 | 0 | 0.3175 | 0 | 0 | 126.5403
3 | 17 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 424.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 415.5747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 393.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 375.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 372.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 377.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 1 | 0.0075 | 0 | 0.0075 | 11 | 3.7598 | 0.0025084 | 0.0025084 | 376.7487 | 0.0075 | 0 | 2.7431 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 2.7431
3 | 18 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 389.3835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 409.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 424.5729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 432.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 433.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 7 | 0 | 20.4283 | 20.4283 | 48 | 6.3664 | 11.7268 | 11.7268 | 430.1342 | 20.4283 | 0 | 7806.364 | 0 | 0 | 0 | 20.4283 | 0 | 0 | 7806.364
3 | 18 | 8 | 0.68083 | 60.1775 | 60.8583 | 47.5861 | 6.9944 | 42.2226 | 42.2226 | 423.7596 | 60.8583 | 0 | 22893.2965 | 0 | 0 | 0 | 60.8583 | 0 | 0 | 22893.2965
3 | 18 | 9 | 0.065 | 82.6316 | 82.6966 | 47.9709 | 7.5707 | 70.9582 | 70.9582 | 422.5915 | 82.6966 | 0 | 30979.8345 | 0 | 0 | 0 | 82.6966 | 0 | 0 | 30979.8345
3 | 18 | 10 | 0.088333 | 88.1354 | 88.2237 | 47.963 | 7.4159 | 71.1734 | 71.1734 | 426.2472 | 88.2237 | 0 | 33373.6475 | 0 | 0 | 0 | 88.2237 | 0 | 0 | 33373.6475
3 | 18 | 11 | 0 | 76.2638 | 76.2638 | 48 | 7.5879 | 65.9043 | 65.9043 | 427.3994 | 76.2638 | 0 | 28934.4284 | 0 | 0 | 0 | 76.2638 | 0 | 0 | 28934.4284
3 | 18 | 12 | 0 | 75 | 75 | 48 | 8.3192 | 92.9239 | 92.9239 | 419.9372 | 75 | 0 | 27895.2917 | 0 | 0 | 0 | 75 | 0 | 0 | 27895.2917
3 | 18 | 13 | 0 | 75 | 75 | 48 | 8.6546 | 116.0113 | 116.0113 | 420.3236 | 75 | 0 | 27924.272 | 0 | 0 | 0 | 75 | 0 | 0 | 27924.272
3 | 18 | 14 | 0 | 50 | 50 | 48 | 8.9299 | 97.145 | 97.145 | 413.4652 | 50 | 0 | 18273.2581 | 0 | 0 | 0 | 50 | 0 | 0 | 18273.2581
3 | 18 | 15 | 6.1867 | 85.4124 | 91.5991 | 45.501 | 8.8009 | 158.8957 | 158.8957 | 409.3374 | 91.5991 | 0 | 33327.0845 | 0 | 0 | 0 | 91.5991 | 0 | 0 | 33327.0845
3 | 18 | 16 | 8.4479 | 773.5322 | 781.9801 | 47.6003 | 9.5837 | 3877.2461 | 288 | 403.3867 | 58.0851 | 723.895 | 20665.8921 | 72.3535 | 0 | 0 | 58.0851 | 723.895 | 0 | 20665.8921
3 | 18 | 17 | 21.3834 | 230.2003 | 251.5837 | 44.8552 | 9.0762 | 565.7643 | 288 | 423.9564 | 128.0676 | 123.516 | 48550.596 | 12.3455 | 0 | 0 | 128.0676 | 123.516 | 0 | 48550.596
3 | 18 | 18 | 0.45417 | 15.5359 | 15.9901 | 46.9491 | 9.4461 | 59.7578 | 59.7578 | 427.461 | 15.9901 | 0 | 6084.4094 | 0 | 0 | 0 | 15.9901 | 0 | 0 | 6084.4094
3 | 18 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 415.0976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 415.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 392.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 381.4885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 23 | 8.4199 | 0 | 8.4199 | 11 | 4.8093 | 3.3849 | 3.3849 | 378.3418 | 8.4199 | 0 | 3092.9796 | 0 | 0 | 0 | 8.4199 | 0 | 0 | 3092.9796
3 | 19 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 383.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 389.6441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 391.8681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 401.1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 418.7216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 432.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 448.3974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 7 | 0 | 19.3875 | 19.3875 | 48 | 5.2137 | 8.4517 | 8.4517 | 459.258 | 19.3875 | 0 | 7973.2636 | 0 | 0 | 0 | 19.3875 | 0 | 0 | 7973.2636
3 | 19 | 8 | 0.18583 | 53.6983 | 53.8842 | 47.8724 | 5.1879 | 23.3642 | 23.3642 | 460.7998 | 53.8842 | 0 | 22250.2497 | 0 | 0 | 0 | 53.8842 | 0 | 0 | 22250.2497
3 | 19 | 9 | 0.14 | 76.329 | 76.469 | 47.9323 | 6.7449 | 48.9932 | 48.9932 | 460.5287 | 76.469 | 0 | 31550.8459 | 0 | 0 | 0 | 76.469 | 0 | 0 | 31550.8459
3 | 19 | 10 | 0.026667 | 75 | 75.0267 | 47.9868 | 8.8783 | 139.0913 | 139.0913 | 461.2758 | 75.0267 | 0 | 31007.6904 | 0 | 0 | 0 | 75.0267 | 0 | 0 | 31007.6904
3 | 19 | 11 | 0.10917 | 75 | 75.1092 | 47.9462 | 9.8676 | 1141.9621 | 288 | 451.4029 | 18.9423 | 56.1668 | 7642.4158 | 5.6139 | 0 | 0 | 18.9423 | 56.1668 | 0 | 7642.4158
3 | 19 | 12 | 0 | 75 | 75 | 48 | 10.2547 | 0 | 0 | 448.728 | 0 | 75 | 0 | 7.4963 | 0 | 0 | 0 | 75 | 0 | 0
3 | 19 | 13 | 3.0433 | 138.2218 | 141.2651 | 47.2029 | 10.031 | 0 | 0 | 450.5423 | 0 | 141.2651 | 0 | 14.1195 | 0 | 0 | 0 | 141.2651 | 0 | 0
3 | 19 | 14 | 1.25 | 208.8272 | 210.0772 | 47.7798 | 9.9364 | 6400.1938 | 288 | 451.476 | 9.4532 | 200.624 | 3816.2164 | 20.0524 | 0 | 0 | 9.4532 | 200.624 | 0 | 3816.2164
3 | 19 | 15 | 3.6092 | 475.4956 | 479.1047 | 47.7213 | 11.1494 | 0 | 0 | 451.4293 | 0 | 479.1047 | 0 | 47.8866 | 0 | 0 | 0 | 479.1047 | 0 | 0
3 | 19 | 16 | 117.8394 | 872.7426 | 990.582 | 43.5985 | 12.5086 | 0 | 0 | 423.8096 | 0 | 990.582 | 0 | 99.0089 | 0 | 0 | 0 | 990.582 | 0 | 0
3 | 19 | 17 | 3.7256 | 153.3447 | 157.0703 | 47.1224 | 12.2591 | 0 | 0 | 437.0931 | 0 | 157.0703 | 0 | 15.6992 | 0 | 0 | 0 | 157.0703 | 0 | 0
3 | 19 | 18 | 0 | 0.55 | 0.55 | 48 | 12.801 | 0 | 0 | 442.7746 | 0 | 0.55 | 0 | 0.054973 | 0 | 0 | 0 | 0.55 | 0 | 0
3 | 19 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 458.3512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 455.3852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 444.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 427.9004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 418.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 415.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 1 | 4.3255 | 0 | 4.3255 | 11 | 3.4588 | 1.3801 | 1.3801 | 412.2446 | 4.3255 | 0 | 1735.5852 | 0 | 0 | 0 | 4.3255 | 0 | 0 | 1735.5852
3 | 20 | 2 | 2.2575 | 0 | 2.2575 | 11 | 3.3555 | 0.70912 | 0.70912 | 421.1508 | 2.2575 | 0 | 925.9155 | 0 | 0 | 0 | 2.2575 | 0 | 0 | 925.9155
3 | 20 | 3 | 0.615 | 0 | 0.615 | 11 | 3.4416 | 0.19571 | 0.19571 | 422.2986 | 0.615 | 0 | 252.9486 | 0 | 0 | 0 | 0.615 | 0 | 0 | 252.9486
3 | 20 | 4 | 6.779 | 0 | 6.779 | 11 | 3.691 | 2.2426 | 2.2426 | 431.7962 | 6.779 | 0 | 2852.5899 | 0 | 0 | 0 | 6.779 | 0 | 0 | 2852.5899
3 | 20 | 5 | 6.7502 | 0 | 6.7502 | 11 | 3.9405 | 2.3249 | 2.3249 | 438.8321 | 6.7502 | 0 | 2887.9552 | 0 | 0 | 0 | 6.7502 | 0 | 0 | 2887.9552
3 | 20 | 6 | 18.736 | 0 | 18.736 | 11 | 4.8093 | 7.5321 | 7.5321 | 451.4223 | 18.736 | 0 | 8251.749 | 0 | 0 | 0 | 18.736 | 0 | 0 | 8251.749
3 | 20 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 453.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 8 | 9.595 | 93.1272 | 102.7222 | 44.5439 | 5.8502 | 51.6415 | 51.6415 | 452.154 | 102.7222 | 0 | 41870.5943 | 0 | 0 | 0 | 102.7222 | 0 | 0 | 41870.5943
3 | 20 | 9 | 0 | 3.6133 | 3.6133 | 48 | 6.7707 | 2.3335 | 2.3335 | 448.9418 | 3.6133 | 0 | 1448.7035 | 0 | 0 | 0 | 3.6133 | 0 | 0 | 1448.7035
3 | 20 | 10 | 0 | 7.8733 | 7.8733 | 48 | 8.9987 | 16.3433 | 16.3433 | 448.9135 | 7.8733 | 0 | 3156.5252 | 0 | 0 | 0 | 7.8733 | 0 | 0 | 3156.5252
3 | 20 | 11 | 0 | 2.0049 | 2.0049 | 48 | 10.0569 | 0 | 0 | 447.284 | 0 | 2.0049 | 0 | 0.20039 | 0 | 0 | 0 | 2.0049 | 0 | 0
3 | 20 | 12 | 0.65424 | 0.53896 | 1.1932 | 27.7127 | 10.1343 | 0 | 0 | 445.722 | 0 | 1.1932 | 0 | 0.11926 | 0 | 0 | 0 | 1.1932 | 0 | 0
3 | 20 | 13 | 3.9383 | 209.5821 | 213.5204 | 47.3175 | 10.2117 | 0 | 0 | 449.4196 | 0 | 213.5204 | 0 | 21.3414 | 0 | 0 | 0 | 213.5204 | 0 | 0
3 | 20 | 14 | 1.1617 | 65.1178 | 66.2795 | 47.3515 | 9.8762 | 1075.033 | 288 | 451.1738 | 17.7562 | 48.5233 | 7170.3493 | 4.8499 | 0 | 0 | 17.7562 | 48.5233 | 0 | 7170.3493
3 | 20 | 15 | 7.4225 | 164.7055 | 172.128 | 46.4045 | 10.9601 | 0 | 0 | 443.4209 | 0 | 172.128 | 0 | 17.2042 | 0 | 0 | 0 | 172.128 | 0 | 0
3 | 20 | 16 | 0.41 | 281.8315 | 282.2415 | 47.9463 | 11.5279 | 0 | 0 | 435.9588 | 0 | 282.2415 | 0 | 28.2101 | 0 | 0 | 0 | 282.2415 | 0 | 0
3 | 20 | 17 | 1.4083 | 0 | 1.4083 | 11 | 11.5451 | 0 | 0 | 463.2501 | 0 | 1.4083 | 0 | 0.14076 | 0 | 0 | 0 | 1.4083 | 0 | 0
3 | 20 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 474.9914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 19 | 11.154 | 0.1 | 11.254 | 11.3288 | 13.1107 | 0 | 0 | 474.673 | 0 | 11.254 | 0 | 1.1248 | 0 | 0 | 0 | 11.254 | 0 | 0
3 | 20 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 471.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 457.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 448.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 442.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 440.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 446.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 456.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 467.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 489.7447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 504.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 503.3935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 7 | 0.19833 | 0 | 0.19833 | 11 | 5.6008 | 0.09406 | 0.09406 | 508.3409 | 0.19833 | 0 | 98.6393 | 0 | 0 | 0 | 0.19833 | 0 | 0 | 98.6393
3 | 21 | 8 | 4.065 | 0.74076 | 4.8058 | 16.7032 | 6.5729 | 2.9247 | 2.9247 | 506.791 | 4.8058 | 0 | 2355.2461 | 0 | 0 | 0 | 4.8058 | 0 | 0 | 2355.2461
3 | 21 | 9 | 5.5149 | 124.2839 | 129.7988 | 46.4279 | 7.7084 | 118.0494 | 118.0494 | 495.9743 | 129.7988 | 0 | 58350.6065 | 0 | 0 | 0 | 129.7988 | 0 | 0 | 58350.6065
3 | 21 | 10 | 0.083333 | 13.9401 | 14.0235 | 47.7801 | 8.9471 | 27.6893 | 27.6893 | 486.9952 | 14.0235 | 0 | 6159.3195 | 0 | 0 | 0 | 14.0235 | 0 | 0 | 6159.3195
3 | 21 | 11 | 0.415 | 208.9133 | 209.3283 | 47.9266 | 9.5923 | 1059.5369 | 288 | 474.5861 | 56.899 | 152.4293 | 24276.4832 | 15.2354 | 0 | 0 | 56.899 | 152.4293 | 0 | 24276.4832
3 | 21 | 12 | 1.1408 | 269.797 | 270.9379 | 47.8442 | 10.2891 | 0 | 0 | 464.6326 | 0 | 270.9379 | 0 | 27.0803 | 0 | 0 | 0 | 270.9379 | 0 | 0
3 | 21 | 13 | 2.1806 | 1.2676 | 3.4482 | 24.6018 | 10.0827 | 0 | 0 | 459.2029 | 0 | 3.4482 | 0 | 0.34465 | 0 | 0 | 0 | 3.4482 | 0 | 0
3 | 21 | 14 | 16.2924 | 120.444 | 136.7364 | 43.5914 | 10.6934 | 0 | 0 | 460.1194 | 0 | 136.7364 | 0 | 13.6668 | 0 | 0 | 0 | 136.7364 | 0 | 0
3 | 21 | 15 | 16.1095 | 69.452 | 85.5615 | 41.0336 | 11.6655 | 0 | 0 | 457.656 | 0 | 85.5615 | 0 | 8.5519 | 0 | 0 | 0 | 85.5615 | 0 | 0
3 | 21 | 16 | 0.81315 | 0 | 0.81315 | 11 | 12.3021 | 0 | 0 | 453.2919 | 0 | 0.81315 | 0 | 0.081274 | 0 | 0 | 0 | 0.81315 | 0 | 0
3 | 21 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 483.4865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 18 | 1.5083 | 0 | 1.5083 | 11 | 12.9559 | 0 | 0 | 498.3787 | 0 | 1.5083 | 0 | 0.15076 | 0 | 0 | 0 | 1.5083 | 0 | 0
3 | 21 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 482.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 460.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 442.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 429.2459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 23 | 0.35833 | 0 | 0.35833 | 11 | 4.5734 | 0.1378 | 0.1378 | 425.4637 | 0.35833 | 0 | 148.5162 | 0 | 0 | 0 | 0.35833 | 0 | 0 | 148.5162
3 | 22 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 423.7935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 434.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 460.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 3 | 5.1399 | 0 | 5.1399 | 11 | 3.4416 | 1.6357 | 1.6357 | 469.5189 | 5.1399 | 0 | 2356.7367 | 0 | 0 | 0 | 5.1399 | 0 | 0 | 2356.7367
3 | 22 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 5 | 4.9183 | 0 | 4.9183 | 11 | 4.0351 | 1.7208 | 1.7208 | 492.8107 | 4.9183 | 0 | 2369.6747 | 0 | 0 | 0 | 4.9183 | 0 | 0 | 2369.6747
3 | 22 | 6 | 6.0482 | 0 | 6.0482 | 11 | 5.1793 | 2.6178 | 2.6178 | 499.8963 | 6.0482 | 0 | 2956.9634 | 0 | 0 | 0 | 6.0482 | 0 | 0 | 2956.9634
3 | 22 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 480.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 476.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 472.1543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 10 | 0 | 19.6291 | 19.6291 | 48 | 8.4482 | 26.3359 | 26.3359 | 465.1211 | 19.6291 | 0 | 8187.701 | 0 | 0 | 0 | 19.6291 | 0 | 0 | 8187.701
3 | 22 | 11 | 0 | 210.1689 | 210.1689 | 48 | 9.7214 | 1547.7781 | 288 | 457.162 | 39.1068 | 171.0621 | 16001.0172 | 17.0977 | 0 | 0 | 39.1068 | 171.0621 | 0 | 16001.0172
3 | 22 | 12 | 0 | 274.9409 | 274.9409 | 48 | 9.4117 | 967.9124 | 288 | 454.4822 | 81.808 | 193.1329 | 33253.4928 | 19.3037 | 0 | 0 | 81.808 | 193.1329 | 0 | 33253.4928
3 | 22 | 13 | 0 | 270.7052 | 270.7052 | 48 | 8.8869 | 505.7193 | 288 | 445.6136 | 154.1628 | 116.5424 | 61297.2295 | 11.6484 | 0 | 0 | 154.1628 | 116.5424 | 0 | 61297.2295
3 | 22 | 14 | 0 | 198.5273 | 198.5273 | 48 | 9.3428 | 626.2613 | 288 | 447.5739 | 91.2972 | 107.2302 | 36479.963 | 10.7177 | 0 | 0 | 91.2972 | 107.2302 | 0 | 36479.963
3 | 22 | 15 | 0 | 295.388 | 295.388 | 48 | 10.0224 | 0 | 0 | 445.6109 | 0 | 295.388 | 0 | 29.5241 | 0 | 0 | 0 | 295.388 | 0 | 0
3 | 22 | 16 | 0 | 82.3084 | 82.3084 | 48 | 11.4074 | 0 | 0 | 447.1238 | 0 | 82.3084 | 0 | 8.2267 | 0 | 0 | 0 | 82.3084 | 0 | 0
3 | 22 | 17 | 0 | 103.875 | 103.875 | 48 | 10.8053 | 0 | 0 | 470.7534 | 0 | 103.875 | 0 | 10.3823 | 0 | 0 | 0 | 103.875 | 0 | 0
3 | 22 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 476.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 454.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 20 | 0.61421 | 0 | 0.61421 | 11 | 8.4138 | 0.80625 | 0.80625 | 429.541 | 0.61421 | 0 | 257.0706 | 0 | 0 | 0 | 0.61421 | 0 | 0 | 257.0706
3 | 22 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 409.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 397.9671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 23 | 0.39083 | 0 | 0.39083 | 11 | 4.5599 | 0.14992 | 0.14992 | 393.6261 | 0.39083 | 0 | 149.543 | 0 | 0 | 0 | 0.39083 | 0 | 0 | 149.543
3 | 23 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 391.1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 390.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 2 | 1.4117 | 0 | 1.4117 | 11 | 4.147 | 0.50334 | 0.50334 | 414.7258 | 1.4117 | 0 | 569.9262 | 0 | 0 | 0 | 1.4117 | 0 | 0 | 569.9262
3 | 23 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 424.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 447.9594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 5 | 155.2502 | 0 | 155.2502 | 11 | 3.9663 | 53.6993 | 53.6993 | 449.3368 | 155.2502 | 0 | 68051.882 | 0 | 0 | 0 | 155.2502 | 0 | 0 | 68051.882
3 | 23 | 6 | 14.6029 | 0 | 14.6029 | 11 | 4.7319 | 5.7844 | 5.7844 | 459.9535 | 14.6029 | 0 | 6556.0273 | 0 | 0 | 0 | 14.6029 | 0 | 0 | 6556.0273
3 | 23 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 453.7555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 8 | 26.3075 | 44.7384 | 71.0459 | 34.2993 | 5.4889 | 32.8594 | 32.8594 | 454.7492 | 71.0459 | 0 | 29871.2453 | 0 | 0 | 0 | 71.0459 | 0 | 0 | 29871.2453
3 | 23 | 9 | 33.6505 | 9.8815 | 43.5319 | 19.3988 | 6.9858 | 30.1157 | 30.1157 | 455.6988 | 43.5319 | 0 | 18992.9893 | 0 | 0 | 0 | 43.5319 | 0 | 0 | 18992.9893
3 | 23 | 10 | 17.6945 | 118.0397 | 135.7343 | 43.1766 | 7.3471 | 106.6666 | 106.6666 | 467.4284 | 135.7343 | 0 | 57585.4989 | 0 | 0 | 0 | 135.7343 | 0 | 0 | 57585.4989
3 | 23 | 11 | 25.3875 | 70.435 | 95.8225 | 38.1971 | 8.9643 | 192.3295 | 192.3295 | 460.4099 | 95.8225 | 0 | 40457.4906 | 0 | 0 | 0 | 95.8225 | 0 | 0 | 40457.4906
3 | 23 | 12 | 22.5758 | 12.5656 | 35.1414 | 24.2302 | 8.2847 | 42.6688 | 42.6688 | 453.7243 | 35.1414 | 0 | 15093.0368 | 0 | 0 | 0 | 35.1414 | 0 | 0 | 15093.0368
3 | 23 | 13 | 1.0908 | 0 | 1.0908 | 11 | 7.8202 | 1.0429 | 1.0429 | 450.0743 | 1.0908 | 0 | 478.9569 | 0 | 0 | 0 | 1.0908 | 0 | 0 | 478.9569
3 | 23 | 14 | 9.9983 | 180.1243 | 190.1226 | 46.0542 | 7.6568 | 169.112 | 169.112 | 445.672 | 190.1226 | 0 | 75976.3909 | 0 | 0 | 0 | 190.1226 | 0 | 0 | 75976.3909
3 | 23 | 15 | 24.0508 | 300.8388 | 324.8897 | 45.261 | 7.7256 | 297.7108 | 288 | 453.229 | 314.2923 | 10.5974 | 128221.2235 | 1.0592 | 0 | 0 | 314.2923 | 10.5974 | 0 | 128221.2235
3 | 23 | 16 | 27.7469 | 82.4662 | 110.2131 | 38.685 | 7.3729 | 87.4601 | 87.4601 | 441.0827 | 110.2131 | 0 | 44349.5062 | 0 | 0 | 0 | 110.2131 | 0 | 0 | 44349.5062
3 | 23 | 17 | 4.4779 | 0 | 4.4779 | 11 | 7.5449 | 3.8019 | 3.8019 | 455.2451 | 4.4779 | 0 | 1989.2637 | 0 | 0 | 0 | 4.4779 | 0 | 0 | 1989.2637
3 | 23 | 18 | 2.1866 | 0 | 2.1866 | 11 | 7.0804 | 1.5617 | 1.5617 | 458.4327 | 2.1866 | 0 | 978.3706 | 0 | 0 | 0 | 2.1866 | 0 | 0 | 978.3706
3 | 23 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 447.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 427.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 21 | 14.7873 | 0 | 14.7873 | 11 | 6.5556 | 8.9543 | 8.9543 | 404.3412 | 14.7873 | 0 | 5816.4662 | 0 | 0 | 0 | 14.7873 | 0 | 0 | 5816.4662
3 | 23 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 386.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 383.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 0 | 1.2642 | 0 | 1.2642 | 11 | 3.8459 | 0.42871 | 0.42871 | 381.8488 | 1.2642 | 0 | 468.8147 | 0 | 0 | 0 | 1.2642 | 0 | 0 | 468.8147
3 | 24 | 1 | 2.8185 | 0 | 2.8185 | 11 | 3.4243 | 0.89459 | 0.89459 | 384.839 | 2.8185 | 0 | 1053.6593 | 0 | 0 | 0 | 2.8185 | 0 | 0 | 1053.6593
3 | 24 | 2 | 0.69667 | 0 | 0.69667 | 11 | 3.3383 | 0.21827 | 0.21827 | 395.016 | 0.69667 | 0 | 267.5311 | 0 | 0 | 0 | 0.69667 | 0 | 0 | 267.5311
3 | 24 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 407.8289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 4 | 1.8583 | 0 | 1.8583 | 11 | 3.2609 | 0.57554 | 0.57554 | 441.3651 | 1.8583 | 0 | 799.7529 | 0 | 0 | 0 | 1.8583 | 0 | 0 | 799.7529
3 | 24 | 5 | 0.245 | 0 | 0.245 | 11 | 3.4071 | 0.077561 | 0.077561 | 452.8153 | 0.245 | 0 | 108.2447 | 0 | 0 | 0 | 0.245 | 0 | 0 | 108.2447
3 | 24 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 463.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 460.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 8 | 7.9667 | 35.3621 | 43.3288 | 41.197 | 7.2524 | 32.8793 | 32.8793 | 442.8632 | 43.3288 | 0 | 17403.717 | 0 | 0 | 0 | 43.3288 | 0 | 0 | 17403.717
3 | 24 | 9 | 9.0783 | 121.2698 | 130.3481 | 45.4231 | 7.6998 | 118.1066 | 118.1066 | 449.3596 | 130.3481 | 0 | 52652.366 | 0 | 0 | 0 | 130.3481 | 0 | 0 | 52652.366
3 | 24 | 10 | 3.6167 | 62.609 | 66.2257 | 45.9794 | 7.8632 | 64.5855 | 64.5855 | 447.6003 | 66.2257 | 0 | 26597.613 | 0 | 0 | 0 | 66.2257 | 0 | 0 | 26597.613
3 | 24 | 11 | 5.3954 | 255.2435 | 260.6389 | 47.2341 | 7.6051 | 226.8492 | 226.8492 | 451.0427 | 260.6389 | 0 | 105248.2301 | 0 | 0 | 0 | 260.6389 | 0 | 0 | 105248.2301
3 | 24 | 12 | 12.0869 | 285.5625 | 297.6494 | 46.4975 | 8.2589 | 356.0646 | 288 | 449.6164 | 240.7514 | 56.898 | 97051.4114 | 5.687 | 0 | 0 | 240.7514 | 56.898 | 0 | 97051.4114
3 | 24 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 433.6501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 426.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 15 | 0.25917 | 0 | 0.25917 | 11 | 7.803 | 0.24584 | 0.24584 | 425.9435 | 0.25917 | 0 | 107.5395 | 0 | 0 | 0 | 0.25917 | 0 | 0 | 107.5395
3 | 24 | 16 | 0.675 | 67.6681 | 68.3431 | 47.6346 | 7.6998 | 61.9247 | 61.9247 | 422.337 | 68.3431 | 0 | 25608.3087 | 0 | 0 | 0 | 68.3431 | 0 | 0 | 25608.3087
3 | 24 | 17 | 0.19167 | 0 | 0.19167 | 11 | 7.6482 | 0.16986 | 0.16986 | 424.3078 | 0.19167 | 0 | 79.2173 | 0 | 0 | 0 | 0.19167 | 0 | 0 | 79.2173
3 | 24 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 435.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 422.7646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 405.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 388.9361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 376.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 23 | 0.071642 | 0 | 0.071642 | 11 | 4.4566 | 0.02697 | 0.02697 | 375.9292 | 0.071642 | 0 | 26.1444 | 0 | 0 | 0 | 0.071642 | 0 | 0 | 26.1444
3 | 25 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 378.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 380.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 2 | 5.4543 | 0 | 5.4543 | 11 | 3.691 | 1.8043 | 1.8043 | 387.1782 | 5.4543 | 0 | 2051.7716 | 0 | 0 | 0 | 5.4543 | 0 | 0 | 2051.7716
3 | 25 | 3 | 0.48083 | 0 | 0.48083 | 11 | 3.6824 | 0.15885 | 0.15885 | 398.9661 | 0.48083 | 0 | 186.547 | 0 | 0 | 0 | 0.48083 | 0 | 0 | 186.547
3 | 25 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 421.4708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 5 | 21.1489 | 0 | 21.1489 | 11 | 3.691 | 6.9962 | 6.9962 | 435.4144 | 21.1489 | 0 | 8975.888 | 0 | 0 | 0 | 21.1489 | 0 | 0 | 8975.888
3 | 25 | 6 | 0.27167 | 0 | 0.27167 | 11 | 4.8007 | 0.10903 | 0.10903 | 431.5065 | 0.27167 | 0 | 114.2376 | 0 | 0 | 0 | 0.27167 | 0 | 0 | 114.2376
3 | 25 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 440.7806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 8 | 13.6647 | 212.0597 | 225.7245 | 45.7601 | 6.9944 | 156.6041 | 156.6041 | 448.2727 | 225.7245 | 0 | 90856.9418 | 0 | 0 | 0 | 225.7245 | 0 | 0 | 90856.9418
3 | 25 | 9 | 3.4075 | 388.499 | 391.9065 | 47.6783 | 7.5707 | 336.2773 | 288 | 451.4895 | 335.6429 | 56.2636 | 135536.3648 | 5.6236 | 0 | 0 | 335.6429 | 56.2636 | 0 | 135536.3648
3 | 25 | 10 | 0.77083 | 214.769 | 215.5399 | 47.8677 | 7.4159 | 173.8841 | 173.8841 | 449.6804 | 215.5399 | 0 | 86606.6644 | 0 | 0 | 0 | 215.5399 | 0 | 0 | 86606.6644
3 | 25 | 11 | 0.52583 | 68.0542 | 68.5801 | 47.7163 | 7.5879 | 59.2643 | 59.2643 | 458.0229 | 68.5801 | 0 | 28138.859 | 0 | 0 | 0 | 68.5801 | 0 | 0 | 28138.859
3 | 25 | 12 | 0.40833 | 53.3882 | 53.7965 | 47.7192 | 8.3192 | 66.6531 | 66.6531 | 450.8864 | 53.7965 | 0 | 21688.9873 | 0 | 0 | 0 | 53.7965 | 0 | 0 | 21688.9873
3 | 25 | 13 | 4.8342 | 36.25 | 41.0842 | 43.6464 | 8.6546 | 63.5498 | 63.5498 | 446.0428 | 41.0842 | 0 | 16532.1384 | 0 | 0 | 0 | 41.0842 | 0 | 0 | 16532.1384
3 | 25 | 14 | 0.6675 | 496.9401 | 497.6076 | 47.9504 | 8.9299 | 966.8015 | 288 | 445.5288 | 148.2321 | 349.3756 | 58933.8867 | 34.9202 | 0 | 0 | 148.2321 | 349.3756 | 0 | 58933.8867
3 | 25 | 15 | 0.35667 | 156.3837 | 156.7404 | 47.9158 | 8.8009 | 271.8954 | 271.8954 | 441.5582 | 156.7404 | 0 | 61699.6676 | 0 | 0 | 0 | 156.7404 | 0 | 0 | 61699.6676
3 | 25 | 16 | 22.8767 | 248.2413 | 271.1179 | 44.878 | 9.5837 | 1344.2682 | 288 | 434.0888 | 58.0851 | 213.0328 | 22607.3545 | 21.2927 | 0 | 0 | 58.0851 | 213.0328 | 0 | 22607.3545
3 | 25 | 17 | 20.385 | 269.0722 | 289.4572 | 45.3943 | 9.0762 | 650.9347 | 288 | 454.6355 | 128.0676 | 161.3896 | 52410.5514 | 16.1309 | 0 | 0 | 128.0676 | 161.3896 | 0 | 52410.5514
3 | 25 | 18 | 2.4158 | 0 | 2.4158 | 11 | 9.4461 | 9.0284 | 9.0284 | 455.0426 | 2.4158 | 0 | 1072.733 | 0 | 0 | 0 | 2.4158 | 0 | 0 | 1072.733
3 | 25 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 445.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 433.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 411.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 404.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 397.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 392.6678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 402.9459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 411.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 3 | 1.3337 | 0 | 1.3337 | 11 | 3.3297 | 0.41732 | 0.41732 | 422.1325 | 1.3337 | 0 | 548.3338 | 0 | 0 | 0 | 1.3337 | 0 | 0 | 548.3338
3 | 26 | 4 | 92.2558 | 0 | 92.2558 | 11 | 3.3469 | 28.9417 | 28.9417 | 444.3159 | 92.2558 | 0 | 39975.8832 | 0 | 0 | 0 | 92.2558 | 0 | 0 | 39975.8832
3 | 26 | 5 | 26.9128 | 0 | 26.9128 | 11 | 3.7857 | 9.0385 | 9.0385 | 449.6076 | 26.9128 | 0 | 11804.1698 | 0 | 0 | 0 | 26.9128 | 0 | 0 | 11804.1698
3 | 26 | 6 | 7.7471 | 0 | 7.7471 | 11 | 4.5255 | 2.9531 | 2.9531 | 456.7123 | 7.7471 | 0 | 3452.9996 | 0 | 0 | 0 | 7.7471 | 0 | 0 | 3452.9996
3 | 26 | 7 | 0.35167 | 0 | 0.35167 | 11 | 5.2137 | 0.1533 | 0.1533 | 454.0322 | 0.35167 | 0 | 155.7997 | 0 | 0 | 0 | 0.35167 | 0 | 0 | 155.7997
3 | 26 | 8 | 10.462 | 98.8331 | 109.2951 | 44.4583 | 5.1879 | 47.3905 | 47.3905 | 453.6319 | 109.2951 | 0 | 44720.6693 | 0 | 0 | 0 | 109.2951 | 0 | 0 | 44720.6693
3 | 26 | 9 | 14.6869 | 142.8516 | 157.5385 | 44.5506 | 6.7449 | 100.9339 | 100.9339 | 444.8852 | 157.5385 | 0 | 63068.1054 | 0 | 0 | 0 | 157.5385 | 0 | 0 | 63068.1054
3 | 26 | 10 | 0.20833 | 310.9086 | 311.1169 | 47.9752 | 8.8783 | 576.7768 | 288 | 432.63 | 155.349 | 155.768 | 59755.7236 | 15.569 | 0 | 0 | 155.349 | 155.768 | 0 | 59755.7236
3 | 26 | 11 | 1.1566 | 311.6217 | 312.7783 | 47.8632 | 9.8676 | 4755.4912 | 288 | 422.0252 | 18.9423 | 293.836 | 7087.5058 | 29.369 | 0 | 0 | 18.9423 | 293.836 | 0 | 7087.5058
3 | 26 | 12 | 24.7929 | 329.5732 | 354.3661 | 45.4113 | 10.2547 | 0 | 0 | 405.1047 | 0 | 354.3661 | 0 | 35.419 | 0 | 0 | 0 | 354.3661 | 0 | 0
3 | 26 | 13 | 16.8725 | 286.8471 | 303.7196 | 45.9445 | 10.031 | 0 | 0 | 409.1034 | 0 | 303.7196 | 0 | 30.3569 | 0 | 0 | 0 | 303.7196 | 0 | 0
3 | 26 | 14 | 1.5192 | 262.2751 | 263.7943 | 47.7869 | 9.9364 | 8036.7334 | 288 | 403.7878 | 9.4532 | 254.3411 | 3365.3437 | 25.4215 | 0 | 0 | 9.4532 | 254.3411 | 0 | 3365.3437
3 | 26 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 405.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 16 | 32.0681 | 14.5896 | 46.6577 | 22.5697 | 12.5086 | 0 | 0 | 404.7691 | 0 | 46.6577 | 0 | 4.6635 | 0 | 0 | 0 | 46.6577 | 0 | 0
3 | 26 | 17 | 49.432 | 227.9573 | 277.3893 | 41.4064 | 12.2591 | 0 | 0 | 429.118 | 0 | 277.3893 | 0 | 27.7251 | 0 | 0 | 0 | 277.3893 | 0 | 0
3 | 26 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 412.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 407.6069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 396.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 379.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 367.3772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 23 | 1.2583 | 0 | 1.2583 | 11 | 3.6704 | 0.41492 | 0.41492 | 366.4779 | 1.2583 | 0 | 447.3097 | 0 | 0 | 0 | 1.2583 | 0 | 0 | 447.3097
3 | 27 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 368.8159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 373.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 2 | 0.705 | 0 | 0.705 | 11 | 3.3555 | 0.22145 | 0.22145 | 379.1306 | 0.705 | 0 | 259.5321 | 0 | 0 | 0 | 0.705 | 0 | 0 | 259.5321
3 | 27 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 379.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 384.4304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 5 | 10.3366 | 0 | 10.3366 | 11 | 3.9405 | 3.5601 | 3.5601 | 411.2746 | 10.3366 | 0 | 4137.4824 | 0 | 0 | 0 | 10.3366 | 0 | 0 | 4137.4824
3 | 27 | 6 | 13.8275 | 0 | 13.8275 | 11 | 4.8093 | 5.5588 | 5.5588 | 417.8899 | 13.8275 | 0 | 5626.2698 | 0 | 0 | 0 | 13.8275 | 0 | 0 | 5626.2698
3 | 27 | 7 | 0.1825 | 0 | 0.1825 | 11 | 5.1706 | 0.078851 | 0.078851 | 435.2678 | 0.1825 | 0 | 77.4289 | 0 | 0 | 0 | 0.1825 | 0 | 0 | 77.4289
3 | 27 | 8 | 0 | 0.66404 | 0.66404 | 48 | 5.8502 | 0.33383 | 0.33383 | 437.678 | 0.66404 | 0 | 258.7614 | 0 | 0 | 0 | 0.66404 | 0 | 0 | 258.7614
3 | 27 | 9 | 0.65833 | 4.2767 | 4.935 | 43.0642 | 6.7707 | 3.187 | 3.187 | 435.8273 | 4.935 | 0 | 1938.2834 | 0 | 0 | 0 | 4.935 | 0 | 0 | 1938.2834
3 | 27 | 10 | 0.82417 | 136.7579 | 137.5821 | 47.7784 | 8.9987 | 285.5904 | 285.5904 | 419.0525 | 137.5821 | 0 | 51080.6818 | 0 | 0 | 0 | 137.5821 | 0 | 0 | 51080.6818
3 | 27 | 11 | 1.4658 | 168.7951 | 170.2609 | 47.6815 | 10.0569 | 0 | 0 | 400.1006 | 0 | 170.2609 | 0 | 17.0176 | 0 | 0 | 0 | 170.2609 | 0 | 0
3 | 27 | 12 | 0.55417 | 0 | 0.55417 | 11 | 10.1343 | 0 | 0 | 387.7156 | 0 | 0.55417 | 0 | 0.055389 | 0 | 0 | 0 | 0.55417 | 0 | 0
3 | 27 | 13 | 0.72583 | 6.5678 | 7.2936 | 44.3179 | 10.2117 | 0 | 0 | 380.1789 | 0 | 7.2936 | 0 | 0.729 | 0 | 0 | 0 | 7.2936 | 0 | 0
3 | 27 | 14 | 0.1525 | 0 | 0.1525 | 11 | 9.8762 | 2.4735 | 2.4735 | 370.7401 | 0.1525 | 0 | 54.8604 | 0 | 0 | 0 | 0.1525 | 0 | 0 | 54.8604
3 | 27 | 15 | 0.675 | 0 | 0.675 | 11 | 10.9601 | 0 | 0 | 377.0461 | 0 | 0.675 | 0 | 0.067466 | 0 | 0 | 0 | 0.675 | 0 | 0
3 | 27 | 16 | 0.01 | 0 | 0.01 | 11 | 11.5279 | 0 | 0 | 384 | 0 | 0.01 | 0 | 0.0009995 | 0 | 0 | 0 | 0.01 | 0 | 0
3 | 27 | 17 | 9.1842 | 12.9441 | 22.1284 | 32.6434 | 11.5451 | 0 | 0 | 393.3223 | 0 | 22.1284 | 0 | 2.2117 | 0 | 0 | 0 | 22.1284 | 0 | 0
3 | 27 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 399.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 397.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 374.3375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 362.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 360.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 348.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 0 | 0.65583 | 0 | 0.65583 | 11 | 3.9577 | 0.22652 | 0.22652 | 352.3089 | 0.65583 | 0 | 223.8417 | 0 | 0 | 0 | 0.65583 | 0 | 0 | 223.8417
3 | 28 | 1 | 3.1265 | 0 | 3.1265 | 11 | 3.6394 | 1.0259 | 1.0259 | 354.38 | 3.1265 | 0 | 1073.5654 | 0 | 0 | 0 | 3.1265 | 0 | 0 | 1073.5654
3 | 28 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 371.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 399.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 419.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 433.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 6 | 2.4253 | 0 | 2.4253 | 11 | 5.3513 | 1.0885 | 1.0885 | 431.1528 | 2.4253 | 0 | 1018.9827 | 0 | 0 | 0 | 2.4253 | 0 | 0 | 1018.9827
3 | 28 | 7 | 3.306 | 0 | 3.306 | 11 | 5.6008 | 1.5679 | 1.5679 | 432.5304 | 3.306 | 0 | 1393.5972 | 0 | 0 | 0 | 3.306 | 0 | 0 | 1393.5972
3 | 28 | 8 | 13.0633 | 190.4638 | 203.5271 | 45.6252 | 6.5729 | 123.8618 | 123.8618 | 441.9833 | 203.5271 | 0 | 80669.6405 | 0 | 0 | 0 | 203.5271 | 0 | 0 | 80669.6405
3 | 28 | 9 | 19.6058 | 395.0896 | 414.6954 | 46.2507 | 7.7084 | 377.157 | 288 | 448.0122 | 316.6646 | 98.0308 | 127223.649 | 9.7982 | 0 | 0 | 316.6646 | 98.0308 | 0 | 127223.649
3 | 28 | 10 | 4.1533 | 451.5193 | 455.6726 | 47.6628 | 8.9471 | 899.725 | 288 | 441.7657 | 145.8598 | 309.8128 | 57483.7799 | 30.9659 | 0 | 0 | 145.8598 | 309.8128 | 0 | 57483.7799
3 | 28 | 11 | 2.3717 | 629.3204 | 631.6921 | 47.8611 | 9.5923 | 3197.3749 | 288 | 444.3659 | 56.899 | 574.7931 | 22560.7156 | 57.4507 | 0 | 0 | 56.899 | 574.7931 | 0 | 22560.7156
3 | 28 | 12 | 6.1525 | 760.6333 | 766.7858 | 47.7031 | 10.2891 | 0 | 0 | 454.074 | 0 | 766.7858 | 0 | 76.6405 | 0 | 0 | 0 | 766.7858 | 0 | 0
3 | 28 | 13 | 70.1033 | 967.0946 | 1037.1979 | 45.4992 | 10.0827 | 0 | 0 | 444.8251 | 0 | 1037.1979 | 0 | 103.6682 | 0 | 0 | 0 | 1037.1979 | 0 | 0
3 | 28 | 14 | 68.3452 | 905.0558 | 973.401 | 45.4021 | 10.6934 | 0 | 0 | 453.5097 | 0 | 973.401 | 0 | 97.2917 | 0 | 0 | 0 | 973.401 | 0 | 0
3 | 28 | 15 | 6.06 | 687.7477 | 693.8077 | 47.6768 | 11.6655 | 0 | 0 | 454.2284 | 0 | 693.8077 | 0 | 69.3463 | 0 | 0 | 0 | 693.8077 | 0 | 0
3 | 28 | 16 | 5.3233 | 499.1057 | 504.4291 | 47.6095 | 12.3021 | 0 | 0 | 439.0799 | 0 | 504.4291 | 0 | 50.4178 | 0 | 0 | 0 | 504.4291 | 0 | 0
3 | 28 | 17 | 18.061 | 175.8955 | 193.9565 | 44.5546 | 12.1989 | 0 | 0 | 449.0312 | 0 | 193.9565 | 0 | 19.386 | 0 | 0 | 0 | 193.9565 | 0 | 0
3 | 28 | 18 | 32.5533 | 36.064 | 68.6172 | 30.4465 | 12.9559 | 0 | 0 | 465.6056 | 0 | 68.6172 | 0 | 6.8583 | 0 | 0 | 0 | 68.6172 | 0 | 0
3 | 28 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 463.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 455.7946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 439.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 22 | 0.8375 | 0 | 0.8375 | 11 | 5.6868 | 0.4051 | 0.4051 | 427.6277 | 0.8375 | 0 | 348.9257 | 0 | 0 | 0 | 0.8375 | 0 | 0 | 348.9257
3 | 28 | 23 | 31.4698 | 0 | 31.4698 | 11 | 4.5734 | 12.1017 | 12.1017 | 421.4735 | 31.4698 | 0 | 12917.512 | 0 | 0 | 0 | 31.4698 | 0 | 0 | 12917.512
3 | 29 | 0 | 73.2368 | 0 | 73.2368 | 11 | 3.8373 | 24.8018 | 24.8018 | 423.3751 | 73.2368 | 0 | 30201.0496 | 0 | 0 | 0 | 73.2368 | 0 | 0 | 30201.0496
3 | 29 | 1 | 86.3041 | 0 | 86.3041 | 11 | 3.605 | 28.1664 | 28.1664 | 423.2414 | 86.3041 | 0 | 35578.1397 | 0 | 0 | 0 | 86.3041 | 0 | 0 | 35578.1397
3 | 29 | 2 | 268.8927 | 0 | 268.8927 | 11 | 3.5018 | 86.3634 | 86.3634 | 431.0944 | 268.8927 | 0 | 112960.3131 | 0 | 0 | 0 | 268.8927 | 0 | 0 | 112960.3131
3 | 29 | 3 | 13.0601 | 0 | 13.0601 | 11 | 3.4416 | 4.1562 | 4.1562 | 432.9797 | 13.0601 | 0 | 5511.0961 | 0 | 0 | 0 | 13.0601 | 0 | 0 | 5511.0961
3 | 29 | 4 | 0.82496 | 0 | 0.82496 | 11 | 3.6222 | 0.26996 | 0.26996 | 450.753 | 0.82496 | 0 | 362.7779 | 0 | 0 | 0 | 0.82496 | 0 | 0 | 362.7779
3 | 29 | 5 | 12.8173 | 0 | 12.8173 | 11 | 4.0351 | 4.4845 | 4.4845 | 453.651 | 12.8173 | 0 | 5673.5952 | 0 | 0 | 0 | 12.8173 | 0 | 0 | 5673.5952
3 | 29 | 6 | 28.6162 | 0 | 28.6162 | 11 | 5.1793 | 12.3859 | 12.3859 | 447.4869 | 28.6162 | 0 | 12490.581 | 0 | 0 | 0 | 28.6162 | 0 | 0 | 12490.581
3 | 29 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 456.7143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 451.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 9 | 16.2866 | 6.6797 | 22.9663 | 21.7613 | 7.6912 | 20.7321 | 20.7321 | 469.6733 | 22.9663 | 0 | 10286.876 | 0 | 0 | 0 | 22.9663 | 0 | 0 | 10286.876
3 | 29 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 470.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 464.6582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 12 | 10.18 | 13.7945 | 23.9745 | 32.2891 | 9.4117 | 84.4006 | 84.4006 | 465.8234 | 23.9745 | 0 | 10393.7457 | 0 | 0 | 0 | 23.9745 | 0 | 0 | 10393.7457
3 | 29 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 457.0032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 455.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 445.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 430.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 17 | 9.0583 | 0 | 9.0583 | 11 | 10.8053 | 0 | 0 | 459.2321 | 0 | 9.0583 | 0 | 0.90538 | 0 | 0 | 0 | 9.0583 | 0 | 0
3 | 29 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 469.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 457.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 20 | 0.16106 | 0 | 0.16106 | 11 | 8.4138 | 0.21142 | 0.21142 | 439.3712 | 0.16106 | 0 | 68.995 | 0 | 0 | 0 | 0.16106 | 0 | 0 | 68.995
3 | 29 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 430.8026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 414.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 412.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 416.7062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 426.9463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 442.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 445.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 444.2469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 5 | 3.9733 | 0 | 3.9733 | 11 | 3.9663 | 1.3743 | 1.3743 | 446.0144 | 3.9733 | 0 | 1728.4358 | 0 | 0 | 0 | 3.9733 | 0 | 0 | 1728.4358
3 | 30 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 450.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 463.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 455.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 9 | 0 | 4.2167 | 4.2167 | 48 | 6.9858 | 2.9171 | 2.9171 | 455.0423 | 4.2167 | 0 | 1716.3753 | 0 | 0 | 0 | 4.2167 | 0 | 0 | 1716.3753
3 | 30 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 447.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 439.498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 12 | 0.77913 | 0 | 0.77913 | 11 | 8.2847 | 0.94601 | 0.94601 | 441.8475 | 0.77913 | 0 | 335.6841 | 0 | 0 | 0 | 0.77913 | 0 | 0 | 335.6841
3 | 30 | 13 | 0.78583 | 0 | 0.78583 | 11 | 7.8202 | 0.75128 | 0.75128 | 429.3478 | 0.78583 | 0 | 328.7517 | 0 | 0 | 0 | 0.78583 | 0 | 0 | 328.7517
3 | 30 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 426.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 15 | 4.5899 | 0 | 4.5899 | 11 | 7.7256 | 4.2059 | 4.2059 | 430.7337 | 4.5899 | 0 | 1926.538 | 0 | 0 | 0 | 4.5899 | 0 | 0 | 1926.538
3 | 30 | 16 | 2.4356 | 0 | 2.4356 | 11 | 7.3729 | 1.9328 | 1.9328 | 427.8766 | 2.4356 | 0 | 1015.3546 | 0 | 0 | 0 | 2.4356 | 0 | 0 | 1015.3546
3 | 30 | 17 | 15.1428 | 0 | 15.1428 | 11 | 7.5449 | 12.857 | 12.857 | 449.9855 | 15.1428 | 0 | 6647.459 | 0 | 0 | 0 | 15.1428 | 0 | 0 | 6647.459
3 | 30 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 443.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 432.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 412.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 397.6096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 385.8156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 383.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 379.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 379.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 389.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 404.2134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 4 | 0.17167 | 0 | 0.17167 | 11 | 3.2609 | 0.053167 | 0.053167 | 425.3143 | 0.17167 | 0 | 71.124 | 0 | 0 | 0 | 0.17167 | 0 | 0 | 71.124
3 | 31 | 5 | 0.22667 | 0 | 0.22667 | 11 | 3.4071 | 0.071757 | 0.071757 | 440.8802 | 0.22667 | 0 | 97.4395 | 0 | 0 | 0 | 0.22667 | 0 | 0 | 97.4395
3 | 31 | 6 | 0.175 | 0 | 0.175 | 11 | 4.9556 | 0.07239 | 0.07239 | 448.8341 | 0.175 | 0 | 76.621 | 0 | 0 | 0 | 0.175 | 0 | 0 | 76.621
3 | 31 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 450.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 8 | 9.1875 | 54.3861 | 63.5736 | 42.6528 | 7.2524 | 48.2417 | 48.2417 | 447.8772 | 63.5736 | 0 | 25761.556 | 0 | 0 | 0 | 63.5736 | 0 | 0 | 25761.556
3 | 31 | 9 | 17.2167 | 92.7784 | 109.9951 | 42.2087 | 7.6998 | 99.665 | 99.665 | 460.7932 | 109.9951 | 0 | 46042.2327 | 0 | 0 | 0 | 109.9951 | 0 | 0 | 46042.2327
3 | 31 | 10 | 0 | 5.145 | 5.145 | 48 | 7.8632 | 5.0176 | 5.0176 | 453.0744 | 5.145 | 0 | 2084.1078 | 0 | 0 | 0 | 5.145 | 0 | 0 | 2084.1078
3 | 31 | 11 | 0 | 0.78667 | 0.78667 | 48 | 7.6051 | 0.68468 | 0.68468 | 453.4071 | 0.78667 | 0 | 318.9202 | 0 | 0 | 0 | 0.78667 | 0 | 0 | 318.9202
3 | 31 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 452.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 442.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 437.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 431.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 16 | 3.865 | 32.1976 | 36.0626 | 44.0345 | 7.6998 | 32.6758 | 32.6758 | 426.9841 | 36.0626 | 0 | 13810.1472 | 0 | 0 | 0 | 36.0626 | 0 | 0 | 13810.1472
3 | 31 | 17 | 0.10083 | 0 | 0.10083 | 11 | 7.6482 | 0.089363 | 0.089363 | 428.1934 | 0.10083 | 0 | 42.067 | 0 | 0 | 0 | 0.10083 | 0 | 0 | 42.067
3 | 31 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 451.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 432.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 421.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 414.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 409.1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 406.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 404.6397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 408.1761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 426.5486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 453.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 472.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 5 | 0.4025 | 0 | 0.4025 | 11 | 3.691 | 0.13315 | 0.13315 | 477.9138 | 0.4025 | 0 | 187.9328 | 0 | 0 | 0 | 0.4025 | 0 | 0 | 187.9328
4 | 1 | 6 | 0.14417 | 0 | 0.14417 | 11 | 4.8007 | 0.057861 | 0.057861 | 477.7843 | 0.14417 | 0 | 67.2947 | 0 | 0 | 0 | 0.14417 | 0 | 0 | 67.2947
4 | 1 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 472.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 8 | 6.0498 | 3.7691 | 9.8188 | 25.2029 | 6.9944 | 6.8122 | 6.8122 | 477.6402 | 9.8188 | 0 | 4442.4121 | 0 | 0 | 0 | 9.8188 | 0 | 0 | 4442.4121
4 | 1 | 9 | 0 | 9.7158 | 9.7158 | 48 | 7.5707 | 8.3367 | 8.3367 | 477.7361 | 9.7158 | 0 | 4175.2329 | 0 | 0 | 0 | 9.7158 | 0 | 0 | 4175.2329
4 | 1 | 10 | 0 | 0.57249 | 0.57249 | 48 | 7.4159 | 0.46185 | 0.46185 | 473.1827 | 0.57249 | 0 | 243.415 | 0 | 0 | 0 | 0.57249 | 0 | 0 | 243.415
4 | 1 | 11 | 2.2931 | 0.033138 | 2.3262 | 11.5271 | 7.5879 | 2.0102 | 2.0102 | 470.4568 | 2.3262 | 0 | 1067.5715 | 0 | 0 | 0 | 2.3262 | 0 | 0 | 1067.5715
4 | 1 | 12 | 0.225 | 0 | 0.225 | 11 | 8.3192 | 0.27877 | 0.27877 | 465.2061 | 0.225 | 0 | 102.1964 | 0 | 0 | 0 | 0.225 | 0 | 0 | 102.1964
4 | 1 | 13 | 6.7187 | 0 | 6.7187 | 11 | 8.6546 | 10.3925 | 10.3925 | 462.9226 | 6.7187 | 0 | 3036.3162 | 0 | 0 | 0 | 6.7187 | 0 | 0 | 3036.3162
4 | 1 | 14 | 20.3236 | 102.0495 | 122.3731 | 41.8551 | 8.9299 | 237.7586 | 237.7586 | 464.116 | 122.3731 | 0 | 51673.3694 | 0 | 0 | 0 | 122.3731 | 0 | 0 | 51673.3694
4 | 1 | 15 | 17.6383 | 594.8374 | 612.4757 | 46.9345 | 8.8009 | 1062.4532 | 288 | 457.6012 | 166.0243 | 446.4514 | 68180.64 | 44.6229 | 0 | 0 | 166.0243 | 446.4514 | 0 | 68180.64
4 | 1 | 16 | 33.1093 | 273.1946 | 306.3039 | 44.0006 | 9.5837 | 1518.7286 | 288 | 461.9888 | 58.0851 | 248.2188 | 24278.8942 | 24.8095 | 0 | 0 | 58.0851 | 248.2188 | 0 | 24278.8942
4 | 1 | 17 | 46.5392 | 283.0267 | 329.5659 | 42.7751 | 9.0762 | 741.1316 | 288 | 466.6877 | 128.0676 | 201.4982 | 54289.4805 | 20.1398 | 0 | 0 | 128.0676 | 201.4982 | 0 | 54289.4805
4 | 1 | 18 | 154.0098 | 351.6447 | 505.6545 | 36.7307 | 9.4461 | 1889.7228 | 288 | 466.1626 | 77.0634 | 428.5911 | 33093.4887 | 42.8378 | 0 | 0 | 77.0634 | 428.5911 | 0 | 33093.4887
4 | 1 | 19 | 4.4665 | 0 | 4.4665 | 11 | 8.0611 | 4.7992 | 4.7992 | 461.1017 | 4.4665 | 0 | 2010.3633 | 0 | 0 | 0 | 4.4665 | 0 | 0 | 2010.3633
4 | 1 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 442.9717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 421.6911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 22 | 0.54917 | 0 | 0.54917 | 11 | 5.4717 | 0.25303 | 0.25303 | 408.1625 | 0.54917 | 0 | 218.1084 | 0 | 0 | 0 | 0.54917 | 0 | 0 | 218.1084
4 | 1 | 23 | 29.358 | 0 | 29.358 | 11 | 4.8093 | 11.8023 | 11.8023 | 402.1283 | 29.358 | 0 | 11482.7316 | 0 | 0 | 0 | 29.358 | 0 | 0 | 11482.7316
4 | 2 | 0 | 1.4767 | 0 | 1.4767 | 11 | 3.3125 | 0.46087 | 0.46087 | 390.0512 | 1.4767 | 0 | 559.7322 | 0 | 0 | 0 | 1.4767 | 0 | 0 | 559.7322
4 | 2 | 1 | 15.8152 | 0 | 15.8152 | 11 | 3.2007 | 4.8548 | 4.8548 | 386.9575 | 15.8152 | 0 | 5945.834 | 0 | 0 | 0 | 15.8152 | 0 | 0 | 5945.834
4 | 2 | 2 | 0.2725 | 0 | 0.2725 | 11 | 3.1921 | 0.083544 | 0.083544 | 394.6295 | 0.2725 | 0 | 104.5391 | 0 | 0 | 0 | 0.2725 | 0 | 0 | 104.5391
4 | 2 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 401.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 404.7988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 413.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 424.4861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 428.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 8 | 0.06 | 0 | 0.06 | 11 | 5.1879 | 0.026016 | 0.026016 | 430.7228 | 0.06 | 0 | 25.1834 | 0 | 0 | 0 | 0.06 | 0 | 0 | 25.1834
4 | 2 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 433.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 10 | 8.6992 | 16.3763 | 25.0755 | 35.164 | 8.8783 | 46.4873 | 46.4873 | 427.6376 | 25.0755 | 0 | 9841.4775 | 0 | 0 | 0 | 25.0755 | 0 | 0 | 9841.4775
4 | 2 | 11 | 8.3492 | 22.6464 | 30.9955 | 38.0334 | 9.8676 | 471.2572 | 288 | 428.4181 | 18.9423 | 12.0532 | 7394.801 | 1.2047 | 0 | 0 | 18.9423 | 12.0532 | 0 | 7394.801
4 | 2 | 12 | 0.19417 | 0 | 0.19417 | 11 | 10.2547 | 0 | 0 | 422.0838 | 0 | 0.19417 | 0 | 0.019407 | 0 | 0 | 0 | 0.19417 | 0 | 0
4 | 2 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 420.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 431.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 426.2153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 16 | 1.0417 | 0 | 1.0417 | 11 | 12.5086 | 0 | 0 | 416.494 | 0 | 1.0417 | 0 | 0.10411 | 0 | 0 | 0 | 1.0417 | 0 | 0
4 | 2 | 17 | 8.7533 | 0.49453 | 9.2479 | 12.9786 | 12.2591 | 0 | 0 | 439.455 | 0 | 9.2479 | 0 | 0.92433 | 0 | 0 | 0 | 9.2479 | 0 | 0
4 | 2 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 463.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 452.8403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 451.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 450.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 438.7767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 434.4282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 434.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 440.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 448.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 463.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 462.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 461.3858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 6 | 6.4333 | 0 | 6.4333 | 11 | 4.8093 | 2.5863 | 2.5863 | 460.9397 | 6.4333 | 0 | 2894.6084 | 0 | 0 | 0 | 6.4333 | 0 | 0 | 2894.6084
4 | 3 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 464.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 8 | 1.7457 | 26.3789 | 28.1246 | 45.7034 | 5.8502 | 14.1391 | 14.1391 | 450.0273 | 28.1246 | 0 | 11371.4466 | 0 | 0 | 0 | 28.1246 | 0 | 0 | 11371.4466
4 | 3 | 9 | 23.2454 | 0 | 23.2454 | 11 | 6.7707 | 15.0121 | 15.0121 | 445.3306 | 23.2454 | 0 | 10096.2095 | 0 | 0 | 0 | 23.2454 | 0 | 0 | 10096.2095
4 | 3 | 10 | 58.7933 | 0 | 58.7933 | 11 | 8.9987 | 122.042 | 122.042 | 430.1979 | 58.7933 | 0 | 24646.0132 | 0 | 0 | 0 | 58.7933 | 0 | 0 | 24646.0132
4 | 3 | 11 | 50.4699 | 0 | 50.4699 | 11 | 10.0569 | 0 | 0 | 422.6687 | 0 | 50.4699 | 0 | 5.0445 | 0 | 0 | 0 | 50.4699 | 0 | 0
4 | 3 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 410.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 13 | 1.9022 | 0 | 1.9022 | 11 | 10.2117 | 0 | 0 | 416.2383 | 0 | 1.9022 | 0 | 0.19012 | 0 | 0 | 0 | 1.9022 | 0 | 0
4 | 3 | 14 | 33.0079 | 0 | 33.0079 | 11 | 9.8762 | 535.3782 | 288 | 427.5125 | 17.7562 | 15.2517 | 7395.6786 | 1.5244 | 0 | 0 | 17.7562 | 15.2517 | 0 | 7395.6786
4 | 3 | 15 | 5.551 | 0 | 5.551 | 11 | 10.9601 | 0 | 0 | 435.3074 | 0 | 5.551 | 0 | 0.55482 | 0 | 0 | 0 | 5.551 | 0 | 0
4 | 3 | 16 | 70.437 | 0 | 70.437 | 11 | 11.5279 | 0 | 0 | 429.6947 | 0 | 70.437 | 0 | 7.0402 | 0 | 0 | 0 | 70.437 | 0 | 0
4 | 3 | 17 | 3.6614 | 0 | 3.6614 | 11 | 11.5451 | 0 | 0 | 441.7039 | 0 | 3.6614 | 0 | 0.36595 | 0 | 0 | 0 | 3.6614 | 0 | 0
4 | 3 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 451.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 449.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 20 | 0.24977 | 0 | 0.24977 | 11 | 12.6978 | 0 | 0 | 435.8771 | 0 | 0.24977 | 0 | 0.024965 | 0 | 0 | 0 | 0.24977 | 0 | 0
4 | 3 | 21 | 13.9524 | 0 | 13.9524 | 11 | 9.8762 | 226.3038 | 226.3038 | 422.0892 | 13.9524 | 0 | 5735.6867 | 0 | 0 | 0 | 13.9524 | 0 | 0 | 5735.6867
4 | 3 | 22 | 75.1376 | 0 | 75.1376 | 11 | 6.1771 | 40.9998 | 40.9998 | 411.8882 | 75.1376 | 0 | 30121.7628 | 0 | 0 | 0 | 75.1376 | 0 | 0 | 30121.7628
4 | 3 | 23 | 109.2245 | 0 | 109.2245 | 11 | 4.6373 | 42.5022 | 42.5022 | 408.8131 | 109.2245 | 0 | 43450.952 | 0 | 0 | 0 | 109.2245 | 0 | 0 | 43450.952
4 | 4 | 0 | 45.8015 | 0 | 45.8015 | 11 | 3.9577 | 15.8197 | 15.8197 | 406.0431 | 45.8015 | 0 | 18093.5823 | 0 | 0 | 0 | 45.8015 | 0 | 0 | 18093.5823
4 | 4 | 1 | 9.0926 | 0 | 9.0926 | 11 | 3.6394 | 2.9835 | 2.9835 | 408.4338 | 9.0926 | 0 | 3613.705 | 0 | 0 | 0 | 9.0926 | 0 | 0 | 3613.705
4 | 4 | 2 | 31.8182 | 0 | 31.8182 | 11 | 3.5276 | 10.2601 | 10.2601 | 437.3343 | 31.8182 | 0 | 13565.1839 | 0 | 0 | 0 | 31.8182 | 0 | 0 | 13565.1839
4 | 4 | 3 | 16.6518 | 0 | 16.6518 | 11 | 3.562 | 5.3982 | 5.3982 | 458.1849 | 16.6518 | 0 | 7446.4295 | 0 | 0 | 0 | 16.6518 | 0 | 0 | 7446.4295
4 | 4 | 4 | 3.6067 | 0 | 3.6067 | 11 | 3.5878 | 1.1739 | 1.1739 | 470.1501 | 3.6067 | 0 | 1656.0028 | 0 | 0 | 0 | 3.6067 | 0 | 0 | 1656.0028
4 | 4 | 5 | 1.8556 | 0 | 1.8556 | 11 | 4.1814 | 0.66553 | 0.66553 | 478.6202 | 1.8556 | 0 | 867.7103 | 0 | 0 | 0 | 1.8556 | 0 | 0 | 867.7103
4 | 4 | 6 | 69.3881 | 0 | 69.3881 | 11 | 5.3513 | 31.1435 | 31.1435 | 479.6694 | 69.3881 | 0 | 32520.0782 | 0 | 0 | 0 | 69.3881 | 0 | 0 | 32520.0782
4 | 4 | 7 | 46.2 | 0 | 46.2 | 11 | 5.6008 | 21.9105 | 21.9105 | 481.7603 | 46.2 | 0 | 21749.1446 | 0 | 0 | 0 | 46.2 | 0 | 0 | 21749.1446
4 | 4 | 8 | 0.63083 | 1.5056 | 2.1364 | 37.0748 | 6.5729 | 1.3002 | 1.3002 | 490.808 | 2.1364 | 0 | 969.3663 | 0 | 0 | 0 | 2.1364 | 0 | 0 | 969.3663
4 | 4 | 9 | 0.25167 | 24.4791 | 24.7308 | 47.6235 | 7.7084 | 22.4922 | 22.4922 | 500.438 | 24.7308 | 0 | 11198.468 | 0 | 0 | 0 | 24.7308 | 0 | 0 | 11198.468
4 | 4 | 10 | 0.435 | 36.5993 | 37.0343 | 47.5654 | 8.9471 | 73.1242 | 73.1242 | 510.4184 | 37.0343 | 0 | 17141.4314 | 0 | 0 | 0 | 37.0343 | 0 | 0 | 17141.4314
4 | 4 | 11 | 0.0066667 | 0 | 0.0066667 | 11 | 9.5923 | 0.033744 | 0.033744 | 508.975 | 0.0066667 | 0 | 3.3198 | 0 | 0 | 0 | 0.0066667 | 0 | 0 | 3.3198
4 | 4 | 12 | 0.4775 | 0 | 0.4775 | 11 | 10.2891 | 0 | 0 | 503.7695 | 0 | 0.4775 | 0 | 0.047726 | 0 | 0 | 0 | 0.4775 | 0 | 0
4 | 4 | 13 | 0.079167 | 1.3131 | 1.3922 | 45.8961 | 10.0827 | 0 | 0 | 506.4572 | 0 | 1.3922 | 0 | 0.13916 | 0 | 0 | 0 | 1.3922 | 0 | 0
4 | 4 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 510.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 514.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 512.0974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 505.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 511.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 518.7885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 507.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 497.061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 482.8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 486.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 0 | 14.8675 | 0 | 14.8675 | 11 | 3.8373 | 5.0349 | 5.0349 | 492.052 | 14.8675 | 0 | 7152.0248 | 0 | 0 | 0 | 14.8675 | 0 | 0 | 7152.0248
4 | 5 | 1 | 109.478 | 0 | 109.478 | 11 | 3.605 | 35.7295 | 35.7295 | 489.4131 | 109.478 | 0 | 52375.7124 | 0 | 0 | 0 | 109.478 | 0 | 0 | 52375.7124
4 | 5 | 2 | 113.2219 | 0 | 113.2219 | 11 | 3.5018 | 36.3648 | 36.3648 | 507.8353 | 113.2219 | 0 | 56252.6277 | 0 | 0 | 0 | 113.2219 | 0 | 0 | 56252.6277
4 | 5 | 3 | 5.8725 | 0 | 5.8725 | 11 | 3.4416 | 1.8688 | 1.8688 | 504.0825 | 5.8725 | 0 | 2895.6476 | 0 | 0 | 0 | 5.8725 | 0 | 0 | 2895.6476
4 | 5 | 4 | 27.3477 | 0 | 27.3477 | 11 | 3.6222 | 8.9493 | 8.9493 | 513.9664 | 27.3477 | 0 | 13754.953 | 0 | 0 | 0 | 27.3477 | 0 | 0 | 13754.953
4 | 5 | 5 | 3.4197 | 0 | 3.4197 | 11 | 4.0351 | 1.1965 | 1.1965 | 516.1253 | 3.4197 | 0 | 1727.3596 | 0 | 0 | 0 | 3.4197 | 0 | 0 | 1727.3596
4 | 5 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 514.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 7 | 0.49667 | 0 | 0.49667 | 11 | 5.3599 | 0.22333 | 0.22333 | 516.6647 | 0.49667 | 0 | 251.1468 | 0 | 0 | 0 | 0.49667 | 0 | 0 | 251.1468
4 | 5 | 8 | 0.295 | 0 | 0.295 | 11 | 6.5729 | 0.17953 | 0.17953 | 525.0625 | 0.295 | 0 | 151.6484 | 0 | 0 | 0 | 0.295 | 0 | 0 | 151.6484
4 | 5 | 9 | 10.0408 | 145.7294 | 155.7703 | 45.615 | 7.6912 | 140.6165 | 140.6165 | 530.2834 | 155.7703 | 0 | 75496.9234 | 0 | 0 | 0 | 155.7703 | 0 | 0 | 75496.9234
4 | 5 | 10 | 49.2228 | 238.878 | 288.1008 | 41.6784 | 8.4482 | 386.5392 | 288 | 531.6028 | 214.6562 | 73.4446 | 105165.2863 | 7.3408 | 0 | 0 | 214.6562 | 73.4446 | 0 | 105165.2863
4 | 5 | 11 | 46.8495 | 312.557 | 359.4065 | 43.177 | 9.7214 | 2646.8307 | 288 | 531.2882 | 39.1068 | 320.2997 | 19088.4687 | 32.014 | 0 | 0 | 39.1068 | 320.2997 | 0 | 19088.4687
4 | 5 | 12 | 36.7475 | 515.6242 | 552.3717 | 45.5385 | 9.4117 | 1944.5903 | 288 | 519.9933 | 81.808 | 470.5637 | 38814.1995 | 47.033 | 0 | 0 | 81.808 | 470.5637 | 0 | 38814.1995
4 | 5 | 13 | 29.5858 | 508.3462 | 537.932 | 45.965 | 8.8869 | 1004.9403 | 288 | 510.9202 | 154.1628 | 383.7692 | 71678.7905 | 38.3578 | 0 | 0 | 154.1628 | 383.7692 | 0 | 71678.7905
4 | 5 | 14 | 42.9767 | 253.765 | 296.7417 | 42.6413 | 9.3428 | 936.0817 | 288 | 498.8462 | 91.2972 | 205.4445 | 41650.209 | 20.5342 | 0 | 0 | 91.2972 | 205.4445 | 0 | 41650.209
4 | 5 | 15 | 48.1075 | 245.6329 | 293.7404 | 41.9403 | 10.0224 | 0 | 0 | 497.1935 | 0 | 293.7404 | 0 | 29.3594 | 0 | 0 | 0 | 293.7404 | 0 | 0
4 | 5 | 16 | 24.7382 | 45.8691 | 70.6073 | 35.0365 | 11.4074 | 0 | 0 | 486.6259 | 0 | 70.6073 | 0 | 7.0572 | 0 | 0 | 0 | 70.6073 | 0 | 0
4 | 5 | 17 | 93.9124 | 196.6935 | 290.6059 | 36.0431 | 10.8053 | 0 | 0 | 499.2926 | 0 | 290.6059 | 0 | 29.0461 | 0 | 0 | 0 | 290.6059 | 0 | 0
4 | 5 | 18 | 6.5125 | 0 | 6.5125 | 11 | 11.5107 | 0 | 0 | 519.1974 | 0 | 6.5125 | 0 | 0.65093 | 0 | 0 | 0 | 6.5125 | 0 | 0
4 | 5 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 520.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 514.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 507.8843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 494.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 23 | 21.1916 | 0 | 21.1916 | 11 | 4.5599 | 8.129 | 8.129 | 504.5958 | 21.1916 | 0 | 10460.0963 | 0 | 0 | 0 | 21.1916 | 0 | 0 | 10460.0963
4 | 6 | 0 | 85.7971 | 0 | 85.7971 | 11 | 4.5083 | 32.6022 | 32.6022 | 506.6329 | 85.7971 | 0 | 42523.8524 | 0 | 0 | 0 | 85.7971 | 0 | 0 | 42523.8524
4 | 6 | 1 | 75.9348 | 0 | 75.9348 | 11 | 4.2072 | 27.3562 | 27.3562 | 513.7116 | 75.9348 | 0 | 38173.3078 | 0 | 0 | 0 | 75.9348 | 0 | 0 | 38173.3078
4 | 6 | 2 | 27.852 | 0 | 27.852 | 11 | 4.147 | 9.9308 | 9.9308 | 518.9062 | 27.852 | 0 | 14146.2251 | 0 | 0 | 0 | 27.852 | 0 | 0 | 14146.2251
4 | 6 | 3 | 63.4608 | 0 | 63.4608 | 11 | 3.7857 | 21.3128 | 21.3128 | 512.2114 | 63.4608 | 0 | 31807.269 | 0 | 0 | 0 | 63.4608 | 0 | 0 | 31807.269
4 | 6 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 514.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 5 | 0.93081 | 0 | 0.93081 | 11 | 3.9663 | 0.32196 | 0.32196 | 508.8537 | 0.93081 | 0 | 463.4054 | 0 | 0 | 0 | 0.93081 | 0 | 0 | 463.4054
4 | 6 | 6 | 0.33667 | 0 | 0.33667 | 11 | 4.7319 | 0.13336 | 0.13336 | 513.89 | 0.33667 | 0 | 169.3063 | 0 | 0 | 0 | 0.33667 | 0 | 0 | 169.3063
4 | 6 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 521.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 8 | 2.4383 | 1.8184 | 4.2567 | 26.8058 | 5.4889 | 1.9688 | 1.9688 | 516.2662 | 4.2567 | 0 | 2083.5049 | 0 | 0 | 0 | 4.2567 | 0 | 0 | 2083.5049
4 | 6 | 9 | 25.8665 | 61.6539 | 87.5204 | 37.0647 | 6.9858 | 60.5473 | 60.5473 | 512.7106 | 87.5204 | 0 | 41628.7104 | 0 | 0 | 0 | 87.5204 | 0 | 0 | 41628.7104
4 | 6 | 10 | 41.1453 | 138.5223 | 179.6676 | 39.5267 | 7.3471 | 141.1916 | 141.1916 | 512.9855 | 179.6676 | 0 | 85065.2183 | 0 | 0 | 0 | 179.6676 | 0 | 0 | 85065.2183
4 | 6 | 11 | 5.8158 | 18.6732 | 24.489 | 39.213 | 8.9643 | 49.153 | 49.153 | 505.845 | 24.489 | 0 | 11427.3595 | 0 | 0 | 0 | 24.489 | 0 | 0 | 11427.3595
4 | 6 | 12 | 3.1 | 197.4395 | 200.5395 | 47.428 | 8.2847 | 243.4954 | 243.4954 | 498.5915 | 200.5395 | 0 | 90476.0862 | 0 | 0 | 0 | 200.5395 | 0 | 0 | 90476.0862
4 | 6 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 500.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 505.1565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 507.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 510.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 512.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 514.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 508.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 478.2916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 450.7457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 434.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 428.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 428.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 1 | 1.8965 | 0 | 1.8965 | 11 | 3.4243 | 0.60196 | 0.60196 | 431.2234 | 1.8965 | 0 | 796.9663 | 0 | 0 | 0 | 1.8965 | 0 | 0 | 796.9663
4 | 7 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 439.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 452.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 492.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 5 | 0.84471 | 0 | 0.84471 | 11 | 3.4071 | 0.26742 | 0.26742 | 503.2428 | 0.84471 | 0 | 415.8038 | 0 | 0 | 0 | 0.84471 | 0 | 0 | 415.8038
4 | 7 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 508.6154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 517.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 519.2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 513.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 10 | 0.13 | 0 | 0.13 | 11 | 7.8632 | 0.12678 | 0.12678 | 512.5805 | 0.13 | 0 | 65.2055 | 0 | 0 | 0 | 0.13 | 0 | 0 | 65.2055
4 | 7 | 11 | 5.9042 | 27.7378 | 33.6419 | 41.5065 | 7.6051 | 29.2805 | 29.2805 | 512.6596 | 33.6419 | 0 | 15850.4957 | 0 | 0 | 0 | 33.6419 | 0 | 0 | 15850.4957
4 | 7 | 12 | 1.892 | 0 | 1.892 | 11 | 8.2589 | 2.2633 | 2.2633 | 507.6841 | 1.892 | 0 | 939.7262 | 0 | 0 | 0 | 1.892 | 0 | 0 | 939.7262
4 | 7 | 13 | 1.4033 | 0 | 1.4033 | 11 | 8.5686 | 2.0407 | 2.0407 | 502.4654 | 1.4033 | 0 | 689.6898 | 0 | 0 | 0 | 1.4033 | 0 | 0 | 689.6898
4 | 7 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 508.4882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 510.6879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 508.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 507.1929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 520.7857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 517.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 506.5329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 495.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 488.9446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 471.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 473.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 477.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 483.7153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 491.1738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 501.2984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 507.1435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 503.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 509.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 514.6856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 509.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 512.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 506.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 503.1393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 507.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 14 | 4.4683 | 18.69 | 23.1582 | 40.8611 | 8.9299 | 44.9941 | 44.9941 | 499.3339 | 23.1582 | 0 | 10617.4185 | 0 | 0 | 0 | 23.1582 | 0 | 0 | 10617.4185
4 | 8 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 496.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 16 | 0.34247 | 0 | 0.34247 | 11 | 9.5837 | 1.698 | 1.698 | 487.8668 | 0.34247 | 0 | 163.3115 | 0 | 0 | 0 | 0.34247 | 0 | 0 | 163.3115
4 | 8 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 500.4439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 509.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 19 | 155.1798 | 0 | 155.1798 | 11 | 8.0611 | 166.74 | 166.74 | 509.5258 | 155.1798 | 0 | 77361.1305 | 0 | 0 | 0 | 155.1798 | 0 | 0 | 77361.1305
4 | 8 | 20 | 99.1513 | 0 | 99.1513 | 11 | 11.2698 | 0 | 0 | 504.3755 | 0 | 99.1513 | 0 | 9.9102 | 0 | 0 | 0 | 99.1513 | 0 | 0
4 | 8 | 21 | 40.7394 | 0 | 40.7394 | 11 | 9.1708 | 102.0077 | 102.0077 | 483.6202 | 40.7394 | 0 | 19254.2442 | 0 | 0 | 0 | 40.7394 | 0 | 0 | 19254.2442
4 | 8 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 466.1234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 460.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 459.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 1 | 3.1408 | 0 | 3.1408 | 11 | 3.2007 | 0.96414 | 0.96414 | 451.854 | 3.1408 | 0 | 1384.649 | 0 | 0 | 0 | 3.1408 | 0 | 0 | 1384.649
4 | 9 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 464.9052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 470.8403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 470.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 478.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 482.9486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 486.3424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 498.0343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 501.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 501.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 497.3377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 492.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 13 | 0 | 50.3333 | 50.3333 | 48 | 10.031 | 0 | 0 | 489.0471 | 0 | 50.3333 | 0 | 5.0308 | 0 | 0 | 0 | 50.3333 | 0 | 0
4 | 9 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 490.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 485.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 473.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 477.7634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 487.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 486.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 490.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 485.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 484.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 476.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 481.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 479.5114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 476.9564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 467.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 457.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 458.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 6 | 4.4091 | 0 | 4.4091 | 11 | 4.8093 | 1.7725 | 1.7725 | 463.0862 | 4.4091 | 0 | 1993.3038 | 0 | 0 | 0 | 4.4091 | 0 | 0 | 1993.3038
4 | 10 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 467.6255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 468.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 470.1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 464.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 457.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 460.1705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 13 | 0 | 5.7443 | 5.7443 | 48 | 10.2117 | 0 | 0 | 457.2097 | 0 | 5.7443 | 0 | 0.57414 | 0 | 0 | 0 | 5.7443 | 0 | 0
4 | 10 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 461.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 452.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 452.9903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 464.1908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 456.7247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 465.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 450.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 430.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 430.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 423.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 0 | 5.1209 | 0 | 5.1209 | 11 | 3.9577 | 1.7687 | 1.7687 | 427.8571 | 5.1209 | 0 | 2134.6729 | 0 | 0 | 0 | 5.1209 | 0 | 0 | 2134.6729
4 | 11 | 1 | 0.1036 | 0 | 0.1036 | 11 | 3.6394 | 0.033992 | 0.033992 | 444.1953 | 0.1036 | 0 | 44.8771 | 0 | 0 | 0 | 0.1036 | 0 | 0 | 44.8771
4 | 11 | 2 | 10.7473 | 0 | 10.7473 | 11 | 3.5276 | 3.4656 | 3.4656 | 460.7324 | 10.7473 | 0 | 4833.425 | 0 | 0 | 0 | 10.7473 | 0 | 0 | 4833.425
4 | 11 | 3 | 4.7183 | 0 | 4.7183 | 11 | 3.562 | 1.5296 | 1.5296 | 460.5714 | 4.7183 | 0 | 2121.2279 | 0 | 0 | 0 | 4.7183 | 0 | 0 | 2121.2279
4 | 11 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 463.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 5 | 11.8163 | 0 | 11.8163 | 11 | 4.1814 | 4.2381 | 4.2381 | 467.2288 | 11.8163 | 0 | 5390.9255 | 0 | 0 | 0 | 11.8163 | 0 | 0 | 5390.9255
4 | 11 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 472.1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 476.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 8 | 0.3025 | 0 | 0.3025 | 11 | 6.5729 | 0.18409 | 0.18409 | 482.6546 | 0.3025 | 0 | 142.6755 | 0 | 0 | 0 | 0.3025 | 0 | 0 | 142.6755
4 | 11 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 475.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 10 | 16.5972 | 0 | 16.5972 | 11 | 8.9471 | 32.7711 | 32.7711 | 474.4442 | 16.5972 | 0 | 7691.8701 | 0 | 0 | 0 | 16.5972 | 0 | 0 | 7691.8701
4 | 11 | 11 | 8.0546 | 0 | 8.0546 | 11 | 9.5923 | 40.7693 | 40.7693 | 467.9833 | 8.0546 | 0 | 3680.8267 | 0 | 0 | 0 | 8.0546 | 0 | 0 | 3680.8267
4 | 11 | 12 | 9.5425 | 33.7844 | 43.3269 | 39.851 | 10.2891 | 0 | 0 | 468.9531 | 0 | 43.3269 | 0 | 4.3305 | 0 | 0 | 0 | 43.3269 | 0 | 0
4 | 11 | 13 | 16.4687 | 47.1664 | 63.6351 | 38.4245 | 10.0827 | 0 | 0 | 468.5065 | 0 | 63.6351 | 0 | 6.3603 | 0 | 0 | 0 | 63.6351 | 0 | 0
4 | 11 | 14 | 6.9575 | 64.1841 | 71.1416 | 44.3815 | 10.6934 | 0 | 0 | 471.7993 | 0 | 71.1416 | 0 | 7.1106 | 0 | 0 | 0 | 71.1416 | 0 | 0
4 | 11 | 15 | 16.0442 | 16.2969 | 32.3411 | 29.6446 | 11.6655 | 0 | 0 | 470.8857 | 0 | 32.3411 | 0 | 3.2325 | 0 | 0 | 0 | 32.3411 | 0 | 0
4 | 11 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 452.7251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 470.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 478.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 474.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 446.5857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 427.8047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 409.6501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 23 | 2.0127 | 0 | 2.0127 | 11 | 4.5734 | 0.77398 | 0.77398 | 413.5582 | 2.0127 | 0 | 810.2233 | 0 | 0 | 0 | 2.0127 | 0 | 0 | 810.2233
4 | 12 | 0 | 12.7063 | 0 | 12.7063 | 11 | 3.8373 | 4.303 | 4.303 | 418.5911 | 12.7063 | 0 | 5178.9583 | 0 | 0 | 0 | 12.7063 | 0 | 0 | 5178.9583
4 | 12 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 424.6399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 437.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 447.9279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 473.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 5 | 0.3975 | 0 | 0.3975 | 11 | 4.0351 | 0.13908 | 0.13908 | 473.3637 | 0.3975 | 0 | 183.7896 | 0 | 0 | 0 | 0.3975 | 0 | 0 | 183.7896
4 | 12 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 476.9785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 479.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 8 | 0 | 3.1625 | 3.1625 | 48 | 6.5729 | 1.9246 | 1.9246 | 484.2169 | 3.1625 | 0 | 1379.5178 | 0 | 0 | 0 | 3.1625 | 0 | 0 | 1379.5178
4 | 12 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 483.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 10 | 0 | 0.011254 | 0.011254 | 48 | 8.4482 | 0.0151 | 0.0151 | 487.2369 | 0.011254 | 0 | 4.9433 | 0 | 0 | 0 | 0.011254 | 0 | 0 | 4.9433
4 | 12 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 484.9435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 476.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 471.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 471.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 474.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 470.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 471.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 486.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 483.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 465.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 447.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 440.3779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 23 | 6.0162 | 0 | 6.0162 | 11 | 4.5599 | 2.3078 | 2.3078 | 437.0631 | 6.0162 | 0 | 2563.2977 | 0 | 0 | 0 | 6.0162 | 0 | 0 | 2563.2977
4 | 13 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 433.6419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 1 | 17.585 | 0 | 17.585 | 11 | 4.2072 | 6.3352 | 6.3352 | 443.6356 | 17.585 | 0 | 7607.9025 | 0 | 0 | 0 | 17.585 | 0 | 0 | 7607.9025
4 | 13 | 2 | 13.526 | 0 | 13.526 | 11 | 4.147 | 4.8228 | 4.8228 | 450.6472 | 13.526 | 0 | 5946.6667 | 0 | 0 | 0 | 13.526 | 0 | 0 | 5946.6667
4 | 13 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 461.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 474.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 5 | 0.23417 | 0 | 0.23417 | 11 | 3.9663 | 0.080996 | 0.080996 | 477.684 | 0.23417 | 0 | 109.2818 | 0 | 0 | 0 | 0.23417 | 0 | 0 | 109.2818
4 | 13 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 481.3613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 478.6075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 8 | 11.765 | 0 | 11.765 | 11 | 5.4889 | 5.4414 | 5.4414 | 482.1502 | 11.765 | 0 | 5543.1014 | 0 | 0 | 0 | 11.765 | 0 | 0 | 5543.1014
4 | 13 | 9 | 12.9733 | 41.5812 | 54.5545 | 39.2012 | 6.9858 | 37.7412 | 37.7412 | 487.3863 | 54.5545 | 0 | 24450.5326 | 0 | 0 | 0 | 54.5545 | 0 | 0 | 24450.5326
4 | 13 | 10 | 0.88399 | 3.8437 | 4.7277 | 41.0818 | 7.3471 | 3.7153 | 3.7153 | 491.2606 | 4.7277 | 0 | 2128.3279 | 0 | 0 | 0 | 4.7277 | 0 | 0 | 2128.3279
4 | 13 | 11 | 0 | 36.8142 | 36.8142 | 48 | 8.9643 | 73.8914 | 73.8914 | 488.6602 | 36.8142 | 0 | 16222.5598 | 0 | 0 | 0 | 36.8142 | 0 | 0 | 16222.5598
4 | 13 | 12 | 0 | 163.9677 | 163.9677 | 48 | 8.2847 | 199.0898 | 199.0898 | 485.8668 | 163.9677 | 0 | 71795.9967 | 0 | 0 | 0 | 163.9677 | 0 | 0 | 71795.9967
4 | 13 | 13 | 0 | 98.8982 | 98.8982 | 48 | 7.8202 | 94.55 | 94.55 | 484.0303 | 98.8982 | 0 | 43122.6033 | 0 | 0 | 0 | 98.8982 | 0 | 0 | 43122.6033
4 | 13 | 14 | 27.167 | 137.9808 | 165.1478 | 41.9135 | 7.6568 | 146.8971 | 146.8971 | 484.7036 | 165.1478 | 0 | 73125.8289 | 0 | 0 | 0 | 165.1478 | 0 | 0 | 73125.8289
4 | 13 | 15 | 43.8468 | 244.3567 | 288.2035 | 42.3709 | 7.7256 | 264.0937 | 264.0937 | 485.7586 | 288.2035 | 0 | 127785.8888 | 0 | 0 | 0 | 288.2035 | 0 | 0 | 127785.8888
4 | 13 | 16 | 50.8115 | 128.1856 | 178.9971 | 37.4969 | 7.3729 | 142.0439 | 142.0439 | 478.5221 | 178.9971 | 0 | 78942.2389 | 0 | 0 | 0 | 178.9971 | 0 | 0 | 78942.2389
4 | 13 | 17 | 66.4325 | 48.5871 | 115.0196 | 26.6297 | 7.5449 | 97.6578 | 97.6578 | 473.2333 | 115.0196 | 0 | 51368.1914 | 0 | 0 | 0 | 115.0196 | 0 | 0 | 51368.1914
4 | 13 | 18 | 0.68917 | 0 | 0.68917 | 11 | 7.0804 | 0.4922 | 0.4922 | 479.6123 | 0.68917 | 0 | 322.952 | 0 | 0 | 0 | 0.68917 | 0 | 0 | 322.952
4 | 13 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 464.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 443.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 438.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 421.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 23 | 41.6176 | 0 | 41.6176 | 11 | 4.5954 | 16.0692 | 16.0692 | 430.5092 | 41.6176 | 0 | 17458.9765 | 0 | 0 | 0 | 41.6176 | 0 | 0 | 17458.9765
4 | 14 | 0 | 57.8345 | 0 | 57.8345 | 11 | 3.8459 | 19.6132 | 19.6132 | 439.0153 | 57.8345 | 0 | 24754.0658 | 0 | 0 | 0 | 57.8345 | 0 | 0 | 24754.0658
4 | 14 | 1 | 73.0922 | 0 | 73.0922 | 11 | 3.4243 | 23.1997 | 23.1997 | 449.3808 | 73.0922 | 0 | 32042.2331 | 0 | 0 | 0 | 73.0922 | 0 | 0 | 32042.2331
4 | 14 | 2 | 105.9498 | 0 | 105.9498 | 11 | 3.3383 | 33.1948 | 33.1948 | 466.5805 | 105.9498 | 0 | 48268.6544 | 0 | 0 | 0 | 105.9498 | 0 | 0 | 48268.6544
4 | 14 | 3 | 132.37 | 0 | 132.37 | 11 | 3.3039 | 41.2595 | 41.2595 | 464.6958 | 132.37 | 0 | 60055.7115 | 0 | 0 | 0 | 132.37 | 0 | 0 | 60055.7115
4 | 14 | 4 | 118.2347 | 0 | 118.2347 | 11 | 3.2609 | 36.6185 | 36.6185 | 477.3856 | 118.2347 | 0 | 55142.9632 | 0 | 0 | 0 | 118.2347 | 0 | 0 | 55142.9632
4 | 14 | 5 | 1.0375 | 0 | 1.0375 | 11 | 3.4071 | 0.32845 | 0.32845 | 485.697 | 1.0375 | 0 | 492.4982 | 0 | 0 | 0 | 1.0375 | 0 | 0 | 492.4982
4 | 14 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 491.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 489.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 489.4501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 9 | 40.4966 | 366.9641 | 407.4608 | 44.3226 | 7.6998 | 369.1944 | 288 | 482.6854 | 317.8507 | 89.61 | 139333.9101 | 8.9565 | 0 | 0 | 317.8507 | 89.61 | 0 | 139333.9101
4 | 14 | 10 | 19.2961 | 473.4001 | 492.6961 | 46.5509 | 7.8632 | 480.4936 | 288 | 480.7402 | 295.314 | 197.3821 | 128222.1613 | 19.7284 | 0 | 0 | 295.314 | 197.3821 | 0 | 128222.1613
4 | 14 | 11 | 13.9242 | 393.334 | 407.2582 | 46.735 | 7.6051 | 354.4604 | 288 | 487.1225 | 330.8983 | 76.3599 | 145723.5076 | 7.6322 | 0 | 0 | 330.8983 | 76.3599 | 0 | 145723.5076
4 | 14 | 12 | 22.6293 | 91.6894 | 114.3187 | 40.6759 | 8.2589 | 136.7543 | 136.7543 | 479.1902 | 114.3187 | 0 | 50130.3913 | 0 | 0 | 0 | 114.3187 | 0 | 0 | 50130.3913
4 | 14 | 13 | 44.6185 | 205.1683 | 249.7868 | 41.3908 | 8.5686 | 363.2342 | 288 | 475.5195 | 198.0502 | 51.7366 | 85979.2573 | 5.1711 | 0 | 0 | 198.0502 | 51.7366 | 0 | 85979.2573
4 | 14 | 14 | 8.7174 | 281.5926 | 290.3099 | 46.889 | 8.6374 | 443.407 | 288 | 469.3385 | 188.561 | 101.7489 | 79657.4963 | 10.1698 | 0 | 0 | 188.561 | 101.7489 | 0 | 79657.4963
4 | 14 | 15 | 34.9367 | 556.8761 | 591.8128 | 45.8158 | 7.803 | 561.372 | 288 | 470.3539 | 303.617 | 288.1958 | 128896.9962 | 28.8052 | 0 | 0 | 303.617 | 288.1958 | 0 | 128896.9962
4 | 14 | 16 | 29.4783 | 98.5353 | 128.0137 | 39.4798 | 7.6998 | 115.9913 | 115.9913 | 465.2433 | 128.0137 | 0 | 54503.548 | 0 | 0 | 0 | 128.0137 | 0 | 0 | 54503.548
4 | 14 | 17 | 59.2947 | 121.3089 | 180.6036 | 35.8524 | 7.6482 | 160.0586 | 160.0586 | 469.4216 | 180.6036 | 0 | 78304.1672 | 0 | 0 | 0 | 180.6036 | 0 | 0 | 78304.1672
4 | 14 | 18 | 0.88833 | 0 | 0.88833 | 11 | 7.3041 | 0.68698 | 0.68698 | 476.7842 | 0.88833 | 0 | 413.7717 | 0 | 0 | 0 | 0.88833 | 0 | 0 | 413.7717
4 | 14 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 467.8273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 442.7631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 427.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 415.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 421.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 420.1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 1 | 1.4756 | 0 | 1.4756 | 11 | 3.7598 | 0.49354 | 0.49354 | 428.2011 | 1.4756 | 0 | 615.6403 | 0 | 0 | 0 | 1.4756 | 0 | 0 | 615.6403
4 | 15 | 2 | 27.444 | 0 | 27.444 | 11 | 3.691 | 9.0787 | 9.0787 | 441.8087 | 27.444 | 0 | 11823.1276 | 0 | 0 | 0 | 27.444 | 0 | 0 | 11823.1276
4 | 15 | 3 | 10.5942 | 0 | 10.5942 | 11 | 3.6824 | 3.4999 | 3.4999 | 446.2302 | 10.5942 | 0 | 4610.9006 | 0 | 0 | 0 | 10.5942 | 0 | 0 | 4610.9006
4 | 15 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 460.0511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 5 | 11.6596 | 0 | 11.6596 | 11 | 3.691 | 3.8571 | 3.8571 | 466.8415 | 11.6596 | 0 | 5314.9384 | 0 | 0 | 0 | 11.6596 | 0 | 0 | 5314.9384
4 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 477.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 479.7711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 483.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 483.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 10 | 31.867 | 11.6686 | 43.5355 | 20.9169 | 7.4159 | 35.1217 | 35.1217 | 485.8782 | 43.5355 | 0 | 20242.3398 | 0 | 0 | 0 | 43.5355 | 0 | 0 | 20242.3398
4 | 15 | 11 | 47.7484 | 177.463 | 225.2114 | 40.1554 | 7.5879 | 194.6193 | 194.6193 | 488.4626 | 225.2114 | 0 | 100963.912 | 0 | 0 | 0 | 225.2114 | 0 | 0 | 100963.912
4 | 15 | 12 | 39.6504 | 45.279 | 84.9294 | 30.7261 | 8.3192 | 105.2263 | 105.2263 | 486.6485 | 84.9294 | 0 | 38721.2212 | 0 | 0 | 0 | 84.9294 | 0 | 0 | 38721.2212
4 | 15 | 13 | 24.9967 | 77.4452 | 102.4418 | 38.9717 | 8.6546 | 158.4589 | 158.4589 | 483.8604 | 102.4418 | 0 | 45575.2133 | 0 | 0 | 0 | 102.4418 | 0 | 0 | 45575.2133
4 | 15 | 14 | 13.5619 | 36.4097 | 49.9716 | 37.9585 | 8.9299 | 97.0897 | 97.0897 | 479.2046 | 49.9716 | 0 | 22049.7611 | 0 | 0 | 0 | 49.9716 | 0 | 0 | 22049.7611
4 | 15 | 15 | 9.5826 | 164.2968 | 173.8793 | 45.9609 | 8.8009 | 301.6261 | 288 | 470.0525 | 166.0243 | 7.8551 | 70409.4901 | 0.78512 | 0 | 0 | 166.0243 | 7.8551 | 0 | 70409.4901
4 | 15 | 16 | 1.097 | 0.75329 | 1.8503 | 26.0631 | 9.5837 | 9.1744 | 9.1744 | 452.3277 | 1.8503 | 0 | 788.7323 | 0 | 0 | 0 | 1.8503 | 0 | 0 | 788.7323
4 | 15 | 17 | 92.1976 | 0 | 92.1976 | 11 | 9.0762 | 207.3352 | 207.3352 | 450.1949 | 92.1976 | 0 | 40492.7413 | 0 | 0 | 0 | 92.1976 | 0 | 0 | 40492.7413
4 | 15 | 18 | 49.3208 | 0 | 49.3208 | 11 | 9.4461 | 184.3207 | 184.3207 | 455.9844 | 49.3208 | 0 | 21946.9705 | 0 | 0 | 0 | 49.3208 | 0 | 0 | 21946.9705
4 | 15 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 455.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 437.9894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 415.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 404.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 406.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 0 | 0.39333 | 0 | 0.39333 | 11 | 3.3125 | 0.12276 | 0.12276 | 406.1091 | 0.39333 | 0 | 155.4096 | 0 | 0 | 0 | 0.39333 | 0 | 0 | 155.4096
4 | 16 | 1 | 50.3049 | 0 | 50.3049 | 11 | 3.2007 | 15.4421 | 15.4421 | 409.9252 | 50.3049 | 0 | 20067.8887 | 0 | 0 | 0 | 50.3049 | 0 | 0 | 20067.8887
4 | 16 | 2 | 16.8897 | 0 | 16.8897 | 11 | 3.1921 | 5.1781 | 5.1781 | 423.13 | 16.8897 | 0 | 6960.7331 | 0 | 0 | 0 | 16.8897 | 0 | 0 | 6960.7331
4 | 16 | 3 | 9.5217 | 0 | 9.5217 | 11 | 3.3297 | 2.9794 | 2.9794 | 432.245 | 9.5217 | 0 | 4010.954 | 0 | 0 | 0 | 9.5217 | 0 | 0 | 4010.954
4 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 433.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 5 | 9.9587 | 0 | 9.9587 | 11 | 3.7857 | 3.3445 | 3.3445 | 445.6025 | 9.9587 | 0 | 4328.0664 | 0 | 0 | 0 | 9.9587 | 0 | 0 | 4328.0664
4 | 16 | 6 | 18.2662 | 0 | 18.2662 | 11 | 4.5255 | 6.9628 | 6.9628 | 451.8 | 18.2662 | 0 | 8051.749 | 0 | 0 | 0 | 18.2662 | 0 | 0 | 8051.749
4 | 16 | 7 | 0.36917 | 0 | 0.36917 | 11 | 5.2137 | 0.16093 | 0.16093 | 455.0287 | 0.36917 | 0 | 163.9206 | 0 | 0 | 0 | 0.36917 | 0 | 0 | 163.9206
4 | 16 | 8 | 11.5452 | 279.5952 | 291.1404 | 46.5328 | 5.1879 | 126.2388 | 126.2388 | 462.3115 | 291.1404 | 0 | 121049.9867 | 0 | 0 | 0 | 291.1404 | 0 | 0 | 121049.9867
4 | 16 | 9 | 6.2674 | 510.7769 | 517.0443 | 47.5515 | 6.7449 | 331.267 | 288 | 464.4013 | 449.5128 | 67.5315 | 187379.3085 | 6.7498 | 0 | 0 | 449.5128 | 67.5315 | 0 | 187379.3085
4 | 16 | 10 | 42.5746 | 486.0927 | 528.6673 | 45.0203 | 8.8783 | 980.0915 | 288 | 454.247 | 155.349 | 373.3184 | 63572.9316 | 37.3133 | 0 | 0 | 155.349 | 373.3184 | 0 | 63572.9316
4 | 16 | 11 | 37.6781 | 358.3921 | 396.0702 | 44.4802 | 9.8676 | 6021.8636 | 288 | 448.863 | 18.9423 | 377.1278 | 7659.959 | 37.694 | 0 | 0 | 18.9423 | 377.1278 | 0 | 7659.959
4 | 16 | 12 | 85.5717 | 192.0989 | 277.6706 | 36.5974 | 10.2547 | 0 | 0 | 454.568 | 0 | 277.6706 | 0 | 27.7533 | 0 | 0 | 0 | 277.6706 | 0 | 0
4 | 16 | 13 | 58.9352 | 6.4344 | 65.3696 | 14.6419 | 10.031 | 0 | 0 | 462.297 | 0 | 65.3696 | 0 | 6.5337 | 0 | 0 | 0 | 65.3696 | 0 | 0
4 | 16 | 14 | 23.6001 | 70.2263 | 93.8264 | 38.6934 | 9.9364 | 2858.5073 | 288 | 462.2755 | 9.4532 | 84.3732 | 4004.2009 | 8.4331 | 0 | 0 | 9.4532 | 84.3732 | 0 | 4004.2009
4 | 16 | 15 | 12.0183 | 227.2806 | 239.2989 | 46.1417 | 11.1494 | 0 | 0 | 464.1087 | 0 | 239.2989 | 0 | 23.918 | 0 | 0 | 0 | 239.2989 | 0 | 0
4 | 16 | 16 | 3.6072 | 0 | 3.6072 | 11 | 12.5086 | 0 | 0 | 454.9496 | 0 | 3.6072 | 0 | 0.36054 | 0 | 0 | 0 | 3.6072 | 0 | 0
4 | 16 | 17 | 0.79996 | 1.3242 | 2.1241 | 34.0656 | 12.2591 | 0 | 0 | 439.567 | 0 | 2.1241 | 0 | 0.21231 | 0 | 0 | 0 | 2.1241 | 0 | 0
4 | 16 | 18 | 0.17833 | 0 | 0.17833 | 11 | 12.801 | 0 | 0 | 455.4306 | 0 | 0.17833 | 0 | 0.017824 | 0 | 0 | 0 | 0.17833 | 0 | 0
4 | 16 | 19 | 0 | 0.041667 | 0.041667 | 48 | 12.7322 | 0 | 0 | 449.8424 | 0 | 0.041667 | 0 | 0.0041646 | 0 | 0 | 0 | 0.041667 | 0 | 0
4 | 16 | 20 | 5.4489 | 0 | 5.4489 | 11 | 13.3172 | 0 | 0 | 433.868 | 0 | 5.4489 | 0 | 0.54462 | 0 | 0 | 0 | 5.4489 | 0 | 0
4 | 16 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 410.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 391.082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 23 | 17.1725 | 0 | 17.1725 | 11 | 3.6704 | 5.6624 | 5.6624 | 388.8836 | 17.1725 | 0 | 6489.221 | 0 | 0 | 0 | 17.1725 | 0 | 0 | 6489.221
4 | 17 | 0 | 6.0867 | 0 | 6.0867 | 11 | 3.5706 | 1.9758 | 1.9758 | 389.884 | 6.0867 | 0 | 2306.1409 | 0 | 0 | 0 | 6.0867 | 0 | 0 | 2306.1409
4 | 17 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 390.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 403.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 413.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 405.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 419.7984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 433.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 7 | 6.9718 | 0 | 6.9718 | 11 | 5.1706 | 3.0122 | 3.0122 | 435.6704 | 6.9718 | 0 | 2960.7301 | 0 | 0 | 0 | 6.9718 | 0 | 0 | 2960.7301
4 | 17 | 8 | 15.6317 | 238.3693 | 254.0009 | 45.723 | 5.8502 | 127.694 | 127.694 | 438.4442 | 254.0009 | 0 | 99751.5649 | 0 | 0 | 0 | 254.0009 | 0 | 0 | 99751.5649
4 | 17 | 9 | 17.0392 | 440.395 | 457.4342 | 46.6218 | 6.7707 | 295.4137 | 288 | 441.1344 | 445.9543 | 11.4798 | 175934.6131 | 1.1474 | 0 | 0 | 445.9543 | 11.4798 | 0 | 175934.6131
4 | 17 | 10 | 12.1875 | 327.6977 | 339.8852 | 46.6733 | 8.9987 | 705.5274 | 288 | 449.27 | 138.7429 | 201.1423 | 55857.4551 | 20.1042 | 0 | 0 | 138.7429 | 201.1423 | 0 | 55857.4551
4 | 17 | 11 | 0.705 | 134.3374 | 135.0424 | 47.8068 | 10.0569 | 0 | 0 | 453.1283 | 0 | 135.0424 | 0 | 13.4975 | 0 | 0 | 0 | 135.0424 | 0 | 0
4 | 17 | 12 | 0 | 0.65033 | 0.65033 | 48 | 10.1343 | 0 | 0 | 451.1293 | 0 | 0.65033 | 0 | 0.065001 | 0 | 0 | 0 | 0.65033 | 0 | 0
4 | 17 | 13 | 2.0027 | 0 | 2.0027 | 11 | 10.2117 | 0 | 0 | 453.8847 | 0 | 2.0027 | 0 | 0.20017 | 0 | 0 | 0 | 2.0027 | 0 | 0
4 | 17 | 14 | 6.8803 | 11.5557 | 18.4361 | 34.1916 | 9.8762 | 299.0278 | 288 | 461.7645 | 17.7562 | 0.6799 | 7592.0687 | 0.067956 | 0 | 0 | 17.7562 | 0.6799 | 0 | 7592.0687
4 | 17 | 15 | 0.31583 | 0 | 0.31583 | 11 | 10.9601 | 0 | 0 | 461.7994 | 0 | 0.31583 | 0 | 0.031568 | 0 | 0 | 0 | 0.31583 | 0 | 0
4 | 17 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 462.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 17 | 0.965 | 0 | 0.965 | 11 | 11.5451 | 0 | 0 | 453.4853 | 0 | 0.965 | 0 | 0.096452 | 0 | 0 | 0 | 0.965 | 0 | 0
4 | 17 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 468.8305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 19 | 0.060138 | 0 | 0.060138 | 11 | 13.1107 | 0 | 0 | 466.0543 | 0 | 0.060138 | 0 | 0.0060108 | 0 | 0 | 0 | 0.060138 | 0 | 0
4 | 17 | 20 | 4.9964 | 0 | 4.9964 | 11 | 12.6978 | 0 | 0 | 455.2989 | 0 | 4.9964 | 0 | 0.49939 | 0 | 0 | 0 | 4.9964 | 0 | 0
4 | 17 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 427.8227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 413.9919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 23 | 8.0459 | 0 | 8.0459 | 11 | 4.6373 | 3.1309 | 3.1309 | 413.0282 | 8.0459 | 0 | 3234.6776 | 0 | 0 | 0 | 8.0459 | 0 | 0 | 3234.6776
4 | 18 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 417.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 414.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 436.3164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 459.3772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 480.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 479.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 485.2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 7 | 6.6234 | 146.6084 | 153.2318 | 46.4007 | 5.6008 | 72.6708 | 72.6708 | 485.7601 | 153.2318 | 0 | 67323.8467 | 0 | 0 | 0 | 153.2318 | 0 | 0 | 67323.8467
4 | 18 | 8 | 91.6807 | 620.4749 | 712.1557 | 43.2367 | 6.5729 | 433.4011 | 288 | 483.6519 | 473.2357 | 238.92 | 208420.1447 | 23.8801 | 0 | 0 | 473.2357 | 238.92 | 0 | 208420.1447
4 | 18 | 9 | 109.6732 | 877.5591 | 987.2322 | 43.8896 | 7.7084 | 897.8676 | 288 | 477.4847 | 316.6646 | 670.5676 | 137304.2275 | 67.0234 | 0 | 0 | 316.6646 | 670.5676 | 0 | 137304.2275
4 | 18 | 10 | 187.5998 | 927.4462 | 1115.046 | 41.775 | 8.9471 | 2201.6571 | 288 | 479.1155 | 145.8598 | 969.1862 | 63790.3973 | 96.8704 | 0 | 0 | 145.8598 | 969.1862 | 0 | 63790.3973
4 | 18 | 11 | 5.7844 | 612.7061 | 618.4905 | 47.654 | 9.5923 | 3130.5535 | 288 | 476.7155 | 56.899 | 561.5915 | 24413.1565 | 56.1312 | 0 | 0 | 56.899 | 561.5915 | 0 | 24413.1565
4 | 18 | 12 | 15.8547 | 344.6368 | 360.4915 | 46.3727 | 10.2891 | 0 | 0 | 473.4997 | 0 | 360.4915 | 0 | 36.0312 | 0 | 0 | 0 | 360.4915 | 0 | 0
4 | 18 | 13 | 4.06 | 190.8901 | 194.9501 | 47.2294 | 10.0827 | 0 | 0 | 471.8401 | 0 | 194.9501 | 0 | 19.4853 | 0 | 0 | 0 | 194.9501 | 0 | 0
4 | 18 | 14 | 2.0933 | 103.3758 | 105.4691 | 47.2656 | 10.6934 | 0 | 0 | 476.2115 | 0 | 105.4691 | 0 | 10.5417 | 0 | 0 | 0 | 105.4691 | 0 | 0
4 | 18 | 15 | 0.16417 | 20.3525 | 20.5167 | 47.7039 | 11.6655 | 0 | 0 | 483.1598 | 0 | 20.5167 | 0 | 2.0506 | 0 | 0 | 0 | 20.5167 | 0 | 0
4 | 18 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 486.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 478.6212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 490.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 485.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 20 | 7.969 | 0 | 7.969 | 11 | 12.6806 | 0 | 0 | 470.9479 | 0 | 7.969 | 0 | 0.7965 | 0 | 0 | 0 | 7.969 | 0 | 0
4 | 18 | 21 | 0.41863 | 0 | 0.41863 | 11 | 10.3235 | 0 | 0 | 442.8008 | 0 | 0.41863 | 0 | 0.041842 | 0 | 0 | 0 | 0.41863 | 0 | 0
4 | 18 | 22 | 11.307 | 0 | 11.307 | 11 | 5.6868 | 5.4692 | 5.4692 | 417.858 | 11.307 | 0 | 4600.3328 | 0 | 0 | 0 | 11.307 | 0 | 0 | 4600.3328
4 | 18 | 23 | 0.85402 | 0 | 0.85402 | 11 | 4.5734 | 0.32841 | 0.32841 | 401.8047 | 0.85402 | 0 | 333.7541 | 0 | 0 | 0 | 0.85402 | 0 | 0 | 333.7541
4 | 19 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 397.3211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 403.2532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 418.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 3 | 0.53583 | 0 | 0.53583 | 11 | 3.4416 | 0.17052 | 0.17052 | 442.8778 | 0.53583 | 0 | 231.4145 | 0 | 0 | 0 | 0.53583 | 0 | 0 | 231.4145
4 | 19 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 461.8257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 5 | 1.175 | 0 | 1.175 | 11 | 4.0351 | 0.4111 | 0.4111 | 477.1093 | 1.175 | 0 | 547.6784 | 0 | 0 | 0 | 1.175 | 0 | 0 | 547.6784
4 | 19 | 6 | 5.0682 | 0 | 5.0682 | 11 | 5.1793 | 2.1937 | 2.1937 | 482.8794 | 5.0682 | 0 | 2391.5974 | 0 | 0 | 0 | 5.0682 | 0 | 0 | 2391.5974
4 | 19 | 7 | 0.63256 | 0 | 0.63256 | 11 | 5.3599 | 0.28444 | 0.28444 | 479.3698 | 0.63256 | 0 | 296.2716 | 0 | 0 | 0 | 0.63256 | 0 | 0 | 296.2716
4 | 19 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 478.5866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 480.3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 10 | 0.0083333 | 6.0867 | 6.095 | 47.9494 | 8.4482 | 8.1775 | 8.1775 | 481.0068 | 6.095 | 0 | 2639.485 | 0 | 0 | 0 | 6.095 | 0 | 0 | 2639.485
4 | 19 | 11 | 0 | 9.7425 | 9.7425 | 48 | 9.7214 | 71.7481 | 71.7481 | 476.4234 | 9.7425 | 0 | 4173.9153 | 0 | 0 | 0 | 9.7425 | 0 | 0 | 4173.9153
4 | 19 | 12 | 0 | 10.7842 | 10.7842 | 48 | 9.4117 | 37.965 | 37.965 | 473.0327 | 10.7842 | 0 | 4583.6236 | 0 | 0 | 0 | 10.7842 | 0 | 0 | 4583.6236
4 | 19 | 13 | 0 | 9.2596 | 9.2596 | 48 | 8.8869 | 17.2983 | 17.2983 | 470.9973 | 9.2596 | 0 | 3916.7791 | 0 | 0 | 0 | 9.2596 | 0 | 0 | 3916.7791
4 | 19 | 14 | 0 | 13.027 | 13.027 | 48 | 9.3428 | 41.0942 | 41.0942 | 468.9546 | 13.027 | 0 | 5483.786 | 0 | 0 | 0 | 13.027 | 0 | 0 | 5483.786
4 | 19 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 479.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 468.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 466.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 475.3703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 472.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 449.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 425.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 399.7066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 381.3473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 375.5945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 378.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 2 | 7.5258 | 0 | 7.5258 | 11 | 4.147 | 2.6834 | 2.6834 | 393.4172 | 7.5258 | 0 | 2878.0078 | 0 | 0 | 0 | 7.5258 | 0 | 0 | 2878.0078
4 | 20 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 406.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 444.4177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 5 | 36.8736 | 0 | 36.8736 | 11 | 3.9663 | 12.7542 | 12.7542 | 458.8929 | 36.8736 | 0 | 16515.4375 | 0 | 0 | 0 | 36.8736 | 0 | 0 | 16515.4375
4 | 20 | 6 | 8.4967 | 0.028292 | 8.525 | 11.1228 | 4.7319 | 3.3768 | 3.3768 | 469.8317 | 8.525 | 0 | 3910.4739 | 0 | 0 | 0 | 8.525 | 0 | 0 | 3910.4739
4 | 20 | 7 | 1.1692 | 0.76418 | 1.9333 | 25.6247 | 4.99 | 0.80523 | 0.80523 | 470.1621 | 1.9333 | 0 | 859.4457 | 0 | 0 | 0 | 1.9333 | 0 | 0 | 859.4457
4 | 20 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 476.0009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 9 | 0 | 100.5128 | 100.5128 | 48 | 6.9858 | 69.5355 | 69.5355 | 479.9354 | 100.5128 | 0 | 43415.0498 | 0 | 0 | 0 | 100.5128 | 0 | 0 | 43415.0498
4 | 20 | 10 | 0.1725 | 30.7568 | 30.9293 | 47.7936 | 7.3471 | 24.3057 | 24.3057 | 483.9177 | 30.9293 | 0 | 13489.0064 | 0 | 0 | 0 | 30.9293 | 0 | 0 | 13489.0064
4 | 20 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 483.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 479.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 484.4018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 487.2625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 488.0221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 481.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 474.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 18 | 0 | 14.5804 | 14.5804 | 48 | 7.0804 | 10.4132 | 10.4132 | 472.9409 | 14.5804 | 0 | 6195.8109 | 0 | 0 | 0 | 14.5804 | 0 | 0 | 6195.8109
4 | 20 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 461.4465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 452.8179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 431.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 417.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 405.7888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 403.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 409.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 439.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 3 | 0.78987 | 0 | 0.78987 | 11 | 3.3039 | 0.2462 | 0.2462 | 457.5616 | 0.78987 | 0 | 352.7241 | 0 | 0 | 0 | 0.78987 | 0 | 0 | 352.7241
4 | 21 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 473.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 486.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 492.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 493.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 8 | 0.14583 | 0 | 0.14583 | 11 | 7.2524 | 0.11066 | 0.11066 | 493.5927 | 0.14583 | 0 | 70.3781 | 0 | 0 | 0 | 0.14583 | 0 | 0 | 70.3781
4 | 21 | 9 | 0 | 0.46969 | 0.46969 | 48 | 7.6998 | 0.42558 | 0.42558 | 491.365 | 0.46969 | 0 | 208.2453 | 0 | 0 | 0 | 0.46969 | 0 | 0 | 208.2453
4 | 21 | 10 | 0 | 0.025446 | 0.025446 | 48 | 7.8632 | 0.024816 | 0.024816 | 492.9307 | 0.025446 | 0 | 11.3217 | 0 | 0 | 0 | 0.025446 | 0 | 0 | 11.3217
4 | 21 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 492.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 484.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 482.3092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 483.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 486.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 485.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 480.4289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 486.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 494.4022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 484.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 448.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 428.9024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 418.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 0 | 33.6508 | 0 | 33.6508 | 11 | 3.9749 | 11.656 | 11.656 | 413.9089 | 33.6508 | 0 | 13558.1969 | 0 | 0 | 0 | 33.6508 | 0 | 0 | 13558.1969
4 | 22 | 1 | 30.3385 | 0 | 30.3385 | 11 | 3.7598 | 10.1468 | 10.1468 | 416.0111 | 30.3385 | 0 | 12287.4444 | 0 | 0 | 0 | 30.3385 | 0 | 0 | 12287.4444
4 | 22 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 435.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 456.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 471.6269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 5 | 12.7055 | 0 | 12.7055 | 11 | 3.691 | 4.2031 | 4.2031 | 479.0365 | 12.7055 | 0 | 5946.6222 | 0 | 0 | 0 | 12.7055 | 0 | 0 | 5946.6222
4 | 22 | 6 | 0.30081 | 0 | 0.30081 | 11 | 4.8007 | 0.12073 | 0.12073 | 484.652 | 0.30081 | 0 | 142.4812 | 0 | 0 | 0 | 0.30081 | 0 | 0 | 142.4812
4 | 22 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 486.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 476.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 477.1052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 478.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 487.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 483.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 480.9279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 475.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 469.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 465.2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 464.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 475.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 19 | 0 | 0.026667 | 0.026667 | 48 | 8.0611 | 0.028653 | 0.028653 | 467.8763 | 0.026667 | 0 | 11.1967 | 0 | 0 | 0 | 0.026667 | 0 | 0 | 11.1967
4 | 22 | 20 | 0.033333 | 0 | 0.033333 | 11 | 11.2698 | 0 | 0 | 461.9116 | 0 | 0.033333 | 0 | 0.0033317 | 0 | 0 | 0 | 0.033333 | 0 | 0
4 | 22 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 438.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 427.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 414.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 401.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 401.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 409.2554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 3 | 1.8393 | 0 | 1.8393 | 11 | 3.3297 | 0.57552 | 0.57552 | 421.6469 | 1.8393 | 0 | 755.299 | 0 | 0 | 0 | 1.8393 | 0 | 0 | 755.299
4 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 415.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 5 | 3.3261 | 0 | 3.3261 | 11 | 3.7857 | 1.1171 | 1.1171 | 445.1532 | 3.3261 | 0 | 1444.0518 | 0 | 0 | 0 | 3.3261 | 0 | 0 | 1444.0518
4 | 23 | 6 | 22.4192 | 0 | 22.4192 | 11 | 4.5255 | 8.5459 | 8.5459 | 462.1078 | 22.4192 | 0 | 10113.4759 | 0 | 0 | 0 | 22.4192 | 0 | 0 | 10113.4759
4 | 23 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 471.452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 8 | 0.18667 | 4.1054 | 4.2921 | 46.3908 | 5.1879 | 1.861 | 1.861 | 472.166 | 4.2921 | 0 | 1827.4536 | 0 | 0 | 0 | 4.2921 | 0 | 0 | 1827.4536
4 | 23 | 9 | 0 | 5.0275 | 5.0275 | 48 | 6.7449 | 3.2211 | 3.2211 | 476.0642 | 5.0275 | 0 | 2152.1142 | 0 | 0 | 0 | 5.0275 | 0 | 0 | 2152.1142
4 | 23 | 10 | 0.02 | 0 | 0.02 | 11 | 8.8783 | 0.037078 | 0.037078 | 461.4695 | 0.02 | 0 | 9.0094 | 0 | 0 | 0 | 0.02 | 0 | 0 | 9.0094
4 | 23 | 11 | 86.2103 | 0.0070417 | 86.2173 | 11.003 | 9.8676 | 1310.8507 | 288 | 459.8178 | 18.9423 | 67.275 | 8501.6033 | 6.7242 | 0 | 0 | 18.9423 | 67.275 | 0 | 8501.6033
4 | 23 | 12 | 0.18521 | 0 | 0.18521 | 11 | 10.2547 | 0 | 0 | 458.3865 | 0 | 0.18521 | 0 | 0.018512 | 0 | 0 | 0 | 0.18521 | 0 | 0
4 | 23 | 13 | 102.4965 | 0 | 102.4965 | 11 | 10.031 | 0 | 0 | 459.2185 | 0 | 102.4965 | 0 | 10.2446 | 0 | 0 | 0 | 102.4965 | 0 | 0
4 | 23 | 14 | 37.0423 | 55.5461 | 92.5885 | 33.1972 | 9.9364 | 2820.792 | 288 | 461.4641 | 9.4532 | 83.1353 | 4048.4877 | 8.3094 | 0 | 0 | 9.4532 | 83.1353 | 0 | 4048.4877
4 | 23 | 15 | 47.9033 | 139.1678 | 187.0711 | 38.5254 | 11.1494 | 0 | 0 | 457.5762 | 0 | 187.0711 | 0 | 18.6978 | 0 | 0 | 0 | 187.0711 | 0 | 0
4 | 23 | 16 | 14.2796 | 43.6037 | 57.8833 | 38.8722 | 12.5086 | 0 | 0 | 452.384 | 0 | 57.8833 | 0 | 5.7854 | 0 | 0 | 0 | 57.8833 | 0 | 0
4 | 23 | 17 | 56.307 | 10.0123 | 66.3194 | 16.5859 | 12.2591 | 0 | 0 | 445.7746 | 0 | 66.3194 | 0 | 6.6286 | 0 | 0 | 0 | 66.3194 | 0 | 0
4 | 23 | 18 | 2.1384 | 0 | 2.1384 | 11 | 12.801 | 0 | 0 | 476.0087 | 0 | 2.1384 | 0 | 0.21373 | 0 | 0 | 0 | 2.1384 | 0 | 0
4 | 23 | 19 | 0.53044 | 0 | 0.53044 | 11 | 12.7322 | 0 | 0 | 454.154 | 0 | 0.53044 | 0 | 0.053018 | 0 | 0 | 0 | 0.53044 | 0 | 0
4 | 23 | 20 | 84.2394 | 0 | 84.2394 | 11 | 13.3172 | 0 | 0 | 441.7892 | 0 | 84.2394 | 0 | 8.4197 | 0 | 0 | 0 | 84.2394 | 0 | 0
4 | 23 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 423.2297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 401.1992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 23 | 4.1005 | 0 | 4.1005 | 11 | 3.6704 | 1.3521 | 1.3521 | 398.0768 | 4.1005 | 0 | 1587.2179 | 0 | 0 | 0 | 4.1005 | 0 | 0 | 1587.2179
4 | 24 | 0 | 6.8167 | 0 | 6.8167 | 11 | 3.5706 | 2.2128 | 2.2128 | 398.4244 | 6.8167 | 0 | 2640.9554 | 0 | 0 | 0 | 6.8167 | 0 | 0 | 2640.9554
4 | 24 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 401.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 407.3378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 3 | 17.1591 | 0 | 17.1591 | 11 | 3.4416 | 5.4606 | 5.4606 | 410.9732 | 17.1591 | 0 | 6863.198 | 0 | 0 | 0 | 17.1591 | 0 | 0 | 6863.198
4 | 24 | 4 | 1.0868 | 0 | 1.0868 | 11 | 3.691 | 0.35953 | 0.35953 | 422.1613 | 1.0868 | 0 | 446.858 | 0 | 0 | 0 | 1.0868 | 0 | 0 | 446.858
4 | 24 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 424.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 6 | 2.6935 | 0 | 2.6935 | 11 | 4.8093 | 1.0828 | 1.0828 | 436.9825 | 2.6935 | 0 | 1147.3716 | 0 | 0 | 0 | 2.6935 | 0 | 0 | 1147.3716
4 | 24 | 7 | 74.9378 | 194.7643 | 269.7021 | 37.7194 | 5.1706 | 116.527 | 116.527 | 440.6932 | 269.7021 | 0 | 108682.8978 | 0 | 0 | 0 | 269.7021 | 0 | 0 | 108682.8978
4 | 24 | 8 | 231.9722 | 835.2401 | 1067.2123 | 39.9576 | 5.8502 | 536.5199 | 288 | 447.8615 | 572.8718 | 494.3405 | 233676.6429 | 49.4095 | 0 | 0 | 572.8718 | 494.3405 | 0 | 233676.6429
4 | 24 | 9 | 568.0858 | 1351.4263 | 1919.5121 | 37.0497 | 6.7707 | 1239.6325 | 288 | 450.6837 | 445.9543 | 1473.5577 | 184461.8597 | 147.2825 | 0 | 0 | 445.9543 | 1473.5577 | 0 | 184461.8597
4 | 24 | 10 | 71.4333 | 856.0983 | 927.5316 | 45.1505 | 8.9987 | 1925.3528 | 288 | 449.7705 | 138.7429 | 788.7886 | 56138.1727 | 78.8396 | 0 | 0 | 138.7429 | 788.7886 | 0 | 56138.1727
4 | 24 | 11 | 0.75548 | 301.4077 | 302.1632 | 47.9075 | 10.0569 | 0 | 0 | 454.9771 | 0 | 302.1632 | 0 | 30.2013 | 0 | 0 | 0 | 302.1632 | 0 | 0
4 | 24 | 12 | 1.2815 | 40.8603 | 42.1418 | 46.8748 | 10.1343 | 0 | 0 | 454.4046 | 0 | 42.1418 | 0 | 4.2121 | 0 | 0 | 0 | 42.1418 | 0 | 0
4 | 24 | 13 | 0 | 319.5694 | 319.5694 | 48 | 10.2117 | 0 | 0 | 469.8493 | 0 | 319.5694 | 0 | 31.9411 | 0 | 0 | 0 | 319.5694 | 0 | 0
4 | 24 | 14 | 0 | 274.1414 | 274.1414 | 48 | 9.8762 | 4446.4876 | 288 | 471.0823 | 17.7562 | 256.3852 | 7512.3332 | 25.6258 | 0 | 0 | 17.7562 | 256.3852 | 0 | 7512.3332
4 | 24 | 15 | 0 | 455.2605 | 455.2605 | 48 | 10.9601 | 0 | 0 | 468.914 | 0 | 455.2605 | 0 | 45.5034 | 0 | 0 | 0 | 455.2605 | 0 | 0
4 | 24 | 16 | 0 | 190.5499 | 190.5499 | 48 | 11.5279 | 0 | 0 | 461.6529 | 0 | 190.5499 | 0 | 19.0455 | 0 | 0 | 0 | 190.5499 | 0 | 0
4 | 24 | 17 | 17.4764 | 181.891 | 199.3674 | 44.7566 | 11.5451 | 0 | 0 | 454.7419 | 0 | 199.3674 | 0 | 19.9268 | 0 | 0 | 0 | 199.3674 | 0 | 0
4 | 24 | 18 | 0.84863 | 0 | 0.84863 | 11 | 11.9236 | 0 | 0 | 477.2511 | 0 | 0.84863 | 0 | 0.084821 | 0 | 0 | 0 | 0.84863 | 0 | 0
4 | 24 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 461.6661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 440.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 21 | 0.43756 | 0 | 0.43756 | 11 | 9.8762 | 7.097 | 7.097 | 418.3962 | 0.43756 | 0 | 178.2593 | 0 | 0 | 0 | 0.43756 | 0 | 0 | 178.2593
4 | 24 | 22 | 7.8644 | 0 | 7.8644 | 11 | 6.1771 | 4.2913 | 4.2913 | 407.7521 | 7.8644 | 0 | 3120.2076 | 0 | 0 | 0 | 7.8644 | 0 | 0 | 3120.2076
4 | 24 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 406.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 0 | 57.7352 | 0 | 57.7352 | 11 | 3.9577 | 19.9415 | 19.9415 | 407.9479 | 57.7352 | 0 | 22917.8473 | 0 | 0 | 0 | 57.7352 | 0 | 0 | 22917.8473
4 | 25 | 1 | 29.5097 | 0 | 29.5097 | 11 | 3.6394 | 9.6829 | 9.6829 | 409.4331 | 29.5097 | 0 | 11757.6272 | 0 | 0 | 0 | 29.5097 | 0 | 0 | 11757.6272
4 | 25 | 2 | 8.8342 | 0 | 8.8342 | 11 | 3.5276 | 2.8487 | 2.8487 | 414.8186 | 8.8342 | 0 | 3567.4033 | 0 | 0 | 0 | 8.8342 | 0 | 0 | 3567.4033
4 | 25 | 3 | 38.515 | 0 | 38.515 | 11 | 3.562 | 12.4859 | 12.4859 | 432.9067 | 38.515 | 0 | 16249.759 | 0 | 0 | 0 | 38.515 | 0 | 0 | 16249.759
4 | 25 | 4 | 53.6773 | 0 | 53.6773 | 11 | 3.5878 | 17.4713 | 17.4713 | 461.1111 | 53.6773 | 0 | 24160.763 | 0 | 0 | 0 | 53.6773 | 0 | 0 | 24160.763
4 | 25 | 5 | 52.0048 | 0 | 52.0048 | 11 | 4.1814 | 18.6522 | 18.6522 | 460.5922 | 52.0048 | 0 | 23380.9588 | 0 | 0 | 0 | 52.0048 | 0 | 0 | 23380.9588
4 | 25 | 6 | 3.2267 | 0 | 3.2267 | 11 | 5.3513 | 1.4482 | 1.4482 | 469.9619 | 3.2267 | 0 | 1480.9169 | 0 | 0 | 0 | 3.2267 | 0 | 0 | 1480.9169
4 | 25 | 7 | 6.6233 | 69.4061 | 76.0295 | 44.7767 | 5.6008 | 36.0572 | 36.0572 | 455.9196 | 76.0295 | 0 | 31258.9669 | 0 | 0 | 0 | 76.0295 | 0 | 0 | 31258.9669
4 | 25 | 8 | 31.0138 | 627.5963 | 658.6101 | 46.2577 | 6.5729 | 400.8145 | 288 | 460.835 | 473.2357 | 185.3745 | 196192.7786 | 18.5282 | 0 | 0 | 473.2357 | 185.3745 | 0 | 196192.7786
4 | 25 | 9 | 1.5456 | 367.5744 | 369.1201 | 47.8451 | 7.7084 | 335.7072 | 288 | 452.6757 | 316.6646 | 52.4555 | 128195.534 | 5.2429 | 0 | 0 | 316.6646 | 52.4555 | 0 | 128195.534
4 | 25 | 10 | 0 | 652.4721 | 652.4721 | 48 | 8.9471 | 1288.3055 | 288 | 467.9704 | 145.8598 | 506.6123 | 61256.7995 | 50.636 | 0 | 0 | 145.8598 | 506.6123 | 0 | 61256.7995
4 | 25 | 11 | 12.5444 | 395.722 | 408.2664 | 46.8631 | 9.5923 | 2066.4825 | 288 | 484.9294 | 56.899 | 351.3674 | 24925.5149 | 35.1193 | 0 | 0 | 56.899 | 351.3674 | 0 | 24925.5149
4 | 25 | 12 | 0 | 87.9086 | 87.9086 | 48 | 10.2891 | 0 | 0 | 488.2251 | 0 | 87.9086 | 0 | 8.7865 | 0 | 0 | 0 | 87.9086 | 0 | 0
4 | 25 | 13 | 1.9327 | 227.5275 | 229.4601 | 47.6884 | 10.0827 | 0 | 0 | 482.2668 | 0 | 229.4601 | 0 | 22.9346 | 0 | 0 | 0 | 229.4601 | 0 | 0
4 | 25 | 14 | 0 | 122.6191 | 122.6191 | 48 | 10.6934 | 0 | 0 | 484.794 | 0 | 122.6191 | 0 | 12.2558 | 0 | 0 | 0 | 122.6191 | 0 | 0
4 | 25 | 15 | 0 | 180.0508 | 180.0508 | 48 | 11.6655 | 0 | 0 | 488.2364 | 0 | 180.0508 | 0 | 17.9961 | 0 | 0 | 0 | 180.0508 | 0 | 0
4 | 25 | 16 | 3.6475 | 64.99 | 68.6375 | 46.0338 | 12.3021 | 0 | 0 | 485.1027 | 0 | 68.6375 | 0 | 6.8603 | 0 | 0 | 0 | 68.6375 | 0 | 0
4 | 25 | 17 | 16.744 | 1.6604 | 18.4044 | 14.3381 | 12.1989 | 0 | 0 | 501.0172 | 0 | 18.4044 | 0 | 1.8395 | 0 | 0 | 0 | 18.4044 | 0 | 0
4 | 25 | 18 | 157.0451 | 0 | 157.0451 | 11 | 12.9559 | 0 | 0 | 501.4757 | 0 | 157.0451 | 0 | 15.6967 | 0 | 0 | 0 | 157.0451 | 0 | 0
4 | 25 | 19 | 81.3082 | 0 | 81.3082 | 11 | 13.2054 | 0 | 0 | 494.9012 | 0 | 81.3082 | 0 | 8.1268 | 0 | 0 | 0 | 81.3082 | 0 | 0
4 | 25 | 20 | 16.7671 | 0 | 16.7671 | 11 | 12.6806 | 0 | 0 | 478.2078 | 0 | 16.7671 | 0 | 1.6759 | 0 | 0 | 0 | 16.7671 | 0 | 0
4 | 25 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 443.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 22 | 94.3492 | 0 | 94.3492 | 11 | 5.6868 | 45.6368 | 45.6368 | 428.2825 | 94.3492 | 0 | 39370.2536 | 0 | 0 | 0 | 94.3492 | 0 | 0 | 39370.2536
4 | 25 | 23 | 56.8455 | 0 | 56.8455 | 11 | 4.5734 | 21.8599 | 21.8599 | 419.1297 | 56.8455 | 0 | 23200.3259 | 0 | 0 | 0 | 56.8455 | 0 | 0 | 23200.3259
4 | 26 | 0 | 19.4415 | 0 | 19.4415 | 11 | 3.8373 | 6.5839 | 6.5839 | 416.2969 | 19.4415 | 0 | 7879.5869 | 0 | 0 | 0 | 19.4415 | 0 | 0 | 7879.5869
4 | 26 | 1 | 14.6198 | 0 | 14.6198 | 11 | 3.605 | 4.7714 | 4.7714 | 427.0927 | 14.6198 | 0 | 6083.2117 | 0 | 0 | 0 | 14.6198 | 0 | 0 | 6083.2117
4 | 26 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 446.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 3 | 9.7629 | 0 | 9.7629 | 11 | 3.4416 | 3.1069 | 3.1069 | 478.4036 | 9.7629 | 0 | 4563.2228 | 0 | 0 | 0 | 9.7629 | 0 | 0 | 4563.2228
4 | 26 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 500.4013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 5 | 2.3158 | 0 | 2.3158 | 11 | 4.0351 | 0.81025 | 0.81025 | 502.4666 | 2.3158 | 0 | 1138.1458 | 0 | 0 | 0 | 2.3158 | 0 | 0 | 1138.1458
4 | 26 | 6 | 0.47551 | 0 | 0.47551 | 11 | 5.1793 | 0.20582 | 0.20582 | 520.7483 | 0.47551 | 0 | 242.3927 | 0 | 0 | 0 | 0.47551 | 0 | 0 | 242.3927
4 | 26 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 527.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 8 | 8.405 | 246.0807 | 254.4857 | 46.778 | 6.5729 | 154.874 | 154.874 | 523.5366 | 254.4857 | 0 | 121328.2446 | 0 | 0 | 0 | 254.4857 | 0 | 0 | 121328.2446
4 | 26 | 9 | 0 | 235.7775 | 235.7775 | 48 | 7.6912 | 212.8403 | 212.8403 | 524.0939 | 235.7775 | 0 | 112252.228 | 0 | 0 | 0 | 235.7775 | 0 | 0 | 112252.228
4 | 26 | 10 | 9.285 | 345.6793 | 354.9643 | 47.0322 | 8.4482 | 476.2486 | 288 | 529.7494 | 214.6562 | 140.3081 | 103618.2255 | 14.0238 | 0 | 0 | 214.6562 | 140.3081 | 0 | 103618.2255
4 | 26 | 11 | 0 | 329.9827 | 329.9827 | 48 | 9.7214 | 2430.1406 | 288 | 527.9444 | 39.1068 | 290.8759 | 18769.0894 | 29.0731 | 0 | 0 | 39.1068 | 290.8759 | 0 | 18769.0894
4 | 26 | 12 | 5.0352 | 194.34 | 199.3753 | 47.0656 | 9.4117 | 701.8884 | 288 | 524.9494 | 81.808 | 117.5673 | 39094.7197 | 11.7509 | 0 | 0 | 81.808 | 117.5673 | 0 | 39094.7197
4 | 26 | 13 | 10.5883 | 2.4411 | 13.0294 | 17.9322 | 8.8869 | 24.341 | 24.341 | 520.8795 | 13.0294 | 0 | 6553.1152 | 0 | 0 | 0 | 13.0294 | 0 | 0 | 6553.1152
4 | 26 | 14 | 0 | 23.8148 | 23.8148 | 48 | 9.3428 | 75.1247 | 75.1247 | 519.0124 | 23.8148 | 0 | 11217.0761 | 0 | 0 | 0 | 23.8148 | 0 | 0 | 11217.0761
4 | 26 | 15 | 7.8106 | 87.807 | 95.6176 | 44.9776 | 10.0224 | 0 | 0 | 513.7486 | 0 | 95.6176 | 0 | 9.557 | 0 | 0 | 0 | 95.6176 | 0 | 0
4 | 26 | 16 | 17.2742 | 31.3844 | 48.6586 | 34.8647 | 11.4074 | 0 | 0 | 507.234 | 0 | 48.6586 | 0 | 4.8634 | 0 | 0 | 0 | 48.6586 | 0 | 0
4 | 26 | 17 | 2.54 | 2.3419 | 4.8819 | 28.7492 | 10.8053 | 0 | 0 | 510.6153 | 0 | 4.8819 | 0 | 0.48795 | 0 | 0 | 0 | 4.8819 | 0 | 0
4 | 26 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 517.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 513.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 20 | 1.4654 | 0 | 1.4654 | 11 | 8.4138 | 1.9236 | 1.9236 | 491.7106 | 1.4654 | 0 | 704.4499 | 0 | 0 | 0 | 1.4654 | 0 | 0 | 704.4499
4 | 26 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 457.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 439.2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 23 | 1.1184 | 0 | 1.1184 | 11 | 4.5599 | 0.42903 | 0.42903 | 433.9793 | 1.1184 | 0 | 473.0758 | 0 | 0 | 0 | 1.1184 | 0 | 0 | 473.0758
4 | 27 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 426.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 1 | 3.9968 | 0 | 3.9968 | 11 | 4.2072 | 1.4399 | 1.4399 | 422.8141 | 3.9968 | 0 | 1645.9571 | 0 | 0 | 0 | 3.9968 | 0 | 0 | 1645.9571
4 | 27 | 2 | 1.6581 | 0 | 1.6581 | 11 | 4.147 | 0.59121 | 0.59121 | 446.0071 | 1.6581 | 0 | 721.2949 | 0 | 0 | 0 | 1.6581 | 0 | 0 | 721.2949
4 | 27 | 3 | 24.4839 | 0 | 24.4839 | 11 | 3.7857 | 8.2227 | 8.2227 | 477.7873 | 24.4839 | 0 | 11428.783 | 0 | 0 | 0 | 24.4839 | 0 | 0 | 11428.783
4 | 27 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 500.3859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 504.5841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 498.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 505.3736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 8 | 20.1625 | 167.2841 | 187.4466 | 44.0201 | 5.4889 | 86.6959 | 86.6959 | 492.8575 | 187.4466 | 0 | 84133.0562 | 0 | 0 | 0 | 187.4466 | 0 | 0 | 84133.0562
4 | 27 | 9 | 0 | 565.9169 | 565.9169 | 48 | 6.9858 | 391.5056 | 288 | 504.3215 | 416.3007 | 149.6161 | 189966.9575 | 14.9542 | 0 | 0 | 416.3007 | 149.6161 | 0 | 189966.9575
4 | 27 | 10 | 25.8342 | 195.5889 | 221.423 | 43.6831 | 7.3471 | 174.0051 | 174.0051 | 502.5269 | 221.423 | 0 | 101598.5972 | 0 | 0 | 0 | 221.423 | 0 | 0 | 101598.5972
4 | 27 | 11 | 15.3596 | 9.7522 | 25.1118 | 25.369 | 8.9643 | 50.403 | 50.403 | 507.7279 | 25.1118 | 0 | 12112.8929 | 0 | 0 | 0 | 25.1118 | 0 | 0 | 12112.8929
4 | 27 | 12 | 4.1608 | 25.0003 | 29.1611 | 42.7207 | 8.2847 | 35.4075 | 35.4075 | 511.4962 | 29.1611 | 0 | 13670.0307 | 0 | 0 | 0 | 29.1611 | 0 | 0 | 13670.0307
4 | 27 | 13 | 9.0367 | 162.1884 | 171.225 | 46.0473 | 7.8202 | 163.6969 | 163.6969 | 503.1324 | 171.225 | 0 | 78264.423 | 0 | 0 | 0 | 171.225 | 0 | 0 | 78264.423
4 | 27 | 14 | 0 | 127.4993 | 127.4993 | 48 | 7.6568 | 113.4092 | 113.4092 | 510.8458 | 127.4993 | 0 | 59012.5247 | 0 | 0 | 0 | 127.4993 | 0 | 0 | 59012.5247
4 | 27 | 15 | 0.62167 | 5.3256 | 5.9473 | 44.1324 | 7.7256 | 5.4498 | 5.4498 | 511.8781 | 5.9473 | 0 | 2781.8263 | 0 | 0 | 0 | 5.9473 | 0 | 0 | 2781.8263
4 | 27 | 16 | 1.74 | 0 | 1.74 | 11 | 7.3729 | 1.3808 | 1.3808 | 494.1144 | 1.74 | 0 | 840.5989 | 0 | 0 | 0 | 1.74 | 0 | 0 | 840.5989
4 | 27 | 17 | 0 | 22.1689 | 22.1689 | 48 | 7.5449 | 18.8226 | 18.8226 | 501.5677 | 22.1689 | 0 | 10055.104 | 0 | 0 | 0 | 22.1689 | 0 | 0 | 10055.104
4 | 27 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 498.4358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 492.4634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 492.4634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 439.2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 22 | 95.6234 | 0 | 95.6234 | 11 | 4.9212 | 39.2875 | 39.2875 | 420.222 | 95.6234 | 0 | 39131.2149 | 0 | 0 | 0 | 95.6234 | 0 | 0 | 39131.2149
4 | 27 | 23 | 155.7863 | 0 | 155.7863 | 11 | 4.5954 | 60.1516 | 60.1516 | 411.7304 | 155.7863 | 0 | 62428.2979 | 0 | 0 | 0 | 155.7863 | 0 | 0 | 62428.2979
4 | 28 | 0 | 8.0681 | 0 | 8.0681 | 11 | 3.8459 | 2.7361 | 2.7361 | 412.5381 | 8.0681 | 0 | 3239.6651 | 0 | 0 | 0 | 8.0681 | 0 | 0 | 3239.6651
4 | 28 | 1 | 66.0354 | 0 | 66.0354 | 11 | 3.4243 | 20.9598 | 20.9598 | 410.0973 | 66.0354 | 0 | 26354.5485 | 0 | 0 | 0 | 66.0354 | 0 | 0 | 26354.5485
4 | 28 | 2 | 124.4427 | 0 | 124.4427 | 11 | 3.3383 | 38.9888 | 38.9888 | 433.2786 | 124.4427 | 0 | 52549.4682 | 0 | 0 | 0 | 124.4427 | 0 | 0 | 52549.4682
4 | 28 | 3 | 10.2467 | 0 | 10.2467 | 11 | 3.3039 | 3.1939 | 3.1939 | 453.4377 | 10.2467 | 0 | 4533.5117 | 0 | 0 | 0 | 10.2467 | 0 | 0 | 4533.5117
4 | 28 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 508.7241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 513.4664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 6 | 0.22461 | 0 | 0.22461 | 11 | 4.9556 | 0.092911 | 0.092911 | 514.3303 | 0.22461 | 0 | 113.0528 | 0 | 0 | 0 | 0.22461 | 0 | 0 | 113.0528
4 | 28 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 515.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 8 | 18.945 | 108.8497 | 127.7947 | 42.5149 | 7.2524 | 96.9748 | 96.9748 | 509.3699 | 127.7947 | 0 | 59661.6012 | 0 | 0 | 0 | 127.7947 | 0 | 0 | 59661.6012
4 | 28 | 9 | 1.92 | 408.7375 | 410.6575 | 47.827 | 7.6998 | 372.0909 | 288 | 514.5997 | 317.8507 | 92.8068 | 148364.0523 | 9.2761 | 0 | 0 | 317.8507 | 92.8068 | 0 | 148364.0523
4 | 28 | 10 | 0 | 466.021 | 466.021 | 48 | 7.8632 | 454.4792 | 288 | 516.4343 | 295.314 | 170.707 | 138335.2068 | 17.0622 | 0 | 0 | 295.314 | 170.707 | 0 | 138335.2068
4 | 28 | 11 | 0 | 346.9438 | 346.9438 | 48 | 7.6051 | 301.9653 | 288 | 525.9154 | 330.8983 | 16.0455 | 158141.419 | 1.6038 | 0 | 0 | 330.8983 | 16.0455 | 0 | 158141.419
4 | 28 | 12 | 23.0785 | 491.5778 | 514.6563 | 46.3408 | 8.2589 | 615.6601 | 288 | 533.9303 | 240.7514 | 273.9049 | 117387.8341 | 27.3769 | 0 | 0 | 240.7514 | 273.9049 | 0 | 117387.8341
4 | 28 | 13 | 59.6709 | 643.2367 | 702.9075 | 44.859 | 8.5686 | 1022.1521 | 288 | 529.2361 | 198.0502 | 504.8574 | 95930.9614 | 50.4606 | 0 | 0 | 198.0502 | 504.8574 | 0 | 95930.9614
4 | 28 | 14 | 4.3624 | 743.3453 | 747.7077 | 47.7841 | 8.6374 | 1142.0167 | 288 | 529.5458 | 188.561 | 559.1467 | 90841.4622 | 55.8869 | 0 | 0 | 188.561 | 559.1467 | 0 | 90841.4622
4 | 28 | 15 | 4.1617 | 348.9542 | 353.1158 | 47.5639 | 7.803 | 334.9528 | 288 | 524.9768 | 303.617 | 49.4988 | 144950.6742 | 4.9474 | 0 | 0 | 303.617 | 49.4988 | 0 | 144950.6742
4 | 28 | 16 | 0 | 333.6138 | 333.6138 | 48 | 7.6998 | 302.2827 | 288 | 517.5802 | 317.8507 | 15.7631 | 149256.4153 | 1.5755 | 0 | 0 | 317.8507 | 15.7631 | 0 | 149256.4153
4 | 28 | 17 | 21.1995 | 0.0041533 | 21.2036 | 11.0072 | 7.6482 | 18.7915 | 18.7915 | 510.1926 | 21.2036 | 0 | 10584.539 | 0 | 0 | 0 | 21.2036 | 0 | 0 | 10584.539
4 | 28 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 518.2885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 19 | 0.75228 | 0 | 0.75228 | 11 | 7.3127 | 0.58362 | 0.58362 | 527.2195 | 0.75228 | 0 | 388.3394 | 0 | 0 | 0 | 0.75228 | 0 | 0 | 388.3394
4 | 28 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 503.3402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 473.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 458.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 454.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 0 | 0.071128 | 0 | 0.071128 | 11 | 3.9749 | 0.024638 | 0.024638 | 450.3576 | 0.071128 | 0 | 31.2507 | 0 | 0 | 0 | 0.071128 | 0 | 0 | 31.2507
4 | 29 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 456.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 464.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 497.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 516.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 517.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 506.3502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 506.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 515.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 9 | 0.87162 | 0 | 0.87162 | 11 | 7.5707 | 0.7479 | 0.7479 | 523.8343 | 0.87162 | 0 | 446.9992 | 0 | 0 | 0 | 0.87162 | 0 | 0 | 446.9992
4 | 29 | 10 | 29.1552 | 2.514 | 31.6692 | 13.9372 | 7.4159 | 25.5487 | 25.5487 | 523.6251 | 31.6692 | 0 | 16141.3986 | 0 | 0 | 0 | 31.6692 | 0 | 0 | 16141.3986
4 | 29 | 11 | 17.4525 | 21.0318 | 38.4842 | 31.2206 | 7.5879 | 33.2566 | 33.2566 | 528.8185 | 38.4842 | 0 | 19149.6656 | 0 | 0 | 0 | 38.4842 | 0 | 0 | 19149.6656
4 | 29 | 12 | 12.825 | 337.2769 | 350.1019 | 46.6446 | 8.3192 | 433.7709 | 288 | 525.216 | 232.4483 | 117.6535 | 111243.1219 | 11.7595 | 0 | 0 | 232.4483 | 117.6535 | 0 | 111243.1219
4 | 29 | 13 | 0 | 451.4537 | 451.4537 | 48 | 8.6546 | 698.3167 | 288 | 527.9765 | 186.1887 | 265.265 | 89366.2102 | 26.5133 | 0 | 0 | 186.1887 | 265.265 | 0 | 89366.2102
4 | 29 | 14 | 0 | 580.6107 | 580.6107 | 48 | 8.9299 | 1128.0681 | 288 | 522.482 | 148.2321 | 432.3787 | 70333.4556 | 43.2164 | 0 | 0 | 148.2321 | 432.3787 | 0 | 70333.4556
4 | 29 | 15 | 0.72183 | 363.6285 | 364.3503 | 47.9267 | 8.8009 | 632.0335 | 288 | 522.8545 | 166.0243 | 198.326 | 78849.5408 | 19.8227 | 0 | 0 | 166.0243 | 198.326 | 0 | 78849.5408
4 | 29 | 16 | 13.4632 | 5.734 | 19.1973 | 22.0516 | 9.5837 | 95.1848 | 95.1848 | 509.6538 | 19.1973 | 0 | 9360.6368 | 0 | 0 | 0 | 19.1973 | 0 | 0 | 9360.6368
4 | 29 | 17 | 15.7832 | 108.0797 | 123.863 | 43.2853 | 9.0762 | 278.5445 | 278.5445 | 506.0738 | 123.863 | 0 | 57322.37 | 0 | 0 | 0 | 123.863 | 0 | 0 | 57322.37
4 | 29 | 18 | 13.3314 | 0 | 13.3314 | 11 | 9.4461 | 49.8218 | 49.8218 | 519.3404 | 13.3314 | 0 | 6776.8864 | 0 | 0 | 0 | 13.3314 | 0 | 0 | 6776.8864
4 | 29 | 19 | 5.9372 | 0 | 5.9372 | 11 | 8.0611 | 6.3795 | 6.3795 | 513.4844 | 5.9372 | 0 | 2983.3456 | 0 | 0 | 0 | 5.9372 | 0 | 0 | 2983.3456
4 | 29 | 20 | 10.2315 | 0 | 10.2315 | 11 | 11.2698 | 0 | 0 | 495.7732 | 0 | 10.2315 | 0 | 1.0226 | 0 | 0 | 0 | 10.2315 | 0 | 0
4 | 29 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 480.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 22 | 0.48598 | 0 | 0.48598 | 11 | 5.4717 | 0.22392 | 0.22392 | 471.5109 | 0.48598 | 0 | 223.7999 | 0 | 0 | 0 | 0.48598 | 0 | 0 | 223.7999
4 | 29 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 457.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 456.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 460.5546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 2 | 2.5892 | 0 | 2.5892 | 11 | 3.1921 | 0.7938 | 0.7938 | 464.8847 | 2.5892 | 0 | 1175.1989 | 0 | 0 | 0 | 2.5892 | 0 | 0 | 1175.1989
4 | 30 | 3 | 8.3547 | 0 | 8.3547 | 11 | 3.3297 | 2.6142 | 2.6142 | 459.1803 | 8.3547 | 0 | 3744.4078 | 0 | 0 | 0 | 8.3547 | 0 | 0 | 3744.4078
4 | 30 | 4 | 9.0675 | 0 | 9.0675 | 11 | 3.3469 | 2.8446 | 2.8446 | 452.9558 | 9.0675 | 0 | 4007.4549 | 0 | 0 | 0 | 9.0675 | 0 | 0 | 4007.4549
4 | 30 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 470.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 477.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 7 | 9.092 | 0 | 9.092 | 11 | 5.2137 | 3.9635 | 3.9635 | 481.3113 | 9.092 | 0 | 4276.0649 | 0 | 0 | 0 | 9.092 | 0 | 0 | 4276.0649
4 | 30 | 8 | 63.4805 | 6.6678 | 70.1483 | 14.5169 | 5.1879 | 30.4164 | 30.4164 | 483.4529 | 70.1483 | 0 | 32895.0401 | 0 | 0 | 0 | 70.1483 | 0 | 0 | 32895.0401
4 | 30 | 9 | 21.66 | 103.9484 | 125.6084 | 41.6197 | 6.7449 | 80.4765 | 80.4765 | 484.8586 | 125.6084 | 0 | 55674.5257 | 0 | 0 | 0 | 125.6084 | 0 | 0 | 55674.5257
4 | 30 | 10 | 31.5282 | 273.4471 | 304.9753 | 44.175 | 8.8783 | 565.3909 | 288 | 482.8316 | 155.349 | 149.6263 | 68144.8468 | 14.9552 | 0 | 0 | 155.349 | 149.6263 | 0 | 68144.8468
4 | 30 | 11 | 10.34 | 225.9859 | 236.3259 | 46.3811 | 9.8676 | 3593.1061 | 288 | 466.2758 | 18.9423 | 217.3835 | 7953.7886 | 21.7275 | 0 | 0 | 18.9423 | 217.3835 | 0 | 7953.7886
4 | 30 | 12 | 22.7542 | 59.8255 | 82.5796 | 37.8049 | 10.2547 | 0 | 0 | 467.6655 | 0 | 82.5796 | 0 | 8.2539 | 0 | 0 | 0 | 82.5796 | 0 | 0
4 | 30 | 13 | 18.5786 | 2.4855 | 21.0641 | 15.3659 | 10.031 | 0 | 0 | 466.9417 | 0 | 21.0641 | 0 | 2.1054 | 0 | 0 | 0 | 21.0641 | 0 | 0
4 | 30 | 14 | 33.07 | 101.751 | 134.821 | 38.9243 | 9.9364 | 4107.4459 | 288 | 469.0378 | 9.4532 | 125.3679 | 4065.9438 | 12.5306 | 0 | 0 | 9.4532 | 125.3679 | 0 | 4065.9438
4 | 30 | 15 | 22.0816 | 20.9894 | 43.071 | 29.0309 | 11.1494 | 0 | 0 | 479.2896 | 0 | 43.071 | 0 | 4.305 | 0 | 0 | 0 | 43.071 | 0 | 0
4 | 30 | 16 | 12.3218 | 3.54 | 15.8618 | 19.2576 | 12.5086 | 0 | 0 | 467.8572 | 0 | 15.8618 | 0 | 1.5854 | 0 | 0 | 0 | 15.8618 | 0 | 0
4 | 30 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 469.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 472.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 472.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 454.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 21 | 79.9459 | 0 | 79.9459 | 11 | 9.2568 | 223.1945 | 223.1945 | 436.3376 | 79.9459 | 0 | 34004.0101 | 0 | 0 | 0 | 79.9459 | 0 | 0 | 34004.0101
4 | 30 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 421.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 418.7655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 406.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 1 | 1.1451 | 0 | 1.1451 | 11 | 3.4588 | 0.36537 | 0.36537 | 403.9123 | 1.1451 | 0 | 449.9208 | 0 | 0 | 0 | 1.1451 | 0 | 0 | 449.9208
5 | 1 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 416.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 3 | 2.7096 | 0 | 2.7096 | 11 | 3.4416 | 0.86229 | 0.86229 | 424.4336 | 2.7096 | 0 | 1120.2381 | 0 | 0 | 0 | 2.7096 | 0 | 0 | 1120.2381
5 | 1 | 4 | 0.3192 | 0 | 0.3192 | 11 | 3.691 | 0.10559 | 0.10559 | 418.9387 | 0.3192 | 0 | 130.2132 | 0 | 0 | 0 | 0.3192 | 0 | 0 | 130.2132
5 | 1 | 5 | 2.1507 | 0 | 2.1507 | 11 | 3.9405 | 0.74073 | 0.74073 | 438.9277 | 2.1507 | 0 | 920.3347 | 0 | 0 | 0 | 2.1507 | 0 | 0 | 920.3347
5 | 1 | 6 | 5.8509 | 0 | 5.8509 | 11 | 4.8093 | 2.3521 | 2.3521 | 460.9763 | 5.8509 | 0 | 2632.7771 | 0 | 0 | 0 | 5.8509 | 0 | 0 | 2632.7771
5 | 1 | 7 | 4.152 | 0 | 4.152 | 11 | 5.1706 | 1.7939 | 1.7939 | 468.187 | 4.152 | 0 | 1898.2568 | 0 | 0 | 0 | 4.152 | 0 | 0 | 1898.2568
5 | 1 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 470.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 475.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 472.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 11 | 1.6883 | 0.29992 | 1.9883 | 16.5812 | 10.0569 | 0 | 0 | 478.9538 | 0 | 1.9883 | 0 | 0.19873 | 0 | 0 | 0 | 1.9883 | 0 | 0
5 | 1 | 12 | 2.6883 | 0.51392 | 3.2023 | 16.938 | 10.1343 | 0 | 0 | 474.0515 | 0 | 3.2023 | 0 | 0.32007 | 0 | 0 | 0 | 3.2023 | 0 | 0
5 | 1 | 13 | 6.9045 | 0.32762 | 7.2321 | 12.6762 | 10.2117 | 0 | 0 | 480.1823 | 0 | 7.2321 | 0 | 0.72285 | 0 | 0 | 0 | 7.2321 | 0 | 0
5 | 1 | 14 | 5.9158 | 1.9367 | 7.8525 | 20.1253 | 9.8762 | 127.3651 | 127.3651 | 478.7811 | 7.8525 | 0 | 3601.5943 | 0 | 0 | 0 | 7.8525 | 0 | 0 | 3601.5943
5 | 1 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 476.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 476.6442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 464.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 472.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 481.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 445.9812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 437.5597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 422.5752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 415.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 408.5683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 419.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 430.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 463.7757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 480.0086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 481.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 486.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 490.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 486.1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 487.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 10 | 5.0891 | 2.4342 | 7.5233 | 22.9714 | 8.9471 | 14.8548 | 14.8548 | 487.7444 | 7.5233 | 0 | 3496.6296 | 0 | 0 | 0 | 7.5233 | 0 | 0 | 3496.6296
5 | 2 | 11 | 0 | 13.5742 | 13.5742 | 48 | 9.5923 | 68.707 | 68.707 | 486.6115 | 13.5742 | 0 | 5953.7859 | 0 | 0 | 0 | 13.5742 | 0 | 0 | 5953.7859
5 | 2 | 12 | 0 | 11.9942 | 11.9942 | 48 | 10.2891 | 0 | 0 | 489.8038 | 0 | 11.9942 | 0 | 1.1988 | 0 | 0 | 0 | 11.9942 | 0 | 0
5 | 2 | 13 | 0 | 11.4192 | 11.4192 | 48 | 10.0827 | 0 | 0 | 487.3258 | 0 | 11.4192 | 0 | 1.1413 | 0 | 0 | 0 | 11.4192 | 0 | 0
5 | 2 | 14 | 0 | 11.7121 | 11.7121 | 48 | 10.6934 | 0 | 0 | 486.2001 | 0 | 11.7121 | 0 | 1.1706 | 0 | 0 | 0 | 11.7121 | 0 | 0
5 | 2 | 15 | 0 | 0.0066667 | 0.0066667 | 48 | 11.6655 | 0 | 0 | 492.7204 | 0 | 0.0066667 | 0 | 0.00066634 | 0 | 0 | 0 | 0.0066667 | 0 | 0
5 | 2 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 484.7943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 17 | 0 | 0.76667 | 0.76667 | 48 | 12.1989 | 0 | 0 | 479.5776 | 0 | 0.76667 | 0 | 0.076629 | 0 | 0 | 0 | 0.76667 | 0 | 0
5 | 2 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 490.4895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 499.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 491.9096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 462.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 446.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 429.6624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 423.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 423.2702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 438.889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 468.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 478.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 484.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 482.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 483.4052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 483.6765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 480.3528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 10 | 0 | 7.4169 | 7.4169 | 48 | 8.4482 | 9.9511 | 9.9511 | 484.373 | 7.4169 | 0 | 3236.5456 | 0 | 0 | 0 | 7.4169 | 0 | 0 | 3236.5456
5 | 3 | 11 | 0 | 56.406 | 56.406 | 48 | 9.7214 | 415.3988 | 288 | 484.379 | 39.1068 | 17.2992 | 17065.3859 | 1.7291 | 0 | 0 | 39.1068 | 17.2992 | 0 | 17065.3859
5 | 3 | 12 | 0 | 56.6843 | 56.6843 | 48 | 9.4117 | 199.5535 | 199.5535 | 490.0319 | 56.6843 | 0 | 25056.2596 | 0 | 0 | 0 | 56.6843 | 0 | 0 | 25056.2596
5 | 3 | 13 | 0 | 3.82 | 3.82 | 48 | 8.8869 | 7.1363 | 7.1363 | 487.8178 | 3.82 | 0 | 1680.0951 | 0 | 0 | 0 | 3.82 | 0 | 0 | 1680.0951
5 | 3 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 486.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 15 | 0 | 26.3157 | 26.3157 | 48 | 10.0224 | 0 | 0 | 481.4083 | 0 | 26.3157 | 0 | 2.6303 | 0 | 0 | 0 | 26.3157 | 0 | 0
5 | 3 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 468.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 464.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 477.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 464.0117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 433.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 406.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 392.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 387.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 389.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 402.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 418.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 449.7286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 457.0169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 466.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 6 | 0.84167 | 0 | 0.84167 | 11 | 4.7319 | 0.33339 | 0.33339 | 467.6473 | 0.84167 | 0 | 384.3448 | 0 | 0 | 0 | 0.84167 | 0 | 0 | 384.3448
5 | 4 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 462.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 461.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 461.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 456.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 11 | 0 | 40.376 | 40.376 | 48 | 8.9643 | 81.0403 | 81.0403 | 463.9132 | 40.376 | 0 | 16792.8933 | 0 | 0 | 0 | 40.376 | 0 | 0 | 16792.8933
5 | 4 | 12 | 0 | 98.7587 | 98.7587 | 48 | 8.2847 | 119.913 | 119.913 | 459.6236 | 98.7587 | 0 | 40651.4064 | 0 | 0 | 0 | 98.7587 | 0 | 0 | 40651.4064
5 | 4 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 466.3709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 467.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 470.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 469.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 469.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 482.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 478.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 443.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 21 | 48.6811 | 0 | 48.6811 | 11 | 6.5556 | 29.4784 | 29.4784 | 420.9163 | 48.6811 | 0 | 19955.1604 | 0 | 0 | 0 | 48.6811 | 0 | 0 | 19955.1604
5 | 4 | 22 | 3.602 | 0 | 3.602 | 11 | 4.9212 | 1.4799 | 1.4799 | 407.0465 | 3.602 | 0 | 1426.5512 | 0 | 0 | 0 | 3.602 | 0 | 0 | 1426.5512
5 | 4 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 396.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 389.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 394.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 409.871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 449.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 467.2899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 477.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 474.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 465.7441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 467.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 9 | 0 | 25.7503 | 25.7503 | 48 | 7.6998 | 23.3319 | 23.3319 | 464.1226 | 25.7503 | 0 | 10715.2664 | 0 | 0 | 0 | 25.7503 | 0 | 0 | 10715.2664
5 | 5 | 10 | 0 | 9.6836 | 9.6836 | 48 | 7.8632 | 9.4437 | 9.4437 | 473.0504 | 9.6836 | 0 | 4116.0008 | 0 | 0 | 0 | 9.6836 | 0 | 0 | 4116.0008
5 | 5 | 11 | 0 | 1.737 | 1.737 | 48 | 7.6051 | 1.5118 | 1.5118 | 468.9104 | 1.737 | 0 | 731.1052 | 0 | 0 | 0 | 1.737 | 0 | 0 | 731.1052
5 | 5 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 472.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 466.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 14 | 11.3136 | 0 | 11.3136 | 11 | 8.6374 | 17.2798 | 17.2798 | 470.3552 | 11.3136 | 0 | 5196.9417 | 0 | 0 | 0 | 11.3136 | 0 | 0 | 5196.9417
5 | 5 | 15 | 38.5145 | 0 | 38.5145 | 11 | 7.803 | 36.5335 | 36.5335 | 470.4623 | 38.5145 | 0 | 17695.9743 | 0 | 0 | 0 | 38.5145 | 0 | 0 | 17695.9743
5 | 5 | 16 | 52.7746 | 0 | 52.7746 | 11 | 7.6998 | 47.8183 | 47.8183 | 467.533 | 52.7746 | 0 | 24093.3632 | 0 | 0 | 0 | 52.7746 | 0 | 0 | 24093.3632
5 | 5 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 462.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 18 | 2.3408 | 0 | 2.3408 | 11 | 7.3041 | 1.8102 | 1.8102 | 472.9795 | 2.3408 | 0 | 1081.3967 | 0 | 0 | 0 | 2.3408 | 0 | 0 | 1081.3967
5 | 5 | 19 | 53.1322 | 0 | 53.1322 | 11 | 7.3127 | 41.2202 | 41.2202 | 469.5563 | 53.1322 | 0 | 24364.086 | 0 | 0 | 0 | 53.1322 | 0 | 0 | 24364.086
5 | 5 | 20 | 112.6115 | 0 | 112.6115 | 11 | 6.6417 | 69.935 | 69.935 | 449.0053 | 112.6115 | 0 | 49324.4508 | 0 | 0 | 0 | 112.6115 | 0 | 0 | 49324.4508
5 | 5 | 21 | 120.1291 | 0 | 120.1291 | 11 | 5.9879 | 62.4618 | 62.4618 | 422.8093 | 120.1291 | 0 | 49470.2868 | 0 | 0 | 0 | 120.1291 | 0 | 0 | 49470.2868
5 | 5 | 22 | 81.8168 | 0 | 81.8168 | 11 | 5.0846 | 34.7316 | 34.7316 | 407.5162 | 81.8168 | 0 | 32441.6936 | 0 | 0 | 0 | 81.8168 | 0 | 0 | 32441.6936
5 | 5 | 23 | 37.0347 | 0 | 37.0347 | 11 | 4.4566 | 13.942 | 13.942 | 402.1504 | 37.0347 | 0 | 14486.1287 | 0 | 0 | 0 | 37.0347 | 0 | 0 | 14486.1287
5 | 6 | 0 | 9.4355 | 0 | 9.4355 | 11 | 3.9749 | 3.2683 | 3.2683 | 399.5561 | 9.4355 | 0 | 3666.2401 | 0 | 0 | 0 | 9.4355 | 0 | 0 | 3666.2401
5 | 6 | 1 | 87.2642 | 0 | 87.2642 | 11 | 3.7598 | 29.1859 | 29.1859 | 401.2244 | 87.2642 | 0 | 34052.6229 | 0 | 0 | 0 | 87.2642 | 0 | 0 | 34052.6229
5 | 6 | 2 | 105.1323 | 0 | 105.1323 | 11 | 3.691 | 34.7787 | 34.7787 | 421.3915 | 105.1323 | 0 | 43145.4141 | 0 | 0 | 0 | 105.1323 | 0 | 0 | 43145.4141
5 | 6 | 3 | 49.5183 | 0 | 49.5183 | 11 | 3.6824 | 16.3588 | 16.3588 | 436.152 | 49.5183 | 0 | 21052.8243 | 0 | 0 | 0 | 49.5183 | 0 | 0 | 21052.8243
5 | 6 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 444.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 5 | 0.36297 | 0 | 0.36297 | 11 | 3.691 | 0.12007 | 0.12007 | 448.1951 | 0.36297 | 0 | 158.6872 | 0 | 0 | 0 | 0.36297 | 0 | 0 | 158.6872
5 | 6 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 451.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 457.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 8 | 2.0787 | 0 | 2.0787 | 11 | 6.9944 | 1.4421 | 1.4421 | 454.5006 | 2.0787 | 0 | 921.8916 | 0 | 0 | 0 | 2.0787 | 0 | 0 | 921.8916
5 | 6 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 450.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 450.2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 457.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 463.1597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 456.7478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 14 | 2.3267 | 0 | 2.3267 | 11 | 8.9299 | 4.5205 | 4.5205 | 454.1536 | 2.3267 | 0 | 1031.0707 | 0 | 0 | 0 | 2.3267 | 0 | 0 | 1031.0707
5 | 6 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 449.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 443.8527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 443.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 449.3375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 435.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 408.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 385.4237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 367.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 356.9981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 353.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 1 | 7.0137 | 0 | 7.0137 | 11 | 3.2007 | 2.153 | 2.153 | 355.3769 | 7.0137 | 0 | 2415.3487 | 0 | 0 | 0 | 7.0137 | 0 | 0 | 2415.3487
5 | 7 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 364.2065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 375.8276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 369.5976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 383.8124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 402.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 414.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 8 | 0 | 0.045157 | 0.045157 | 48 | 5.1879 | 0.01958 | 0.01958 | 414.5824 | 0.045157 | 0 | 16.5537 | 0 | 0 | 0 | 0.045157 | 0 | 0 | 16.5537
5 | 7 | 9 | 0 | 15.9917 | 15.9917 | 48 | 6.7449 | 10.2458 | 10.2458 | 419.959 | 15.9917 | 0 | 5948.2479 | 0 | 0 | 0 | 15.9917 | 0 | 0 | 5948.2479
5 | 7 | 10 | 0 | 11.1805 | 11.1805 | 48 | 8.8783 | 20.7275 | 20.7275 | 416.1982 | 11.1805 | 0 | 4116.6485 | 0 | 0 | 0 | 11.1805 | 0 | 0 | 4116.6485
5 | 7 | 11 | 0 | 15.6044 | 15.6044 | 48 | 9.8676 | 237.2492 | 237.2492 | 413.7971 | 15.6044 | 0 | 5708.0303 | 0 | 0 | 0 | 15.6044 | 0 | 0 | 5708.0303
5 | 7 | 12 | 0 | 37.3826 | 37.3826 | 48 | 10.2547 | 0 | 0 | 412.113 | 0 | 37.3826 | 0 | 3.7364 | 0 | 0 | 0 | 37.3826 | 0 | 0
5 | 7 | 13 | 0 | 27.9392 | 27.9392 | 48 | 10.031 | 0 | 0 | 404.3957 | 0 | 27.9392 | 0 | 2.7925 | 0 | 0 | 0 | 27.9392 | 0 | 0
5 | 7 | 14 | 2.8092 | 2.8309 | 5.6401 | 29.5714 | 9.9364 | 171.8312 | 171.8312 | 402.9393 | 5.6401 | 0 | 2105.837 | 0 | 0 | 0 | 5.6401 | 0 | 0 | 2105.837
5 | 7 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 411.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 408.6575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 426.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 428.8903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 427.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 410.1758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 392.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 377.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 367.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 0 | 2.9294 | 0 | 2.9294 | 11 | 3.5706 | 0.95095 | 0.95095 | 363.8422 | 2.9294 | 0 | 1033.6329 | 0 | 0 | 0 | 2.9294 | 0 | 0 | 1033.6329
5 | 8 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 360.4159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 361.9797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 361.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 371.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 379.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 391.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 401.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 399.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 403.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 399.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 11 | 0.98003 | 0 | 0.98003 | 11 | 10.0569 | 0 | 0 | 398.8595 | 0 | 0.98003 | 0 | 0.097954 | 0 | 0 | 0 | 0.98003 | 0 | 0
5 | 8 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 403.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 13 | 0.76781 | 6.9505 | 7.7183 | 44.3193 | 10.2117 | 0 | 0 | 407.6726 | 0 | 7.7183 | 0 | 0.77144 | 0 | 0 | 0 | 7.7183 | 0 | 0
5 | 8 | 14 | 0 | 5.7815 | 5.7815 | 48 | 9.8762 | 93.774 | 93.774 | 413.7153 | 5.7815 | 0 | 2114.3804 | 0 | 0 | 0 | 5.7815 | 0 | 0 | 2114.3804
5 | 8 | 15 | 2.2991 | 0.89428 | 3.1934 | 21.3614 | 10.9601 | 0 | 0 | 418.9806 | 0 | 3.1934 | 0 | 0.31918 | 0 | 0 | 0 | 3.1934 | 0 | 0
5 | 8 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 425.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 17 | 2.9734 | 0 | 2.9734 | 11 | 11.5451 | 0 | 0 | 428.5922 | 0 | 2.9734 | 0 | 0.29719 | 0 | 0 | 0 | 2.9734 | 0 | 0
5 | 8 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 455.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 19 | 0 | 0.0024167 | 0.0024167 | 48 | 13.1107 | 0 | 0 | 435.0993 | 0 | 0.0024167 | 0 | 0.00024155 | 0 | 0 | 0 | 0.0024167 | 0 | 0
5 | 8 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 401.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 391.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 22 | 15.6243 | 0 | 15.6243 | 11 | 6.1771 | 8.5256 | 8.5256 | 380.4096 | 15.6243 | 0 | 5771.7718 | 0 | 0 | 0 | 15.6243 | 0 | 0 | 5771.7718
5 | 8 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 379.6484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 375.8775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 1 | 4.3861 | 0 | 4.3861 | 11 | 3.6394 | 1.4392 | 1.4392 | 377.514 | 4.3861 | 0 | 1607.5557 | 0 | 0 | 0 | 4.3861 | 0 | 0 | 1607.5557
5 | 9 | 2 | 21.7118 | 0 | 21.7118 | 11 | 3.5276 | 7.0012 | 7.0012 | 383.9542 | 21.7118 | 0 | 8097.5252 | 0 | 0 | 0 | 21.7118 | 0 | 0 | 8097.5252
5 | 9 | 3 | 48.6835 | 0 | 48.6835 | 11 | 3.562 | 15.7824 | 15.7824 | 413.8786 | 48.6835 | 0 | 19613.5277 | 0 | 0 | 0 | 48.6835 | 0 | 0 | 19613.5277
5 | 9 | 4 | 17.7017 | 0 | 17.7017 | 11 | 3.5878 | 5.7617 | 5.7617 | 427.9632 | 17.7017 | 0 | 7380.9617 | 0 | 0 | 0 | 17.7017 | 0 | 0 | 7380.9617
5 | 9 | 5 | 95.6572 | 0 | 95.6572 | 11 | 4.1814 | 34.3086 | 34.3086 | 441.4563 | 95.6572 | 0 | 41176.2337 | 0 | 0 | 0 | 95.6572 | 0 | 0 | 41176.2337
5 | 9 | 6 | 17.1377 | 40.4359 | 57.5736 | 36.9864 | 5.3513 | 25.8408 | 25.8408 | 451.5562 | 57.5736 | 0 | 23868.2664 | 0 | 0 | 0 | 57.5736 | 0 | 0 | 23868.2664
5 | 9 | 7 | 96.6937 | 300.5624 | 397.2561 | 38.9941 | 5.6008 | 188.4001 | 188.4001 | 458.5145 | 397.2561 | 0 | 166657.0269 | 0 | 0 | 0 | 397.2561 | 0 | 0 | 166657.0269
5 | 9 | 8 | 126.8842 | 647.3759 | 774.2601 | 41.9365 | 6.5729 | 471.1963 | 288 | 453.0327 | 473.2357 | 301.0244 | 194545.3772 | 30.0875 | 0 | 0 | 473.2357 | 301.0244 | 0 | 194545.3772
5 | 9 | 9 | 5.0457 | 742.5732 | 747.6188 | 47.7503 | 7.7084 | 679.9441 | 288 | 446.7101 | 316.6646 | 430.9542 | 126336.4566 | 43.074 | 0 | 0 | 316.6646 | 430.9542 | 0 | 126336.4566
5 | 9 | 10 | 19.1644 | 392.7866 | 411.951 | 46.2787 | 8.9471 | 813.3968 | 288 | 448.0225 | 145.8598 | 266.0912 | 58598.2623 | 26.5959 | 0 | 0 | 145.8598 | 266.0912 | 0 | 58598.2623
5 | 9 | 11 | 34.3002 | 295.1062 | 329.4064 | 44.1473 | 9.5923 | 1667.3247 | 288 | 443.4136 | 56.899 | 272.5075 | 22717.8406 | 27.2372 | 0 | 0 | 56.899 | 272.5075 | 0 | 22717.8406
5 | 9 | 12 | 56.0322 | 276.182 | 332.2142 | 41.7595 | 10.2891 | 0 | 0 | 435.0634 | 0 | 332.2142 | 0 | 33.2049 | 0 | 0 | 0 | 332.2142 | 0 | 0
5 | 9 | 13 | 3.7927 | 487.0452 | 490.8379 | 47.7141 | 10.0827 | 0 | 0 | 441.9286 | 0 | 490.8379 | 0 | 49.0594 | 0 | 0 | 0 | 490.8379 | 0 | 0
5 | 9 | 14 | 0 | 487.0858 | 487.0858 | 48 | 10.6934 | 0 | 0 | 444.7166 | 0 | 487.0858 | 0 | 48.6844 | 0 | 0 | 0 | 487.0858 | 0 | 0
5 | 9 | 15 | 9.6167 | 479.7477 | 489.3643 | 47.2729 | 11.6655 | 0 | 0 | 454.5849 | 0 | 489.3643 | 0 | 48.9121 | 0 | 0 | 0 | 489.3643 | 0 | 0
5 | 9 | 16 | 151.4672 | 768.0185 | 919.4857 | 41.905 | 12.3021 | 0 | 0 | 456.4813 | 0 | 919.4857 | 0 | 91.9028 | 0 | 0 | 0 | 919.4857 | 0 | 0
5 | 9 | 17 | 168.2115 | 536.1361 | 704.3476 | 39.1637 | 12.1989 | 0 | 0 | 452.095 | 0 | 704.3476 | 0 | 70.3997 | 0 | 0 | 0 | 704.3476 | 0 | 0
5 | 9 | 18 | 27.5861 | 63.2431 | 90.8292 | 36.7626 | 12.9559 | 0 | 0 | 466.9662 | 0 | 90.8292 | 0 | 9.0784 | 0 | 0 | 0 | 90.8292 | 0 | 0
5 | 9 | 19 | 0.0071897 | 0 | 0.0071897 | 11 | 13.2054 | 0 | 0 | 463.2231 | 0 | 0.0071897 | 0 | 0.00071861 | 0 | 0 | 0 | 0.0071897 | 0 | 0
5 | 9 | 20 | 5.8467 | 0 | 5.8467 | 11 | 12.6806 | 0 | 0 | 424.0222 | 0 | 5.8467 | 0 | 0.58438 | 0 | 0 | 0 | 5.8467 | 0 | 0
5 | 9 | 21 | 6.689 | 0 | 6.689 | 11 | 10.3235 | 0 | 0 | 403.8113 | 0 | 6.689 | 0 | 0.66857 | 0 | 0 | 0 | 6.689 | 0 | 0
5 | 9 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 391.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 23 | 58.2549 | 0 | 58.2549 | 11 | 4.5734 | 22.4019 | 22.4019 | 386.7212 | 58.2549 | 0 | 21887.6116 | 0 | 0 | 0 | 58.2549 | 0 | 0 | 21887.6116
5 | 10 | 0 | 74.193 | 0 | 74.193 | 11 | 3.8373 | 25.1256 | 25.1256 | 378.8244 | 74.193 | 0 | 27290.0051 | 0 | 0 | 0 | 74.193 | 0 | 0 | 27290.0051
5 | 10 | 1 | 98.9118 | 0 | 98.9118 | 11 | 3.605 | 32.2811 | 32.2811 | 377.8999 | 98.9118 | 0 | 36290.7434 | 0 | 0 | 0 | 98.9118 | 0 | 0 | 36290.7434
5 | 10 | 2 | 293.7121 | 0 | 293.7121 | 11 | 3.5018 | 94.3349 | 94.3349 | 392.2516 | 293.7121 | 0 | 111978.2305 | 0 | 0 | 0 | 293.7121 | 0 | 0 | 111978.2305
5 | 10 | 3 | 311.6848 | 0 | 311.6848 | 11 | 3.4416 | 99.1889 | 99.1889 | 433.5487 | 311.6848 | 0 | 131701.9894 | 0 | 0 | 0 | 311.6848 | 0 | 0 | 131701.9894
5 | 10 | 4 | 20.8238 | 0 | 20.8238 | 11 | 3.6222 | 6.8144 | 6.8144 | 454.5711 | 20.8238 | 0 | 9236.8377 | 0 | 0 | 0 | 20.8238 | 0 | 0 | 9236.8377
5 | 10 | 5 | 0.94996 | 0 | 0.94996 | 11 | 4.0351 | 0.33237 | 0.33237 | 457.6209 | 0.94996 | 0 | 424.2712 | 0 | 0 | 0 | 0.94996 | 0 | 0 | 424.2712
5 | 10 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 468.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 7 | 0.41389 | 0 | 0.41389 | 11 | 5.3599 | 0.18611 | 0.18611 | 474.847 | 0.41389 | 0 | 191.9804 | 0 | 0 | 0 | 0.41389 | 0 | 0 | 191.9804
5 | 10 | 8 | 20.7666 | 28.0915 | 48.8581 | 32.2735 | 6.5729 | 29.7339 | 29.7339 | 478.1461 | 48.8581 | 0 | 21784.4794 | 0 | 0 | 0 | 48.8581 | 0 | 0 | 21784.4794
5 | 10 | 9 | 24.5108 | 8.2018 | 32.7126 | 20.2768 | 7.6912 | 29.5303 | 29.5303 | 487.1345 | 32.7126 | 0 | 15272.1519 | 0 | 0 | 0 | 32.7126 | 0 | 0 | 15272.1519
5 | 10 | 10 | 9.33 | 35.7367 | 45.0667 | 40.34 | 8.4482 | 60.4652 | 60.4652 | 472.0552 | 45.0667 | 0 | 19455.9952 | 0 | 0 | 0 | 45.0667 | 0 | 0 | 19455.9952
5 | 10 | 11 | 9.59 | 137.9052 | 147.4952 | 45.5943 | 9.7214 | 1086.2204 | 288 | 474.2749 | 39.1068 | 108.3884 | 16764.3275 | 10.8334 | 0 | 0 | 39.1068 | 108.3884 | 0 | 16764.3275
5 | 10 | 12 | 6.3533 | 141.404 | 147.7573 | 46.4091 | 9.4117 | 520.1705 | 288 | 464.6713 | 81.808 | 65.9493 | 34217.1963 | 6.5917 | 0 | 0 | 81.808 | 65.9493 | 0 | 34217.1963
5 | 10 | 13 | 11.149 | 281.0761 | 292.225 | 46.5884 | 8.8869 | 545.9216 | 288 | 459.2594 | 154.1628 | 138.0622 | 63618.5288 | 13.7994 | 0 | 0 | 154.1628 | 138.0622 | 0 | 63618.5288
5 | 10 | 14 | 7.9308 | 66.8317 | 74.7625 | 44.075 | 9.3428 | 235.8407 | 235.8407 | 469.8965 | 74.7625 | 0 | 31835.4599 | 0 | 0 | 0 | 74.7625 | 0 | 0 | 31835.4599
5 | 10 | 15 | 20.0592 | 277.9739 | 298.0331 | 45.5097 | 10.0224 | 0 | 0 | 487.7453 | 0 | 298.0331 | 0 | 29.7885 | 0 | 0 | 0 | 298.0331 | 0 | 0
5 | 10 | 16 | 27.6557 | 263.2208 | 290.8765 | 44.4821 | 11.4074 | 0 | 0 | 489.565 | 0 | 290.8765 | 0 | 29.0732 | 0 | 0 | 0 | 290.8765 | 0 | 0
5 | 10 | 17 | 10.7917 | 9.1899 | 19.9816 | 28.017 | 10.8053 | 0 | 0 | 478.3411 | 0 | 19.9816 | 0 | 1.9972 | 0 | 0 | 0 | 19.9816 | 0 | 0
5 | 10 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 485.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 479.4537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 451.1957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 427.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 407.5229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 405.9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 0 | 0.74608 | 0 | 0.74608 | 11 | 4.5083 | 0.2835 | 0.2835 | 401.0851 | 0.74608 | 0 | 291.0341 | 0 | 0 | 0 | 0.74608 | 0 | 0 | 291.0341
5 | 11 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 401.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 416.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 3 | 0.058333 | 0 | 0.058333 | 11 | 3.7857 | 0.019591 | 0.019591 | 450.7073 | 0.058333 | 0 | 25.6496 | 0 | 0 | 0 | 0.058333 | 0 | 0 | 25.6496
5 | 11 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 468.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 482.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 6 | 0 | 0.0087083 | 0.0087083 | 48 | 4.7319 | 0.0034495 | 0.0034495 | 486.7087 | 0.0087083 | 0 | 3.8204 | 0 | 0 | 0 | 0.0087083 | 0 | 0 | 3.8204
5 | 11 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 487.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 489.8376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 481.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 10 | 0 | 15.3255 | 15.3255 | 48 | 7.3471 | 12.0435 | 12.0435 | 487.1313 | 15.3255 | 0 | 6729.8927 | 0 | 0 | 0 | 15.3255 | 0 | 0 | 6729.8927
5 | 11 | 11 | 0 | 4.5281 | 4.5281 | 48 | 8.9643 | 9.0886 | 9.0886 | 484.7522 | 4.5281 | 0 | 1977.6728 | 0 | 0 | 0 | 4.5281 | 0 | 0 | 1977.6728
5 | 11 | 12 | 0 | 67.1165 | 67.1165 | 48 | 8.2847 | 81.4929 | 81.4929 | 487.1308 | 67.1165 | 0 | 29472.9169 | 0 | 0 | 0 | 67.1165 | 0 | 0 | 29472.9169
5 | 11 | 13 | 0.1602 | 0 | 0.1602 | 11 | 7.8202 | 0.15316 | 0.15316 | 477.3986 | 0.1602 | 0 | 74.717 | 0 | 0 | 0 | 0.1602 | 0 | 0 | 74.717
5 | 11 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 482.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 492.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 486.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 475.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 18 | 0 | 0.038708 | 0.038708 | 48 | 7.0804 | 0.027645 | 0.027645 | 490.7175 | 0.038708 | 0 | 17.1369 | 0 | 0 | 0 | 0.038708 | 0 | 0 | 17.1369
5 | 11 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 475.4079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 452.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 415.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 22 | 3.1321 | 0 | 3.1321 | 11 | 4.9212 | 1.2868 | 1.2868 | 393.4037 | 3.1321 | 0 | 1197.7123 | 0 | 0 | 0 | 3.1321 | 0 | 0 | 1197.7123
5 | 11 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 390.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 0 | 0.45 | 0 | 0.45 | 11 | 3.8459 | 0.15261 | 0.15261 | 385.6392 | 0.45 | 0 | 168.5877 | 0 | 0 | 0 | 0.45 | 0 | 0 | 168.5877
5 | 12 | 1 | 0.058333 | 0 | 0.058333 | 11 | 3.4243 | 0.018515 | 0.018515 | 390.594 | 0.058333 | 0 | 22.143 | 0 | 0 | 0 | 0.058333 | 0 | 0 | 22.143
5 | 12 | 2 | 5.34 | 0 | 5.34 | 11 | 3.3383 | 1.6731 | 1.6731 | 410.052 | 5.34 | 0 | 2130.934 | 0 | 0 | 0 | 5.34 | 0 | 0 | 2130.934
5 | 12 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 425.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 4 | 0.025 | 0 | 0.025 | 11 | 3.2609 | 0.0077428 | 0.0077428 | 451.6427 | 0.025 | 0 | 11.0161 | 0 | 0 | 0 | 0.025 | 0 | 0 | 11.0161
5 | 12 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 463.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 6 | 0 | 0.031958 | 0.031958 | 48 | 4.9556 | 0.01322 | 0.01322 | 467.2616 | 0.031958 | 0 | 13.3989 | 0 | 0 | 0 | 0.031958 | 0 | 0 | 13.3989
5 | 12 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 457.9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 465.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 465.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 10 | 2.4975 | 2.7969 | 5.2944 | 30.5461 | 7.8632 | 5.1632 | 5.1632 | 477.549 | 5.2944 | 0 | 2366.5989 | 0 | 0 | 0 | 5.2944 | 0 | 0 | 2366.5989
5 | 12 | 11 | 3.8217 | 0.96777 | 4.7894 | 18.4763 | 7.6051 | 4.1685 | 4.1685 | 458.3674 | 4.7894 | 0 | 2106.8304 | 0 | 0 | 0 | 4.7894 | 0 | 0 | 2106.8304
5 | 12 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 463.8495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 458.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 462.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 15 | 0 | 62.1714 | 62.1714 | 48 | 7.803 | 58.9735 | 58.9735 | 463.8603 | 62.1714 | 0 | 25854.6137 | 0 | 0 | 0 | 62.1714 | 0 | 0 | 25854.6137
5 | 12 | 16 | 0 | 12.1525 | 12.1525 | 48 | 7.6998 | 11.0112 | 11.0112 | 462.3687 | 12.1525 | 0 | 5035.6146 | 0 | 0 | 0 | 12.1525 | 0 | 0 | 5035.6146
5 | 12 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 449.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 463.9791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 455.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 423.1563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 405.2516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 22 | 1.4713 | 0 | 1.4713 | 11 | 5.0846 | 0.62459 | 0.62459 | 400.2454 | 1.4713 | 0 | 572.7109 | 0 | 0 | 0 | 1.4713 | 0 | 0 | 572.7109
5 | 12 | 23 | 1.25 | 0 | 1.25 | 11 | 4.4566 | 0.47057 | 0.47057 | 387.6618 | 1.25 | 0 | 470.8272 | 0 | 0 | 0 | 1.25 | 0 | 0 | 470.8272
5 | 13 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 382.1192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 383.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 396.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 416.9871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 4 | 0.54416 | 0 | 0.54416 | 11 | 3.6824 | 0.17977 | 0.17977 | 441.4351 | 0.54416 | 0 | 234.2271 | 0 | 0 | 0 | 0.54416 | 0 | 0 | 234.2271
5 | 13 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 459.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 457.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 7 | 10.634 | 102.5965 | 113.2306 | 44.5251 | 6.3664 | 64.9994 | 64.9994 | 462.1237 | 113.2306 | 0 | 47284.9238 | 0 | 0 | 0 | 113.2306 | 0 | 0 | 47284.9238
5 | 13 | 8 | 4.2712 | 281.1459 | 285.4171 | 47.4463 | 6.9944 | 198.0179 | 198.0179 | 457.8341 | 285.4171 | 0 | 117131.7128 | 0 | 0 | 0 | 285.4171 | 0 | 0 | 117131.7128
5 | 13 | 9 | 64.5555 | 406.8582 | 471.4137 | 42.9332 | 7.5707 | 404.4988 | 288 | 447.9841 | 335.6429 | 135.7708 | 135952.4698 | 13.5703 | 0 | 0 | 335.6429 | 135.7708 | 0 | 135952.4698
5 | 13 | 10 | 12.5725 | 690.2812 | 702.8537 | 47.3382 | 7.4159 | 567.0184 | 288 | 458.4708 | 356.9935 | 345.8602 | 146771.6697 | 34.5688 | 0 | 0 | 356.9935 | 345.8602 | 0 | 146771.6697
5 | 13 | 11 | 7.6366 | 108.0673 | 115.7039 | 45.5579 | 7.5879 | 99.987 | 99.987 | 469.1296 | 115.7039 | 0 | 49008.9031 | 0 | 0 | 0 | 115.7039 | 0 | 0 | 49008.9031
5 | 13 | 12 | 22.446 | 145.9394 | 168.3854 | 43.0678 | 8.3192 | 208.627 | 208.627 | 460.4863 | 168.3854 | 0 | 70287.1692 | 0 | 0 | 0 | 168.3854 | 0 | 0 | 70287.1692
5 | 13 | 13 | 12.6737 | 108.7481 | 121.4218 | 44.138 | 8.6546 | 187.8174 | 187.8174 | 464.8754 | 121.4218 | 0 | 51086.6979 | 0 | 0 | 0 | 121.4218 | 0 | 0 | 51086.6979
5 | 13 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 457.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 15 | 0 | 61.7069 | 61.7069 | 48 | 8.8009 | 107.0421 | 107.0421 | 459.7498 | 61.7069 | 0 | 25407.7973 | 0 | 0 | 0 | 61.7069 | 0 | 0 | 25407.7973
5 | 13 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 448.5839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 17 | 9.5915 | 0 | 9.5915 | 11 | 9.0762 | 21.5694 | 21.5694 | 455.7144 | 9.5915 | 0 | 4265.4699 | 0 | 0 | 0 | 9.5915 | 0 | 0 | 4265.4699
5 | 13 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 458.3755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 438.4205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 405.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 385.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 379.6454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 370.7067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 0 | 0.33604 | 0 | 0.33604 | 11 | 3.3125 | 0.10488 | 0.10488 | 367.1542 | 0.33604 | 0 | 119.6821 | 0 | 0 | 0 | 0.33604 | 0 | 0 | 119.6821
5 | 14 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 363.9915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 368.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 367.5426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 4 | 6.0761 | 0 | 6.0761 | 11 | 3.3469 | 1.9062 | 1.9062 | 371.0873 | 6.0761 | 0 | 2187.9372 | 0 | 0 | 0 | 6.0761 | 0 | 0 | 2187.9372
5 | 14 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 382.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 389.8666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 406.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 8 | 0 | 0.96846 | 0.96846 | 48 | 5.1879 | 0.41992 | 0.41992 | 408.4898 | 0.96846 | 0 | 349.1194 | 0 | 0 | 0 | 0.96846 | 0 | 0 | 349.1194
5 | 14 | 9 | 0 | 7.1225 | 7.1225 | 48 | 6.7449 | 4.5633 | 4.5633 | 412.3882 | 7.1225 | 0 | 2595.3548 | 0 | 0 | 0 | 7.1225 | 0 | 0 | 2595.3548
5 | 14 | 10 | 0 | 7.4339 | 7.4339 | 48 | 8.8783 | 13.7815 | 13.7815 | 408.2789 | 7.4339 | 0 | 2678.2598 | 0 | 0 | 0 | 7.4339 | 0 | 0 | 2678.2598
5 | 14 | 11 | 0 | 7.7083 | 7.7083 | 48 | 9.8676 | 117.1977 | 117.1977 | 407.144 | 7.7083 | 0 | 2768.4018 | 0 | 0 | 0 | 7.7083 | 0 | 0 | 2768.4018
5 | 14 | 12 | 19.796 | 3.9546 | 23.7506 | 17.1607 | 10.2547 | 0 | 0 | 408.0724 | 0 | 23.7506 | 0 | 2.3739 | 0 | 0 | 0 | 23.7506 | 0 | 0
5 | 14 | 13 | 74.2145 | 3.1439 | 77.3584 | 12.5037 | 10.031 | 0 | 0 | 401.0108 | 0 | 77.3584 | 0 | 7.732 | 0 | 0 | 0 | 77.3584 | 0 | 0
5 | 14 | 14 | 78.0849 | 3.7062 | 81.7911 | 12.6766 | 9.9364 | 2491.839 | 288 | 404.8725 | 9.4532 | 72.3379 | 3707.5025 | 7.2302 | 0 | 0 | 9.4532 | 72.3379 | 0 | 3707.5025
5 | 14 | 15 | 83.22 | 1.3361 | 84.5561 | 11.5847 | 11.1494 | 0 | 0 | 402.29 | 0 | 84.5561 | 0 | 8.4514 | 0 | 0 | 0 | 84.5561 | 0 | 0
5 | 14 | 16 | 127.5203 | 0 | 127.5203 | 11 | 12.5086 | 0 | 0 | 407.278 | 0 | 127.5203 | 0 | 12.7457 | 0 | 0 | 0 | 127.5203 | 0 | 0
5 | 14 | 17 | 104.2859 | 0 | 104.2859 | 11 | 12.2591 | 0 | 0 | 418.1007 | 0 | 104.2859 | 0 | 10.4234 | 0 | 0 | 0 | 104.2859 | 0 | 0
5 | 14 | 18 | 80.9812 | 0.00575 | 80.987 | 11.0026 | 12.801 | 0 | 0 | 439.8814 | 0 | 80.987 | 0 | 8.0947 | 0 | 0 | 0 | 80.987 | 0 | 0
5 | 14 | 19 | 42.0827 | 0 | 42.0827 | 11 | 12.7322 | 0 | 0 | 435.9094 | 0 | 42.0827 | 0 | 4.2062 | 0 | 0 | 0 | 42.0827 | 0 | 0
5 | 14 | 20 | 31.3461 | 0 | 31.3461 | 11 | 13.3172 | 0 | 0 | 410.9865 | 0 | 31.3461 | 0 | 3.133 | 0 | 0 | 0 | 31.3461 | 0 | 0
5 | 14 | 21 | 79.2951 | 0 | 79.2951 | 11 | 9.2568 | 221.3775 | 221.3775 | 388.661 | 79.2951 | 0 | 29946.6676 | 0 | 0 | 0 | 79.2951 | 0 | 0 | 29946.6676
5 | 14 | 22 | 73.2824 | 0 | 73.2824 | 11 | 5.3857 | 33.1363 | 33.1363 | 376.2458 | 73.2824 | 0 | 26766.0711 | 0 | 0 | 0 | 73.2824 | 0 | 0 | 26766.0711
5 | 14 | 23 | 0.0058866 | 0 | 0.0058866 | 11 | 3.6704 | 0.001941 | 0.001941 | 373.2743 | 0.0058866 | 0 | 2.1326 | 0 | 0 | 0 | 0.0058866 | 0 | 0 | 2.1326
5 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 369.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 370.6591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 371.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 3 | 1.7331 | 0 | 1.7331 | 11 | 3.4416 | 0.55152 | 0.55152 | 366.4569 | 1.7331 | 0 | 616.0306 | 0 | 0 | 0 | 1.7331 | 0 | 0 | 616.0306
5 | 15 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 364.2951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 385.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 383.3261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 7 | 23.2857 | 0 | 23.2857 | 11 | 5.1706 | 10.0608 | 10.0608 | 379.7765 | 23.2857 | 0 | 8587.2037 | 0 | 0 | 0 | 23.2857 | 0 | 0 | 8587.2037
5 | 15 | 8 | 18.8805 | 0 | 18.8805 | 11 | 5.8502 | 9.4918 | 9.4918 | 374.3373 | 18.8805 | 0 | 6859.9896 | 0 | 0 | 0 | 18.8805 | 0 | 0 | 6859.9896
5 | 15 | 9 | 3.2681 | 0 | 3.2681 | 11 | 6.7707 | 2.1106 | 2.1106 | 380.3792 | 3.2681 | 0 | 1207.173 | 0 | 0 | 0 | 3.2681 | 0 | 0 | 1207.173
5 | 15 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 385.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 11 | 8.3183 | 3.2727 | 11.5911 | 21.4469 | 10.0569 | 0 | 0 | 380.6329 | 0 | 11.5911 | 0 | 1.1585 | 0 | 0 | 0 | 11.5911 | 0 | 0
5 | 15 | 12 | 10.6166 | 0.25612 | 10.8727 | 11.8716 | 10.1343 | 0 | 0 | 380.8138 | 0 | 10.8727 | 0 | 1.0867 | 0 | 0 | 0 | 10.8727 | 0 | 0
5 | 15 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 383.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 389.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 15 | 8.1882 | 0 | 8.1882 | 11 | 10.9601 | 0 | 0 | 403.4943 | 0 | 8.1882 | 0 | 0.81841 | 0 | 0 | 0 | 8.1882 | 0 | 0
5 | 15 | 16 | 12.8875 | 12.5133 | 25.4008 | 29.2275 | 11.5279 | 0 | 0 | 408.1156 | 0 | 25.4008 | 0 | 2.5388 | 0 | 0 | 0 | 25.4008 | 0 | 0
5 | 15 | 17 | 7.0265 | 0 | 7.0265 | 11 | 11.5451 | 0 | 0 | 420.7624 | 0 | 7.0265 | 0 | 0.7023 | 0 | 0 | 0 | 7.0265 | 0 | 0
5 | 15 | 18 | 15.9928 | 0 | 15.9928 | 11 | 11.9236 | 0 | 0 | 438.2373 | 0 | 15.9928 | 0 | 1.5985 | 0 | 0 | 0 | 15.9928 | 0 | 0
5 | 15 | 19 | 13.0027 | 0 | 13.0027 | 11 | 13.1107 | 0 | 0 | 437.945 | 0 | 13.0027 | 0 | 1.2996 | 0 | 0 | 0 | 13.0027 | 0 | 0
5 | 15 | 20 | 3.5852 | 0 | 3.5852 | 11 | 12.6978 | 0 | 0 | 418.2778 | 0 | 3.5852 | 0 | 0.35834 | 0 | 0 | 0 | 3.5852 | 0 | 0
5 | 15 | 21 | 2.9266 | 0 | 2.9266 | 11 | 9.8762 | 47.4678 | 47.4678 | 395.0536 | 2.9266 | 0 | 1123.9545 | 0 | 0 | 0 | 2.9266 | 0 | 0 | 1123.9545
5 | 15 | 22 | 4.7142 | 0 | 4.7142 | 11 | 6.1771 | 2.5724 | 2.5724 | 380.3512 | 4.7142 | 0 | 1741.1966 | 0 | 0 | 0 | 4.7142 | 0 | 0 | 1741.1966
5 | 15 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 371.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 373.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 377.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 394.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 422.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 432.7489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 445.4651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 6 | 54.6788 | 0 | 54.6788 | 11 | 5.3513 | 24.5415 | 24.5415 | 449.5221 | 54.6788 | 0 | 23977.8743 | 0 | 0 | 0 | 54.6788 | 0 | 0 | 23977.8743
5 | 16 | 7 | 145.4511 | 380.3716 | 525.8227 | 37.7652 | 5.6008 | 249.3733 | 249.3733 | 451.9053 | 525.8227 | 0 | 217764.2703 | 0 | 0 | 0 | 525.8227 | 0 | 0 | 217764.2703
5 | 16 | 8 | 97.7911 | 387.8095 | 485.6005 | 40.5489 | 6.5729 | 295.525 | 288 | 445.9455 | 473.2357 | 12.3649 | 191848.1344 | 1.2359 | 0 | 0 | 473.2357 | 12.3649 | 0 | 191848.1344
5 | 16 | 9 | 99.5113 | 406.4093 | 505.9206 | 40.7223 | 7.7084 | 460.1245 | 288 | 449.9079 | 316.6646 | 189.256 | 129574.5796 | 18.9162 | 0 | 0 | 316.6646 | 189.256 | 0 | 129574.5796
5 | 16 | 10 | 87.7509 | 374.6437 | 462.3946 | 40.9783 | 8.9471 | 912.9977 | 288 | 447.0447 | 145.8598 | 316.5348 | 59228.7587 | 31.6377 | 0 | 0 | 145.8598 | 316.5348 | 0 | 59228.7587
5 | 16 | 11 | 87.8125 | 57.0898 | 144.9023 | 25.5776 | 9.5923 | 733.4382 | 288 | 450.1267 | 56.899 | 88.0034 | 24156.4032 | 8.796 | 0 | 0 | 56.899 | 88.0034 | 0 | 24156.4032
5 | 16 | 12 | 108.4326 | 15.2801 | 123.7127 | 15.57 | 10.2891 | 0 | 0 | 444.9839 | 0 | 123.7127 | 0 | 12.3651 | 0 | 0 | 0 | 123.7127 | 0 | 0
5 | 16 | 13 | 89.9236 | 0 | 89.9236 | 11 | 10.0827 | 0 | 0 | 442.2338 | 0 | 89.9236 | 0 | 8.9879 | 0 | 0 | 0 | 89.9236 | 0 | 0
5 | 16 | 14 | 14.111 | 0 | 14.111 | 11 | 10.6934 | 0 | 0 | 441.0916 | 0 | 14.111 | 0 | 1.4104 | 0 | 0 | 0 | 14.111 | 0 | 0
5 | 16 | 15 | 3.4232 | 0 | 3.4232 | 11 | 11.6655 | 0 | 0 | 441.407 | 0 | 3.4232 | 0 | 0.34215 | 0 | 0 | 0 | 3.4232 | 0 | 0
5 | 16 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 441.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 455.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 475.6382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 459.2153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 432.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 412.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 22 | 1.1456 | 0 | 1.1456 | 11 | 5.6868 | 0.55415 | 0.55415 | 397.5875 | 1.1456 | 0 | 442.89 | 0 | 0 | 0 | 1.1456 | 0 | 0 | 442.89
5 | 16 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 396.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 0 | 26.3265 | 0 | 26.3265 | 11 | 3.8373 | 8.9155 | 8.9155 | 396.3013 | 26.3265 | 0 | 10143.6532 | 0 | 0 | 0 | 26.3265 | 0 | 0 | 10143.6532
5 | 17 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 402.4876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 414.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 3 | 22.5225 | 0 | 22.5225 | 11 | 3.4416 | 7.1674 | 7.1674 | 437.872 | 22.5225 | 0 | 9614.2145 | 0 | 0 | 0 | 22.5225 | 0 | 0 | 9614.2145
5 | 17 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 467.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 480.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 484.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 474.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 483.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 477.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 477.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 477.5595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 477.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 476.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 14 | 7.3659 | 0 | 7.3659 | 11 | 9.3428 | 23.2361 | 23.2361 | 473.621 | 7.3659 | 0 | 3407.6363 | 0 | 0 | 0 | 7.3659 | 0 | 0 | 3407.6363
5 | 17 | 15 | 2.8416 | 0 | 2.8416 | 11 | 10.0224 | 0 | 0 | 474.7388 | 0 | 2.8416 | 0 | 0.28402 | 0 | 0 | 0 | 2.8416 | 0 | 0
5 | 17 | 16 | 37.9417 | 4.3532 | 42.2949 | 14.8082 | 11.4074 | 0 | 0 | 461.537 | 0 | 42.2949 | 0 | 4.2274 | 0 | 0 | 0 | 42.2949 | 0 | 0
5 | 17 | 17 | 19.8 | 95.8268 | 115.6268 | 41.6641 | 10.8053 | 0 | 0 | 459.7552 | 0 | 115.6268 | 0 | 11.5569 | 0 | 0 | 0 | 115.6268 | 0 | 0
5 | 17 | 18 | 12.0508 | 0 | 12.0508 | 11 | 11.5107 | 0 | 0 | 460.4303 | 0 | 12.0508 | 0 | 1.2045 | 0 | 0 | 0 | 12.0508 | 0 | 0
5 | 17 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 459.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 429.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 21 | 9.5326 | 0 | 9.5326 | 11 | 7.4847 | 7.9003 | 7.9003 | 403.5718 | 9.5326 | 0 | 3742.2385 | 0 | 0 | 0 | 9.5326 | 0 | 0 | 3742.2385
5 | 17 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 386.1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 23 | 0.28188 | 0 | 0.28188 | 11 | 4.5599 | 0.10813 | 0.10813 | 377.401 | 0.28188 | 0 | 103.2829 | 0 | 0 | 0 | 0.28188 | 0 | 0 | 103.2829
5 | 18 | 0 | 13.9101 | 0 | 13.9101 | 11 | 4.5083 | 5.2857 | 5.2857 | 378.1702 | 13.9101 | 0 | 5107.3788 | 0 | 0 | 0 | 13.9101 | 0 | 0 | 5107.3788
5 | 18 | 1 | 12.0166 | 0 | 12.0166 | 11 | 4.2072 | 4.3291 | 4.3291 | 379.854 | 12.0166 | 0 | 4432.3587 | 0 | 0 | 0 | 12.0166 | 0 | 0 | 4432.3587
5 | 18 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 393.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 424.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 441.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 5 | 0.43874 | 0 | 0.43874 | 11 | 3.9663 | 0.15176 | 0.15176 | 448.974 | 0.43874 | 0 | 192.1571 | 0 | 0 | 0 | 0.43874 | 0 | 0 | 192.1571
5 | 18 | 6 | 12.6535 | 0 | 12.6535 | 11 | 4.7319 | 5.0122 | 5.0122 | 455.4385 | 12.6535 | 0 | 5623.6892 | 0 | 0 | 0 | 12.6535 | 0 | 0 | 5623.6892
5 | 18 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 458.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 457.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 9 | 8.7917 | 12.5969 | 21.3885 | 32.7913 | 6.9858 | 14.7968 | 14.7968 | 452.7888 | 21.3885 | 0 | 8983.1367 | 0 | 0 | 0 | 21.3885 | 0 | 0 | 8983.1367
5 | 18 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 451.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 452.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 452.5887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 450.2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 451.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 451.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 444.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 436.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 442.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 438.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 20 | 2.4281 | 0 | 2.4281 | 11 | 7.3471 | 1.9081 | 1.9081 | 409.822 | 2.4281 | 0 | 968.3804 | 0 | 0 | 0 | 2.4281 | 0 | 0 | 968.3804
5 | 18 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 380.7648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 375.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 375.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 0 | 5.5847 | 0 | 5.5847 | 11 | 3.8459 | 1.8939 | 1.8939 | 373.8651 | 5.5847 | 0 | 2026.5072 | 0 | 0 | 0 | 5.5847 | 0 | 0 | 2026.5072
5 | 19 | 1 | 0.33831 | 0 | 0.33831 | 11 | 3.4243 | 0.10738 | 0.10738 | 373.8881 | 0.33831 | 0 | 122.7676 | 0 | 0 | 0 | 0.33831 | 0 | 0 | 122.7676
5 | 19 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 388.6896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 3 | 1.528 | 0 | 1.528 | 11 | 3.3039 | 0.47629 | 0.47629 | 417.2382 | 1.528 | 0 | 620.7465 | 0 | 0 | 0 | 1.528 | 0 | 0 | 620.7465
5 | 19 | 4 | 0.39856 | 0 | 0.39856 | 11 | 3.2609 | 0.12344 | 0.12344 | 443.1177 | 0.39856 | 0 | 172.2254 | 0 | 0 | 0 | 0.39856 | 0 | 0 | 172.2254
5 | 19 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 450.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 457.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 461.7841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 458.1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 459.9537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 459.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 458.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 461.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 458.0079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 14 | 0 | 63.3547 | 63.3547 | 48 | 8.6374 | 96.7653 | 96.7653 | 455.9127 | 63.3547 | 0 | 25843.1909 | 0 | 0 | 0 | 63.3547 | 0 | 0 | 25843.1909
5 | 19 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 458.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 455.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 17 | 0.067243 | 0 | 0.067243 | 11 | 7.6482 | 0.059594 | 0.059594 | 441.0307 | 0.067243 | 0 | 28.9165 | 0 | 0 | 0 | 0.067243 | 0 | 0 | 28.9165
5 | 19 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 454.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 441.1051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 20 | 1.7461 | 0 | 1.7461 | 11 | 6.6417 | 1.0844 | 1.0844 | 410.049 | 1.7461 | 0 | 696.7702 | 0 | 0 | 0 | 1.7461 | 0 | 0 | 696.7702
5 | 19 | 21 | 8.423 | 0 | 8.423 | 11 | 5.9879 | 4.3796 | 4.3796 | 369.8677 | 8.423 | 0 | 3022.7385 | 0 | 0 | 0 | 8.423 | 0 | 0 | 3022.7385
5 | 19 | 22 | 6.8049 | 0 | 6.8049 | 11 | 5.0846 | 2.8887 | 2.8887 | 363.5606 | 6.8049 | 0 | 2399.1404 | 0 | 0 | 0 | 6.8049 | 0 | 0 | 2399.1404
5 | 19 | 23 | 6.1812 | 0 | 6.1812 | 11 | 4.4566 | 2.3269 | 2.3269 | 353.6301 | 6.1812 | 0 | 2117.8514 | 0 | 0 | 0 | 6.1812 | 0 | 0 | 2117.8514
5 | 20 | 0 | 2.4679 | 0 | 2.4679 | 11 | 3.9749 | 0.85485 | 0.85485 | 344.0931 | 2.4679 | 0 | 822.0557 | 0 | 0 | 0 | 2.4679 | 0 | 0 | 822.0557
5 | 20 | 1 | 106.2498 | 0 | 106.2498 | 11 | 3.7598 | 35.5357 | 35.5357 | 348.5209 | 106.2498 | 0 | 35861.542 | 0 | 0 | 0 | 106.2498 | 0 | 0 | 35861.542
5 | 20 | 2 | 133.0132 | 0 | 133.0132 | 11 | 3.691 | 44.0019 | 44.0019 | 356.5176 | 133.0132 | 0 | 45958.3815 | 0 | 0 | 0 | 133.0132 | 0 | 0 | 45958.3815
5 | 20 | 3 | 171.1095 | 0 | 171.1095 | 11 | 3.6824 | 56.5275 | 56.5275 | 379.091 | 171.1095 | 0 | 62983.8617 | 0 | 0 | 0 | 171.1095 | 0 | 0 | 62983.8617
5 | 20 | 4 | 142.0132 | 0 | 142.0132 | 11 | 3.6824 | 46.9153 | 46.9153 | 406.3229 | 142.0132 | 0 | 56141.0662 | 0 | 0 | 0 | 142.0132 | 0 | 0 | 56141.0662
5 | 20 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 426.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 439.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 7 | 14.7649 | 0 | 14.7649 | 11 | 6.3664 | 8.4757 | 8.4757 | 437.4326 | 14.7649 | 0 | 6296.2511 | 0 | 0 | 0 | 14.7649 | 0 | 0 | 6296.2511
5 | 20 | 8 | 1.5683 | 0 | 1.5683 | 11 | 6.9944 | 1.088 | 1.088 | 428.2657 | 1.5683 | 0 | 654.3773 | 0 | 0 | 0 | 1.5683 | 0 | 0 | 654.3773
5 | 20 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 425.6235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 10 | 7.1799 | 0 | 7.1799 | 11 | 7.4159 | 5.7923 | 5.7923 | 429.2454 | 7.1799 | 0 | 3002.9521 | 0 | 0 | 0 | 7.1799 | 0 | 0 | 3002.9521
5 | 20 | 11 | 6.8838 | 0 | 6.8838 | 11 | 7.5879 | 5.9487 | 5.9487 | 431.778 | 6.8838 | 0 | 2896.533 | 0 | 0 | 0 | 6.8838 | 0 | 0 | 2896.533
5 | 20 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 439.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 442.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 435.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 15 | 0 | 0.40463 | 0.40463 | 48 | 8.8009 | 0.70191 | 0.70191 | 416.827 | 0.40463 | 0 | 149.2386 | 0 | 0 | 0 | 0.40463 | 0 | 0 | 149.2386
5 | 20 | 16 | 31.9533 | 7.3116 | 39.2649 | 17.8899 | 9.5837 | 194.6846 | 194.6846 | 401.5587 | 39.2649 | 0 | 15064.7012 | 0 | 0 | 0 | 39.2649 | 0 | 0 | 15064.7012
5 | 20 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 393.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 410.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 407.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 20 | 2.4856 | 0 | 2.4856 | 11 | 11.2698 | 0 | 0 | 388.9084 | 0 | 2.4856 | 0 | 0.24843 | 0 | 0 | 0 | 2.4856 | 0 | 0
5 | 20 | 21 | 5.1282 | 0 | 5.1282 | 11 | 9.1708 | 12.8405 | 12.8405 | 377.4678 | 5.1282 | 0 | 1879.3121 | 0 | 0 | 0 | 5.1282 | 0 | 0 | 1879.3121
5 | 20 | 22 | 11.11 | 0 | 11.11 | 11 | 5.4717 | 5.119 | 5.119 | 374.5127 | 11.11 | 0 | 4038.6129 | 0 | 0 | 0 | 11.11 | 0 | 0 | 4038.6129
5 | 20 | 23 | 43.7335 | 0 | 43.7335 | 11 | 4.8093 | 17.5814 | 17.5814 | 369.8846 | 43.7335 | 0 | 15695.2793 | 0 | 0 | 0 | 43.7335 | 0 | 0 | 15695.2793
5 | 21 | 0 | 80.1639 | 0 | 80.1639 | 11 | 3.3125 | 25.0191 | 25.0191 | 372.734 | 80.1639 | 0 | 28998.0212 | 0 | 0 | 0 | 80.1639 | 0 | 0 | 28998.0212
5 | 21 | 1 | 3.806 | 0 | 3.806 | 11 | 3.2007 | 1.1683 | 1.1683 | 370.5389 | 3.806 | 0 | 1368.4153 | 0 | 0 | 0 | 3.806 | 0 | 0 | 1368.4153
5 | 21 | 2 | 7.8338 | 0 | 7.8338 | 11 | 3.1921 | 2.4017 | 2.4017 | 374.3644 | 7.8338 | 0 | 2846.5276 | 0 | 0 | 0 | 7.8338 | 0 | 0 | 2846.5276
5 | 21 | 3 | 1.0651 | 0 | 1.0651 | 11 | 3.3297 | 0.33327 | 0.33327 | 373.1014 | 1.0651 | 0 | 385.6749 | 0 | 0 | 0 | 1.0651 | 0 | 0 | 385.6749
5 | 21 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 375.0918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 397.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 408.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 7 | 0 | 0.017042 | 0.017042 | 48 | 5.2137 | 0.0074291 | 0.0074291 | 414.3871 | 0.017042 | 0 | 6.2438 | 0 | 0 | 0 | 0.017042 | 0 | 0 | 6.2438
5 | 21 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 418.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 9 | 0 | 0.086625 | 0.086625 | 48 | 6.7449 | 0.0555 | 0.0555 | 410.7797 | 0.086625 | 0 | 31.4258 | 0 | 0 | 0 | 0.086625 | 0 | 0 | 31.4258
5 | 21 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 407.4986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 409.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 406.6472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 416.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 415.4195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 414.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 414.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 412.5011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 18 | 5.5011 | 0 | 5.5011 | 11 | 12.801 | 0 | 0 | 417.3633 | 0 | 5.5011 | 0 | 0.54984 | 0 | 0 | 0 | 5.5011 | 0 | 0
5 | 21 | 19 | 0.089316 | 0 | 0.089316 | 11 | 12.7322 | 0 | 0 | 422.0125 | 0 | 0.089316 | 0 | 0.0089272 | 0 | 0 | 0 | 0.089316 | 0 | 0
5 | 21 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 409.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 386.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 366.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 23 | 0.85367 | 0 | 0.85367 | 11 | 3.6704 | 0.28148 | 0.28148 | 362.2818 | 0.85367 | 0 | 299.878 | 0 | 0 | 0 | 0.85367 | 0 | 0 | 299.878
5 | 22 | 0 | 0.13111 | 0 | 0.13111 | 11 | 3.5706 | 0.042559 | 0.042559 | 361.8374 | 0.13111 | 0 | 45.9968 | 0 | 0 | 0 | 0.13111 | 0 | 0 | 45.9968
5 | 22 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 354.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 353.5765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 348.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 347.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 356.624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 375.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 7 | 10.574 | 81.6213 | 92.1953 | 43.7564 | 5.1706 | 39.8337 | 39.8337 | 380.8233 | 92.1953 | 0 | 31075.9925 | 0 | 0 | 0 | 92.1953 | 0 | 0 | 31075.9925
5 | 22 | 8 | 19.6191 | 349.1189 | 368.738 | 46.0314 | 5.8502 | 185.3758 | 185.3758 | 386.1211 | 368.738 | 0 | 125404.0027 | 0 | 0 | 0 | 368.738 | 0 | 0 | 125404.0027
5 | 22 | 9 | 30.7575 | 456.2431 | 487.0006 | 45.6632 | 6.7707 | 314.5079 | 288 | 388.9988 | 445.9543 | 41.0463 | 153112.0098 | 4.1026 | 0 | 0 | 445.9543 | 41.0463 | 0 | 153112.0098
5 | 22 | 10 | 39.6 | 450.4807 | 490.0807 | 45.0103 | 8.9987 | 1017.3004 | 288 | 389.85 | 138.7429 | 351.3377 | 47844.0744 | 35.1163 | 0 | 0 | 138.7429 | 351.3377 | 0 | 47844.0744
5 | 22 | 11 | 29.7 | 462.9221 | 492.6221 | 45.7693 | 10.0569 | 0 | 0 | 382.092 | 0 | 492.6221 | 0 | 49.2377 | 0 | 0 | 0 | 492.6221 | 0 | 0
5 | 22 | 12 | 27.3475 | 204.0374 | 231.385 | 43.6269 | 10.1343 | 0 | 0 | 384.6706 | 0 | 231.385 | 0 | 23.127 | 0 | 0 | 0 | 231.385 | 0 | 0
5 | 22 | 13 | 27.7233 | 216.833 | 244.5563 | 43.8056 | 10.2117 | 0 | 0 | 392.68 | 0 | 244.5563 | 0 | 24.4435 | 0 | 0 | 0 | 244.5563 | 0 | 0
5 | 22 | 14 | 43.7265 | 521.9145 | 565.641 | 45.1397 | 9.8762 | 9174.5198 | 288 | 404.4319 | 17.7562 | 547.8848 | 6379.6623 | 54.7612 | 0 | 0 | 17.7562 | 547.8848 | 0 | 6379.6623
5 | 22 | 15 | 52.7388 | 256.9009 | 309.6397 | 41.698 | 10.9601 | 0 | 0 | 409.6787 | 0 | 309.6397 | 0 | 30.9486 | 0 | 0 | 0 | 309.6397 | 0 | 0
5 | 22 | 16 | 55.0679 | 384.5175 | 439.5855 | 43.3649 | 11.5279 | 0 | 0 | 411.5075 | 0 | 439.5855 | 0 | 43.9367 | 0 | 0 | 0 | 439.5855 | 0 | 0
5 | 22 | 17 | 40.168 | 198.1028 | 238.2708 | 41.7625 | 11.5451 | 0 | 0 | 409.1129 | 0 | 238.2708 | 0 | 23.8152 | 0 | 0 | 0 | 238.2708 | 0 | 0
5 | 22 | 18 | 1.0737 | 0 | 1.0737 | 11 | 11.9236 | 0 | 0 | 412.3878 | 0 | 1.0737 | 0 | 0.10732 | 0 | 0 | 0 | 1.0737 | 0 | 0
5 | 22 | 19 | 1.167 | 0 | 1.167 | 11 | 13.1107 | 0 | 0 | 403.8196 | 0 | 1.167 | 0 | 0.11665 | 0 | 0 | 0 | 1.167 | 0 | 0
5 | 22 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 384.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 21 | 0.34309 | 0 | 0.34309 | 11 | 9.8762 | 5.5647 | 5.5647 | 367.9157 | 0.34309 | 0 | 122.4528 | 0 | 0 | 0 | 0.34309 | 0 | 0 | 122.4528
5 | 22 | 22 | 0.53825 | 0 | 0.53825 | 11 | 6.1771 | 0.2937 | 0.2937 | 362.6495 | 0.53825 | 0 | 189.2751 | 0 | 0 | 0 | 0.53825 | 0 | 0 | 189.2751
5 | 22 | 23 | 59.6807 | 0 | 59.6807 | 11 | 4.6373 | 23.2234 | 23.2234 | 362.3521 | 59.6807 | 0 | 20968.9555 | 0 | 0 | 0 | 59.6807 | 0 | 0 | 20968.9555
5 | 23 | 0 | 4.2292 | 0 | 4.2292 | 11 | 3.9577 | 1.4607 | 1.4607 | 366.3512 | 4.2292 | 0 | 1502.8434 | 0 | 0 | 0 | 4.2292 | 0 | 0 | 1502.8434
5 | 23 | 1 | 7.4825 | 0 | 7.4825 | 11 | 3.6394 | 2.4552 | 2.4552 | 367.154 | 7.4825 | 0 | 2664.9047 | 0 | 0 | 0 | 7.4825 | 0 | 0 | 2664.9047
5 | 23 | 2 | 36.3333 | 0 | 36.3333 | 11 | 3.5276 | 11.7161 | 11.7161 | 373.7843 | 36.3333 | 0 | 13181.1444 | 0 | 0 | 0 | 36.3333 | 0 | 0 | 13181.1444
5 | 23 | 3 | 11.4646 | 0 | 11.4646 | 11 | 3.562 | 3.7166 | 3.7166 | 400.3121 | 11.4646 | 0 | 4463.2935 | 0 | 0 | 0 | 11.4646 | 0 | 0 | 4463.2935
5 | 23 | 4 | 6.9249 | 0 | 6.9249 | 11 | 3.5878 | 2.254 | 2.254 | 426.6298 | 6.9249 | 0 | 2878.2113 | 0 | 0 | 0 | 6.9249 | 0 | 0 | 2878.2113
5 | 23 | 5 | 12.8472 | 0 | 12.8472 | 11 | 4.1814 | 4.6078 | 4.6078 | 441.9669 | 12.8472 | 0 | 5536.698 | 0 | 0 | 0 | 12.8472 | 0 | 0 | 5536.698
5 | 23 | 6 | 58.6239 | 0 | 58.6239 | 11 | 5.3513 | 26.3122 | 26.3122 | 451.7289 | 58.6239 | 0 | 25837.2394 | 0 | 0 | 0 | 58.6239 | 0 | 0 | 25837.2394
5 | 23 | 7 | 59.5636 | 521.5232 | 581.0869 | 44.2074 | 5.6008 | 275.5826 | 275.5826 | 463.566 | 581.0869 | 0 | 243683.81 | 0 | 0 | 0 | 581.0869 | 0 | 0 | 243683.81
5 | 23 | 8 | 3.291 | 157.859 | 161.1499 | 47.2444 | 6.5729 | 98.072 | 98.072 | 458.861 | 161.1499 | 0 | 66331.9907 | 0 | 0 | 0 | 161.1499 | 0 | 0 | 66331.9907
5 | 23 | 9 | 22.2227 | 122.5359 | 144.7586 | 42.3199 | 7.7084 | 131.655 | 131.655 | 469.1141 | 144.7586 | 0 | 61782.1432 | 0 | 0 | 0 | 144.7586 | 0 | 0 | 61782.1432
5 | 23 | 10 | 24.4345 | 0 | 24.4345 | 11 | 8.9471 | 48.2458 | 48.2458 | 472.1813 | 24.4345 | 0 | 11268.7113 | 0 | 0 | 0 | 24.4345 | 0 | 0 | 11268.7113
5 | 23 | 11 | 0.36729 | 0 | 0.36729 | 11 | 9.5923 | 1.8591 | 1.8591 | 467.3849 | 0.36729 | 0 | 167.6245 | 0 | 0 | 0 | 0.36729 | 0 | 0 | 167.6245
5 | 23 | 12 | 1.3767 | 0 | 1.3767 | 11 | 10.2891 | 0 | 0 | 470.3015 | 0 | 1.3767 | 0 | 0.13761 | 0 | 0 | 0 | 1.3767 | 0 | 0
5 | 23 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 464.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 477.3688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 15 | 0 | 25.7379 | 25.7379 | 48 | 11.6655 | 0 | 0 | 484.6025 | 0 | 25.7379 | 0 | 2.5725 | 0 | 0 | 0 | 25.7379 | 0 | 0
5 | 23 | 16 | 3.9908 | 65.8184 | 69.8092 | 45.8848 | 12.3021 | 0 | 0 | 471.9961 | 0 | 69.8092 | 0 | 6.9774 | 0 | 0 | 0 | 69.8092 | 0 | 0
5 | 23 | 17 | 24.7461 | 295.9227 | 320.6687 | 45.1447 | 12.1989 | 0 | 0 | 467.7535 | 0 | 320.6687 | 0 | 32.0509 | 0 | 0 | 0 | 320.6687 | 0 | 0
5 | 23 | 18 | 3.9658 | 67.8652 | 71.831 | 45.9572 | 12.9559 | 0 | 0 | 473.8895 | 0 | 71.831 | 0 | 7.1795 | 0 | 0 | 0 | 71.831 | 0 | 0
5 | 23 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 455.2307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 421.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 21 | 0.24479 | 0 | 0.24479 | 11 | 10.3235 | 0 | 0 | 394.5965 | 0 | 0.24479 | 0 | 0.024467 | 0 | 0 | 0 | 0.24479 | 0 | 0
5 | 23 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 381.2262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 23 | 1.0606 | 0 | 1.0606 | 11 | 4.5734 | 0.40785 | 0.40785 | 372.5594 | 1.0606 | 0 | 383.4644 | 0 | 0 | 0 | 1.0606 | 0 | 0 | 383.4644
5 | 24 | 0 | 2.6173 | 0 | 2.6173 | 11 | 3.8373 | 0.88637 | 0.88637 | 364.879 | 2.6173 | 0 | 926.2218 | 0 | 0 | 0 | 2.6173 | 0 | 0 | 926.2218
5 | 24 | 1 | 15.5796 | 0 | 15.5796 | 11 | 3.605 | 5.0846 | 5.0846 | 366.3673 | 15.5796 | 0 | 5536.4789 | 0 | 0 | 0 | 15.5796 | 0 | 0 | 5536.4789
5 | 24 | 2 | 130.2525 | 0 | 130.2525 | 11 | 3.5018 | 41.8347 | 41.8347 | 373.9442 | 130.2525 | 0 | 47274.4073 | 0 | 0 | 0 | 130.2525 | 0 | 0 | 47274.4073
5 | 24 | 3 | 11.7838 | 0 | 11.7838 | 11 | 3.4416 | 3.75 | 3.75 | 398.8038 | 11.7838 | 0 | 4569.7942 | 0 | 0 | 0 | 11.7838 | 0 | 0 | 4569.7942
5 | 24 | 4 | 14.4903 | 0 | 14.4903 | 11 | 3.6222 | 4.7418 | 4.7418 | 427.4649 | 14.4903 | 0 | 6034.7077 | 0 | 0 | 0 | 14.4903 | 0 | 0 | 6034.7077
5 | 24 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 449.5788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 462.5143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 7 | 0 | 46.6118 | 46.6118 | 48 | 5.3599 | 20.9595 | 20.9595 | 465.8361 | 46.6118 | 0 | 19476.0966 | 0 | 0 | 0 | 46.6118 | 0 | 0 | 19476.0966
5 | 24 | 8 | 23.7058 | 196.2281 | 219.9339 | 44.0119 | 6.5729 | 133.8466 | 133.8466 | 473.6767 | 219.9339 | 0 | 94497.8641 | 0 | 0 | 0 | 219.9339 | 0 | 0 | 94497.8641
5 | 24 | 9 | 32.4791 | 4.6189 | 37.0981 | 15.6067 | 7.6912 | 33.489 | 33.489 | 469.3505 | 37.0981 | 0 | 16833.0118 | 0 | 0 | 0 | 37.0981 | 0 | 0 | 16833.0118
5 | 24 | 10 | 10.5581 | 9.9286 | 20.4867 | 28.9315 | 8.4482 | 27.4866 | 27.4866 | 467.5474 | 20.4867 | 0 | 8985.788 | 0 | 0 | 0 | 20.4867 | 0 | 0 | 8985.788
5 | 24 | 11 | 39.7448 | 212.6827 | 252.4275 | 42.1743 | 9.7214 | 1858.9889 | 288 | 469.8465 | 39.1068 | 213.3207 | 16724.8904 | 21.3215 | 0 | 0 | 39.1068 | 213.3207 | 0 | 16724.8904
5 | 24 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 472.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 475.7478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 473.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 480.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 16 | 38.3342 | 383.6722 | 422.0064 | 44.639 | 11.4074 | 0 | 0 | 483.9782 | 0 | 422.0064 | 0 | 42.1797 | 0 | 0 | 0 | 422.0064 | 0 | 0
5 | 24 | 17 | 14.2491 | 219.8025 | 234.0516 | 45.7474 | 10.8053 | 0 | 0 | 482.3444 | 0 | 234.0516 | 0 | 23.3935 | 0 | 0 | 0 | 234.0516 | 0 | 0
5 | 24 | 18 | 14.1067 | 177.4044 | 191.5111 | 45.2746 | 11.5107 | 0 | 0 | 488.6145 | 0 | 191.5111 | 0 | 19.1416 | 0 | 0 | 0 | 191.5111 | 0 | 0
5 | 24 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 477.3625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 448.7392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 21 | 5.6895 | 0 | 5.6895 | 11 | 7.4847 | 4.7152 | 4.7152 | 415.4825 | 5.6895 | 0 | 2301.2888 | 0 | 0 | 0 | 5.6895 | 0 | 0 | 2301.2888
5 | 24 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 398.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 388.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 383.5519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 385.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 395.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 402.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 425.2829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 443.7824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 457.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 469.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 474.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 9 | 0 | 2.112 | 2.112 | 48 | 6.9858 | 1.4611 | 1.4611 | 471.2707 | 2.112 | 0 | 893.9503 | 0 | 0 | 0 | 2.112 | 0 | 0 | 893.9503
5 | 25 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 476.2423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 468.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 12 | 0 | 58.9013 | 58.9013 | 48 | 8.2847 | 71.518 | 71.518 | 473.0812 | 58.9013 | 0 | 25037.8195 | 0 | 0 | 0 | 58.9013 | 0 | 0 | 25037.8195
5 | 25 | 13 | 0 | 4.8666 | 4.8666 | 48 | 7.8202 | 4.6527 | 4.6527 | 473.9349 | 4.8666 | 0 | 2072.87 | 0 | 0 | 0 | 4.8666 | 0 | 0 | 2072.87
5 | 25 | 14 | 0 | 21.1745 | 21.1745 | 48 | 7.6568 | 18.8345 | 18.8345 | 476.531 | 21.1745 | 0 | 9073.9374 | 0 | 0 | 0 | 21.1745 | 0 | 0 | 9073.9374
5 | 25 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 475.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 475.4161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 473.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 482.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 471.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 455.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 439.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 22 | 7.8121 | 0 | 7.8121 | 11 | 4.9212 | 3.2096 | 3.2096 | 426.595 | 7.8121 | 0 | 3246.6609 | 0 | 0 | 0 | 7.8121 | 0 | 0 | 3246.6609
5 | 25 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 413.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 410.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 1 | 33.0659 | 0 | 33.0659 | 11 | 3.4243 | 10.4952 | 10.4952 | 411.3742 | 33.0659 | 0 | 13238.7426 | 0 | 0 | 0 | 33.0659 | 0 | 0 | 13238.7426
5 | 26 | 2 | 14.4481 | 0 | 14.4481 | 11 | 3.3383 | 4.5267 | 4.5267 | 414.9887 | 14.4481 | 0 | 5836.8711 | 0 | 0 | 0 | 14.4481 | 0 | 0 | 5836.8711
5 | 26 | 3 | 3.4418 | 0 | 3.4418 | 11 | 3.3039 | 1.0728 | 1.0728 | 438.6239 | 3.4418 | 0 | 1471.7811 | 0 | 0 | 0 | 3.4418 | 0 | 0 | 1471.7811
5 | 26 | 4 | 0.98763 | 0 | 0.98763 | 11 | 3.2609 | 0.30588 | 0.30588 | 452.1068 | 0.98763 | 0 | 435.6505 | 0 | 0 | 0 | 0.98763 | 0 | 0 | 435.6505
5 | 26 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 462.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 6 | 1.7063 | 0 | 1.7063 | 11 | 4.9556 | 0.70582 | 0.70582 | 474.4617 | 1.7063 | 0 | 790.801 | 0 | 0 | 0 | 1.7063 | 0 | 0 | 790.801
5 | 26 | 7 | 0 | 39.1593 | 39.1593 | 48 | 6.5556 | 23.7126 | 23.7126 | 475.9071 | 39.1593 | 0 | 16756.5631 | 0 | 0 | 0 | 39.1593 | 0 | 0 | 16756.5631
5 | 26 | 8 | 18.8058 | 342.5487 | 361.3546 | 46.0744 | 7.2524 | 274.2077 | 274.2077 | 484.6029 | 361.3546 | 0 | 158464.2851 | 0 | 0 | 0 | 361.3546 | 0 | 0 | 158464.2851
5 | 26 | 9 | 0 | 192.1613 | 192.1613 | 48 | 7.6998 | 174.1146 | 174.1146 | 491.6017 | 192.1613 | 0 | 85243.0837 | 0 | 0 | 0 | 192.1613 | 0 | 0 | 85243.0837
5 | 26 | 10 | 9.4133 | 480.2262 | 489.6396 | 47.2887 | 7.8632 | 477.5127 | 288 | 498.2903 | 295.314 | 194.3256 | 133187.082 | 19.4229 | 0 | 0 | 295.314 | 194.3256 | 0 | 133187.082
5 | 26 | 11 | 34.0325 | 583.0051 | 617.0376 | 45.9593 | 7.6051 | 537.0436 | 288 | 497.7728 | 330.8983 | 286.1392 | 149504.3399 | 28.5997 | 0 | 0 | 330.8983 | 286.1392 | 0 | 149504.3399
5 | 26 | 12 | 5.4618 | 350.0175 | 355.4793 | 47.4315 | 8.2589 | 425.2439 | 288 | 498.1143 | 240.7514 | 114.728 | 108502.4995 | 11.4671 | 0 | 0 | 240.7514 | 114.728 | 0 | 108502.4995
5 | 26 | 13 | 0 | 352.7051 | 352.7051 | 48 | 8.5686 | 512.8957 | 288 | 505.6427 | 198.0502 | 154.655 | 90636.2075 | 15.4578 | 0 | 0 | 198.0502 | 154.655 | 0 | 90636.2075
5 | 26 | 14 | 0 | 309.3839 | 309.3839 | 48 | 8.6374 | 472.5397 | 288 | 506.8563 | 188.561 | 120.8229 | 86522.4056 | 12.0763 | 0 | 0 | 188.561 | 120.8229 | 0 | 86522.4056
5 | 26 | 15 | 16.2283 | 172.3273 | 188.5556 | 44.8155 | 7.803 | 178.857 | 178.857 | 503.3587 | 188.5556 | 0 | 86460.892 | 0 | 0 | 0 | 188.5556 | 0 | 0 | 86460.892
5 | 26 | 16 | 3.0191 | 245.4364 | 248.4555 | 47.5504 | 7.6998 | 225.122 | 225.122 | 513.0703 | 248.4555 | 0 | 115661.0028 | 0 | 0 | 0 | 248.4555 | 0 | 0 | 115661.0028
5 | 26 | 17 | 9.2833 | 50.7167 | 60 | 42.2753 | 7.6482 | 53.1745 | 53.1745 | 500.6829 | 60 | 0 | 27504.4599 | 0 | 0 | 0 | 60 | 0 | 0 | 27504.4599
5 | 26 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 510.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 510.8743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 504.8817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 469.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 22 | 1.4906 | 0 | 1.4906 | 11 | 5.0846 | 0.63277 | 0.63277 | 445.0383 | 1.4906 | 0 | 646.9834 | 0 | 0 | 0 | 1.4906 | 0 | 0 | 646.9834
5 | 26 | 23 | 3.3528 | 0 | 3.3528 | 11 | 4.4566 | 1.2622 | 1.2622 | 427.9489 | 3.3528 | 0 | 1397.9395 | 0 | 0 | 0 | 3.3528 | 0 | 0 | 1397.9395
5 | 27 | 0 | 50.3217 | 0 | 50.3217 | 11 | 3.9749 | 17.4306 | 17.4306 | 422.591 | 50.3217 | 0 | 20711.9766 | 0 | 0 | 0 | 50.3217 | 0 | 0 | 20711.9766
5 | 27 | 1 | 48.1314 | 0 | 48.1314 | 11 | 3.7598 | 16.0977 | 16.0977 | 430.908 | 48.1314 | 0 | 20210.7633 | 0 | 0 | 0 | 48.1314 | 0 | 0 | 20210.7633
5 | 27 | 2 | 47.5018 | 0 | 47.5018 | 11 | 3.691 | 15.714 | 15.714 | 437.8183 | 47.5018 | 0 | 20274.6194 | 0 | 0 | 0 | 47.5018 | 0 | 0 | 20274.6194
5 | 27 | 3 | 46.4799 | 0 | 46.4799 | 11 | 3.6824 | 15.355 | 15.355 | 444.8548 | 46.4799 | 0 | 20165.5373 | 0 | 0 | 0 | 46.4799 | 0 | 0 | 20165.5373
5 | 27 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 452.7985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 5 | 0.74439 | 0 | 0.74439 | 11 | 3.691 | 0.24625 | 0.24625 | 476.1024 | 0.74439 | 0 | 346.2198 | 0 | 0 | 0 | 0.74439 | 0 | 0 | 346.2198
5 | 27 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 492.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 7 | 0 | 1.373 | 1.373 | 48 | 6.3664 | 0.78817 | 0.78817 | 494.3268 | 1.373 | 0 | 612.8133 | 0 | 0 | 0 | 1.373 | 0 | 0 | 612.8133
5 | 27 | 8 | 0 | 70.9802 | 70.9802 | 48 | 6.9944 | 49.245 | 49.245 | 496.7813 | 70.9802 | 0 | 31854.5956 | 0 | 0 | 0 | 70.9802 | 0 | 0 | 31854.5956
5 | 27 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 498.3979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 497.5713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 11 | 0 | 3.5506 | 3.5506 | 48 | 7.5879 | 3.0683 | 3.0683 | 499.7526 | 3.5506 | 0 | 1604.0043 | 0 | 0 | 0 | 3.5506 | 0 | 0 | 1604.0043
5 | 27 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 500.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 505.3115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 14 | 0 | 22.368 | 22.368 | 48 | 8.9299 | 43.4588 | 43.4588 | 504.857 | 22.368 | 0 | 10218.9824 | 0 | 0 | 0 | 22.368 | 0 | 0 | 10218.9824
5 | 27 | 15 | 5.281 | 155.9337 | 161.2147 | 46.788 | 8.8009 | 279.6569 | 279.6569 | 507.0521 | 161.2147 | 0 | 74201.3374 | 0 | 0 | 0 | 161.2147 | 0 | 0 | 74201.3374
5 | 27 | 16 | 25.0221 | 272.5174 | 297.5395 | 44.8884 | 9.5837 | 1475.2726 | 288 | 504.6226 | 58.0851 | 239.4544 | 26703.7081 | 23.9335 | 0 | 0 | 58.0851 | 239.4544 | 0 | 26703.7081
5 | 27 | 17 | 22.2508 | 267.1009 | 289.3517 | 45.1547 | 9.0762 | 650.6976 | 288 | 497.7314 | 128.0676 | 161.2841 | 57960.4164 | 16.1204 | 0 | 0 | 128.0676 | 161.2841 | 0 | 57960.4164
5 | 27 | 18 | 21.2942 | 138.4539 | 159.7481 | 43.068 | 9.4461 | 597.0077 | 288 | 500.8932 | 77.0634 | 82.6847 | 35281.5783 | 8.2644 | 0 | 0 | 77.0634 | 82.6847 | 0 | 35281.5783
5 | 27 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 503.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 481.5027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 453.4022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 436.109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 424.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 0 | 0.38622 | 0 | 0.38622 | 11 | 3.3125 | 0.12054 | 0.12054 | 412.1053 | 0.38622 | 0 | 154.9164 | 0 | 0 | 0 | 0.38622 | 0 | 0 | 154.9164
5 | 28 | 1 | 5.7268 | 0 | 5.7268 | 11 | 3.2007 | 1.758 | 1.758 | 405.6165 | 5.7268 | 0 | 2259.8937 | 0 | 0 | 0 | 5.7268 | 0 | 0 | 2259.8937
5 | 28 | 2 | 13.8395 | 0 | 13.8395 | 11 | 3.1921 | 4.2429 | 4.2429 | 396.1938 | 13.8395 | 0 | 5330.8887 | 0 | 0 | 0 | 13.8395 | 0 | 0 | 5330.8887
5 | 28 | 3 | 0.30929 | 0 | 0.30929 | 11 | 3.3297 | 0.096779 | 0.096779 | 392.9503 | 0.30929 | 0 | 118.1344 | 0 | 0 | 0 | 0.30929 | 0 | 0 | 118.1344
5 | 28 | 4 | 7.7193 | 0 | 7.7193 | 11 | 3.3469 | 2.4216 | 2.4216 | 398.0121 | 7.7193 | 0 | 2987.4578 | 0 | 0 | 0 | 7.7193 | 0 | 0 | 2987.4578
5 | 28 | 5 | 14.928 | 0 | 14.928 | 11 | 3.7857 | 5.0135 | 5.0135 | 411.7119 | 14.928 | 0 | 5981.8446 | 0 | 0 | 0 | 14.928 | 0 | 0 | 5981.8446
5 | 28 | 6 | 0 | 0.28583 | 0.28583 | 48 | 4.5255 | 0.10896 | 0.10896 | 441.1775 | 0.28583 | 0 | 112.3832 | 0 | 0 | 0 | 0.28583 | 0 | 0 | 112.3832
5 | 28 | 7 | 0.36549 | 69.8495 | 70.2149 | 47.8074 | 5.2137 | 30.6093 | 30.6093 | 461.5801 | 70.2149 | 0 | 29053.0247 | 0 | 0 | 0 | 70.2149 | 0 | 0 | 29053.0247
5 | 28 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 474.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 482.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 484.3597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 480.2103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 481.3709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 481.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 482.3753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 485.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 479.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 473.1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 484.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 484.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 20 | 5.9043 | 0 | 5.9043 | 11 | 13.3172 | 0 | 0 | 473.0945 | 0 | 5.9043 | 0 | 0.59014 | 0 | 0 | 0 | 5.9043 | 0 | 0
5 | 28 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 455.9399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 453.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 435.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 423.1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 1 | 1.3494 | 0 | 1.3494 | 11 | 3.4588 | 0.43056 | 0.43056 | 416.1553 | 1.3494 | 0 | 546.7269 | 0 | 0 | 0 | 1.3494 | 0 | 0 | 546.7269
5 | 29 | 2 | 4.9607 | 0 | 4.9607 | 11 | 3.3555 | 1.5582 | 1.5582 | 410.271 | 4.9607 | 0 | 1980.6639 | 0 | 0 | 0 | 4.9607 | 0 | 0 | 1980.6639
5 | 29 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 406.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 4 | 5.4524 | 0 | 5.4524 | 11 | 3.691 | 1.8037 | 1.8037 | 408.7861 | 5.4524 | 0 | 2168.8714 | 0 | 0 | 0 | 5.4524 | 0 | 0 | 2168.8714
5 | 29 | 5 | 0.0093145 | 0 | 0.0093145 | 11 | 3.9405 | 0.0032081 | 0.0032081 | 421.048 | 0.0093145 | 0 | 3.8194 | 0 | 0 | 0 | 0.0093145 | 0 | 0 | 3.8194
5 | 29 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 441.9692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 7 | 1.8663 | 0 | 1.8663 | 11 | 5.1706 | 0.80634 | 0.80634 | 463.5347 | 1.8663 | 0 | 844.5565 | 0 | 0 | 0 | 1.8663 | 0 | 0 | 844.5565
5 | 29 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 481.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 485.1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 487.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 11 | 28.9636 | 0 | 28.9636 | 11 | 10.0569 | 0 | 0 | 482.6864 | 0 | 28.9636 | 0 | 2.8949 | 0 | 0 | 0 | 28.9636 | 0 | 0
5 | 29 | 12 | 18.9253 | 0 | 18.9253 | 11 | 10.1343 | 0 | 0 | 474.4074 | 0 | 18.9253 | 0 | 1.8916 | 0 | 0 | 0 | 18.9253 | 0 | 0
5 | 29 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 479.1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 477.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 488.0882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 490.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 17 | 0.84054 | 0 | 0.84054 | 11 | 11.5451 | 0 | 0 | 490.0434 | 0 | 0.84054 | 0 | 0.084012 | 0 | 0 | 0 | 0.84054 | 0 | 0
5 | 29 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 487.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 482.8053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 460.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 441.6253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 428.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 422.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 0 | 2.0321 | 0 | 2.0321 | 11 | 3.9577 | 0.70187 | 0.70187 | 417.9821 | 2.0321 | 0 | 827.0153 | 0 | 0 | 0 | 2.0321 | 0 | 0 | 827.0153
5 | 30 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 419.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 417.0346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 411.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 414.5723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 422.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 447.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 7 | 0.94022 | 0 | 0.94022 | 11 | 5.6008 | 0.4459 | 0.4459 | 466.004 | 0.94022 | 0 | 427.8023 | 0 | 0 | 0 | 0.94022 | 0 | 0 | 427.8023
5 | 30 | 8 | 14.6132 | 65.5897 | 80.2029 | 41.2585 | 6.5729 | 48.8096 | 48.8096 | 485.9058 | 80.2029 | 0 | 35662.0008 | 0 | 0 | 0 | 80.2029 | 0 | 0 | 35662.0008
5 | 30 | 9 | 31.0753 | 3.3558 | 34.431 | 14.6061 | 7.7084 | 31.3143 | 31.3143 | 500.0621 | 34.431 | 0 | 16714.743 | 0 | 0 | 0 | 34.431 | 0 | 0 | 16714.743
5 | 30 | 10 | 0.54147 | 0 | 0.54147 | 11 | 8.9471 | 1.0691 | 1.0691 | 506.977 | 0.54147 | 0 | 268.559 | 0 | 0 | 0 | 0.54147 | 0 | 0 | 268.559
5 | 30 | 11 | 8.9333 | 0 | 8.9333 | 11 | 9.5923 | 45.2169 | 45.2169 | 504.2447 | 8.9333 | 0 | 4406.3065 | 0 | 0 | 0 | 8.9333 | 0 | 0 | 4406.3065
5 | 30 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 502.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 13 | 0.73219 | 0 | 0.73219 | 11 | 10.0827 | 0 | 0 | 498.441 | 0 | 0.73219 | 0 | 0.073182 | 0 | 0 | 0 | 0.73219 | 0 | 0
5 | 30 | 14 | 51.0233 | 51.2912 | 102.3145 | 29.5484 | 10.6934 | 0 | 0 | 496.5463 | 0 | 102.3145 | 0 | 10.2264 | 0 | 0 | 0 | 102.3145 | 0 | 0
5 | 30 | 15 | 62.6976 | 131.0149 | 193.7125 | 36.0245 | 11.6655 | 0 | 0 | 501.8188 | 0 | 193.7125 | 0 | 19.3616 | 0 | 0 | 0 | 193.7125 | 0 | 0
5 | 30 | 16 | 1.0972 | 84.6336 | 85.7308 | 47.5265 | 12.3021 | 0 | 0 | 511.7298 | 0 | 85.7308 | 0 | 8.5688 | 0 | 0 | 0 | 85.7308 | 0 | 0
5 | 30 | 17 | 0 | 33.8039 | 33.8039 | 48 | 12.1989 | 0 | 0 | 497.9607 | 0 | 33.8039 | 0 | 3.3787 | 0 | 0 | 0 | 33.8039 | 0 | 0
5 | 30 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 506.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 503.8848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 480.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 449.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 441.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 23 | 2.0253 | 0 | 2.0253 | 11 | 4.5734 | 0.77881 | 0.77881 | 429.8109 | 2.0253 | 0 | 848.1984 | 0 | 0 | 0 | 2.0253 | 0 | 0 | 848.1984
5 | 31 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 426.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 428.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 433.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 437.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 452.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 482.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 500.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 514.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 523.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 519.9555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 515.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 508.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 510.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 506.6268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 515.5005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 516.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 522.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 516.3965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 523.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 514.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 505.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 475.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 455.4354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 440.3377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 433.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 434.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 442.0129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 457.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 488.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 510.3628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 534.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 542.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 538.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 534.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 527.6439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 532.502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 530.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 529.6996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 530.3651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 540.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 544.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 548.2652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 553.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 549.1593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 528.6232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 505.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 459.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 452.0926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 439.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 435.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 445.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 462.9641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 483.4612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 498.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 510.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 7 | 0 | 175.5227 | 175.5227 | 48 | 6.5556 | 106.2862 | 106.2862 | 516.7961 | 175.5227 | 0 | 82284.3606 | 0 | 0 | 0 | 175.5227 | 0 | 0 | 82284.3606
6 | 2 | 8 | 3.8492 | 360.7879 | 364.6371 | 47.6094 | 7.2524 | 276.6986 | 276.6986 | 515.6793 | 364.6371 | 0 | 170675.6457 | 0 | 0 | 0 | 364.6371 | 0 | 0 | 170675.6457
6 | 2 | 9 | 0 | 345.1326 | 345.1326 | 48 | 7.6998 | 312.7197 | 288 | 510.9315 | 317.8507 | 27.2819 | 147143.1144 | 2.7268 | 0 | 0 | 317.8507 | 27.2819 | 0 | 147143.1144
6 | 2 | 10 | 0 | 320.689 | 320.689 | 48 | 7.8632 | 312.7465 | 288 | 505.9832 | 295.314 | 25.375 | 135248.8536 | 2.5362 | 0 | 0 | 295.314 | 25.375 | 0 | 135248.8536
6 | 2 | 11 | 0 | 114.5665 | 114.5665 | 48 | 7.6051 | 99.7138 | 99.7138 | 503.7501 | 114.5665 | 0 | 52213.6753 | 0 | 0 | 0 | 114.5665 | 0 | 0 | 52213.6753
6 | 2 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 498.7565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 13 | 0 | 232.9151 | 232.9151 | 48 | 8.5686 | 338.6998 | 288 | 504.475 | 198.0502 | 34.8649 | 90404.9331 | 3.4848 | 0 | 0 | 198.0502 | 34.8649 | 0 | 90404.9331
6 | 2 | 14 | 0 | 351.1838 | 351.1838 | 48 | 8.6374 | 536.3831 | 288 | 502.5861 | 188.561 | 162.6228 | 85717.1995 | 16.2542 | 0 | 0 | 188.561 | 162.6228 | 0 | 85717.1995
6 | 2 | 15 | 0 | 154.4704 | 154.4704 | 48 | 7.803 | 146.5249 | 146.5249 | 512.8748 | 154.4704 | 0 | 71809.3784 | 0 | 0 | 0 | 154.4704 | 0 | 0 | 71809.3784
6 | 2 | 16 | 0 | 202.2415 | 202.2415 | 48 | 7.6998 | 183.2481 | 183.2481 | 513.8283 | 202.2415 | 0 | 94209.8101 | 0 | 0 | 0 | 202.2415 | 0 | 0 | 94209.8101
6 | 2 | 17 | 0 | 31.9235 | 31.9235 | 48 | 7.6482 | 28.292 | 28.292 | 517.0559 | 31.9235 | 0 | 14973.9246 | 0 | 0 | 0 | 31.9235 | 0 | 0 | 14973.9246
6 | 2 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 517.6934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 515.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 491.4548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 469.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 450.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 439.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 430.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 433.6575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 445.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 468.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 486.4015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 496.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 6 | 15.1154 | 0 | 15.1154 | 11 | 4.8007 | 6.0666 | 6.0666 | 504.1293 | 15.1154 | 0 | 7453.8671 | 0 | 0 | 0 | 15.1154 | 0 | 0 | 7453.8671
6 | 3 | 7 | 34.3012 | 0 | 34.3012 | 11 | 6.3664 | 19.6904 | 19.6904 | 510.1588 | 34.3012 | 0 | 17121.7586 | 0 | 0 | 0 | 34.3012 | 0 | 0 | 17121.7586
6 | 3 | 8 | 30.1546 | 4.4119 | 34.5665 | 15.7225 | 6.9944 | 23.9817 | 23.9817 | 503.1612 | 34.5665 | 0 | 16849.0573 | 0 | 0 | 0 | 34.5665 | 0 | 0 | 16849.0573
6 | 3 | 9 | 2.82 | 54.9855 | 57.8055 | 46.195 | 7.5707 | 49.6003 | 49.6003 | 505.5617 | 57.8055 | 0 | 26553.9394 | 0 | 0 | 0 | 57.8055 | 0 | 0 | 26553.9394
6 | 3 | 10 | 7.9558 | 37.8927 | 45.8486 | 41.5796 | 7.4159 | 36.9878 | 36.9878 | 506.2564 | 45.8486 | 0 | 21304.7688 | 0 | 0 | 0 | 45.8486 | 0 | 0 | 21304.7688
6 | 3 | 11 | 4.0605 | 46.6556 | 50.716 | 45.0377 | 7.5879 | 43.8269 | 43.8269 | 501.0169 | 50.716 | 0 | 23125.4541 | 0 | 0 | 0 | 50.716 | 0 | 0 | 23125.4541
6 | 3 | 12 | 0 | 76.6013 | 76.6013 | 48 | 8.3192 | 94.9078 | 94.9078 | 497.6436 | 76.6013 | 0 | 34443.2804 | 0 | 0 | 0 | 76.6013 | 0 | 0 | 34443.2804
6 | 3 | 13 | 8.0832 | 57.7739 | 65.8571 | 43.4587 | 8.6546 | 101.869 | 101.869 | 499.7721 | 65.8571 | 0 | 30051.5017 | 0 | 0 | 0 | 65.8571 | 0 | 0 | 30051.5017
6 | 3 | 14 | 0 | 26.7497 | 26.7497 | 48 | 8.9299 | 51.972 | 51.972 | 498.0357 | 26.7497 | 0 | 12038.3317 | 0 | 0 | 0 | 26.7497 | 0 | 0 | 12038.3317
6 | 3 | 15 | 0 | 28.4335 | 28.4335 | 48 | 8.8009 | 49.3233 | 49.3233 | 495.7604 | 28.4335 | 0 | 12731.4114 | 0 | 0 | 0 | 28.4335 | 0 | 0 | 12731.4114
6 | 3 | 16 | 0 | 0.18992 | 0.18992 | 48 | 9.5837 | 0.94165 | 0.94165 | 495.7604 | 0.18992 | 0 | 85.0369 | 0 | 0 | 0 | 0.18992 | 0 | 0 | 85.0369
6 | 3 | 17 | 0.2206 | 0 | 0.2206 | 11 | 9.0762 | 0.4961 | 0.4961 | 495.7604 | 0.2206 | 0 | 106.9397 | 0 | 0 | 0 | 0.2206 | 0 | 0 | 106.9397
6 | 3 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 495.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 495.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 495.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 483.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 462.6298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 452.4276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 445.6566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 445.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 2 | 5.7553 | 0 | 5.7553 | 11 | 3.1921 | 1.7645 | 1.7645 | 444.9461 | 5.7553 | 0 | 2497.4969 | 0 | 0 | 0 | 5.7553 | 0 | 0 | 2497.4969
6 | 4 | 3 | 9.2338 | 0 | 9.2338 | 11 | 3.3297 | 2.8893 | 2.8893 | 442.0949 | 9.2338 | 0 | 3980.642 | 0 | 0 | 0 | 9.2338 | 0 | 0 | 3980.642
6 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 444.5681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 462.2779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 487.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 505.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 8 | 0 | 42.4457 | 42.4457 | 48 | 5.1879 | 18.4045 | 18.4045 | 526.5079 | 42.4457 | 0 | 20310.613 | 0 | 0 | 0 | 42.4457 | 0 | 0 | 20310.613
6 | 4 | 9 | 0 | 23.3073 | 23.3073 | 48 | 6.7449 | 14.9328 | 14.9328 | 531.8244 | 23.3073 | 0 | 11276.6407 | 0 | 0 | 0 | 23.3073 | 0 | 0 | 11276.6407
6 | 4 | 10 | 0 | 27.7106 | 27.7106 | 48 | 8.8783 | 51.3723 | 51.3723 | 524.1808 | 27.7106 | 0 | 13195.2335 | 0 | 0 | 0 | 27.7106 | 0 | 0 | 13195.2335
6 | 4 | 11 | 0 | 155.1015 | 155.1015 | 48 | 9.8676 | 2358.1677 | 288 | 523.4851 | 18.9423 | 136.1591 | 9006.802 | 13.6091 | 0 | 0 | 18.9423 | 136.1591 | 0 | 9006.802
6 | 4 | 12 | 0 | 3.7197 | 3.7197 | 48 | 10.2547 | 0 | 0 | 518.2842 | 0 | 3.7197 | 0 | 0.37179 | 0 | 0 | 0 | 3.7197 | 0 | 0
6 | 4 | 13 | 0 | 7.5197 | 7.5197 | 48 | 10.031 | 0 | 0 | 518.8208 | 0 | 7.5197 | 0 | 0.7516 | 0 | 0 | 0 | 7.5197 | 0 | 0
6 | 4 | 14 | 0 | 0.59055 | 0.59055 | 48 | 9.9364 | 17.9918 | 17.9918 | 521.8597 | 0.59055 | 0 | 279.8398 | 0 | 0 | 0 | 0.59055 | 0 | 0 | 279.8398
6 | 4 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 529.8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 531.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 524.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 526.6658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 513.1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 493.8909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 457.5466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 446.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 436.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 423.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 419.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 421.9366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 418.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 417.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 428.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 6 | 2.2857 | 50.7561 | 53.0418 | 46.4056 | 4.8093 | 21.3235 | 21.3235 | 440.3786 | 53.0418 | 0 | 20897.0468 | 0 | 0 | 0 | 53.0418 | 0 | 0 | 20897.0468
6 | 5 | 7 | 0.028333 | 67.4377 | 67.466 | 47.9845 | 5.1706 | 29.1492 | 29.1492 | 457.7602 | 67.466 | 0 | 27645.924 | 0 | 0 | 0 | 67.466 | 0 | 0 | 27645.924
6 | 5 | 8 | 0.16343 | 0 | 0.16343 | 11 | 5.8502 | 0.082161 | 0.082161 | 458.3833 | 0.16343 | 0 | 73.1161 | 0 | 0 | 0 | 0.16343 | 0 | 0 | 73.1161
6 | 5 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 475.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 468.5068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 471.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 472.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 475.3626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 479.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 492.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 496.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 494.2802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 501.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 479.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 451.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 431.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 425.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 23 | 0.65709 | 0 | 0.65709 | 11 | 4.6373 | 0.25569 | 0.25569 | 430.591 | 0.65709 | 0 | 275.7083 | 0 | 0 | 0 | 0.65709 | 0 | 0 | 275.7083
6 | 6 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 436.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 1 | 0.24333 | 0 | 0.24333 | 11 | 3.6394 | 0.079844 | 0.079844 | 441.6211 | 0.24333 | 0 | 104.7845 | 0 | 0 | 0 | 0.24333 | 0 | 0 | 104.7845
6 | 6 | 2 | 44.1507 | 0 | 44.1507 | 11 | 3.5276 | 14.2369 | 14.2369 | 444.6464 | 44.1507 | 0 | 19145.7981 | 0 | 0 | 0 | 44.1507 | 0 | 0 | 19145.7981
6 | 6 | 3 | 1.0958 | 0 | 1.0958 | 11 | 3.562 | 0.35523 | 0.35523 | 451.1279 | 1.0958 | 0 | 482.2739 | 0 | 0 | 0 | 1.0958 | 0 | 0 | 482.2739
6 | 6 | 4 | 0.21667 | 0 | 0.21667 | 11 | 3.5878 | 0.070522 | 0.070522 | 469.4659 | 0.21667 | 0 | 99.3343 | 0 | 0 | 0 | 0.21667 | 0 | 0 | 99.3343
6 | 6 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 491.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 6 | 3.2941 | 0 | 3.2941 | 11 | 5.3513 | 1.4785 | 1.4785 | 508.7139 | 3.2941 | 0 | 1639.532 | 0 | 0 | 0 | 3.2941 | 0 | 0 | 1639.532
6 | 6 | 7 | 1.4283 | 189.4295 | 190.8578 | 47.7231 | 5.6008 | 90.515 | 90.515 | 519.8062 | 190.8578 | 0 | 90100.7452 | 0 | 0 | 0 | 190.8578 | 0 | 0 | 90100.7452
6 | 6 | 8 | 1.6292 | 414.6618 | 416.2909 | 47.8552 | 6.5729 | 253.3448 | 253.3448 | 522.3565 | 416.2909 | 0 | 197530.5759 | 0 | 0 | 0 | 416.2909 | 0 | 0 | 197530.5759
6 | 6 | 9 | 3.1891 | 155.1116 | 158.3008 | 47.2546 | 7.7084 | 143.9713 | 143.9713 | 513.2952 | 158.3008 | 0 | 73774.5862 | 0 | 0 | 0 | 158.3008 | 0 | 0 | 73774.5862
6 | 6 | 10 | 4.3324 | 137.4432 | 141.7756 | 46.8693 | 8.9471 | 279.9358 | 279.9358 | 509.0368 | 141.7756 | 0 | 65524.083 | 0 | 0 | 0 | 141.7756 | 0 | 0 | 65524.083
6 | 6 | 11 | 1.265 | 203.8562 | 205.1212 | 47.7718 | 9.5923 | 1038.2422 | 288 | 510.7192 | 56.899 | 148.2222 | 26341.2242 | 14.8149 | 0 | 0 | 56.899 | 148.2222 | 0 | 26341.2242
6 | 6 | 12 | 3.974 | 38.1003 | 42.0744 | 44.5053 | 10.2891 | 0 | 0 | 508.7822 | 0 | 42.0744 | 0 | 4.2053 | 0 | 0 | 0 | 42.0744 | 0 | 0
6 | 6 | 13 | 9.2907 | 0 | 9.2907 | 11 | 10.0827 | 0 | 0 | 507.8622 | 0 | 9.2907 | 0 | 0.92861 | 0 | 0 | 0 | 9.2907 | 0 | 0
6 | 6 | 14 | 2.275 | 0 | 2.275 | 11 | 10.6934 | 0 | 0 | 505.6665 | 0 | 2.275 | 0 | 0.22739 | 0 | 0 | 0 | 2.275 | 0 | 0
6 | 6 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 515.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 521.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 519.0856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 522.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 519.6326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 501.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 478.5289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 465.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 23 | 1.8429 | 0 | 1.8429 | 11 | 4.5734 | 0.70868 | 0.70868 | 462.5175 | 1.8429 | 0 | 832.0892 | 0 | 0 | 0 | 1.8429 | 0 | 0 | 832.0892
6 | 7 | 0 | 0.39046 | 0 | 0.39046 | 11 | 3.8373 | 0.13223 | 0.13223 | 454.0979 | 0.39046 | 0 | 173.0103 | 0 | 0 | 0 | 0.39046 | 0 | 0 | 173.0103
6 | 7 | 1 | 0.24667 | 0 | 0.24667 | 11 | 3.605 | 0.080503 | 0.080503 | 453.2404 | 0.24667 | 0 | 109.086 | 0 | 0 | 0 | 0.24667 | 0 | 0 | 109.086
6 | 7 | 2 | 0.55898 | 0 | 0.55898 | 11 | 3.5018 | 0.17953 | 0.17953 | 456.0562 | 0.55898 | 0 | 248.7758 | 0 | 0 | 0 | 0.55898 | 0 | 0 | 248.7758
6 | 7 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 468.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 491.3618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 511.9787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 515.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 509.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 500.2099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 505.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 514.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 511.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 499.6937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 494.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 496.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 511.5777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 508.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 501.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 505.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 489.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 463.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 446.6148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 440.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 439.2761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 0 | 6.4891 | 0 | 6.4891 | 11 | 4.5083 | 2.4658 | 2.4658 | 432.9625 | 6.4891 | 0 | 2738.173 | 0 | 0 | 0 | 6.4891 | 0 | 0 | 2738.173
6 | 8 | 1 | 4.0063 | 0 | 4.0063 | 11 | 4.2072 | 1.4433 | 1.4433 | 434.3372 | 4.0063 | 0 | 1696.0131 | 0 | 0 | 0 | 4.0063 | 0 | 0 | 1696.0131
6 | 8 | 2 | 10.7092 | 0 | 10.7092 | 11 | 4.147 | 3.8184 | 3.8184 | 441.1053 | 10.7092 | 0 | 4606.0753 | 0 | 0 | 0 | 10.7092 | 0 | 0 | 4606.0753
6 | 8 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 448.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 456.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 460.5344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 469.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 477.8244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 478.8073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 479.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 476.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 467.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 459.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 457.5677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 470.2436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 476.0908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 484.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 477.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 476.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 466.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 448.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 435.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 422.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 420.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 417.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 413.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 422.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 433.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 450.2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 466.7702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 472.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 477.927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 8 | 5.9469 | 0 | 5.9469 | 11 | 7.2524 | 4.5127 | 4.5127 | 479.5575 | 5.9469 | 0 | 2786.4643 | 0 | 0 | 0 | 5.9469 | 0 | 0 | 2786.4643
6 | 9 | 9 | 4.0127 | 0 | 4.0127 | 11 | 7.6998 | 3.6358 | 3.6358 | 480.2888 | 4.0127 | 0 | 1883.115 | 0 | 0 | 0 | 4.0127 | 0 | 0 | 1883.115
6 | 9 | 10 | 26.7217 | 32.0747 | 58.7964 | 31.1843 | 7.8632 | 57.3402 | 57.3402 | 495.716 | 58.7964 | 0 | 27312.8036 | 0 | 0 | 0 | 58.7964 | 0 | 0 | 27312.8036
6 | 9 | 11 | 48.9966 | 0 | 48.9966 | 11 | 7.6051 | 42.6446 | 42.6446 | 488.5688 | 48.9966 | 0 | 23399.2486 | 0 | 0 | 0 | 48.9966 | 0 | 0 | 23399.2486
6 | 9 | 12 | 2.4287 | 0 | 2.4287 | 11 | 8.2589 | 2.9053 | 2.9053 | 484.7927 | 2.4287 | 0 | 1150.6779 | 0 | 0 | 0 | 2.4287 | 0 | 0 | 1150.6779
6 | 9 | 13 | 13.2525 | 0 | 13.2525 | 11 | 8.5686 | 19.2715 | 19.2715 | 487.2762 | 13.2525 | 0 | 6311.871 | 0 | 0 | 0 | 13.2525 | 0 | 0 | 6311.871
6 | 9 | 14 | 6.0518 | 0 | 6.0518 | 11 | 8.6374 | 9.2433 | 9.2433 | 496.2139 | 6.0518 | 0 | 2936.4262 | 0 | 0 | 0 | 6.0518 | 0 | 0 | 2936.4262
6 | 9 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 511.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 515.8096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 499.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 501.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 491.4387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 468.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 442.2948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 428.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 23 | 5.1556 | 0 | 5.1556 | 11 | 4.4566 | 1.9409 | 1.9409 | 418.9966 | 5.1556 | 0 | 2103.4687 | 0 | 0 | 0 | 5.1556 | 0 | 0 | 2103.4687
6 | 10 | 0 | 16.3278 | 0 | 16.3278 | 11 | 3.9749 | 5.6557 | 5.6557 | 420.0138 | 16.3278 | 0 | 6678.2931 | 0 | 0 | 0 | 16.3278 | 0 | 0 | 6678.2931
6 | 10 | 1 | 57.0527 | 0 | 57.0527 | 11 | 3.7598 | 19.0815 | 19.0815 | 423.0114 | 57.0527 | 0 | 23506.3744 | 0 | 0 | 0 | 57.0527 | 0 | 0 | 23506.3744
6 | 10 | 2 | 44.2806 | 0 | 44.2806 | 11 | 3.691 | 14.6484 | 14.6484 | 425.3202 | 44.2806 | 0 | 18346.3352 | 0 | 0 | 0 | 44.2806 | 0 | 0 | 18346.3352
6 | 10 | 3 | 1.4775 | 0 | 1.4775 | 11 | 3.6824 | 0.48809 | 0.48809 | 430.2797 | 1.4775 | 0 | 619.4683 | 0 | 0 | 0 | 1.4775 | 0 | 0 | 619.4683
6 | 10 | 4 | 4.7658 | 0 | 4.7658 | 11 | 3.6824 | 1.5744 | 1.5744 | 441.3653 | 4.7658 | 0 | 2051.0313 | 0 | 0 | 0 | 4.7658 | 0 | 0 | 2051.0313
6 | 10 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 460.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 472.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 7 | 0.392 | 0 | 0.392 | 11 | 6.3664 | 0.22503 | 0.22503 | 488.785 | 0.392 | 0 | 187.2917 | 0 | 0 | 0 | 0.392 | 0 | 0 | 187.2917
6 | 10 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 497.9022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 9 | 0 | 22.379 | 22.379 | 48 | 7.5707 | 19.2024 | 19.2024 | 502.1234 | 22.379 | 0 | 10162.8464 | 0 | 0 | 0 | 22.379 | 0 | 0 | 10162.8464
6 | 10 | 10 | 0 | 51.877 | 51.877 | 48 | 7.4159 | 41.8511 | 41.8511 | 504.3476 | 51.877 | 0 | 23673.9578 | 0 | 0 | 0 | 51.877 | 0 | 0 | 23673.9578
6 | 10 | 11 | 0 | 196.9476 | 196.9476 | 48 | 7.5879 | 170.1947 | 170.1947 | 493.6926 | 196.9476 | 0 | 87778.0817 | 0 | 0 | 0 | 196.9476 | 0 | 0 | 87778.0817
6 | 10 | 12 | 0 | 8.6853 | 8.6853 | 48 | 8.3192 | 10.7609 | 10.7609 | 495.6773 | 8.6853 | 0 | 3888.1895 | 0 | 0 | 0 | 8.6853 | 0 | 0 | 3888.1895
6 | 10 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 494.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 14 | 0 | 3.4787 | 3.4787 | 48 | 8.9299 | 6.7587 | 6.7587 | 499.7711 | 3.4787 | 0 | 1571.5536 | 0 | 0 | 0 | 3.4787 | 0 | 0 | 1571.5536
6 | 10 | 15 | 0 | 16.4137 | 16.4137 | 48 | 8.8009 | 28.4726 | 28.4726 | 503.7904 | 16.4137 | 0 | 7481.207 | 0 | 0 | 0 | 16.4137 | 0 | 0 | 7481.207
6 | 10 | 16 | 0 | 7.9256 | 7.9256 | 48 | 9.5837 | 39.2971 | 39.2971 | 522.9494 | 7.9256 | 0 | 3764.261 | 0 | 0 | 0 | 7.9256 | 0 | 0 | 3764.261
6 | 10 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 518.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 525.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 518.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 496.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 474.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 450.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 450.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 448.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 438.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 433.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 430.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 434.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 445.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 471.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 491.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 8 | 11.459 | 0 | 11.459 | 11 | 5.1879 | 4.9686 | 4.9686 | 503.3174 | 11.459 | 0 | 5641.4479 | 0 | 0 | 0 | 11.459 | 0 | 0 | 5641.4479
6 | 11 | 9 | 26.848 | 0 | 26.848 | 11 | 6.7449 | 17.2014 | 17.2014 | 512.1797 | 26.848 | 0 | 13455.6902 | 0 | 0 | 0 | 26.848 | 0 | 0 | 13455.6902
6 | 11 | 10 | 25.3578 | 0 | 25.3578 | 11 | 8.8783 | 47.0106 | 47.0106 | 512.09 | 25.3578 | 0 | 12706.5425 | 0 | 0 | 0 | 25.3578 | 0 | 0 | 12706.5425
6 | 11 | 11 | 0 | 146.4178 | 146.4178 | 48 | 9.8676 | 2226.141 | 288 | 511.8316 | 18.9423 | 127.4755 | 8786.0575 | 12.7412 | 0 | 0 | 18.9423 | 127.4755 | 0 | 8786.0575
6 | 11 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 512.8254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 514.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 522.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 533.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 539.5142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 551.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 18 | 1.4061 | 0 | 1.4061 | 11 | 12.801 | 0 | 0 | 560.2404 | 0 | 1.4061 | 0 | 0.14054 | 0 | 0 | 0 | 1.4061 | 0 | 0
6 | 11 | 19 | 0.56943 | 0 | 0.56943 | 11 | 12.7322 | 0 | 0 | 552.495 | 0 | 0.56943 | 0 | 0.056915 | 0 | 0 | 0 | 0.56943 | 0 | 0
6 | 11 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 551.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 530.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 506.7618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 23 | 5.3374 | 0 | 5.3374 | 11 | 3.6704 | 1.7599 | 1.7599 | 494.4419 | 5.3374 | 0 | 2580.3305 | 0 | 0 | 0 | 5.3374 | 0 | 0 | 2580.3305
6 | 12 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 483.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 474.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 467.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 458.9271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 460.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 5 | 1.6256 | 0 | 1.6256 | 11 | 3.9405 | 0.5599 | 0.5599 | 479.5295 | 1.6256 | 0 | 761.6616 | 0 | 0 | 0 | 1.6256 | 0 | 0 | 761.6616
6 | 12 | 6 | 54.6072 | 0 | 54.6072 | 11 | 4.8093 | 21.9528 | 21.9528 | 496.0355 | 54.6072 | 0 | 26486.4535 | 0 | 0 | 0 | 54.6072 | 0 | 0 | 26486.4535
6 | 12 | 7 | 1.07 | 0 | 1.07 | 11 | 5.1706 | 0.4623 | 0.4623 | 516.3337 | 1.07 | 0 | 540.7036 | 0 | 0 | 0 | 1.07 | 0 | 0 | 540.7036
6 | 12 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 530.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 9 | 25.4019 | 0 | 25.4019 | 11 | 6.7707 | 16.4047 | 16.4047 | 536.4651 | 25.4019 | 0 | 13347.7926 | 0 | 0 | 0 | 25.4019 | 0 | 0 | 13347.7926
6 | 12 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 531.7598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 528.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 524.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 524.4948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 525.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 525.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 531.9202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 517.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 514.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 506.8017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 495.0846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 21 | 4.63 | 0 | 4.63 | 11 | 9.8762 | 75.0965 | 75.0965 | 476.1985 | 4.63 | 0 | 2153.8511 | 0 | 0 | 0 | 4.63 | 0 | 0 | 2153.8511
6 | 12 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 467.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 464.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 464.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 464.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 464.3483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 468.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 480.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 494.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 497.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 7 | 0 | 9.9512 | 9.9512 | 48 | 5.6008 | 4.7194 | 4.7194 | 510.3752 | 9.9512 | 0 | 4601.188 | 0 | 0 | 0 | 9.9512 | 0 | 0 | 4601.188
6 | 13 | 8 | 0 | 2.1119 | 2.1119 | 48 | 6.5729 | 1.2852 | 1.2852 | 520.6312 | 2.1119 | 0 | 998.1411 | 0 | 0 | 0 | 2.1119 | 0 | 0 | 998.1411
6 | 13 | 9 | 0.0091667 | 18.4361 | 18.4453 | 47.9816 | 7.7084 | 16.7756 | 16.7756 | 532.8884 | 18.4453 | 0 | 8944.2409 | 0 | 0 | 0 | 18.4453 | 0 | 0 | 8944.2409
6 | 13 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 534.4347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 524.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 519.6727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 529.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 14 | 0 | 3.755 | 3.755 | 48 | 10.6934 | 0 | 0 | 537.1602 | 0 | 3.755 | 0 | 0.37532 | 0 | 0 | 0 | 3.755 | 0 | 0
6 | 13 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 543.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 557.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 556.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 556.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 541.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 517.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 491.8406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 22 | 5.3826 | 0 | 5.3826 | 11 | 5.6868 | 2.6036 | 2.6036 | 473.7836 | 5.3826 | 0 | 2490.9588 | 0 | 0 | 0 | 5.3826 | 0 | 0 | 2490.9588
6 | 13 | 23 | 4.2857 | 0 | 4.2857 | 11 | 4.5734 | 1.6481 | 1.6481 | 477.7046 | 4.2857 | 0 | 2000.1645 | 0 | 0 | 0 | 4.2857 | 0 | 0 | 2000.1645
6 | 14 | 0 | 1.5241 | 0 | 1.5241 | 11 | 3.8373 | 0.51615 | 0.51615 | 471.832 | 1.5241 | 0 | 702.3655 | 0 | 0 | 0 | 1.5241 | 0 | 0 | 702.3655
6 | 14 | 1 | 10.8554 | 0 | 10.8554 | 11 | 3.605 | 3.5428 | 3.5428 | 471.558 | 10.8554 | 0 | 4999.5501 | 0 | 0 | 0 | 10.8554 | 0 | 0 | 4999.5501
6 | 14 | 2 | 3.2499 | 0 | 3.2499 | 11 | 3.5018 | 1.0438 | 1.0438 | 476.4553 | 3.2499 | 0 | 1512.6608 | 0 | 0 | 0 | 3.2499 | 0 | 0 | 1512.6608
6 | 14 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 492.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 4 | 2.9474 | 0 | 2.9474 | 11 | 3.6222 | 0.96452 | 0.96452 | 509.547 | 2.9474 | 0 | 1469.4261 | 0 | 0 | 0 | 2.9474 | 0 | 0 | 1469.4261
6 | 14 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 515.7989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 525.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 536.6471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 8 | 7.3901 | 0 | 7.3901 | 11 | 6.5729 | 4.4974 | 4.4974 | 552.0488 | 7.3901 | 0 | 3998.3866 | 0 | 0 | 0 | 7.3901 | 0 | 0 | 3998.3866
6 | 14 | 9 | 2.9021 | 0 | 2.9021 | 11 | 7.6912 | 2.6198 | 2.6198 | 562.8146 | 2.9021 | 0 | 1601.4081 | 0 | 0 | 0 | 2.9021 | 0 | 0 | 1601.4081
6 | 14 | 10 | 4.4218 | 0 | 4.4218 | 11 | 8.4482 | 5.9327 | 5.9327 | 562.1136 | 4.4218 | 0 | 2436.9265 | 0 | 0 | 0 | 4.4218 | 0 | 0 | 2436.9265
6 | 14 | 11 | 6.606 | 137.7114 | 144.3174 | 46.3063 | 9.7214 | 1062.8184 | 288 | 555.1722 | 39.1068 | 105.2106 | 19900.1144 | 10.5158 | 0 | 0 | 39.1068 | 105.2106 | 0 | 19900.1144
6 | 14 | 12 | 161.6027 | 266.5025 | 428.1053 | 34.0331 | 9.4117 | 1507.1182 | 288 | 555.7746 | 81.808 | 346.2973 | 42682.626 | 34.6125 | 0 | 0 | 81.808 | 346.2973 | 0 | 42682.626
6 | 14 | 13 | 0.86513 | 16.6775 | 17.5426 | 46.1753 | 8.8869 | 32.7723 | 32.7723 | 557.0876 | 17.5426 | 0 | 8962.739 | 0 | 0 | 0 | 17.5426 | 0 | 0 | 8962.739
6 | 14 | 14 | 0.68169 | 4.4543 | 5.136 | 43.0891 | 9.3428 | 16.2017 | 16.2017 | 554.3515 | 5.136 | 0 | 2625.8455 | 0 | 0 | 0 | 5.136 | 0 | 0 | 2625.8455
6 | 14 | 15 | 2.7312 | 0 | 2.7312 | 11 | 10.0224 | 0 | 0 | 561.4075 | 0 | 2.7312 | 0 | 0.27299 | 0 | 0 | 0 | 2.7312 | 0 | 0
6 | 14 | 16 | 0 | 0.21937 | 0.21937 | 48 | 11.4074 | 0 | 0 | 572.7272 | 0 | 0.21937 | 0 | 0.021926 | 0 | 0 | 0 | 0.21937 | 0 | 0
6 | 14 | 17 | 0 | 13.6897 | 13.6897 | 48 | 10.8053 | 0 | 0 | 566.5048 | 0 | 13.6897 | 0 | 1.3683 | 0 | 0 | 0 | 13.6897 | 0 | 0
6 | 14 | 18 | 15.1334 | 0 | 15.1334 | 11 | 11.5107 | 0 | 0 | 568.3928 | 0 | 15.1334 | 0 | 1.5126 | 0 | 0 | 0 | 15.1334 | 0 | 0
6 | 14 | 19 | 0.21299 | 0 | 0.21299 | 11 | 10.8913 | 0 | 0 | 556.577 | 0 | 0.21299 | 0 | 0.021288 | 0 | 0 | 0 | 0.21299 | 0 | 0
6 | 14 | 20 | 2.6025 | 0 | 2.6025 | 11 | 8.4138 | 3.4162 | 3.4162 | 529.4612 | 2.6025 | 0 | 1349.3066 | 0 | 0 | 0 | 2.6025 | 0 | 0 | 1349.3066
6 | 14 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 497.6278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 22 | 2.4842 | 0 | 2.4842 | 11 | 5.575 | 1.1713 | 1.1713 | 481.4065 | 2.4842 | 0 | 1168.5692 | 0 | 0 | 0 | 2.4842 | 0 | 0 | 1168.5692
6 | 14 | 23 | 1.7513 | 0 | 1.7513 | 11 | 4.5599 | 0.67178 | 0.67178 | 473.0593 | 1.7513 | 0 | 809.1929 | 0 | 0 | 0 | 1.7513 | 0 | 0 | 809.1929
6 | 15 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 469.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 467.4457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 471.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 494.2227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 510.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 5 | 0.24583 | 0 | 0.24583 | 11 | 3.9663 | 0.085031 | 0.085031 | 522.2781 | 0.24583 | 0 | 125.6892 | 0 | 0 | 0 | 0.24583 | 0 | 0 | 125.6892
6 | 15 | 6 | 19.6523 | 0 | 19.6523 | 11 | 4.7319 | 7.7845 | 7.7845 | 538.1378 | 19.6523 | 0 | 10359.4537 | 0 | 0 | 0 | 19.6523 | 0 | 0 | 10359.4537
6 | 15 | 7 | 1.4168 | 117.7101 | 119.127 | 47.5599 | 4.99 | 49.6157 | 49.6157 | 550.4005 | 119.127 | 0 | 59901.8791 | 0 | 0 | 0 | 119.127 | 0 | 0 | 59901.8791
6 | 15 | 8 | 33.7566 | 333.1754 | 366.9321 | 44.5961 | 5.4889 | 169.7096 | 169.7096 | 557.8724 | 366.9321 | 0 | 188337.5287 | 0 | 0 | 0 | 366.9321 | 0 | 0 | 188337.5287
6 | 15 | 9 | 25.6928 | 251.5782 | 277.271 | 44.5715 | 6.9858 | 191.8182 | 191.8182 | 565.2946 | 277.271 | 0 | 144381.3883 | 0 | 0 | 0 | 277.271 | 0 | 0 | 144381.3883
6 | 15 | 10 | 3.1749 | 197.5245 | 200.6993 | 47.4147 | 7.3471 | 157.7194 | 157.7194 | 558.499 | 200.6993 | 0 | 102574.2924 | 0 | 0 | 0 | 200.6993 | 0 | 0 | 102574.2924
6 | 15 | 11 | 35.5005 | 303.8325 | 339.333 | 44.1291 | 8.9643 | 681.0901 | 288 | 559.4615 | 143.4875 | 195.8455 | 73943.7593 | 19.5748 | 0 | 0 | 143.4875 | 195.8455 | 0 | 73943.7593
6 | 15 | 12 | 27.4666 | 376.0289 | 403.4955 | 45.4813 | 8.2847 | 489.9249 | 288 | 558.9279 | 237.1929 | 166.3026 | 121785.8947 | 16.622 | 0 | 0 | 237.1929 | 166.3026 | 0 | 121785.8947
6 | 15 | 13 | 25.114 | 674.1601 | 699.2741 | 46.6712 | 7.8202 | 668.5294 | 288 | 560.5683 | 301.2447 | 398.0294 | 154808.8105 | 39.7831 | 0 | 0 | 301.2447 | 398.0294 | 0 | 154808.8105
6 | 15 | 14 | 29.7518 | 296.6668 | 326.4186 | 44.6276 | 7.6568 | 290.3457 | 288 | 559.9553 | 323.7815 | 2.6372 | 166853.559 | 0.26359 | 0 | 0 | 323.7815 | 2.6372 | 0 | 166853.559
6 | 15 | 15 | 30.6417 | 401.2915 | 431.9332 | 45.3752 | 7.7256 | 395.7996 | 288 | 564.5239 | 314.2923 | 117.6409 | 163164.4516 | 11.7582 | 0 | 0 | 314.2923 | 117.6409 | 0 | 163164.4516
6 | 15 | 16 | 20.6097 | 211.3085 | 231.9181 | 44.712 | 7.3729 | 184.0396 | 184.0396 | 570.6918 | 231.9181 | 0 | 121984.2615 | 0 | 0 | 0 | 231.9181 | 0 | 0 | 121984.2615
6 | 15 | 17 | 0 | 8.255 | 8.255 | 48 | 7.5449 | 7.0089 | 7.0089 | 574.4562 | 8.255 | 0 | 4345.891 | 0 | 0 | 0 | 8.255 | 0 | 0 | 4345.891
6 | 15 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 580.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 569.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 555.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 532.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 500.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 23 | 0.46905 | 0 | 0.46905 | 11 | 4.5954 | 0.18111 | 0.18111 | 496.271 | 0.46905 | 0 | 227.6181 | 0 | 0 | 0 | 0.46905 | 0 | 0 | 227.6181
6 | 16 | 0 | 31.2352 | 0 | 31.2352 | 11 | 3.8459 | 10.5927 | 10.5927 | 488.6296 | 31.2352 | 0 | 14918.8655 | 0 | 0 | 0 | 31.2352 | 0 | 0 | 14918.8655
6 | 16 | 1 | 18.2162 | 0 | 18.2162 | 11 | 3.4243 | 5.7819 | 5.7819 | 481.9524 | 18.2162 | 0 | 8578.975 | 0 | 0 | 0 | 18.2162 | 0 | 0 | 8578.975
6 | 16 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 489.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 3 | 5.9342 | 0 | 5.9342 | 11 | 3.3039 | 1.8497 | 1.8497 | 507.6316 | 5.9342 | 0 | 2947.1269 | 0 | 0 | 0 | 5.9342 | 0 | 0 | 2947.1269
6 | 16 | 4 | 11.1342 | 0 | 11.1342 | 11 | 3.2609 | 3.4484 | 3.4484 | 521.9944 | 11.1342 | 0 | 5689.5162 | 0 | 0 | 0 | 11.1342 | 0 | 0 | 5689.5162
6 | 16 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 544.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 544.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 550.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 546.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 541.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 10 | 0.38667 | 37.1143 | 37.501 | 47.6185 | 7.8632 | 36.5722 | 36.5722 | 540.1825 | 37.501 | 0 | 18471.6186 | 0 | 0 | 0 | 37.501 | 0 | 0 | 18471.6186
6 | 16 | 11 | 0.175 | 54.9011 | 55.0761 | 47.8824 | 7.6051 | 47.9359 | 47.9359 | 543.6447 | 55.0761 | 0 | 27304.6607 | 0 | 0 | 0 | 55.0761 | 0 | 0 | 27304.6607
6 | 16 | 12 | 0 | 55.1842 | 55.1842 | 48 | 8.2589 | 66.0144 | 66.0144 | 541.0967 | 55.1842 | 0 | 27211.1522 | 0 | 0 | 0 | 55.1842 | 0 | 0 | 27211.1522
6 | 16 | 13 | 32.2275 | 434.9776 | 467.2051 | 45.4478 | 8.5686 | 679.3989 | 288 | 535.4505 | 198.0502 | 269.1549 | 97045.1211 | 26.9021 | 0 | 0 | 198.0502 | 269.1549 | 0 | 97045.1211
6 | 16 | 14 | 21.1882 | 269.671 | 290.8592 | 45.3047 | 8.6374 | 444.2459 | 288 | 535.4547 | 188.561 | 102.2982 | 92423.1755 | 10.2247 | 0 | 0 | 188.561 | 102.2982 | 0 | 92423.1755
6 | 16 | 15 | 22.1983 | 249.2781 | 271.4765 | 44.9746 | 7.803 | 257.5127 | 257.5127 | 546.9673 | 271.4765 | 0 | 136279.2098 | 0 | 0 | 0 | 271.4765 | 0 | 0 | 136279.2098
6 | 16 | 16 | 0.73583 | 92.217 | 92.9528 | 47.7071 | 7.6998 | 84.2232 | 84.2232 | 550.8932 | 92.9528 | 0 | 46772.5754 | 0 | 0 | 0 | 92.9528 | 0 | 0 | 46772.5754
6 | 16 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 558.0683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 566.0187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 560.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 541.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 21 | 2.5849 | 0 | 2.5849 | 11 | 5.9879 | 1.344 | 1.344 | 513.3473 | 2.5849 | 0 | 1298.5185 | 0 | 0 | 0 | 2.5849 | 0 | 0 | 1298.5185
6 | 16 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 492.9957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 23 | 0.6975 | 0 | 0.6975 | 11 | 4.4566 | 0.26258 | 0.26258 | 480.9184 | 0.6975 | 0 | 327.7681 | 0 | 0 | 0 | 0.6975 | 0 | 0 | 327.7681
6 | 17 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 475.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 471.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 477.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 3 | 0.43733 | 0 | 0.43733 | 11 | 3.6824 | 0.14447 | 0.14447 | 491.1739 | 0.43733 | 0 | 209.9933 | 0 | 0 | 0 | 0.43733 | 0 | 0 | 209.9933
6 | 17 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 502.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 532.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 6 | 0.24583 | 0.62798 | 0.87381 | 37.5906 | 4.8007 | 0.3507 | 0.3507 | 550.3441 | 0.87381 | 0 | 448.0489 | 0 | 0 | 0 | 0.87381 | 0 | 0 | 448.0489
6 | 17 | 7 | 13.7683 | 119.4568 | 133.2252 | 44.1762 | 6.3664 | 76.4772 | 76.4772 | 556.4761 | 133.2252 | 0 | 68251.2423 | 0 | 0 | 0 | 133.2252 | 0 | 0 | 68251.2423
6 | 17 | 8 | 34.9652 | 174.6968 | 209.662 | 41.8295 | 6.9944 | 145.4602 | 145.4602 | 554.3216 | 209.662 | 0 | 107450.1329 | 0 | 0 | 0 | 209.662 | 0 | 0 | 107450.1329
6 | 17 | 9 | 41.4182 | 372.0284 | 413.4465 | 44.2934 | 7.5707 | 354.7598 | 288 | 555.5263 | 335.6429 | 77.8036 | 171591.7003 | 7.7765 | 0 | 0 | 335.6429 | 77.8036 | 0 | 171591.7003
6 | 17 | 10 | 25.4504 | 490.0301 | 515.4805 | 46.1732 | 7.4159 | 415.8574 | 288 | 551.9347 | 356.9935 | 158.487 | 180553.5483 | 15.8408 | 0 | 0 | 356.9935 | 158.487 | 0 | 180553.5483
6 | 17 | 11 | 0 | 476.0351 | 476.0351 | 48 | 7.5879 | 411.3717 | 288 | 550.5807 | 333.2706 | 142.7644 | 167495.3958 | 14.2693 | 0 | 0 | 333.2706 | 142.7644 | 0 | 167495.3958
6 | 17 | 12 | 0 | 395.9673 | 395.9673 | 48 | 8.3192 | 490.5975 | 288 | 552.9821 | 232.4483 | 163.519 | 117382.2399 | 16.3438 | 0 | 0 | 232.4483 | 163.519 | 0 | 117382.2399
6 | 17 | 13 | 0.78569 | 426.9085 | 427.6942 | 47.932 | 8.6546 | 661.565 | 288 | 552.4136 | 186.1887 | 241.5055 | 93928.7803 | 24.1385 | 0 | 0 | 186.1887 | 241.5055 | 0 | 93928.7803
6 | 17 | 14 | 0 | 265.0672 | 265.0672 | 48 | 8.9299 | 514.9989 | 288 | 553.3283 | 148.2321 | 116.8352 | 74905.8717 | 11.6777 | 0 | 0 | 148.2321 | 116.8352 | 0 | 74905.8717
6 | 17 | 15 | 0 | 294.2964 | 294.2964 | 48 | 8.8009 | 510.5119 | 288 | 563.1664 | 166.0243 | 128.2721 | 85530.12 | 12.8208 | 0 | 0 | 166.0243 | 128.2721 | 0 | 85530.12
6 | 17 | 16 | 0 | 302.7171 | 302.7171 | 48 | 9.5837 | 1500.9444 | 288 | 569.4909 | 58.0851 | 244.632 | 30290.8567 | 24.451 | 0 | 0 | 58.0851 | 244.632 | 0 | 30290.8567
6 | 17 | 17 | 0 | 4.7666 | 4.7666 | 48 | 9.0762 | 10.7191 | 10.7191 | 572.2863 | 4.7666 | 0 | 2499.0543 | 0 | 0 | 0 | 4.7666 | 0 | 0 | 2499.0543
6 | 17 | 18 | 0 | 128.4673 | 128.4673 | 48 | 9.4461 | 480.1058 | 288 | 565.8387 | 77.0634 | 51.4039 | 39906.4226 | 5.1378 | 0 | 0 | 77.0634 | 51.4039 | 0 | 39906.4226
6 | 17 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 550.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 20 | 1.7508 | 0 | 1.7508 | 11 | 11.2698 | 0 | 0 | 527.5151 | 0 | 1.7508 | 0 | 0.17499 | 0 | 0 | 0 | 1.7508 | 0 | 0
6 | 17 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 497.7205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 481.3818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 475.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 474.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 473.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 472.4038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 470.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 473.4556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 488.4738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 515.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 533.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 8 | 0 | 16.2821 | 16.2821 | 48 | 5.1879 | 7.06 | 7.06 | 553.9129 | 16.2821 | 0 | 8237.3429 | 0 | 0 | 0 | 16.2821 | 0 | 0 | 8237.3429
6 | 18 | 9 | 0 | 73.1192 | 73.1192 | 48 | 6.7449 | 46.847 | 46.847 | 564.2397 | 73.1192 | 0 | 37747.0495 | 0 | 0 | 0 | 73.1192 | 0 | 0 | 37747.0495
6 | 18 | 10 | 0 | 65.3815 | 65.3815 | 48 | 8.8783 | 121.2101 | 121.2101 | 569.3888 | 65.3815 | 0 | 34089.1549 | 0 | 0 | 0 | 65.3815 | 0 | 0 | 34089.1549
6 | 18 | 11 | 0 | 129.1471 | 129.1471 | 48 | 9.8676 | 1963.557 | 288 | 557.7533 | 18.9423 | 110.2048 | 9655.9219 | 11.015 | 0 | 0 | 18.9423 | 110.2048 | 0 | 9655.9219
6 | 18 | 12 | 0 | 112.4696 | 112.4696 | 48 | 10.2547 | 0 | 0 | 556.7643 | 0 | 112.4696 | 0 | 11.2414 | 0 | 0 | 0 | 112.4696 | 0 | 0
6 | 18 | 13 | 0 | 91.0559 | 91.0559 | 48 | 10.031 | 0 | 0 | 558.542 | 0 | 91.0559 | 0 | 9.1011 | 0 | 0 | 0 | 91.0559 | 0 | 0
6 | 18 | 14 | 0 | 62.0931 | 62.0931 | 48 | 9.9364 | 1891.7222 | 288 | 555.7988 | 9.4532 | 52.6399 | 4800.3179 | 5.2614 | 0 | 0 | 9.4532 | 52.6399 | 0 | 4800.3179
6 | 18 | 15 | 0 | 29.1947 | 29.1947 | 48 | 11.1494 | 0 | 0 | 557.7347 | 0 | 29.1947 | 0 | 2.918 | 0 | 0 | 0 | 29.1947 | 0 | 0
6 | 18 | 16 | 0 | 3.6886 | 3.6886 | 48 | 12.5086 | 0 | 0 | 563.4359 | 0 | 3.6886 | 0 | 0.36867 | 0 | 0 | 0 | 3.6886 | 0 | 0
6 | 18 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 570.3494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 565.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 554.2129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 531.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 493.3457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 477.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 468.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 460.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 459.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 460.1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 462.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 464.9481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 5 | 2.1128 | 1.4833 | 3.5961 | 26.2619 | 3.9405 | 1.2386 | 1.2386 | 475.5243 | 3.5961 | 0 | 1615.5985 | 0 | 0 | 0 | 3.5961 | 0 | 0 | 1615.5985
6 | 19 | 6 | 8.0166 | 10.7942 | 18.8108 | 32.2317 | 4.8093 | 7.5622 | 7.5622 | 498.2261 | 18.8108 | 0 | 8765.7237 | 0 | 0 | 0 | 18.8108 | 0 | 0 | 8765.7237
6 | 19 | 7 | 0 | 0.40571 | 0.40571 | 48 | 5.1706 | 0.17529 | 0.17529 | 523.4325 | 0.40571 | 0 | 192.8888 | 0 | 0 | 0 | 0.40571 | 0 | 0 | 192.8888
6 | 19 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 554.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 564.8588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 10 | 14.9614 | 0 | 14.9614 | 11 | 8.9987 | 31.0566 | 31.0566 | 568.0837 | 14.9614 | 0 | 8334.7476 | 0 | 0 | 0 | 14.9614 | 0 | 0 | 8334.7476
6 | 19 | 11 | 25.7712 | 0 | 25.7712 | 11 | 10.0569 | 0 | 0 | 565.6191 | 0 | 25.7712 | 0 | 2.5758 | 0 | 0 | 0 | 25.7712 | 0 | 0
6 | 19 | 12 | 0.048999 | 0 | 0.048999 | 11 | 10.1343 | 0 | 0 | 557.8046 | 0 | 0.048999 | 0 | 0.0048974 | 0 | 0 | 0 | 0.048999 | 0 | 0
6 | 19 | 13 | 0 | 2.7542 | 2.7542 | 48 | 10.2117 | 0 | 0 | 552.7442 | 0 | 2.7542 | 0 | 0.27528 | 0 | 0 | 0 | 2.7542 | 0 | 0
6 | 19 | 14 | 0 | 7.4509 | 7.4509 | 48 | 9.8762 | 120.852 | 120.852 | 555.0703 | 7.4509 | 0 | 3778.153 | 0 | 0 | 0 | 7.4509 | 0 | 0 | 3778.153
6 | 19 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 558.1436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 567.9891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 17 | 0.47758 | 0 | 0.47758 | 11 | 11.5451 | 0 | 0 | 578.6347 | 0 | 0.47758 | 0 | 0.047734 | 0 | 0 | 0 | 0.47758 | 0 | 0
6 | 19 | 18 | 13.9091 | 0 | 13.9091 | 11 | 11.9236 | 0 | 0 | 583.9911 | 0 | 13.9091 | 0 | 1.3902 | 0 | 0 | 0 | 13.9091 | 0 | 0
6 | 19 | 19 | 19.0385 | 0 | 19.0385 | 11 | 13.1107 | 0 | 0 | 572.7656 | 0 | 19.0385 | 0 | 1.9029 | 0 | 0 | 0 | 19.0385 | 0 | 0
6 | 19 | 20 | 28.4147 | 0 | 28.4147 | 11 | 12.6978 | 0 | 0 | 540.9322 | 0 | 28.4147 | 0 | 2.8401 | 0 | 0 | 0 | 28.4147 | 0 | 0
6 | 19 | 21 | 60.9591 | 0 | 60.9591 | 11 | 9.8762 | 988.7369 | 288 | 503.6068 | 17.7562 | 43.2029 | 8746.824 | 4.3181 | 0 | 0 | 17.7562 | 43.2029 | 0 | 8746.824
6 | 19 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 484.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 23 | 5.1313 | 0 | 5.1313 | 11 | 4.6373 | 1.9967 | 1.9967 | 474.7276 | 5.1313 | 0 | 2379.5367 | 0 | 0 | 0 | 5.1313 | 0 | 0 | 2379.5367
6 | 20 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 471.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 468.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 471.8257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 477.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 491.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 516.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 536.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 7 | 0.70667 | 250.9297 | 251.6363 | 47.8961 | 5.6008 | 119.3394 | 119.3394 | 546.4078 | 251.6363 | 0 | 125443.6542 | 0 | 0 | 0 | 251.6363 | 0 | 0 | 125443.6542
6 | 20 | 8 | 0.063333 | 485.6832 | 485.7465 | 47.9952 | 6.5729 | 295.6138 | 288 | 559.5089 | 473.2357 | 12.5108 | 242066.5258 | 1.2505 | 0 | 0 | 473.2357 | 12.5108 | 0 | 242066.5258
6 | 20 | 9 | 0.02 | 139.0156 | 139.0356 | 47.9947 | 7.7084 | 126.45 | 126.45 | 552.8494 | 139.0356 | 0 | 70192.766 | 0 | 0 | 0 | 139.0356 | 0 | 0 | 70192.766
6 | 20 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 548.5892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 546.9572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 550.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 554.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 557.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 15 | 0 | 37.725 | 37.725 | 48 | 11.6655 | 0 | 0 | 563.1789 | 0 | 37.725 | 0 | 3.7706 | 0 | 0 | 0 | 37.725 | 0 | 0
6 | 20 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 568.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 578.4743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 585.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 19 | 0 | 0.8 | 0.8 | 48 | 13.2054 | 0 | 0 | 574.8951 | 0 | 0.8 | 0 | 0.07996 | 0 | 0 | 0 | 0.8 | 0 | 0
6 | 20 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 554.7589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 527.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 520.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 508.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 498.1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 497.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 506.5259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 526.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 4 | 0.97917 | 0 | 0.97917 | 11 | 3.6222 | 0.32042 | 0.32042 | 544.9814 | 0.97917 | 0 | 522.8567 | 0 | 0 | 0 | 0.97917 | 0 | 0 | 522.8567
6 | 21 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 559.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 568.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 578.8639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 582.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 581.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 569.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 11 | 0 | 8.3717 | 8.3717 | 48 | 9.7214 | 61.6533 | 61.6533 | 563.525 | 8.3717 | 0 | 4315.8447 | 0 | 0 | 0 | 8.3717 | 0 | 0 | 4315.8447
6 | 21 | 12 | 0 | 3.3016 | 3.3016 | 48 | 9.4117 | 11.6231 | 11.6231 | 559.4407 | 3.3016 | 0 | 1688.5726 | 0 | 0 | 0 | 3.3016 | 0 | 0 | 1688.5726
6 | 21 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 560.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 14 | 0 | 27.0426 | 27.0426 | 48 | 9.3428 | 85.3068 | 85.3068 | 563.0952 | 27.0426 | 0 | 13929.5056 | 0 | 0 | 0 | 27.0426 | 0 | 0 | 13929.5056
6 | 21 | 15 | 3.6514 | 0 | 3.6514 | 11 | 10.0224 | 0 | 0 | 567.0415 | 0 | 3.6514 | 0 | 0.36496 | 0 | 0 | 0 | 3.6514 | 0 | 0
6 | 21 | 16 | 3.8208 | 0 | 3.8208 | 11 | 11.4074 | 0 | 0 | 582.5069 | 0 | 3.8208 | 0 | 0.38189 | 0 | 0 | 0 | 3.8208 | 0 | 0
6 | 21 | 17 | 3.8466 | 0 | 3.8466 | 11 | 10.8053 | 0 | 0 | 581.0169 | 0 | 3.8466 | 0 | 0.38447 | 0 | 0 | 0 | 3.8466 | 0 | 0
6 | 21 | 18 | 3.7873 | 7.1849 | 10.9721 | 35.2286 | 11.5107 | 0 | 0 | 572.058 | 0 | 10.9721 | 0 | 1.0967 | 0 | 0 | 0 | 10.9721 | 0 | 0
6 | 21 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 573.9961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 556.5795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 539.4466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 521.5388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 23 | 3.3164 | 0 | 3.3164 | 11 | 4.5599 | 1.2721 | 1.2721 | 510.8479 | 3.3164 | 0 | 1657.673 | 0 | 0 | 0 | 3.3164 | 0 | 0 | 1657.673
6 | 22 | 0 | 43.9085 | 0 | 43.9085 | 11 | 4.5083 | 16.6849 | 16.6849 | 502.9129 | 43.9085 | 0 | 21599.1636 | 0 | 0 | 0 | 43.9085 | 0 | 0 | 21599.1636
6 | 22 | 1 | 21.3736 | 0 | 21.3736 | 11 | 4.2072 | 7.7 | 7.7 | 501.4356 | 21.3736 | 0 | 10482.3894 | 0 | 0 | 0 | 21.3736 | 0 | 0 | 10482.3894
6 | 22 | 2 | 9.0933 | 0 | 9.0933 | 11 | 4.147 | 3.2423 | 3.2423 | 499.0776 | 9.0933 | 0 | 4438.2527 | 0 | 0 | 0 | 9.0933 | 0 | 0 | 4438.2527
6 | 22 | 3 | 9.34 | 0 | 9.34 | 11 | 3.7857 | 3.1368 | 3.1368 | 514.0284 | 9.34 | 0 | 4698.2855 | 0 | 0 | 0 | 9.34 | 0 | 0 | 4698.2855
6 | 22 | 4 | 4.6375 | 0 | 4.6375 | 11 | 3.7254 | 1.5425 | 1.5425 | 526.8323 | 4.6375 | 0 | 2392.1721 | 0 | 0 | 0 | 4.6375 | 0 | 0 | 2392.1721
6 | 22 | 5 | 4.7975 | 0 | 4.7975 | 11 | 3.9663 | 1.6594 | 1.6594 | 540.4546 | 4.7975 | 0 | 2540.0586 | 0 | 0 | 0 | 4.7975 | 0 | 0 | 2540.0586
6 | 22 | 6 | 0.078333 | 0 | 0.078333 | 11 | 4.7319 | 0.031029 | 0.031029 | 544.5387 | 0.078333 | 0 | 41.7939 | 0 | 0 | 0 | 0.078333 | 0 | 0 | 41.7939
6 | 22 | 7 | 1.625 | 0 | 1.625 | 11 | 4.99 | 0.67678 | 0.67678 | 551.359 | 1.625 | 0 | 878.0569 | 0 | 0 | 0 | 1.625 | 0 | 0 | 878.0569
6 | 22 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 563.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 564.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 561.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 550.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 553.6086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 556.0745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 562.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 566.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 579.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 571.5254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 567.7935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 564.4005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 556.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 537.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 517.2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 23 | 0.31478 | 0 | 0.31478 | 11 | 4.5954 | 0.12154 | 0.12154 | 506.248 | 0.31478 | 0 | 155.8949 | 0 | 0 | 0 | 0.31478 | 0 | 0 | 155.8949
6 | 23 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 501.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 504.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 510.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 524.2537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 543.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 549.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 560.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 575.8214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 577.2582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 575.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 570.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 570.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 575.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 572.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 572.9433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 577.6039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 583.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 585.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 583.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 573.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 554.9253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 540.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 521.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 23 | 6.3161 | 0 | 6.3161 | 11 | 4.4566 | 2.3777 | 2.3777 | 516.5617 | 6.3161 | 0 | 3193.1773 | 0 | 0 | 0 | 6.3161 | 0 | 0 | 3193.1773
6 | 24 | 0 | 16.1426 | 0 | 16.1426 | 11 | 3.9749 | 5.5915 | 5.5915 | 511.6389 | 16.1426 | 0 | 8081.6213 | 0 | 0 | 0 | 16.1426 | 0 | 0 | 8081.6213
6 | 24 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 508.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 515.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 525.9082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 538.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 556.9234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 570.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 585.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 8 | 0 | 25.2862 | 25.2862 | 48 | 6.9944 | 17.5432 | 17.5432 | 591.7917 | 25.2862 | 0 | 13750.4151 | 0 | 0 | 0 | 25.2862 | 0 | 0 | 13750.4151
6 | 24 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 589.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 578.8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 579.6996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 576.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 575.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 14 | 2.3493 | 0 | 2.3493 | 11 | 8.9299 | 4.5645 | 4.5645 | 582.3693 | 2.3493 | 0 | 1342.3182 | 0 | 0 | 0 | 2.3493 | 0 | 0 | 1342.3182
6 | 24 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 586.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 598.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 602.4906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 606.6991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 19 | 54.972 | 0 | 54.972 | 11 | 8.0611 | 59.0672 | 59.0672 | 602.0297 | 54.972 | 0 | 32490.0858 | 0 | 0 | 0 | 54.972 | 0 | 0 | 32490.0858
6 | 24 | 20 | 76.2692 | 0 | 76.2692 | 11 | 11.2698 | 0 | 0 | 583.8553 | 0 | 76.2692 | 0 | 7.6231 | 0 | 0 | 0 | 76.2692 | 0 | 0
6 | 24 | 21 | 0.92344 | 0 | 0.92344 | 11 | 9.1708 | 2.3122 | 2.3122 | 551.8293 | 0.92344 | 0 | 499.4219 | 0 | 0 | 0 | 0.92344 | 0 | 0 | 499.4219
6 | 24 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 524.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 23 | 0.66424 | 0 | 0.66424 | 11 | 4.8093 | 0.26703 | 0.26703 | 517.7361 | 0.66424 | 0 | 336.5956 | 0 | 0 | 0 | 0.66424 | 0 | 0 | 336.5956
6 | 25 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 507.8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 501.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 502.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 3 | 0.22705 | 0 | 0.22705 | 11 | 3.3297 | 0.071044 | 0.071044 | 499.7356 | 0.22705 | 0 | 110.9662 | 0 | 0 | 0 | 0.22705 | 0 | 0 | 110.9662
6 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 503.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 524.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 544.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 572.111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 8 | 12.2181 | 0 | 12.2181 | 11 | 5.1879 | 5.2978 | 5.2978 | 588.5602 | 12.2181 | 0 | 7056.6713 | 0 | 0 | 0 | 12.2181 | 0 | 0 | 7056.6713
6 | 25 | 9 | 10.0262 | 0 | 10.0262 | 11 | 6.7449 | 6.4237 | 6.4237 | 597.7493 | 10.0262 | 0 | 5882.8369 | 0 | 0 | 0 | 10.0262 | 0 | 0 | 5882.8369
6 | 25 | 10 | 25.4936 | 0 | 25.4936 | 11 | 8.8783 | 47.2623 | 47.2623 | 592.5372 | 25.4936 | 0 | 14825.477 | 0 | 0 | 0 | 25.4936 | 0 | 0 | 14825.477
6 | 25 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 581.4351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 584.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 583.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 582.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 584.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 593.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 596.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 597.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 19 | 4.5724 | 0 | 4.5724 | 11 | 12.7322 | 0 | 0 | 588.8621 | 0 | 4.5724 | 0 | 0.45702 | 0 | 0 | 0 | 4.5724 | 0 | 0
6 | 25 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 563.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 548.0397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 532.6186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 513.3707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 0 | 1.1652 | 0 | 1.1652 | 11 | 3.5706 | 0.37823 | 0.37823 | 504.3132 | 1.1652 | 0 | 574.7949 | 0 | 0 | 0 | 1.1652 | 0 | 0 | 574.7949
6 | 26 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 497.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 492.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 487.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 496.3824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 514.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 526.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 7 | 0 | 32.5943 | 32.5943 | 48 | 5.1706 | 14.0826 | 14.0826 | 561.0232 | 32.5943 | 0 | 16721.6105 | 0 | 0 | 0 | 32.5943 | 0 | 0 | 16721.6105
6 | 26 | 8 | 0 | 6.4697 | 6.4697 | 48 | 5.8502 | 3.2525 | 3.2525 | 581.2552 | 6.4697 | 0 | 3450.0048 | 0 | 0 | 0 | 6.4697 | 0 | 0 | 3450.0048
6 | 26 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 596.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 598.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 581.6584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 577.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 579.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 576.6893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 583.8285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 592.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 17 | 0 | 58.0642 | 58.0642 | 48 | 11.5451 | 0 | 0 | 600.8287 | 0 | 58.0642 | 0 | 5.8035 | 0 | 0 | 0 | 58.0642 | 0 | 0
6 | 26 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 603.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 602.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 585.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 559.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 528.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 518.9647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 511.3109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 508.8252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 510.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 519.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 538.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 561.1699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 584.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 595.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 586.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 579.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 579.9785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 576.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 12 | 0 | 22.8717 | 22.8717 | 48 | 10.2891 | 0 | 0 | 575.67 | 0 | 22.8717 | 0 | 2.286 | 0 | 0 | 0 | 22.8717 | 0 | 0
6 | 27 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 574.7369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 573.3022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 573.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 578.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 585.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 594.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 591.4813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 572.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 548.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 526.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 521.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 515.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 514.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 2 | 0.23167 | 0 | 0.23167 | 11 | 3.5018 | 0.074407 | 0.074407 | 531.3844 | 0.23167 | 0 | 120.5557 | 0 | 0 | 0 | 0.23167 | 0 | 0 | 120.5557
6 | 28 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 544.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 552.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 566.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 579.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 589.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 592.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 590.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 578.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 572.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 570.9693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 571.3632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 570.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 577.3414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 583.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 578.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 576.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 566.2225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 543.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 521.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 501.2509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 492.6654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 0 | 0.18879 | 0 | 0.18879 | 11 | 4.5083 | 0.071738 | 0.071738 | 489.5909 | 0.18879 | 0 | 90.3517 | 0 | 0 | 0 | 0.18879 | 0 | 0 | 90.3517
6 | 29 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 488.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 2 | 8.4581 | 0 | 8.4581 | 11 | 4.147 | 3.0158 | 3.0158 | 491.4101 | 8.4581 | 0 | 4063.3568 | 0 | 0 | 0 | 8.4581 | 0 | 0 | 4063.3568
6 | 29 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 503.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 518.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 539.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 6 | 1.2108 | 0 | 1.2108 | 11 | 4.7319 | 0.47962 | 0.47962 | 548.1275 | 1.2108 | 0 | 650.3643 | 0 | 0 | 0 | 1.2108 | 0 | 0 | 650.3643
6 | 29 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 560.2508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 561.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 9 | 1.0751 | 0 | 1.0751 | 11 | 6.9858 | 0.74374 | 0.74374 | 567.568 | 1.0751 | 0 | 598.3466 | 0 | 0 | 0 | 1.0751 | 0 | 0 | 598.3466
6 | 29 | 10 | 0.45008 | 0 | 0.45008 | 11 | 7.3471 | 0.3537 | 0.3537 | 567.2004 | 0.45008 | 0 | 250.337 | 0 | 0 | 0 | 0.45008 | 0 | 0 | 250.337
6 | 29 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 555.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 551.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 553.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 552.6413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 561.9482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 570.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 567.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 566.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 562.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 543.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 514.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 499.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 490.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 484.6756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 1 | 11.9727 | 0 | 11.9727 | 11 | 3.4243 | 3.8002 | 3.8002 | 486.0572 | 11.9727 | 0 | 5687.7227 | 0 | 0 | 0 | 11.9727 | 0 | 0 | 5687.7227
6 | 30 | 2 | 7.9853 | 0 | 7.9853 | 11 | 3.3383 | 2.5018 | 2.5018 | 487.0423 | 7.9853 | 0 | 3801.3197 | 0 | 0 | 0 | 7.9853 | 0 | 0 | 3801.3197
6 | 30 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 490.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 499.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 504.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 529.3343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 543.3235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 553.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 557.2563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 544.5123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 550.0303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 549.0164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 549.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 549.6498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 549.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 558.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 563.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 563.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 19 | 21.525 | 0 | 21.525 | 11 | 7.3127 | 16.6992 | 16.6992 | 559.2065 | 21.525 | 0 | 11800.1452 | 0 | 0 | 0 | 21.525 | 0 | 0 | 11800.1452
6 | 30 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 545.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 515.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 484.4458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 23 | 1.8504 | 0 | 1.8504 | 11 | 4.4566 | 0.6966 | 0.6966 | 472.2185 | 1.8504 | 0 | 853.4419 | 0 | 0 | 0 | 1.8504 | 0 | 0 | 853.4419
7 | 1 | 0 | 3.2806 | 0 | 3.2806 | 11 | 3.9749 | 1.1363 | 1.1363 | 466.2021 | 3.2806 | 0 | 1493.3192 | 0 | 0 | 0 | 3.2806 | 0 | 0 | 1493.3192
7 | 1 | 1 | 0.33357 | 0 | 0.33357 | 11 | 3.7598 | 0.11156 | 0.11156 | 468.6905 | 0.33357 | 0 | 152.6719 | 0 | 0 | 0 | 0.33357 | 0 | 0 | 152.6719
7 | 1 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 471.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 475.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 494.0266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 499.8229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 6 | 1.2477 | 0 | 1.2477 | 11 | 4.8007 | 0.50077 | 0.50077 | 514.1451 | 1.2477 | 0 | 627.7819 | 0 | 0 | 0 | 1.2477 | 0 | 0 | 627.7819
7 | 1 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 531.2569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 537.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 541.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 10 | 19.6849 | 0 | 19.6849 | 11 | 7.4159 | 15.8806 | 15.8806 | 540.6832 | 19.6849 | 0 | 10426.7697 | 0 | 0 | 0 | 19.6849 | 0 | 0 | 10426.7697
7 | 1 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 542.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 541.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 13 | 12.998 | 0 | 12.998 | 11 | 8.6546 | 20.1056 | 20.1056 | 544.8561 | 12.998 | 0 | 6939.0662 | 0 | 0 | 0 | 12.998 | 0 | 0 | 6939.0662
7 | 1 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 545.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 540.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 542.8449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 539.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 525.5288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 517.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 499.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 475.5355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 468.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 469.4052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 0 | 5.12 | 0 | 5.12 | 11 | 3.3125 | 1.5979 | 1.5979 | 461.6806 | 5.12 | 0 | 2307.4658 | 0 | 0 | 0 | 5.12 | 0 | 0 | 2307.4658
7 | 2 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 458.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 456.4199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 458.8499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 454.7168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 471.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 6 | 3.2195 | 0 | 3.2195 | 11 | 4.5255 | 1.2272 | 1.2272 | 484.6886 | 3.2195 | 0 | 1525.0336 | 0 | 0 | 0 | 3.2195 | 0 | 0 | 1525.0336
7 | 2 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 497.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 8 | 0 | 25.9345 | 25.9345 | 48 | 5.1879 | 11.2452 | 11.2452 | 508.975 | 25.9345 | 0 | 11955.1448 | 0 | 0 | 0 | 25.9345 | 0 | 0 | 11955.1448
7 | 2 | 9 | 3.7607 | 23.7983 | 27.559 | 42.9509 | 6.7449 | 17.6569 | 17.6569 | 516.9928 | 27.559 | 0 | 13064.1343 | 0 | 0 | 0 | 27.559 | 0 | 0 | 13064.1343
7 | 2 | 10 | 2.5076 | 82.5366 | 85.0442 | 46.909 | 8.8783 | 157.6626 | 157.6626 | 518.3002 | 85.0442 | 0 | 40089.0697 | 0 | 0 | 0 | 85.0442 | 0 | 0 | 40089.0697
7 | 2 | 11 | 0 | 62.5666 | 62.5666 | 48 | 9.8676 | 951.2646 | 288 | 512.2371 | 18.9423 | 43.6243 | 8793.7393 | 4.3603 | 0 | 0 | 18.9423 | 43.6243 | 0 | 8793.7393
7 | 2 | 12 | 0 | 80.2317 | 80.2317 | 48 | 10.2547 | 0 | 0 | 510.3894 | 0 | 80.2317 | 0 | 8.0192 | 0 | 0 | 0 | 80.2317 | 0 | 0
7 | 2 | 13 | 0 | 109.5683 | 109.5683 | 48 | 10.031 | 0 | 0 | 509.1392 | 0 | 109.5683 | 0 | 10.9514 | 0 | 0 | 0 | 109.5683 | 0 | 0
7 | 2 | 14 | 0 | 74.8309 | 74.8309 | 48 | 9.9364 | 2279.7904 | 288 | 508.4538 | 9.4532 | 65.3777 | 4352.7571 | 6.5345 | 0 | 0 | 9.4532 | 65.3777 | 0 | 4352.7571
7 | 2 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 508.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 516.4948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 509.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 510.6769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 505.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 484.8261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 474.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 474.4005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 474.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 468.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 466.0166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 462.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 461.5608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 461.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 465.1134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 469.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 7 | 6.0332 | 0 | 6.0332 | 11 | 5.1706 | 2.6067 | 2.6067 | 473.1546 | 6.0332 | 0 | 2788.2514 | 0 | 0 | 0 | 6.0332 | 0 | 0 | 2788.2514
7 | 3 | 8 | 18.8439 | 0 | 18.8439 | 11 | 5.8502 | 9.4734 | 9.4734 | 481.3458 | 18.8439 | 0 | 8863.1643 | 0 | 0 | 0 | 18.8439 | 0 | 0 | 8863.1643
7 | 3 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 487.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 493.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 489.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 497.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 481.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 472.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 483.5378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 483.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 479.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 479.4376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 479.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 467.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 21 | 0.67572 | 0 | 0.67572 | 11 | 9.8762 | 10.96 | 10.96 | 462.7852 | 0.67572 | 0 | 305.2815 | 0 | 0 | 0 | 0.67572 | 0 | 0 | 305.2815
7 | 3 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 459.4586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 458.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 0 | 0.6154 | 0 | 0.6154 | 11 | 3.9577 | 0.21256 | 0.21256 | 457.3927 | 0.6154 | 0 | 274.7109 | 0 | 0 | 0 | 0.6154 | 0 | 0 | 274.7109
7 | 4 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 457.9443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 462.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 466.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 467.5814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 468.4392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 474.6074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 7 | 0.0083333 | 20.94 | 20.9484 | 47.9853 | 5.6008 | 9.9348 | 9.9348 | 490.3139 | 20.9484 | 0 | 9266.0661 | 0 | 0 | 0 | 20.9484 | 0 | 0 | 9266.0661
7 | 4 | 8 | 1.5438 | 11.3852 | 12.9291 | 43.5819 | 6.5729 | 7.8683 | 7.8683 | 501.4325 | 12.9291 | 0 | 5919.5839 | 0 | 0 | 0 | 12.9291 | 0 | 0 | 5919.5839
7 | 4 | 9 | 0 | 22.3899 | 22.3899 | 48 | 7.7084 | 20.3632 | 20.3632 | 508.3425 | 22.3899 | 0 | 10307.0272 | 0 | 0 | 0 | 22.3899 | 0 | 0 | 10307.0272
7 | 4 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 515.9599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 11 | 1.613 | 0 | 1.613 | 11 | 9.5923 | 8.1642 | 8.1642 | 515.6221 | 1.613 | 0 | 813.9404 | 0 | 0 | 0 | 1.613 | 0 | 0 | 813.9404
7 | 4 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 504.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 501.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 499.7477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 513.4458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 526.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 526.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 525.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 521.1495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 504.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 495.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 489.9349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 487.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 484.0463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 484.3395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 487.0711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 3 | 11.3817 | 0 | 11.3817 | 11 | 3.4416 | 3.622 | 3.622 | 495.9598 | 11.3817 | 0 | 5519.6619 | 0 | 0 | 0 | 11.3817 | 0 | 0 | 5519.6619
7 | 5 | 4 | 7.2736 | 0 | 7.2736 | 11 | 3.6222 | 2.3802 | 2.3802 | 507.1879 | 7.2736 | 0 | 3609.0696 | 0 | 0 | 0 | 7.2736 | 0 | 0 | 3609.0696
7 | 5 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 527.8048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 6 | 5.2787 | 0 | 5.2787 | 11 | 5.1793 | 2.2848 | 2.2848 | 547.1731 | 5.2787 | 0 | 2830.3175 | 0 | 0 | 0 | 5.2787 | 0 | 0 | 2830.3175
7 | 5 | 7 | 27.1746 | 214.432 | 241.6066 | 43.8384 | 5.3599 | 108.6411 | 108.6411 | 565.0334 | 241.6066 | 0 | 125924.1355 | 0 | 0 | 0 | 241.6066 | 0 | 0 | 125924.1355
7 | 5 | 8 | 10.4158 | 685.2678 | 695.6836 | 47.446 | 6.5729 | 423.3766 | 288 | 576.1067 | 473.2357 | 222.448 | 250181.0959 | 22.2337 | 0 | 0 | 473.2357 | 222.448 | 0 | 250181.0959
7 | 5 | 9 | 3.4517 | 46.4829 | 49.9345 | 45.4424 | 7.6912 | 45.0768 | 45.0768 | 580.0014 | 49.9345 | 0 | 26692.9544 | 0 | 0 | 0 | 49.9345 | 0 | 0 | 26692.9544
7 | 5 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 571.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 566.3405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 567.1741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 571.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 571.9559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 576.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 584.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 596.7315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 597.7167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 19 | 1.7663 | 0 | 1.7663 | 11 | 10.8913 | 0 | 0 | 593.444 | 0 | 1.7663 | 0 | 0.17654 | 0 | 0 | 0 | 1.7663 | 0 | 0
7 | 5 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 577.6578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 21 | 1.1924 | 0 | 1.1924 | 11 | 7.4847 | 0.98818 | 0.98818 | 549.7003 | 1.1924 | 0 | 642.3213 | 0 | 0 | 0 | 1.1924 | 0 | 0 | 642.3213
7 | 5 | 22 | 13.6666 | 0 | 13.6666 | 11 | 5.575 | 6.4437 | 6.4437 | 535.8672 | 13.6666 | 0 | 7173.1475 | 0 | 0 | 0 | 13.6666 | 0 | 0 | 7173.1475
7 | 5 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 519.8336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 0 | 0.13417 | 0 | 0.13417 | 11 | 4.5083 | 0.050982 | 0.050982 | 508.7203 | 0.13417 | 0 | 66.7775 | 0 | 0 | 0 | 0.13417 | 0 | 0 | 66.7775
7 | 6 | 1 | 57.6942 | 0 | 57.6942 | 11 | 4.2072 | 20.7849 | 20.7849 | 502.8352 | 57.6942 | 0 | 28376.0526 | 0 | 0 | 0 | 57.6942 | 0 | 0 | 28376.0526
7 | 6 | 2 | 17.6182 | 0 | 17.6182 | 11 | 4.147 | 6.2819 | 6.2819 | 511.7601 | 17.6182 | 0 | 8822.493 | 0 | 0 | 0 | 17.6182 | 0 | 0 | 8822.493
7 | 6 | 3 | 22.8272 | 0 | 22.8272 | 11 | 3.7857 | 7.6663 | 7.6663 | 525.6813 | 22.8272 | 0 | 11748.7121 | 0 | 0 | 0 | 22.8272 | 0 | 0 | 11748.7121
7 | 6 | 4 | 36.3472 | 0 | 36.3472 | 11 | 3.7254 | 12.0899 | 12.0899 | 545.1175 | 36.3472 | 0 | 19413.6781 | 0 | 0 | 0 | 36.3472 | 0 | 0 | 19413.6781
7 | 6 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 560.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 6 | 26.6575 | 0 | 26.6575 | 11 | 4.7319 | 10.5593 | 10.5593 | 568.9524 | 26.6575 | 0 | 14873.6035 | 0 | 0 | 0 | 26.6575 | 0 | 0 | 14873.6035
7 | 6 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 580.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 8 | 0.62793 | 0 | 0.62793 | 11 | 5.4889 | 0.29042 | 0.29042 | 585.116 | 0.62793 | 0 | 360.5058 | 0 | 0 | 0 | 0.62793 | 0 | 0 | 360.5058
7 | 6 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 583.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 571.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 11 | 0 | 53.2767 | 53.2767 | 48 | 8.9643 | 106.934 | 106.934 | 570.1693 | 53.2767 | 0 | 27819.4712 | 0 | 0 | 0 | 53.2767 | 0 | 0 | 27819.4712
7 | 6 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 570.9912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 13 | 1.4526 | 0 | 1.4526 | 11 | 7.8202 | 1.3888 | 1.3888 | 570.9231 | 1.4526 | 0 | 813.3713 | 0 | 0 | 0 | 1.4526 | 0 | 0 | 813.3713
7 | 6 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 574.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 581.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 596.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 602.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 605.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 601.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 20 | 28.0861 | 0 | 28.0861 | 11 | 7.3471 | 22.0715 | 22.0715 | 592.6578 | 28.0861 | 0 | 16336.5278 | 0 | 0 | 0 | 28.0861 | 0 | 0 | 16336.5278
7 | 6 | 21 | 10.3117 | 0 | 10.3117 | 11 | 6.5556 | 6.2441 | 6.2441 | 581.0244 | 10.3117 | 0 | 5877.9017 | 0 | 0 | 0 | 10.3117 | 0 | 0 | 5877.9017
7 | 6 | 22 | 17.5402 | 0 | 17.5402 | 11 | 4.9212 | 7.2065 | 7.2065 | 561.964 | 17.5402 | 0 | 9664.0231 | 0 | 0 | 0 | 17.5402 | 0 | 0 | 9664.0231
7 | 6 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 541.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 526.2466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 521.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 524.4224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 531.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 548.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 563.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 6 | 25.5622 | 0.91417 | 26.4763 | 12.2775 | 4.9556 | 10.9521 | 10.9521 | 583.5321 | 26.4763 | 0 | 15124.7275 | 0 | 0 | 0 | 26.4763 | 0 | 0 | 15124.7275
7 | 7 | 7 | 1.2491 | 209.3255 | 210.5745 | 47.7805 | 6.5556 | 127.5115 | 127.5115 | 582.0179 | 210.5745 | 0 | 112496.7823 | 0 | 0 | 0 | 210.5745 | 0 | 0 | 112496.7823
7 | 7 | 8 | 0 | 125.3062 | 125.3062 | 48 | 7.2524 | 95.0865 | 95.0865 | 577.5434 | 125.3062 | 0 | 66355.0924 | 0 | 0 | 0 | 125.3062 | 0 | 0 | 66355.0924
7 | 7 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 574.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 573.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 574.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 572.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 577.7084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 581.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 580.8424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 584.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 577.9771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 581.4043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 582.6672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 574.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 561.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 550.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 533.5841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 517.5575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 512.8521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 520.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 540.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 555.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 567.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 6 | 2.2266 | 0 | 2.2266 | 11 | 4.8007 | 0.89363 | 0.89363 | 579.7454 | 2.2266 | 0 | 1266.3492 | 0 | 0 | 0 | 2.2266 | 0 | 0 | 1266.3492
7 | 8 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 589.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 589.3848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 585.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 578.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 579.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 579.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 13 | 2.0893 | 0 | 2.0893 | 11 | 8.6546 | 3.2318 | 3.2318 | 573.1611 | 2.0893 | 0 | 1174.5402 | 0 | 0 | 0 | 2.0893 | 0 | 0 | 1174.5402
7 | 8 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 575.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 573.7152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 584.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 579.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 581.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 577.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 562.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 537.9421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 522.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 23 | 2.0827 | 0 | 2.0827 | 11 | 4.8093 | 0.83729 | 0.83729 | 508.3876 | 2.0827 | 0 | 1035.9334 | 0 | 0 | 0 | 2.0827 | 0 | 0 | 1035.9334
7 | 9 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 503.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 498.8564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 498.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 503.4714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 511.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 519.4504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 6 | 1.0608 | 0 | 1.0608 | 11 | 4.5255 | 0.40435 | 0.40435 | 534.2831 | 1.0608 | 0 | 555.0845 | 0 | 0 | 0 | 1.0608 | 0 | 0 | 555.0845
7 | 9 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 552.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 558.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 557.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 10 | 1.0696 | 0 | 1.0696 | 11 | 8.8783 | 1.983 | 1.983 | 558.5516 | 1.0696 | 0 | 585.6818 | 0 | 0 | 0 | 1.0696 | 0 | 0 | 585.6818
7 | 9 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 557.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 555.2634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 559.3777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 556.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 560.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 16 | 42.4417 | 0 | 42.4417 | 11 | 12.5086 | 0 | 0 | 572.2746 | 0 | 42.4417 | 0 | 4.2421 | 0 | 0 | 0 | 42.4417 | 0 | 0
7 | 9 | 17 | 58.0055 | 0 | 58.0055 | 11 | 12.2591 | 0 | 0 | 570.8921 | 0 | 58.0055 | 0 | 5.7977 | 0 | 0 | 0 | 58.0055 | 0 | 0
7 | 9 | 18 | 107.6999 | 0 | 107.6999 | 11 | 12.801 | 0 | 0 | 563.5428 | 0 | 107.6999 | 0 | 10.7646 | 0 | 0 | 0 | 107.6999 | 0 | 0
7 | 9 | 19 | 82.3266 | 0 | 82.3266 | 11 | 12.7322 | 0 | 0 | 557.993 | 0 | 82.3266 | 0 | 8.2286 | 0 | 0 | 0 | 82.3266 | 0 | 0
7 | 9 | 20 | 29.4754 | 0 | 29.4754 | 11 | 13.3172 | 0 | 0 | 546.0187 | 0 | 29.4754 | 0 | 2.9461 | 0 | 0 | 0 | 29.4754 | 0 | 0
7 | 9 | 21 | 66.8148 | 0 | 66.8148 | 11 | 9.2568 | 186.5348 | 186.5348 | 525.7268 | 66.8148 | 0 | 34391.3858 | 0 | 0 | 0 | 66.8148 | 0 | 0 | 34391.3858
7 | 9 | 22 | 16.5484 | 0 | 16.5484 | 11 | 5.3857 | 7.4827 | 7.4827 | 504.1979 | 16.5484 | 0 | 8161.6348 | 0 | 0 | 0 | 16.5484 | 0 | 0 | 8161.6348
7 | 9 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 501.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 0 | 0.18347 | 0 | 0.18347 | 11 | 3.5706 | 0.059558 | 0.059558 | 490.3554 | 0.18347 | 0 | 87.9484 | 0 | 0 | 0 | 0.18347 | 0 | 0 | 87.9484
7 | 10 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 482.8025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 482.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 483.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 484.6916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 496.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 514.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 531.4809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 8 | 21.75 | 29.2498 | 50.9998 | 32.2205 | 5.8502 | 25.6392 | 25.6392 | 548.513 | 50.9998 | 0 | 26330.8249 | 0 | 0 | 0 | 50.9998 | 0 | 0 | 26330.8249
7 | 10 | 9 | 67.9474 | 341.1443 | 409.0917 | 41.8545 | 6.7707 | 264.1939 | 264.1939 | 562.2264 | 409.0917 | 0 | 212879.831 | 0 | 0 | 0 | 409.0917 | 0 | 0 | 212879.831
7 | 10 | 10 | 18.829 | 0 | 18.829 | 11 | 8.9987 | 39.085 | 39.085 | 576.1455 | 18.829 | 0 | 10641.1482 | 0 | 0 | 0 | 18.829 | 0 | 0 | 10641.1482
7 | 10 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 577.3009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 577.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 13 | 57.788 | 0 | 57.788 | 11 | 10.2117 | 0 | 0 | 568.679 | 0 | 57.788 | 0 | 5.7759 | 0 | 0 | 0 | 57.788 | 0 | 0
7 | 10 | 14 | 3.0268 | 0 | 3.0268 | 11 | 9.8762 | 49.0944 | 49.0944 | 569.1397 | 3.0268 | 0 | 1689.3998 | 0 | 0 | 0 | 3.0268 | 0 | 0 | 1689.3998
7 | 10 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 569.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 16 | 0 | 0.4605 | 0.4605 | 48 | 11.5279 | 0 | 0 | 584.3386 | 0 | 0.4605 | 0 | 0.046027 | 0 | 0 | 0 | 0.4605 | 0 | 0
7 | 10 | 17 | 8.6319 | 0 | 8.6319 | 11 | 11.5451 | 0 | 0 | 580.0085 | 0 | 8.6319 | 0 | 0.86276 | 0 | 0 | 0 | 8.6319 | 0 | 0
7 | 10 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 578.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 567.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 549.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 518.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 510.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 23 | 1.3302 | 0 | 1.3302 | 11 | 4.6373 | 0.51762 | 0.51762 | 502.371 | 1.3302 | 0 | 653.6303 | 0 | 0 | 0 | 1.3302 | 0 | 0 | 653.6303
7 | 11 | 0 | 0.11344 | 0 | 0.11344 | 11 | 3.9577 | 0.039183 | 0.039183 | 493.4683 | 0.11344 | 0 | 54.7331 | 0 | 0 | 0 | 0.11344 | 0 | 0 | 54.7331
7 | 11 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 493.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 500.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 510.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 517.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 540.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 560.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 577.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 8 | 22.2516 | 144.2554 | 166.507 | 43.0554 | 6.5729 | 101.3322 | 101.3322 | 581.8101 | 166.507 | 0 | 89706.4262 | 0 | 0 | 0 | 166.507 | 0 | 0 | 89706.4262
7 | 11 | 9 | 24.0135 | 289.7451 | 313.7586 | 45.1682 | 7.7084 | 285.357 | 285.357 | 586.1474 | 313.7586 | 0 | 169736.8324 | 0 | 0 | 0 | 313.7586 | 0 | 0 | 169736.8324
7 | 11 | 10 | 54.9908 | 48.3575 | 103.3483 | 28.3126 | 8.9471 | 204.061 | 204.061 | 581.7627 | 103.3483 | 0 | 57198.1085 | 0 | 0 | 0 | 103.3483 | 0 | 0 | 57198.1085
7 | 11 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 577.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 575.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 572.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 571.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 572.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 582.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 587.8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 589.9374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 588.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 565.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 538.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 22 | 0.38742 | 0 | 0.38742 | 11 | 5.6868 | 0.1874 | 0.1874 | 519.7406 | 0.38742 | 0 | 197.0976 | 0 | 0 | 0 | 0.38742 | 0 | 0 | 197.0976
7 | 11 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 508.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 498.4971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 492.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 505.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 524.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 542.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 566.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 6 | 2.3399 | 0 | 2.3399 | 11 | 5.1793 | 1.0128 | 1.0128 | 581.6128 | 2.3399 | 0 | 1335.1621 | 0 | 0 | 0 | 2.3399 | 0 | 0 | 1335.1621
7 | 12 | 7 | 1.2434 | 23.6889 | 24.9324 | 46.1547 | 5.3599 | 11.2111 | 11.2111 | 593.7226 | 24.9324 | 0 | 13652.1573 | 0 | 0 | 0 | 24.9324 | 0 | 0 | 13652.1573
7 | 12 | 8 | 0 | 135.9456 | 135.9456 | 48 | 6.5729 | 82.7332 | 82.7332 | 596.5192 | 135.9456 | 0 | 74568.7577 | 0 | 0 | 0 | 135.9456 | 0 | 0 | 74568.7577
7 | 12 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 590.6247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 580.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 569.7207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 568.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 570.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 572.1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 572.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 584.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 595.9032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 598.3258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 592.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 588.9193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 568.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 542.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 530.5891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 518.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 517.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 530.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 550.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 567.3908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 584.2162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 585.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 594.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 8 | 0.43115 | 100.3089 | 100.74 | 47.8416 | 5.4889 | 46.5932 | 46.5932 | 593.3697 | 100.74 | 0 | 54956.4986 | 0 | 0 | 0 | 100.74 | 0 | 0 | 54956.4986
7 | 13 | 9 | 18.6027 | 302.2231 | 320.8258 | 45.8546 | 6.9858 | 221.9497 | 221.9497 | 589.8093 | 320.8258 | 0 | 174514.6781 | 0 | 0 | 0 | 320.8258 | 0 | 0 | 174514.6781
7 | 13 | 10 | 0 | 31.8787 | 31.8787 | 48 | 7.3471 | 25.0518 | 25.0518 | 580.5266 | 31.8787 | 0 | 16976.2547 | 0 | 0 | 0 | 31.8787 | 0 | 0 | 16976.2547
7 | 13 | 11 | 0.74167 | 134.9959 | 135.7375 | 47.7978 | 8.9643 | 272.4447 | 272.4447 | 573.6187 | 135.7375 | 0 | 71373.6373 | 0 | 0 | 0 | 135.7375 | 0 | 0 | 71373.6373
7 | 13 | 12 | 0 | 35.1554 | 35.1554 | 48 | 8.2847 | 42.6858 | 42.6858 | 575.8923 | 35.1554 | 0 | 18558.2854 | 0 | 0 | 0 | 35.1554 | 0 | 0 | 18558.2854
7 | 13 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 573.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 574.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 576.1485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 578.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 592.2937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 594.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 587.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 581.6025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 558.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 530.8717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 509.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 0 | 6.7492 | 0 | 6.7492 | 11 | 3.8459 | 2.2888 | 2.2888 | 501.1172 | 6.7492 | 0 | 3307.8864 | 0 | 0 | 0 | 6.7492 | 0 | 0 | 3307.8864
7 | 14 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 503.4551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 496.0485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 515.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 528.6616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 536.0502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 544.6137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 553.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 560.714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 561.1605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 559.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 544.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 546.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 545.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 547.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 554.5756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 562.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 565.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 569.7702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 569.1659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 20 | 0.23329 | 0 | 0.23329 | 11 | 6.6417 | 0.14488 | 0.14488 | 554.7318 | 0.23329 | 0 | 126.8481 | 0 | 0 | 0 | 0.23329 | 0 | 0 | 126.8481
7 | 14 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 561.1158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 538.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 523.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 509.5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 500.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 510.6531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 528.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 546.3196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 561.9061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 573.9893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 582.2275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 581.0657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 572.1932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 568.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 567.7763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 568.2583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 567.5839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 570.2534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 573.1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 580.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 580.4325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 583.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 574.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 566.8208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 540.694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 519.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 23 | 0.92951 | 0 | 0.92951 | 11 | 4.8093 | 0.37367 | 0.37367 | 513.1481 | 0.92951 | 0 | 466.75 | 0 | 0 | 0 | 0.92951 | 0 | 0 | 466.75
7 | 16 | 0 | 0.93788 | 0 | 0.93788 | 11 | 3.3125 | 0.29271 | 0.29271 | 497.5315 | 0.93788 | 0 | 456.31 | 0 | 0 | 0 | 0.93788 | 0 | 0 | 456.31
7 | 16 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 491.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 491.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 492.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 503.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 525.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 6 | 1.5842 | 0 | 1.5842 | 11 | 4.5255 | 0.60389 | 0.60389 | 545.6996 | 1.5842 | 0 | 847.0971 | 0 | 0 | 0 | 1.5842 | 0 | 0 | 847.0971
7 | 16 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 557.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 571.9974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 574.7401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 580.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 573.5129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 12 | 0.22736 | 0 | 0.22736 | 11 | 10.2547 | 0 | 0 | 575.0345 | 0 | 0.22736 | 0 | 0.022724 | 0 | 0 | 0 | 0.22736 | 0 | 0
7 | 16 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 569.9594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 564.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 568.0953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 16 | 1.2124 | 0 | 1.2124 | 11 | 12.5086 | 0 | 0 | 574.2843 | 0 | 1.2124 | 0 | 0.12118 | 0 | 0 | 0 | 1.2124 | 0 | 0
7 | 16 | 17 | 0.95781 | 0 | 0.95781 | 11 | 12.2591 | 0 | 0 | 567.8068 | 0 | 0.95781 | 0 | 0.095733 | 0 | 0 | 0 | 0.95781 | 0 | 0
7 | 16 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 564.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 552.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 533.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 506.8196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 22 | 0.68712 | 0 | 0.68712 | 11 | 5.3857 | 0.3107 | 0.3107 | 491.7644 | 0.68712 | 0 | 330.3451 | 0 | 0 | 0 | 0.68712 | 0 | 0 | 330.3451
7 | 16 | 23 | 21.271 | 0 | 21.271 | 11 | 3.6704 | 7.0138 | 7.0138 | 483.7274 | 21.271 | 0 | 10055.3801 | 0 | 0 | 0 | 21.271 | 0 | 0 | 10055.3801
7 | 17 | 0 | 3.9715 | 0 | 3.9715 | 11 | 3.5706 | 1.2892 | 1.2892 | 478.2413 | 3.9715 | 0 | 1855.6468 | 0 | 0 | 0 | 3.9715 | 0 | 0 | 1855.6468
7 | 17 | 1 | 16.5471 | 0 | 16.5471 | 11 | 3.4588 | 5.2797 | 5.2797 | 472.0657 | 16.5471 | 0 | 7629.3228 | 0 | 0 | 0 | 16.5471 | 0 | 0 | 7629.3228
7 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 469.6705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 3 | 0.040169 | 0 | 0.040169 | 11 | 3.4416 | 0.012783 | 0.012783 | 465.7045 | 0.040169 | 0 | 18.2651 | 0 | 0 | 0 | 0.040169 | 0 | 0 | 18.2651
7 | 17 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 465.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 470.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 6 | 0.10116 | 0 | 0.10116 | 11 | 4.8093 | 0.040667 | 0.040667 | 489.5972 | 0.10116 | 0 | 48.4138 | 0 | 0 | 0 | 0.10116 | 0 | 0 | 48.4138
7 | 17 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 518.9802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 538.6402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 557.6802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 10 | 0 | 107.9068 | 107.9068 | 48 | 8.9987 | 223.9908 | 223.9908 | 563.8274 | 107.9068 | 0 | 55661.2675 | 0 | 0 | 0 | 107.9068 | 0 | 0 | 55661.2675
7 | 17 | 11 | 0 | 53.3514 | 53.3514 | 48 | 10.0569 | 0 | 0 | 572.1663 | 0 | 53.3514 | 0 | 5.3325 | 0 | 0 | 0 | 53.3514 | 0 | 0
7 | 17 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 569.3423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 562.9861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 562.277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 564.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 575.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 590.1881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 588.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 579.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 20 | 12.6691 | 0 | 12.6691 | 11 | 12.6978 | 0 | 0 | 563.6432 | 0 | 12.6691 | 0 | 1.2663 | 0 | 0 | 0 | 12.6691 | 0 | 0
7 | 17 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 534.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 518.2563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 505.6319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 0 | 0.0083333 | 0 | 0.0083333 | 11 | 3.9577 | 0.0028783 | 0.0028783 | 493.4265 | 0.0083333 | 0 | 4.0202 | 0 | 0 | 0 | 0.0083333 | 0 | 0 | 4.0202
7 | 18 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 500.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 507.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 527.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 543.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 560.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 570.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 577.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 582.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 575.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 572.6474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 572.0378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 573.8904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 572.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 566.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 575.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 585.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 593.5012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 595.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 593.164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 575.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 550.3614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 536.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 522.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 509.7932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 508.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 520.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 534.3812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 557.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 572.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 579.4122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 7 | 0.50333 | 0 | 0.50333 | 11 | 5.3599 | 0.22633 | 0.22633 | 581.711 | 0.50333 | 0 | 287.2562 | 0 | 0 | 0 | 0.50333 | 0 | 0 | 287.2562
7 | 19 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 581.6936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 573.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 566.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 562.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 565.1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 562.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 565.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 568.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 575.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 580.4676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 586.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 590.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 20 | 0 | 0.20167 | 0.20167 | 48 | 8.4138 | 0.26472 | 0.26472 | 578.2666 | 0.20167 | 0 | 106.9371 | 0 | 0 | 0 | 0.20167 | 0 | 0 | 106.9371
7 | 19 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 554.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 532.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 23 | 4.2481 | 0 | 4.2481 | 11 | 4.5599 | 1.6295 | 1.6295 | 516.6341 | 4.2481 | 0 | 2147.9785 | 0 | 0 | 0 | 4.2481 | 0 | 0 | 2147.9785
7 | 20 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 499.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 495.0245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 504.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 3 | 0.62864 | 0 | 0.62864 | 11 | 3.7857 | 0.21112 | 0.21112 | 522.5749 | 0.62864 | 0 | 321.5952 | 0 | 0 | 0 | 0.62864 | 0 | 0 | 321.5952
7 | 20 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 543.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 563.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 6 | 25.2969 | 0 | 25.2969 | 11 | 4.7319 | 10.0204 | 10.0204 | 577.2019 | 25.2969 | 0 | 14323.1442 | 0 | 0 | 0 | 25.2969 | 0 | 0 | 14323.1442
7 | 20 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 578.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 577.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 574.4409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 568.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 561.9144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 12 | 0.12104 | 0 | 0.12104 | 11 | 8.2847 | 0.14697 | 0.14697 | 563.0283 | 0.12104 | 0 | 66.8174 | 0 | 0 | 0 | 0.12104 | 0 | 0 | 66.8174
7 | 20 | 13 | 0 | 4.9967 | 4.9967 | 48 | 7.8202 | 4.777 | 4.777 | 565.8942 | 4.9967 | 0 | 2587.7448 | 0 | 0 | 0 | 4.9967 | 0 | 0 | 2587.7448
7 | 20 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 566.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 568.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 16 | 0 | 66.43 | 66.43 | 48 | 7.3729 | 52.7158 | 52.7158 | 575.101 | 66.43 | 0 | 35015.3221 | 0 | 0 | 0 | 66.43 | 0 | 0 | 35015.3221
7 | 20 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 587.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 588.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 587.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 575.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 549.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 522.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 509.8925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 0 | 1.1406 | 0 | 1.1406 | 11 | 3.8459 | 0.38681 | 0.38681 | 505.8557 | 1.1406 | 0 | 564.4447 | 0 | 0 | 0 | 1.1406 | 0 | 0 | 564.4447
7 | 21 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 502.5025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 512.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 526.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 541.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 567.412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 586.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 7 | 0 | 72.6286 | 72.6286 | 48 | 6.5556 | 43.9796 | 43.9796 | 587.3764 | 72.6286 | 0 | 39174.1683 | 0 | 0 | 0 | 72.6286 | 0 | 0 | 39174.1683
7 | 21 | 8 | 0 | 34.1529 | 34.1529 | 48 | 7.2524 | 25.9164 | 25.9164 | 584.2134 | 34.1529 | 0 | 18313.2508 | 0 | 0 | 0 | 34.1529 | 0 | 0 | 18313.2508
7 | 21 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 585.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 577.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 577.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 12 | 0.016667 | 13.6076 | 13.6243 | 47.9547 | 8.2589 | 16.2981 | 16.2981 | 577.1986 | 13.6243 | 0 | 7210.5636 | 0 | 0 | 0 | 13.6243 | 0 | 0 | 7210.5636
7 | 21 | 13 | 0 | 48.5646 | 48.5646 | 48 | 8.5686 | 70.6215 | 70.6215 | 578.8096 | 48.5646 | 0 | 25778.5569 | 0 | 0 | 0 | 48.5646 | 0 | 0 | 25778.5569
7 | 21 | 14 | 0.0083333 | 0 | 0.0083333 | 11 | 8.6374 | 0.012728 | 0.012728 | 578.9074 | 0.0083333 | 0 | 4.7326 | 0 | 0 | 0 | 0.0083333 | 0 | 0 | 4.7326
7 | 21 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 578.7708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 585.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 594.0632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 596.5103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 592.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 588.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 557.8798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 531.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 512.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 501.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 494.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 499.4499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 523.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 531.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 563.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 6 | 0.80644 | 0 | 0.80644 | 11 | 4.8007 | 0.32366 | 0.32366 | 575.3507 | 0.80644 | 0 | 455.1131 | 0 | 0 | 0 | 0.80644 | 0 | 0 | 455.1131
7 | 22 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 575.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 578.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 9 | 0.15674 | 0 | 0.15674 | 11 | 7.5707 | 0.13449 | 0.13449 | 573.3749 | 0.15674 | 0 | 88.1485 | 0 | 0 | 0 | 0.15674 | 0 | 0 | 88.1485
7 | 22 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 573.8788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 579.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 581.4292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 582.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 582.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 582.5303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 588.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 594.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 594.4111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 597.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 597.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 580.3323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 560.7816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 544.1858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 528.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 520.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 519.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 3 | 2.8422 | 0 | 2.8422 | 11 | 3.3297 | 0.88934 | 0.88934 | 517.8166 | 2.8422 | 0 | 1440.4881 | 0 | 0 | 0 | 2.8422 | 0 | 0 | 1440.4881
7 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 525.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 558.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 583.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 588.3894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 596.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 9 | 1.1918 | 0 | 1.1918 | 11 | 6.7449 | 0.76358 | 0.76358 | 595.4168 | 1.1918 | 0 | 696.5076 | 0 | 0 | 0 | 1.1918 | 0 | 0 | 696.5076
7 | 23 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 588.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 587.4154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 583.6288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 585.0797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 581.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 15 | 0 | 73.1125 | 73.1125 | 48 | 11.1494 | 0 | 0 | 586.0821 | 0 | 73.1125 | 0 | 7.3076 | 0 | 0 | 0 | 73.1125 | 0 | 0
7 | 23 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 593.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 600.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 601.8737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 599.4021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 594.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 578.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 554.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 23 | 0.88296 | 0 | 0.88296 | 11 | 3.6704 | 0.29114 | 0.29114 | 529.989 | 0.88296 | 0 | 458.2474 | 0 | 0 | 0 | 0.88296 | 0 | 0 | 458.2474
7 | 24 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 517.5457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 512.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 507.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 504.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 504.4797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 527.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 547.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 7 | 16.3429 | 0 | 16.3429 | 11 | 5.1706 | 7.0611 | 7.0611 | 564.929 | 16.3429 | 0 | 9052.7801 | 0 | 0 | 0 | 16.3429 | 0 | 0 | 9052.7801
7 | 24 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 578.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 586.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 10 | 0 | 7.1118 | 7.1118 | 48 | 8.9987 | 14.7625 | 14.7625 | 584.8176 | 7.1118 | 0 | 3817.7195 | 0 | 0 | 0 | 7.1118 | 0 | 0 | 3817.7195
7 | 24 | 11 | 0 | 11.1046 | 11.1046 | 48 | 10.0569 | 0 | 0 | 588.7753 | 0 | 11.1046 | 0 | 1.1099 | 0 | 0 | 0 | 11.1046 | 0 | 0
7 | 24 | 12 | 0 | 44.2484 | 44.2484 | 48 | 10.1343 | 0 | 0 | 588.3003 | 0 | 44.2484 | 0 | 4.4226 | 0 | 0 | 0 | 44.2484 | 0 | 0
7 | 24 | 13 | 0 | 56.6104 | 56.6104 | 48 | 10.2117 | 0 | 0 | 584.7645 | 0 | 56.6104 | 0 | 5.6582 | 0 | 0 | 0 | 56.6104 | 0 | 0
7 | 24 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 585.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 15 | 0 | 47.841 | 47.841 | 48 | 10.9601 | 0 | 0 | 586.6438 | 0 | 47.841 | 0 | 4.7817 | 0 | 0 | 0 | 47.841 | 0 | 0
7 | 24 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 595.428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 593.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 598.1643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 592.7346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 594.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 578.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 560.7956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 544.0179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 534.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 532.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 538.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 554.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 570.3454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 583.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 596.4622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 601.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 596.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 587.8459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 586.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 587.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 12 | 0 | 0.1315 | 0.1315 | 48 | 10.2891 | 0 | 0 | 588.3929 | 0 | 0.1315 | 0 | 0.013143 | 0 | 0 | 0 | 0.1315 | 0 | 0
7 | 25 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 596.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 595.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 597.2072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 16 | 0 | 62.3726 | 62.3726 | 48 | 12.3021 | 0 | 0 | 600.7164 | 0 | 62.3726 | 0 | 6.2342 | 0 | 0 | 0 | 62.3726 | 0 | 0
7 | 25 | 17 | 0 | 4.7656 | 4.7656 | 48 | 12.1989 | 0 | 0 | 602.5901 | 0 | 4.7656 | 0 | 0.47632 | 0 | 0 | 0 | 4.7656 | 0 | 0
7 | 25 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 604.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 602.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 599.7297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 588.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 568.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 553.8167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 542.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 538.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 545.514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 564.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 579.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 588.2636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 592.1843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 596.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 8 | 0 | 2.1786 | 2.1786 | 48 | 6.5729 | 1.3258 | 1.3258 | 595.969 | 2.1786 | 0 | 1193.8024 | 0 | 0 | 0 | 2.1786 | 0 | 0 | 1193.8024
7 | 26 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 590.6201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 587.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 588.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 586.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 589.7472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 589.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 586.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 598.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 605.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 607.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 604.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 20 | 2.9198 | 0 | 2.9198 | 11 | 8.4138 | 3.8327 | 3.8327 | 598.4682 | 2.9198 | 0 | 1715.2604 | 0 | 0 | 0 | 2.9198 | 0 | 0 | 1715.2604
7 | 26 | 21 | 0.90951 | 0 | 0.90951 | 11 | 7.4847 | 0.75377 | 0.75377 | 588.2211 | 0.90951 | 0 | 524.9871 | 0 | 0 | 0 | 0.90951 | 0 | 0 | 524.9871
7 | 26 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 563.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 550.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 0 | 1.7311 | 0 | 1.7311 | 11 | 4.5083 | 0.65779 | 0.65779 | 539.8517 | 1.7311 | 0 | 915.4702 | 0 | 0 | 0 | 1.7311 | 0 | 0 | 915.4702
7 | 27 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 535.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 540.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 551.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 569.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 5 | 22.299 | 0 | 22.299 | 11 | 3.9663 | 7.713 | 7.713 | 575.5088 | 22.299 | 0 | 12587.9695 | 0 | 0 | 0 | 22.299 | 0 | 0 | 12587.9695
7 | 27 | 6 | 2.6942 | 0 | 2.6942 | 11 | 4.7319 | 1.0672 | 1.0672 | 590.1405 | 2.6942 | 0 | 1560.3411 | 0 | 0 | 0 | 2.6942 | 0 | 0 | 1560.3411
7 | 27 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 599.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 8 | 1.8064 | 0 | 1.8064 | 11 | 5.4889 | 0.83548 | 0.83548 | 600.6088 | 1.8064 | 0 | 1065.0762 | 0 | 0 | 0 | 1.8064 | 0 | 0 | 1065.0762
7 | 27 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 593.2077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 591.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 588.445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 12 | 2.8586 | 0 | 2.8586 | 11 | 8.2847 | 3.4709 | 3.4709 | 590.0641 | 2.8586 | 0 | 1655.3271 | 0 | 0 | 0 | 2.8586 | 0 | 0 | 1655.3271
7 | 27 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 589.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 593.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 595.6827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 597.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 600.4651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 606.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 606.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 601.3114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 590.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 576.9826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 562.1581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 0 | 0.49093 | 0 | 0.49093 | 11 | 3.8459 | 0.16649 | 0.16649 | 552.512 | 0.49093 | 0 | 265.8433 | 0 | 0 | 0 | 0.49093 | 0 | 0 | 265.8433
7 | 28 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 546.7414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 556.6134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 572.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 588.1835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 597.8084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 599.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 601.6848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 595.5324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 589.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 584.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 586.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 578.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 575.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 577.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 590.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 597.7293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 602.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 602.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 596.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 589.7814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 573.2051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 550.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 538.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 525.5047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 525.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 534.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 554.4856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 560.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 565.8156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 579.3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 584.5349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 585.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 584.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 578.2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 574.3246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 573.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 573.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 573.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 578.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 588.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 590.7193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 592.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 590.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 582.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 566.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 554.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 532.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 513.5555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 504.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 503.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 506.9464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 516.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 533.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 554.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 572.4143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 8 | 0 | 5.1253 | 5.1253 | 48 | 5.1879 | 2.2223 | 2.2223 | 574.8516 | 5.1253 | 0 | 2700.2518 | 0 | 0 | 0 | 5.1253 | 0 | 0 | 2700.2518
7 | 30 | 9 | 0 | 0.69019 | 0.69019 | 48 | 6.7449 | 0.4422 | 0.4422 | 576.5239 | 0.69019 | 0 | 364.7844 | 0 | 0 | 0 | 0.69019 | 0 | 0 | 364.7844
7 | 30 | 10 | 0 | 0.20222 | 0.20222 | 48 | 8.8783 | 0.3749 | 0.3749 | 568.3735 | 0.20222 | 0 | 105.2311 | 0 | 0 | 0 | 0.20222 | 0 | 0 | 105.2311
7 | 30 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 564.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 12 | 0 | 1.7278 | 1.7278 | 48 | 10.2547 | 0 | 0 | 570.0868 | 0 | 1.7278 | 0 | 0.1727 | 0 | 0 | 0 | 1.7278 | 0 | 0
7 | 30 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 571.6714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 577.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 584.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 590.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 588.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 18 | 2.2138 | 0 | 2.2138 | 11 | 12.801 | 0 | 0 | 585.4547 | 0 | 2.2138 | 0 | 0.22127 | 0 | 0 | 0 | 2.2138 | 0 | 0
7 | 30 | 19 | 25.5019 | 0 | 25.5019 | 11 | 12.7322 | 0 | 0 | 583.2378 | 0 | 25.5019 | 0 | 2.5489 | 0 | 0 | 0 | 25.5019 | 0 | 0
7 | 30 | 20 | 4.2065 | 0 | 4.2065 | 11 | 13.3172 | 0 | 0 | 565.021 | 0 | 4.2065 | 0 | 0.42044 | 0 | 0 | 0 | 4.2065 | 0 | 0
7 | 30 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 547.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 536.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 23 | 5.2554 | 0 | 5.2554 | 11 | 3.6704 | 1.7329 | 1.7329 | 517.7904 | 5.2554 | 0 | 2663.3703 | 0 | 0 | 0 | 5.2554 | 0 | 0 | 2663.3703
7 | 31 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 507.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 497.2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 496.3586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 500.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 502.2126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 518.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 543.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 7 | 0.79572 | 0 | 0.79572 | 11 | 5.1706 | 0.3438 | 0.3438 | 567.8731 | 0.79572 | 0 | 443.1134 | 0 | 0 | 0 | 0.79572 | 0 | 0 | 443.1134
7 | 31 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 585.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 589.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 588.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 11 | 0 | 40.6775 | 40.6775 | 48 | 10.0569 | 0 | 0 | 586.5984 | 0 | 40.6775 | 0 | 4.0657 | 0 | 0 | 0 | 40.6775 | 0 | 0
7 | 31 | 12 | 0 | 54.7229 | 54.7229 | 48 | 10.1343 | 0 | 0 | 584.5196 | 0 | 54.7229 | 0 | 5.4696 | 0 | 0 | 0 | 54.7229 | 0 | 0
7 | 31 | 13 | 0 | 13.5043 | 13.5043 | 48 | 10.2117 | 0 | 0 | 579.4365 | 0 | 13.5043 | 0 | 1.3498 | 0 | 0 | 0 | 13.5043 | 0 | 0
7 | 31 | 14 | 0 | 10.7863 | 10.7863 | 48 | 9.8762 | 174.9498 | 174.9498 | 578.6936 | 10.7863 | 0 | 5724.2008 | 0 | 0 | 0 | 10.7863 | 0 | 0 | 5724.2008
7 | 31 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 583.6067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 590.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 593.8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 595.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 595.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 584.4285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 555.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 534.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 520.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 510.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 509.8268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 517.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 539.2165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 4 | 1.2528 | 0 | 1.2528 | 11 | 3.5878 | 0.40775 | 0.40775 | 550.4749 | 1.2528 | 0 | 675.8281 | 0 | 0 | 0 | 1.2528 | 0 | 0 | 675.8281
8 | 1 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 566.9938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 6 | 0.15866 | 0 | 0.15866 | 11 | 5.3513 | 0.071212 | 0.071212 | 581.9538 | 0.15866 | 0 | 90.5879 | 0 | 0 | 0 | 0.15866 | 0 | 0 | 90.5879
8 | 1 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 590.327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 588.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 581.9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 578.2672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 575.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 574.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 573.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 575.6944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 577.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 583.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 593.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 595.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 588.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 577.6782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 21 | 0.026459 | 0 | 0.026459 | 11 | 10.3235 | 0 | 0 | 559.4935 | 0 | 0.026459 | 0 | 0.0026446 | 0 | 0 | 0 | 0.026459 | 0 | 0
8 | 1 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 534.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 519.9094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 513.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 511.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 519.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 539.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 553.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 571.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 583.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 595.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 600.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 592.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 587.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 584.8442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 575.0718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 575.286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 578.3529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 580.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 589.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 594.6971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 593.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 587.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 573.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 547.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 534.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 528.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 516.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 1 | 10.9017 | 0 | 10.9017 | 11 | 4.2072 | 3.9274 | 3.9274 | 513.5968 | 10.9017 | 0 | 5479.1805 | 0 | 0 | 0 | 10.9017 | 0 | 0 | 5479.1805
8 | 3 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 519.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 3 | 1.334 | 0 | 1.334 | 11 | 3.7857 | 0.44801 | 0.44801 | 539.1343 | 1.334 | 0 | 704.5234 | 0 | 0 | 0 | 1.334 | 0 | 0 | 704.5234
8 | 3 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 552.7788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 566.9477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 6 | 27.055 | 0 | 27.055 | 11 | 4.7319 | 10.7168 | 10.7168 | 583.2064 | 27.055 | 0 | 15481.0676 | 0 | 0 | 0 | 27.055 | 0 | 0 | 15481.0676
8 | 3 | 7 | 0.76167 | 0 | 0.76167 | 11 | 4.99 | 0.31723 | 0.31723 | 592.531 | 0.76167 | 0 | 442.935 | 0 | 0 | 0 | 0.76167 | 0 | 0 | 442.935
8 | 3 | 8 | 0.66597 | 3.527 | 4.193 | 42.1233 | 5.4889 | 1.9393 | 1.9393 | 593.312 | 4.193 | 0 | 2311.1194 | 0 | 0 | 0 | 4.193 | 0 | 0 | 2311.1194
8 | 3 | 9 | 1.5389 | 0 | 1.5389 | 11 | 6.9858 | 1.0646 | 1.0646 | 584.915 | 1.5389 | 0 | 883.2193 | 0 | 0 | 0 | 1.5389 | 0 | 0 | 883.2193
8 | 3 | 10 | 2.1949 | 25.6536 | 27.8485 | 45.0839 | 7.3471 | 21.8847 | 21.8847 | 582.119 | 27.8485 | 0 | 14955.6031 | 0 | 0 | 0 | 27.8485 | 0 | 0 | 14955.6031
8 | 3 | 11 | 2.1859 | 0 | 2.1859 | 11 | 8.9643 | 4.3873 | 4.3873 | 574.4702 | 2.1859 | 0 | 1231.6625 | 0 | 0 | 0 | 2.1859 | 0 | 0 | 1231.6625
8 | 3 | 12 | 0 | 13.054 | 13.054 | 48 | 8.2847 | 15.8502 | 15.8502 | 568.6408 | 13.054 | 0 | 6796.4466 | 0 | 0 | 0 | 13.054 | 0 | 0 | 6796.4466
8 | 3 | 13 | 0 | 22.2491 | 22.2491 | 48 | 7.8202 | 21.2709 | 21.2709 | 567.4115 | 22.2491 | 0 | 11556.4208 | 0 | 0 | 0 | 22.2491 | 0 | 0 | 11556.4208
8 | 3 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 567.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 571.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 16 | 0 | 5.0945 | 5.0945 | 48 | 7.3729 | 4.0427 | 4.0427 | 580.8032 | 5.0945 | 0 | 2714.3418 | 0 | 0 | 0 | 5.0945 | 0 | 0 | 2714.3418
8 | 3 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 581.7455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 590.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 580.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 567.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 549.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 482.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 469.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 460.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 459.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 2 | 0.043699 | 0 | 0.043699 | 11 | 3.3383 | 0.013691 | 0.013691 | 465.3003 | 0.043699 | 0 | 19.8526 | 0 | 0 | 0 | 0.043699 | 0 | 0 | 19.8526
8 | 4 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 487.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 501.6585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 516.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 528.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 542.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 549.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 549.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 544.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 536.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 537.6826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 534.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 536.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 537.2061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 16 | 14.4383 | 0 | 14.4383 | 11 | 7.6998 | 13.0824 | 13.0824 | 545.5964 | 14.4383 | 0 | 7718.6812 | 0 | 0 | 0 | 14.4383 | 0 | 0 | 7718.6812
8 | 4 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 545.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 548.2697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 537.5319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 20 | 6.3254 | 0 | 6.3254 | 11 | 6.6417 | 3.9282 | 3.9282 | 523.9764 | 6.3254 | 0 | 3244.7749 | 0 | 0 | 0 | 6.3254 | 0 | 0 | 3244.7749
8 | 4 | 21 | 61.5615 | 0 | 61.5615 | 11 | 5.9879 | 32.0092 | 32.0092 | 544.731 | 61.5615 | 0 | 32857.2866 | 0 | 0 | 0 | 61.5615 | 0 | 0 | 32857.2866
8 | 4 | 22 | 130.9533 | 0 | 130.9533 | 11 | 5.0846 | 55.5902 | 55.5902 | 526.5209 | 130.9533 | 0 | 67509.1566 | 0 | 0 | 0 | 130.9533 | 0 | 0 | 67509.1566
8 | 4 | 23 | 46.3525 | 0 | 46.3525 | 11 | 4.4566 | 17.4497 | 17.4497 | 508.3293 | 46.3525 | 0 | 23052.446 | 0 | 0 | 0 | 46.3525 | 0 | 0 | 23052.446
8 | 5 | 0 | 2.9049 | 0 | 2.9049 | 11 | 3.9749 | 1.0062 | 1.0062 | 503.5799 | 2.9049 | 0 | 1430.8729 | 0 | 0 | 0 | 2.9049 | 0 | 0 | 1430.8729
8 | 5 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 498.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 494.9632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 509.1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 524.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 544.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 561.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 575.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 575.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 577.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 566.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 563.6816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 564.6543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 564.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 564.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 567.2998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 576.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 586.2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 585.9812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 576.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 566.8367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 548.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 22 | 54.5867 | 0 | 54.5867 | 11 | 5.4717 | 25.1511 | 25.1511 | 522.2694 | 54.5867 | 0 | 27908.5155 | 0 | 0 | 0 | 54.5867 | 0 | 0 | 27908.5155
8 | 5 | 23 | 49.965 | 0 | 49.965 | 11 | 4.8093 | 20.0866 | 20.0866 | 509.5002 | 49.965 | 0 | 24907.5782 | 0 | 0 | 0 | 49.965 | 0 | 0 | 24907.5782
8 | 6 | 0 | 9.0097 | 0 | 9.0097 | 11 | 3.3125 | 2.8119 | 2.8119 | 499.9439 | 9.0097 | 0 | 4405.2338 | 0 | 0 | 0 | 9.0097 | 0 | 0 | 4405.2338
8 | 6 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 493.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 491.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 501.5476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 499.6055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 517.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 543.7297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 564.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 582.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 579.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 570.539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 566.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 12 | 0 | 9.8044 | 9.8044 | 48 | 10.2547 | 0 | 0 | 562.3745 | 0 | 9.8044 | 0 | 0.97996 | 0 | 0 | 0 | 9.8044 | 0 | 0
8 | 6 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 565.5764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 565.9799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 578.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 581.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 579.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 581.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 569.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 550.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 21 | 2.4249 | 0 | 2.4249 | 11 | 9.2568 | 6.7699 | 6.7699 | 526.0577 | 2.4249 | 0 | 1248.9651 | 0 | 0 | 0 | 2.4249 | 0 | 0 | 1248.9651
8 | 6 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 517.2728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 23 | 6.7988 | 0 | 6.7988 | 11 | 3.6704 | 2.2418 | 2.2418 | 500.4553 | 6.7988 | 0 | 3327.7251 | 0 | 0 | 0 | 6.7988 | 0 | 0 | 3327.7251
8 | 7 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 492.1044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 486.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 484.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 483.6589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 484.138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 499.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 522.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 7 | 0.908 | 0 | 0.908 | 11 | 5.1706 | 0.39231 | 0.39231 | 531.9468 | 0.908 | 0 | 473.0183 | 0 | 0 | 0 | 0.908 | 0 | 0 | 473.0183
8 | 7 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 549.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 567.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 580.8851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 585.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 581.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 571.8487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 567.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 574.1675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 16 | 0.055177 | 0 | 0.055177 | 11 | 11.5279 | 0 | 0 | 584.523 | 0 | 0.055177 | 0 | 0.0055149 | 0 | 0 | 0 | 0.055177 | 0 | 0
8 | 7 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 577.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 574.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 553.7154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 528.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 505.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 487.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 23 | 23.3902 | 0 | 23.3902 | 11 | 4.6373 | 9.1017 | 9.1017 | 485.0357 | 23.3902 | 0 | 11087.7682 | 0 | 0 | 0 | 23.3902 | 0 | 0 | 11087.7682
8 | 8 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 479.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 480.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 487.9957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 494.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 502.9195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 519.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 6 | 19.3341 | 0 | 19.3341 | 11 | 5.3513 | 8.6777 | 8.6777 | 537.3582 | 19.3341 | 0 | 10176.6366 | 0 | 0 | 0 | 19.3341 | 0 | 0 | 10176.6366
8 | 8 | 7 | 80.3913 | 201.5808 | 281.9722 | 37.4512 | 5.6008 | 133.7263 | 133.7263 | 555.1573 | 281.9722 | 0 | 145978.7062 | 0 | 0 | 0 | 281.9722 | 0 | 0 | 145978.7062
8 | 8 | 8 | 112.6346 | 598.1546 | 710.7892 | 42.1368 | 6.5729 | 432.5695 | 288 | 571.848 | 473.2357 | 237.5536 | 250678.2368 | 23.7435 | 0 | 0 | 473.2357 | 237.5536 | 0 | 250678.2368
8 | 8 | 9 | 40.01 | 387.2647 | 427.2747 | 44.5353 | 7.7084 | 388.5976 | 288 | 569.4564 | 316.6646 | 110.6101 | 166223.9275 | 11.0555 | 0 | 0 | 316.6646 | 110.6101 | 0 | 166223.9275
8 | 8 | 10 | 0.74829 | 1.9084 | 2.6567 | 37.5784 | 8.9471 | 5.2456 | 5.2456 | 566.3168 | 2.6567 | 0 | 1404.6817 | 0 | 0 | 0 | 2.6567 | 0 | 0 | 1404.6817
8 | 8 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 564.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 562.8541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 564.4222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 567.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 571.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 580.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 581.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 579.5581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 19 | 0 | 13.8117 | 13.8117 | 48 | 13.2054 | 0 | 0 | 555.1458 | 0 | 13.8117 | 0 | 1.3805 | 0 | 0 | 0 | 13.8117 | 0 | 0
8 | 8 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 529.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 21 | 4.9383 | 0 | 4.9383 | 11 | 10.3235 | 0 | 0 | 501.4361 | 0 | 4.9383 | 0 | 0.49358 | 0 | 0 | 0 | 4.9383 | 0 | 0
8 | 8 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 483.8632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 23 | 0.9577 | 0 | 0.9577 | 11 | 4.5734 | 0.36828 | 0.36828 | 480.241 | 0.9577 | 0 | 449.3924 | 0 | 0 | 0 | 0.9577 | 0 | 0 | 449.3924
8 | 9 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 473.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 1 | 0.058795 | 0 | 0.058795 | 11 | 3.605 | 0.019188 | 0.019188 | 474.5281 | 0.058795 | 0 | 27.253 | 0 | 0 | 0 | 0.058795 | 0 | 0 | 27.253
8 | 9 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 485.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 503.8013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 518.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 526.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 543.3996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 562.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 572.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 578.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 570.3937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 568.6107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 563.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 562.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 564.1032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 568.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 575.4955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 580.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 584.9619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 580.6038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 564.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 549.3549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 531.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 516.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 0 | 0.64052 | 0 | 0.64052 | 11 | 4.5083 | 0.24339 | 0.24339 | 507.5575 | 0.64052 | 0 | 318.0535 | 0 | 0 | 0 | 0.64052 | 0 | 0 | 318.0535
8 | 10 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 505.8085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 513.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 538.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 556.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 562.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 573.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 578.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 581.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 582.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 574.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 568.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 12 | 13.8242 | 0 | 13.8242 | 11 | 8.2847 | 16.7854 | 16.7854 | 568.4463 | 13.8242 | 0 | 7706.2707 | 0 | 0 | 0 | 13.8242 | 0 | 0 | 7706.2707
8 | 10 | 13 | 8.7209 | 0 | 8.7209 | 11 | 7.8202 | 8.3374 | 8.3374 | 569.7077 | 8.7209 | 0 | 4872.4186 | 0 | 0 | 0 | 8.7209 | 0 | 0 | 4872.4186
8 | 10 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 573.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 573.8321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 577.6469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 587.6566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 594.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 596.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 596.3733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 583.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 562.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 548.603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 529.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 1 | 0.91839 | 0 | 0.91839 | 11 | 3.4243 | 0.2915 | 0.2915 | 527.4738 | 0.91839 | 0 | 474.3247 | 0 | 0 | 0 | 0.91839 | 0 | 0 | 474.3247
8 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 539.2909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 560.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 564.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 578.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 593.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 590.9684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 587.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 582.1084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 577.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 575.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 574.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 571.1993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 566.7415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 569.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 580.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 588.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 594.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 592.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 586.4328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 581.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 567.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 554.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 544.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 537.6482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 549.3747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 571.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 574.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 575.3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 581.3861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 586.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 583.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 578.9464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 576.9715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 570.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 573.6809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 571.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 573.1538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 574.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 573.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 574.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 583.5253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 586.9569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 581.8701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 575.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 566.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 544.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 535.5053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 525.5814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 521.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 526.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 528.8168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 550.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 568.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 576.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 577.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 574.7755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 566.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 11 | 0 | 71.4855 | 71.4855 | 48 | 9.8676 | 1086.8685 | 288 | 563.729 | 18.9423 | 52.5432 | 9769.1163 | 5.2517 | 0 | 0 | 18.9423 | 52.5432 | 0 | 9769.1163
8 | 13 | 12 | 0 | 55.5848 | 55.5848 | 48 | 10.2547 | 0 | 0 | 565.4399 | 0 | 55.5848 | 0 | 5.5557 | 0 | 0 | 0 | 55.5848 | 0 | 0
8 | 13 | 13 | 0 | 4.5126 | 4.5126 | 48 | 10.031 | 0 | 0 | 565.3052 | 0 | 4.5126 | 0 | 0.45103 | 0 | 0 | 0 | 4.5126 | 0 | 0
8 | 13 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 565.7951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 571.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 579.9991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 583.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 585.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 584.9147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 579.0818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 569.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 560.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 544.7813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 526.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 516.301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 507.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 507.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 508.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 530.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 554.0741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 570.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 574.3977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 576.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 568.1877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 565.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 570.1391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 574.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 581.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 15 | 0 | 5.8655 | 5.8655 | 48 | 10.9601 | 0 | 0 | 583.2305 | 0 | 5.8655 | 0 | 0.58625 | 0 | 0 | 0 | 5.8655 | 0 | 0
8 | 14 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 585.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 579.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 581.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 580.3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 566.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 552.9715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 527.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 512.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 501.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 501.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 509.3709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 3 | 0.53808 | 0 | 0.53808 | 11 | 3.562 | 0.17444 | 0.17444 | 531.5503 | 0.53808 | 0 | 280.0967 | 0 | 0 | 0 | 0.53808 | 0 | 0 | 280.0967
8 | 15 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 544.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 551.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 560.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 571.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 568.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 565.5997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 10 | 0 | 4.785 | 4.785 | 48 | 8.9471 | 9.4479 | 9.4479 | 560.7674 | 4.785 | 0 | 2453.5709 | 0 | 0 | 0 | 4.785 | 0 | 0 | 2453.5709
8 | 15 | 11 | 0 | 4.9047 | 4.9047 | 48 | 9.5923 | 24.8255 | 24.8255 | 562.1644 | 4.9047 | 0 | 2521.8084 | 0 | 0 | 0 | 4.9047 | 0 | 0 | 2521.8084
8 | 15 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 559.9453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 564.5077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 563.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 574.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 575.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 571.1547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 575.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 563.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 542.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 527.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 509.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 496.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 489.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 488.7583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 491.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 518.8716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 538.0827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 552.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 562.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 571.5415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 571.9021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 569.8586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 568.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 11 | 0 | 17.4072 | 17.4072 | 48 | 9.7214 | 128.1941 | 128.1941 | 566.2818 | 17.4072 | 0 | 9021.8147 | 0 | 0 | 0 | 17.4072 | 0 | 0 | 9021.8147
8 | 16 | 12 | 0 | 6.3683 | 6.3683 | 48 | 9.4117 | 22.4191 | 22.4191 | 564.6682 | 6.3683 | 0 | 3290.289 | 0 | 0 | 0 | 6.3683 | 0 | 0 | 3290.289
8 | 16 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 563.3136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 566.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 15 | 0 | 12.6089 | 12.6089 | 48 | 10.0224 | 0 | 0 | 572.3307 | 0 | 12.6089 | 0 | 1.2603 | 0 | 0 | 0 | 12.6089 | 0 | 0
8 | 16 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 578.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 580.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 580.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 580.3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 566.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 549.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 532.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 518.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 509.4625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 503.1795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 511.464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 541.0733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 556.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 566.5764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 570.3304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 574.5951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 570.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 566.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 562.3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 11 | 0 | 31.6914 | 31.6914 | 48 | 8.9643 | 63.6092 | 63.6092 | 559.9574 | 31.6914 | 0 | 16224.647 | 0 | 0 | 0 | 31.6914 | 0 | 0 | 16224.647
8 | 17 | 12 | 0.000375 | 321.7775 | 321.7778 | 48 | 8.2847 | 390.7031 | 288 | 560.0897 | 237.1929 | 84.5849 | 121464.063 | 8.4543 | 0 | 0 | 237.1929 | 84.5849 | 0 | 121464.063
8 | 17 | 13 | 0 | 474.0974 | 474.0974 | 48 | 7.8202 | 453.253 | 288 | 558.637 | 301.2447 | 172.8527 | 153826.706 | 17.2767 | 0 | 0 | 301.2447 | 172.8527 | 0 | 153826.706
8 | 17 | 14 | 0 | 349.1491 | 349.1491 | 48 | 7.6568 | 310.5642 | 288 | 558.0459 | 323.7815 | 25.3676 | 165143.4103 | 2.5355 | 0 | 0 | 323.7815 | 25.3676 | 0 | 165143.4103
8 | 17 | 15 | 3.5261 | 179.417 | 182.9432 | 47.2868 | 7.7256 | 167.639 | 167.639 | 567.0244 | 182.9432 | 0 | 95082.4442 | 0 | 0 | 0 | 182.9432 | 0 | 0 | 95082.4442
8 | 17 | 16 | 1.8474 | 61.2659 | 63.1134 | 46.917 | 7.3729 | 50.0839 | 50.0839 | 576.1057 | 63.1134 | 0 | 33398.8823 | 0 | 0 | 0 | 63.1134 | 0 | 0 | 33398.8823
8 | 17 | 17 | 0 | 4.3407 | 4.3407 | 48 | 7.5449 | 3.6855 | 3.6855 | 581.4784 | 4.3407 | 0 | 2315.6807 | 0 | 0 | 0 | 4.3407 | 0 | 0 | 2315.6807
8 | 17 | 18 | 0 | 22.5887 | 22.5887 | 48 | 7.0804 | 16.1327 | 16.1327 | 582.671 | 22.5887 | 0 | 12077.5251 | 0 | 0 | 0 | 22.5887 | 0 | 0 | 12077.5251
8 | 17 | 19 | 0 | 1.7025 | 1.7025 | 48 | 7.7772 | 1.5962 | 1.5962 | 578.0826 | 1.7025 | 0 | 902.4657 | 0 | 0 | 0 | 1.7025 | 0 | 0 | 902.4657
8 | 17 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 564.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 539.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 520.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 508.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 497.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 496.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 501.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 533.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 550.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 558.0774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 567.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 569.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 571.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 9 | 1.2689 | 0 | 1.2689 | 11 | 7.6998 | 1.1498 | 1.1498 | 564.4594 | 1.2689 | 0 | 702.3 | 0 | 0 | 0 | 1.2689 | 0 | 0 | 702.3
8 | 18 | 10 | 0 | 3.5714 | 3.5714 | 48 | 7.8632 | 3.483 | 3.483 | 557.244 | 3.5714 | 0 | 1818.7361 | 0 | 0 | 0 | 3.5714 | 0 | 0 | 1818.7361
8 | 18 | 11 | 0 | 0.5598 | 0.5598 | 48 | 7.6051 | 0.48723 | 0.48723 | 551.8839 | 0.5598 | 0 | 282.075 | 0 | 0 | 0 | 0.5598 | 0 | 0 | 282.075
8 | 18 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 549.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 548.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 549.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 15 | 2.05 | 0 | 2.05 | 11 | 7.803 | 1.9445 | 1.9445 | 554.5322 | 2.05 | 0 | 1114.2183 | 0 | 0 | 0 | 2.05 | 0 | 0 | 1114.2183
8 | 18 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 565.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 569.4906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 572.5555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 568.3795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 557.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 538.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 513.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 498.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 488.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 485.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 492.5915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 511.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 529.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 542.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 558.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 569.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 8 | 1.4136 | 0 | 1.4136 | 11 | 6.9944 | 0.98072 | 0.98072 | 569.7104 | 1.4136 | 0 | 789.7792 | 0 | 0 | 0 | 1.4136 | 0 | 0 | 789.7792
8 | 19 | 9 | 8.8525 | 0 | 8.8525 | 11 | 7.5707 | 7.5959 | 7.5959 | 563.5602 | 8.8525 | 0 | 4891.539 | 0 | 0 | 0 | 8.8525 | 0 | 0 | 4891.539
8 | 19 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 554.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 11 | 2.2213 | 0 | 2.2213 | 11 | 7.5879 | 1.9195 | 1.9195 | 556.7509 | 2.2213 | 0 | 1212.2594 | 0 | 0 | 0 | 2.2213 | 0 | 0 | 1212.2594
8 | 19 | 12 | 0 | 33.561 | 33.561 | 48 | 8.3192 | 41.5815 | 41.5815 | 554.9291 | 33.561 | 0 | 17013.0341 | 0 | 0 | 0 | 33.561 | 0 | 0 | 17013.0341
8 | 19 | 13 | 0 | 110.3709 | 110.3709 | 48 | 8.6546 | 170.7236 | 170.7236 | 555.4692 | 110.3709 | 0 | 56009.8086 | 0 | 0 | 0 | 110.3709 | 0 | 0 | 56009.8086
8 | 19 | 14 | 0 | 10.9744 | 10.9744 | 48 | 8.9299 | 21.3221 | 21.3221 | 557.432 | 10.9744 | 0 | 5590.7095 | 0 | 0 | 0 | 10.9744 | 0 | 0 | 5590.7095
8 | 19 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 561.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 570.6194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 573.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 573.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 564.3223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 544.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 513.4388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 494.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 480.9378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 473.223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 465.1336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 465.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 464.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 467.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 490.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 510.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 531.3034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 8 | 2.9811 | 0 | 2.9811 | 11 | 5.1879 | 1.2926 | 1.2926 | 540.6206 | 2.9811 | 0 | 1578.8529 | 0 | 0 | 0 | 2.9811 | 0 | 0 | 1578.8529
8 | 20 | 9 | 6.1249 | 0 | 6.1249 | 11 | 6.7449 | 3.9242 | 3.9242 | 542.952 | 6.1249 | 0 | 3258.168 | 0 | 0 | 0 | 6.1249 | 0 | 0 | 3258.168
8 | 20 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 538.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 536.6735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 535.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 530.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 534.9045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 539.0802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 551.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 553.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 552.8318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 541.6958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 525.8671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 495.3884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 478.7963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 466.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 457.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 453.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 452.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 455.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 456.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 467.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 486.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 497.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 516.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 533.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 531.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 530.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 530.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 525.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 533.7659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 540.8551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 544.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 541.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 541.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 518.6545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 491.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 471.9078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 467.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 457.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 453.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 1 | 16.7813 | 0 | 16.7813 | 11 | 3.6394 | 5.5064 | 5.5064 | 455.057 | 16.7813 | 0 | 7451.8657 | 0 | 0 | 0 | 16.7813 | 0 | 0 | 7451.8657
8 | 22 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 470.4839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 4 | 0.98669 | 0 | 0.98669 | 11 | 3.5878 | 0.32115 | 0.32115 | 480.5913 | 0.98669 | 0 | 463.3402 | 0 | 0 | 0 | 0.98669 | 0 | 0 | 463.3402
8 | 22 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 499.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 6 | 4.1059 | 0 | 4.1059 | 11 | 5.3513 | 1.8428 | 1.8428 | 517.8002 | 4.1059 | 0 | 2080.8497 | 0 | 0 | 0 | 4.1059 | 0 | 0 | 2080.8497
8 | 22 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 529.8296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 8 | 0 | 27.4779 | 27.4779 | 48 | 6.5729 | 16.7224 | 16.7224 | 538.5395 | 27.4779 | 0 | 13478.9871 | 0 | 0 | 0 | 27.4779 | 0 | 0 | 13478.9871
8 | 22 | 9 | 4.3726 | 56.3833 | 60.7559 | 45.3371 | 7.7084 | 55.2563 | 55.2563 | 538.9629 | 60.7559 | 0 | 29990.6872 | 0 | 0 | 0 | 60.7559 | 0 | 0 | 29990.6872
8 | 22 | 10 | 0.73609 | 242.4488 | 243.1849 | 47.888 | 8.9471 | 480.1683 | 288 | 529.4913 | 145.8598 | 97.3251 | 70246.563 | 9.7277 | 0 | 0 | 145.8598 | 97.3251 | 0 | 70246.563
8 | 22 | 11 | 0 | 175.906 | 175.906 | 48 | 9.5923 | 890.3663 | 288 | 536.5909 | 56.899 | 119.007 | 27800.3176 | 11.8948 | 0 | 0 | 56.899 | 119.007 | 0 | 27800.3176
8 | 22 | 12 | 3.1301 | 233.3193 | 236.4494 | 47.5102 | 10.2891 | 0 | 0 | 540.0501 | 0 | 236.4494 | 0 | 23.6332 | 0 | 0 | 0 | 236.4494 | 0 | 0
8 | 22 | 13 | 0 | 249.1205 | 249.1205 | 48 | 10.0827 | 0 | 0 | 542.7415 | 0 | 249.1205 | 0 | 24.8997 | 0 | 0 | 0 | 249.1205 | 0 | 0
8 | 22 | 14 | 0 | 180.3197 | 180.3197 | 48 | 10.6934 | 0 | 0 | 541.3409 | 0 | 180.3197 | 0 | 18.023 | 0 | 0 | 0 | 180.3197 | 0 | 0
8 | 22 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 548.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 543.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 543.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 544.3645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 521.4715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 494.0058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 470.3623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 461.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 462.8633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 460.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 457.6109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 459.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 472.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 480.9002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 5 | 0.68102 | 0 | 0.68102 | 11 | 4.0351 | 0.23827 | 0.23827 | 484.4759 | 0.68102 | 0 | 322.4486 | 0 | 0 | 0 | 0.68102 | 0 | 0 | 322.4486
8 | 23 | 6 | 2.7252 | 0 | 2.7252 | 11 | 5.1793 | 1.1796 | 1.1796 | 500.753 | 2.7252 | 0 | 1334.6914 | 0 | 0 | 0 | 2.7252 | 0 | 0 | 1334.6914
8 | 23 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 519.7935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 533.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 534.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 537.2158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 533.3248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 543.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 13 | 0 | 0.38996 | 0.38996 | 48 | 8.8869 | 0.7285 | 0.7285 | 543.4287 | 0.38996 | 0 | 193.1965 | 0 | 0 | 0 | 0.38996 | 0 | 0 | 193.1965
8 | 23 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 549.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 558.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 558.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 565.4693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 552.6767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 532.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 500.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 21 | 0.52258 | 0 | 0.52258 | 11 | 7.4847 | 0.4331 | 0.4331 | 480.119 | 0.52258 | 0 | 245.1516 | 0 | 0 | 0 | 0.52258 | 0 | 0 | 245.1516
8 | 23 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 469.135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 464.5572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 460.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 459.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 463.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 480.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 491.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 497.6418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 6 | 6.2716 | 0 | 6.2716 | 11 | 4.7319 | 2.4842 | 2.4842 | 516.3909 | 6.2716 | 0 | 3169.6042 | 0 | 0 | 0 | 6.2716 | 0 | 0 | 3169.6042
8 | 24 | 7 | 0.66301 | 0 | 0.66301 | 11 | 4.99 | 0.27614 | 0.27614 | 533.7927 | 0.66301 | 0 | 346.617 | 0 | 0 | 0 | 0.66301 | 0 | 0 | 346.617
8 | 24 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 549.8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 564.2229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 560.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 554.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 547.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 549.9343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 554.7367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 562.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 567.1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 572.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 578.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 571.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 542.7244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 519.2255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 498.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 489.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 479.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 471.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 605.4748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 634.6591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 642.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 647.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 663.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 7 | 20.4585 | 0.23 | 20.6885 | 11.4113 | 6.5556 | 12.5277 | 12.5277 | 677.5259 | 20.6885 | 0 | 13780.9021 | 0 | 0 | 0 | 20.6885 | 0 | 0 | 13780.9021
8 | 25 | 8 | 8.505 | 92.3019 | 100.8068 | 44.8784 | 7.2524 | 76.4955 | 76.4955 | 683.3963 | 100.8068 | 0 | 64366.9787 | 0 | 0 | 0 | 100.8068 | 0 | 0 | 64366.9787
8 | 25 | 9 | 2.6216 | 0.083333 | 2.705 | 12.1399 | 7.6998 | 2.4509 | 2.4509 | 675.3535 | 2.705 | 0 | 1793.9653 | 0 | 0 | 0 | 2.705 | 0 | 0 | 1793.9653
8 | 25 | 10 | 1.7533 | 0 | 1.7533 | 11 | 7.8632 | 1.7098 | 1.7098 | 658.8558 | 1.7533 | 0 | 1135.8532 | 0 | 0 | 0 | 1.7533 | 0 | 0 | 1135.8532
8 | 25 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 652.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 650.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 644.5045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 650.7654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 653.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 670.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 673.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 678.0014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 688.6989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 688.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 554.9477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 529.6412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 519.9622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 0 | 0.35215 | 0 | 0.35215 | 11 | 3.9749 | 0.12198 | 0.12198 | 509.0827 | 0.35215 | 0 | 175.4015 | 0 | 0 | 0 | 0.35215 | 0 | 0 | 175.4015
8 | 26 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 502.4672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 505.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 535.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 542.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 558.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 571.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 578.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 574.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 567.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 565.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 563.6274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 565.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 566.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 569.9393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 572.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 577.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 573.0211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 579.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 580.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 572.8132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 554.6565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 530.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 511.8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 501.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 494.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 492.664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 496.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 496.8365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 513.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 542.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 557.4536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 571.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 572.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 562.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 568.7542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 12 | 0 | 0.95921 | 0.95921 | 48 | 10.2547 | 0 | 0 | 571.8025 | 0 | 0.95921 | 0 | 0.095873 | 0 | 0 | 0 | 0.95921 | 0 | 0
8 | 27 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 570.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 571.7285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 581.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 584.6521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 589.5501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 583.8803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 571.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 549.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 531.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 22 | 3.8394 | 0 | 3.8394 | 11 | 5.3857 | 1.7361 | 1.7361 | 515.6758 | 3.8394 | 0 | 1937.6595 | 0 | 0 | 0 | 3.8394 | 0 | 0 | 1937.6595
8 | 27 | 23 | 19.449 | 0 | 19.449 | 11 | 3.6704 | 6.413 | 6.413 | 507.0332 | 19.449 | 0 | 9647.3589 | 0 | 0 | 0 | 19.449 | 0 | 0 | 9647.3589
8 | 28 | 0 | 17.7678 | 0 | 17.7678 | 11 | 3.5706 | 5.7677 | 5.7677 | 492.7575 | 17.7678 | 0 | 8559.7495 | 0 | 0 | 0 | 17.7678 | 0 | 0 | 8559.7495
8 | 28 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 490.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 490.8805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 493.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 489.8637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 500.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 526.9546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 555.3381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 574.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 590.7872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 10 | 0 | 0.90088 | 0.90088 | 48 | 8.9987 | 1.87 | 1.87 | 595.5776 | 0.90087 | 0 | 493.299 | 0 | 0 | 0 | 0.90087 | 0 | 0 | 493.299
8 | 28 | 11 | 4.6933 | 146.7433 | 151.4367 | 46.8533 | 10.0569 | 0 | 0 | 584.0489 | 0 | 151.4367 | 0 | 15.1361 | 0 | 0 | 0 | 151.4367 | 0 | 0
8 | 28 | 12 | 4.6767 | 172.5468 | 177.2235 | 47.0236 | 10.1343 | 0 | 0 | 578.7639 | 0 | 177.2235 | 0 | 17.7135 | 0 | 0 | 0 | 177.2235 | 0 | 0
8 | 28 | 13 | 2.4581 | 6.0267 | 8.4849 | 37.2808 | 10.2117 | 0 | 0 | 578.1655 | 0 | 8.4849 | 0 | 0.84807 | 0 | 0 | 0 | 8.4849 | 0 | 0
8 | 28 | 14 | 1.3655 | 0.092122 | 1.4577 | 13.3384 | 9.8762 | 23.6426 | 23.6426 | 578.9169 | 1.4577 | 0 | 824.4157 | 0 | 0 | 0 | 1.4577 | 0 | 0 | 824.4157
8 | 28 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 581.4955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 591.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 593.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 18 | 14.6873 | 0 | 14.6873 | 11 | 11.9236 | 0 | 0 | 592.1871 | 0 | 14.6873 | 0 | 1.468 | 0 | 0 | 0 | 14.6873 | 0 | 0
8 | 28 | 19 | 107.0842 | 0 | 107.0842 | 11 | 13.1107 | 0 | 0 | 574.2965 | 0 | 107.0842 | 0 | 10.7031 | 0 | 0 | 0 | 107.0842 | 0 | 0
8 | 28 | 20 | 87.4291 | 0 | 87.4291 | 11 | 12.6978 | 0 | 0 | 547.6132 | 0 | 87.4291 | 0 | 8.7386 | 0 | 0 | 0 | 87.4291 | 0 | 0
8 | 28 | 21 | 53.8431 | 0 | 53.8431 | 11 | 9.8762 | 873.3185 | 288 | 524.9157 | 17.7562 | 36.0869 | 9125.1888 | 3.6069 | 0 | 0 | 17.7562 | 36.0869 | 0 | 9125.1888
8 | 28 | 22 | 8.7931 | 0 | 8.7931 | 11 | 6.1771 | 4.7981 | 4.7981 | 508.0829 | 8.7931 | 0 | 4370.9218 | 0 | 0 | 0 | 8.7931 | 0 | 0 | 4370.9218
8 | 28 | 23 | 0.17219 | 0 | 0.17219 | 11 | 4.6373 | 0.067004 | 0.067004 | 499.0939 | 0.17219 | 0 | 84.045 | 0 | 0 | 0 | 0.17219 | 0 | 0 | 84.045
8 | 29 | 0 | 0.15988 | 0 | 0.15988 | 11 | 3.9577 | 0.055222 | 0.055222 | 496.1975 | 0.15988 | 0 | 77.5728 | 0 | 0 | 0 | 0.15988 | 0 | 0 | 77.5728
8 | 29 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 496.6124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 504.3699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 533.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 4 | 0.30331 | 0 | 0.30331 | 11 | 3.5878 | 0.098724 | 0.098724 | 542.9295 | 0.30331 | 0 | 161.3403 | 0 | 0 | 0 | 0.30331 | 0 | 0 | 161.3403
8 | 29 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 552.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 570.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 7 | 9.2433 | 26.9389 | 36.1823 | 38.5478 | 5.6008 | 17.1596 | 17.1596 | 588.578 | 36.1823 | 0 | 19901.3481 | 0 | 0 | 0 | 36.1823 | 0 | 0 | 19901.3481
8 | 29 | 8 | 2.3325 | 273.434 | 275.7665 | 47.687 | 6.5729 | 167.8249 | 167.8249 | 587.6649 | 275.7665 | 0 | 148907.8111 | 0 | 0 | 0 | 275.7665 | 0 | 0 | 148907.8111
8 | 29 | 9 | 0.38592 | 461.985 | 462.3709 | 47.9691 | 7.7084 | 420.517 | 288 | 583.0561 | 316.6646 | 145.7064 | 169443.0944 | 14.5634 | 0 | 0 | 316.6646 | 145.7064 | 0 | 169443.0944
8 | 29 | 10 | 0 | 54.8412 | 54.8412 | 48 | 8.9471 | 108.284 | 108.284 | 578.3595 | 54.8412 | 0 | 29085.569 | 0 | 0 | 0 | 54.8412 | 0 | 0 | 29085.569
8 | 29 | 11 | 0.0625 | 70.5517 | 70.6142 | 47.9673 | 9.5923 | 357.4211 | 288 | 576.8241 | 56.899 | 13.7152 | 30091.4098 | 1.3708 | 0 | 0 | 56.899 | 13.7152 | 0 | 30091.4098
8 | 29 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 576.9619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 576.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 578.649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 588.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 589.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 591.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 593.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 593.8012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 562.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 535.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 517.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 512.6749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 502.8307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 500.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 507.6929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 532.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 540.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 548.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 6 | 31.6081 | 0 | 31.6081 | 11 | 5.1793 | 13.6809 | 13.6809 | 562.2912 | 31.6081 | 0 | 17425.2747 | 0 | 0 | 0 | 31.6081 | 0 | 0 | 17425.2747
8 | 30 | 7 | 13.0121 | 0 | 13.0121 | 11 | 5.3599 | 5.851 | 5.851 | 567.4477 | 13.0121 | 0 | 7240.5309 | 0 | 0 | 0 | 13.0121 | 0 | 0 | 7240.5309
8 | 30 | 8 | 2.9682 | 0 | 2.9682 | 11 | 6.5729 | 1.8064 | 1.8064 | 570.9088 | 2.9682 | 0 | 1661.9404 | 0 | 0 | 0 | 2.9682 | 0 | 0 | 1661.9404
8 | 30 | 9 | 0.5432 | 0 | 0.5432 | 11 | 7.6912 | 0.49036 | 0.49036 | 577.8148 | 0.5432 | 0 | 307.8942 | 0 | 0 | 0 | 0.5432 | 0 | 0 | 307.8942
8 | 30 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 572.0567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 575.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 573.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 574.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 571.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 581.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 588.6953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 592.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 596.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 584.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 556.0108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 535.2032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 510.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 501.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 493.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 492.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 493.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 529.2494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 546.6573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 554.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 6 | 2.5967 | 0 | 2.5967 | 11 | 4.7319 | 1.0286 | 1.0286 | 564.3368 | 2.5967 | 0 | 1436.877 | 0 | 0 | 0 | 2.5967 | 0 | 0 | 1436.877
8 | 31 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 574.7114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 576.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 570.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 564.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 565.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 12 | 1.882 | 0 | 1.882 | 11 | 8.2847 | 2.2851 | 2.2851 | 564.2844 | 1.882 | 0 | 1041.255 | 0 | 0 | 0 | 1.882 | 0 | 0 | 1041.255
8 | 31 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 567.2749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 568.6603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 571.764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 576.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 585.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 586.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 574.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 545.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 523.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 514.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 23 | 4.5348 | 0 | 4.5348 | 11 | 4.5954 | 1.7509 | 1.7509 | 504.2114 | 4.5348 | 0 | 2236.6016 | 0 | 0 | 0 | 4.5348 | 0 | 0 | 2236.6016
9 | 1 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 490.4579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 486.9034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 495.5028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 524.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 539.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 554.6273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 565.6561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 570.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 8 | 43.6533 | 0 | 43.6533 | 11 | 7.2524 | 33.1256 | 33.1256 | 570.3464 | 43.6533 | 0 | 24417.3329 | 0 | 0 | 0 | 43.6533 | 0 | 0 | 24417.3329
9 | 1 | 9 | 0.79083 | 16.9881 | 17.7789 | 46.3542 | 7.6998 | 16.1092 | 16.1092 | 567.2505 | 17.7789 | 0 | 9260.961 | 0 | 0 | 0 | 17.7789 | 0 | 0 | 9260.961
9 | 1 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 563.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 562.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 12 | 23.4924 | 0 | 23.4924 | 11 | 8.2589 | 28.1028 | 28.1028 | 554.3688 | 23.4924 | 0 | 12765.0093 | 0 | 0 | 0 | 23.4924 | 0 | 0 | 12765.0093
9 | 1 | 13 | 38.5843 | 0 | 38.5843 | 11 | 8.5686 | 56.1084 | 56.1084 | 554.3376 | 38.5843 | 0 | 20964.2996 | 0 | 0 | 0 | 38.5843 | 0 | 0 | 20964.2996
9 | 1 | 14 | 40.9571 | 4.6317 | 45.5888 | 14.7591 | 8.6374 | 69.6304 | 69.6304 | 556.9129 | 45.5888 | 0 | 24716.146 | 0 | 0 | 0 | 45.5888 | 0 | 0 | 24716.146
9 | 1 | 15 | 14.2417 | 0.49638 | 14.738 | 12.2462 | 7.803 | 13.98 | 13.98 | 558.9947 | 14.738 | 0 | 8058.0025 | 0 | 0 | 0 | 14.738 | 0 | 0 | 8058.0025
9 | 1 | 16 | 0.47978 | 0 | 0.47978 | 11 | 7.6998 | 0.43472 | 0.43472 | 559.9767 | 0.47978 | 0 | 263.3869 | 0 | 0 | 0 | 0.47978 | 0 | 0 | 263.3869
9 | 1 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 562.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 558.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 537.1634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 504.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 21 | 1.8605 | 0 | 1.8605 | 11 | 5.9879 | 0.96739 | 0.96739 | 476.7255 | 1.8605 | 0 | 866.4937 | 0 | 0 | 0 | 1.8605 | 0 | 0 | 866.4937
9 | 1 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 466.2956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 460.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 456.2705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 456.0474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 463.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 482.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 487.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 493.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 512.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 523.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 8 | 1.25 | 21.031 | 22.281 | 45.9242 | 6.9944 | 15.4582 | 15.4582 | 526.9921 | 22.281 | 0 | 10718.6561 | 0 | 0 | 0 | 22.281 | 0 | 0 | 10718.6561
9 | 2 | 9 | 0.1275 | 25.8418 | 25.9693 | 47.8183 | 7.5707 | 22.2831 | 22.2831 | 524.872 | 25.9693 | 0 | 12388.7676 | 0 | 0 | 0 | 25.9693 | 0 | 0 | 12388.7676
9 | 2 | 10 | 1.5692 | 93.3748 | 94.9439 | 47.3885 | 7.4159 | 76.5948 | 76.5948 | 518.2911 | 94.9439 | 0 | 44709.3497 | 0 | 0 | 0 | 94.9439 | 0 | 0 | 44709.3497
9 | 2 | 11 | 0 | 113.0678 | 113.0678 | 48 | 7.5879 | 97.709 | 97.709 | 519.2528 | 113.0678 | 0 | 53283.5251 | 0 | 0 | 0 | 113.0678 | 0 | 0 | 53283.5251
9 | 2 | 12 | 0 | 51.8902 | 51.8902 | 48 | 8.3192 | 64.2912 | 64.2912 | 518.2112 | 51.8902 | 0 | 24399.351 | 0 | 0 | 0 | 51.8902 | 0 | 0 | 24399.351
9 | 2 | 13 | 0 | 6.4654 | 6.4654 | 48 | 8.6546 | 10.0008 | 10.0008 | 521.9436 | 6.4654 | 0 | 3064.2473 | 0 | 0 | 0 | 6.4654 | 0 | 0 | 3064.2473
9 | 2 | 14 | 0 | 38.1832 | 38.1832 | 48 | 8.9299 | 74.1861 | 74.1861 | 535.1632 | 38.1832 | 0 | 18601.4457 | 0 | 0 | 0 | 38.1832 | 0 | 0 | 18601.4457
9 | 2 | 15 | 0 | 14.7322 | 14.7322 | 48 | 8.8009 | 25.5557 | 25.5557 | 538.7708 | 14.7322 | 0 | 7230.1239 | 0 | 0 | 0 | 14.7322 | 0 | 0 | 7230.1239
9 | 2 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 521.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 529.755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 514.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 494.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 475.7839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 459.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 451.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 450.9333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 449.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 447.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 447.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 449.681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 446.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 453.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 466.6403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 480.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 8 | 0 | 0.11579 | 0.11579 | 48 | 5.1879 | 0.050207 | 0.050207 | 496.2454 | 0.11579 | 0 | 51.9031 | 0 | 0 | 0 | 0.11579 | 0 | 0 | 51.9031
9 | 3 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 507.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 500.3827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 498.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 500.3741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 503.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 510.6152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 522.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 520.087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 519.3841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 510.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 499.1121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 481.5059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 470.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 457.0869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 448.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 442.7518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 1 | 0.099123 | 0 | 0.099123 | 11 | 3.4588 | 0.031627 | 0.031627 | 443.6859 | 0.099123 | 0 | 42.889 | 0 | 0 | 0 | 0.099123 | 0 | 0 | 42.889
9 | 4 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 442.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 444.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 438.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 439.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 451.6306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 466.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 485.176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 498.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 10 | 0 | 0 | 0 | 0 | 8.9987 | 0 | 0 | 505.8421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 11 | 12.0775 | 0.19008 | 12.2676 | 11.5733 | 10.0569 | 0 | 0 | 515.2792 | 0 | 12.2676 | 0 | 1.2261 | 0 | 0 | 0 | 12.2676 | 0 | 0
9 | 4 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 524.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 524.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 527.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 525.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 519.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 513.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 502.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 482.9962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 458.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 441.9435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 429.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 427.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 427.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 425.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 428.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 427.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 433.9122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 435.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 449.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 7 | 16.9912 | 4.1142 | 21.1054 | 18.2126 | 5.6008 | 10.0093 | 10.0093 | 473.815 | 21.1054 | 0 | 9615.6878 | 0 | 0 | 0 | 21.1054 | 0 | 0 | 9615.6878
9 | 5 | 8 | 43.4731 | 182.9396 | 226.4127 | 40.8957 | 6.5729 | 137.7894 | 137.7894 | 499.7363 | 226.4127 | 0 | 103887.3199 | 0 | 0 | 0 | 226.4127 | 0 | 0 | 103887.3199
9 | 5 | 9 | 39.1759 | 15.4657 | 54.6416 | 21.4724 | 7.7084 | 49.6954 | 49.6954 | 520.8323 | 54.6416 | 0 | 27285.8255 | 0 | 0 | 0 | 54.6416 | 0 | 0 | 27285.8255
9 | 5 | 10 | 39.1299 | 371.771 | 410.9008 | 44.4765 | 8.9471 | 811.3232 | 288 | 531.5097 | 145.8598 | 265.041 | 71038.5588 | 26.4909 | 0 | 0 | 145.8598 | 265.041 | 0 | 71038.5588
9 | 5 | 11 | 8.8525 | 569.1481 | 578.0006 | 47.4333 | 9.5923 | 2925.6097 | 288 | 531.683 | 56.899 | 521.1016 | 27553.3048 | 52.0842 | 0 | 0 | 56.899 | 521.1016 | 0 | 27553.3048
9 | 5 | 12 | 39.8083 | 540.2462 | 580.0545 | 45.4607 | 10.2891 | 0 | 0 | 527.459 | 0 | 580.0545 | 0 | 57.9766 | 0 | 0 | 0 | 580.0545 | 0 | 0
9 | 5 | 13 | 36.2664 | 429.13 | 465.3964 | 45.1167 | 10.0827 | 0 | 0 | 533.26 | 0 | 465.3964 | 0 | 46.5165 | 0 | 0 | 0 | 465.3964 | 0 | 0
9 | 5 | 14 | 26.3483 | 360.3415 | 386.6898 | 45.4789 | 10.6934 | 0 | 0 | 533.5885 | 0 | 386.6898 | 0 | 38.6498 | 0 | 0 | 0 | 386.6898 | 0 | 0
9 | 5 | 15 | 16.0794 | 149.3043 | 165.3837 | 44.4027 | 11.6655 | 0 | 0 | 542.1457 | 0 | 165.3837 | 0 | 16.5301 | 0 | 0 | 0 | 165.3837 | 0 | 0
9 | 5 | 16 | 45.6505 | 5.74 | 51.3906 | 15.1327 | 12.3021 | 0 | 0 | 546.4324 | 0 | 51.3906 | 0 | 5.1365 | 0 | 0 | 0 | 51.3906 | 0 | 0
9 | 5 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 550.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 553.3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 525.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 502.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 478.7694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 462.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 455.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 450.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 452.1474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 458.4349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 482.5716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 490.2951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 506.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 532.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 547.4332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 8 | 37.4513 | 91.8542 | 129.3054 | 37.2835 | 6.5729 | 78.6922 | 78.6922 | 556.7198 | 129.3054 | 0 | 67165.9355 | 0 | 0 | 0 | 129.3054 | 0 | 0 | 67165.9355
9 | 6 | 9 | 27.8003 | 36.9642 | 64.7645 | 32.1177 | 7.6912 | 58.464 | 58.464 | 555.3546 | 64.7645 | 0 | 33887.1768 | 0 | 0 | 0 | 64.7645 | 0 | 0 | 33887.1768
9 | 6 | 10 | 17.2678 | 25.7169 | 42.9847 | 33.1364 | 8.4482 | 57.6718 | 57.6718 | 549.8714 | 42.9847 | 0 | 22211.7145 | 0 | 0 | 0 | 42.9847 | 0 | 0 | 22211.7145
9 | 6 | 11 | 3.6064 | 2.6143 | 6.2207 | 26.5494 | 9.7214 | 45.812 | 45.812 | 545.2881 | 6.2207 | 0 | 3226.9168 | 0 | 0 | 0 | 6.2207 | 0 | 0 | 3226.9168
9 | 6 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 543.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 542.8137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 14 | 16.3579 | 0 | 16.3579 | 11 | 9.3428 | 51.6016 | 51.6016 | 541.6126 | 16.3579 | 0 | 8679.723 | 0 | 0 | 0 | 16.3579 | 0 | 0 | 8679.723
9 | 6 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 546.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 554.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 565.1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 561.3615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 555.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 548.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 527.7757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 505.0836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 496.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 484.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 479.0369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 489.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 525.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 535.2965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 541.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 556.6885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 565.1615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 569.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 9 | 0.80258 | 0 | 0.80258 | 11 | 6.9858 | 0.55523 | 0.55523 | 568.4131 | 0.80258 | 0 | 447.3687 | 0 | 0 | 0 | 0.80258 | 0 | 0 | 447.3687
9 | 7 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 564.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 557.2362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 551.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 552.8507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 555.5169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 560.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 563.5858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 566.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 568.8591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 564.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 554.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 538.4631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 522.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 501.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 492.5185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 494.2947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 503.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 542.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 552.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 556.7677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 559.4901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 577.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 8 | 0 | 0.021625 | 0.021625 | 48 | 7.2524 | 0.01641 | 0.01641 | 569.2932 | 0.021625 | 0 | 11.273 | 0 | 0 | 0 | 0.021625 | 0 | 0 | 11.273
9 | 8 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 570.4592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 10 | 1.1574 | 0 | 1.1574 | 11 | 7.8632 | 1.1287 | 1.1287 | 575.6506 | 1.1574 | 0 | 653.5351 | 0 | 0 | 0 | 1.1574 | 0 | 0 | 653.5351
9 | 8 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 575.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 574.7596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 13 | 0.65432 | 0 | 0.65432 | 11 | 8.5686 | 0.95149 | 0.95149 | 572.6934 | 0.65432 | 0 | 367.5261 | 0 | 0 | 0 | 0.65432 | 0 | 0 | 367.5261
9 | 8 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 573.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 15 | 7.7661 | 0 | 7.7661 | 11 | 7.803 | 7.3667 | 7.3667 | 578.3201 | 7.7661 | 0 | 4405.8822 | 0 | 0 | 0 | 7.7661 | 0 | 0 | 4405.8822
9 | 8 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 584.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 584.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 584.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 583.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 570.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 547.6939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 535.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 0 | 20.7167 | 0 | 20.7167 | 11 | 3.9749 | 7.1759 | 7.1759 | 524.0983 | 20.7167 | 0 | 10629.6855 | 0 | 0 | 0 | 20.7167 | 0 | 0 | 10629.6855
9 | 9 | 1 | 124.9414 | 0 | 124.9414 | 11 | 3.7598 | 41.7872 | 41.7872 | 524.1086 | 124.9414 | 0 | 64108.5247 | 0 | 0 | 0 | 124.9414 | 0 | 0 | 64108.5247
9 | 9 | 2 | 129.6089 | 0 | 129.6089 | 11 | 3.691 | 42.8757 | 42.8757 | 539.6709 | 129.6089 | 0 | 68520.4561 | 0 | 0 | 0 | 129.6089 | 0 | 0 | 68520.4561
9 | 9 | 3 | 0.031615 | 0 | 0.031615 | 11 | 3.6824 | 0.010444 | 0.010444 | 562.1587 | 0.031615 | 0 | 17.4248 | 0 | 0 | 0 | 0.031615 | 0 | 0 | 17.4248
9 | 9 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 577.7335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 574.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 6 | 17.4136 | 0 | 17.4136 | 11 | 4.8007 | 6.9889 | 6.9889 | 579.1439 | 17.4136 | 0 | 9893.438 | 0 | 0 | 0 | 17.4136 | 0 | 0 | 9893.438
9 | 9 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 580.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 8 | 12.1661 | 0 | 12.1661 | 11 | 6.9944 | 8.4406 | 8.4406 | 576.6854 | 12.1661 | 0 | 6882.1805 | 0 | 0 | 0 | 12.1661 | 0 | 0 | 6882.1805
9 | 9 | 9 | 101.6978 | 0 | 101.6978 | 11 | 7.5707 | 87.2623 | 87.2623 | 568.3489 | 101.6978 | 0 | 56681.1482 | 0 | 0 | 0 | 101.6978 | 0 | 0 | 56681.1482
9 | 9 | 10 | 7.7129 | 0 | 7.7129 | 11 | 7.4159 | 6.2223 | 6.2223 | 573.3318 | 7.7129 | 0 | 4337.2143 | 0 | 0 | 0 | 7.7129 | 0 | 0 | 4337.2143
9 | 9 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 575.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 577.897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 579.6134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 580.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 586.8871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 586.3986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 586.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 586.726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 590.5267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 576.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 561.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 548.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 532.8269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 517.1737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 517.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 513.9487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 519.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 515.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 535.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 552.5124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 565.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 569.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 9 | 1.645 | 0 | 1.645 | 11 | 6.7449 | 1.0539 | 1.0539 | 556.3659 | 1.645 | 0 | 897.1269 | 0 | 0 | 0 | 1.645 | 0 | 0 | 897.1269
9 | 10 | 10 | 0.36667 | 0 | 0.36667 | 11 | 8.8783 | 0.67976 | 0.67976 | 553.4202 | 0.36667 | 0 | 198.8874 | 0 | 0 | 0 | 0.36667 | 0 | 0 | 198.8874
9 | 10 | 11 | 0.45128 | 0 | 0.45128 | 11 | 9.8676 | 6.8613 | 6.8613 | 551.708 | 0.45128 | 0 | 244.0121 | 0 | 0 | 0 | 0.45128 | 0 | 0 | 244.0121
9 | 10 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 549.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 545.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 543.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 557.1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 568.2551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 577.4215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 579.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 572.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 554.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 535.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 513.7735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 504.7132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 495.1931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 485.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 483.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 487.7845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 488.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 503.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 510.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 530.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 544.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 549.5645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 10 | 25.775 | 0 | 25.775 | 11 | 8.9987 | 53.5032 | 53.5032 | 556.6752 | 25.775 | 0 | 14064.752 | 0 | 0 | 0 | 25.775 | 0 | 0 | 14064.752
9 | 11 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 551.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 552.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 553.7106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 556.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 564.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 556.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 562.6842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 549.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 532.9625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 505.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 21 | 0.26229 | 0 | 0.26229 | 11 | 9.8762 | 4.2542 | 4.2542 | 480.6294 | 0.26229 | 0 | 123.177 | 0 | 0 | 0 | 0.26229 | 0 | 0 | 123.177
9 | 11 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 463.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 457.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 453.2526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 453.0687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 461.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 488.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 506.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 503.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 6 | 5.2893 | 0 | 5.2893 | 11 | 5.3513 | 2.374 | 2.374 | 515.163 | 5.2893 | 0 | 2666.6847 | 0 | 0 | 0 | 5.2893 | 0 | 0 | 2666.6847
9 | 12 | 7 | 3.5028 | 0 | 3.5028 | 11 | 5.6008 | 1.6612 | 1.6612 | 533.0978 | 3.5028 | 0 | 1828.8278 | 0 | 0 | 0 | 3.5028 | 0 | 0 | 1828.8278
9 | 12 | 8 | 17.3564 | 61.246 | 78.6025 | 39.8299 | 6.5729 | 47.8356 | 47.8356 | 544.5193 | 78.6025 | 0 | 39669.8296 | 0 | 0 | 0 | 78.6025 | 0 | 0 | 39669.8296
9 | 12 | 9 | 13.0525 | 262.8226 | 275.8751 | 46.2494 | 7.7084 | 250.9028 | 250.9028 | 546.3741 | 275.8751 | 0 | 137971.9641 | 0 | 0 | 0 | 275.8751 | 0 | 0 | 137971.9641
9 | 12 | 10 | 46.8675 | 163.9624 | 210.8299 | 39.7749 | 8.9471 | 416.2833 | 288 | 546.5024 | 145.8598 | 64.9701 | 73911.167 | 6.4938 | 0 | 0 | 145.8598 | 64.9701 | 0 | 73911.167
9 | 12 | 11 | 27.9984 | 1.3481 | 29.3465 | 12.6997 | 9.5923 | 148.5401 | 148.5401 | 546.7607 | 29.3465 | 0 | 15672.7963 | 0 | 0 | 0 | 29.3465 | 0 | 0 | 15672.7963
9 | 12 | 12 | 13.065 | 0 | 13.065 | 11 | 10.2891 | 0 | 0 | 543.8611 | 0 | 13.065 | 0 | 1.3058 | 0 | 0 | 0 | 13.065 | 0 | 0
9 | 12 | 13 | 54.2836 | 0 | 54.2836 | 11 | 10.0827 | 0 | 0 | 545.8789 | 0 | 54.2836 | 0 | 5.4257 | 0 | 0 | 0 | 54.2836 | 0 | 0
9 | 12 | 14 | 0.67901 | 0 | 0.67901 | 11 | 10.6934 | 0 | 0 | 549.4767 | 0 | 0.67901 | 0 | 0.067867 | 0 | 0 | 0 | 0.67901 | 0 | 0
9 | 12 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 554.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 554.3234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 562.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 553.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 531.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 498.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 472.8958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 458.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 456.7348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 452.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 456.8076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 465.7633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 3 | 6.3041 | 0 | 6.3041 | 11 | 3.4416 | 2.0062 | 2.0062 | 494.4676 | 6.3041 | 0 | 3047.8402 | 0 | 0 | 0 | 6.3041 | 0 | 0 | 3047.8402
9 | 13 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 507.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 507.4122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 523.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 542.6389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 8 | 0 | 0.032458 | 0.032458 | 48 | 6.5729 | 0.019753 | 0.019753 | 557.9085 | 0.032458 | 0 | 16.5508 | 0 | 0 | 0 | 0.032458 | 0 | 0 | 16.5508
9 | 13 | 9 | 71.4358 | 0 | 71.4358 | 11 | 7.6912 | 64.4863 | 64.4863 | 565.1126 | 71.4358 | 0 | 39583.4969 | 0 | 0 | 0 | 71.4358 | 0 | 0 | 39583.4969
9 | 13 | 10 | 71.5 | 0 | 71.5 | 11 | 8.4482 | 95.9302 | 95.9302 | 558.291 | 71.5 | 0 | 39131.3035 | 0 | 0 | 0 | 71.5 | 0 | 0 | 39131.3035
9 | 13 | 11 | 76.675 | 0 | 76.675 | 11 | 9.7214 | 564.6691 | 288 | 552.4319 | 39.1068 | 37.5682 | 21173.669 | 3.755 | 0 | 0 | 39.1068 | 37.5682 | 0 | 21173.669
9 | 13 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 550.1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 13 | 30.6994 | 0 | 30.6994 | 11 | 8.8869 | 57.3513 | 57.3513 | 547.8901 | 30.6994 | 0 | 16482.2168 | 0 | 0 | 0 | 30.6994 | 0 | 0 | 16482.2168
9 | 13 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 549.3313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 557.1335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 562.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 568.7073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 569.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 558.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 544.3516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 512.6619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 494.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 485.5796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 475.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 475.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 483.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 510.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 530.1564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 531.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 543.9171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 548.5195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 553.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 558.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 558.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 11 | 0 | 0.82032 | 0.82032 | 48 | 8.9643 | 1.6465 | 1.6465 | 554.3765 | 0.82032 | 0 | 415.3912 | 0 | 0 | 0 | 0.82032 | 0 | 0 | 415.3912
9 | 14 | 12 | 2.0284 | 0.82417 | 2.8526 | 21.69 | 8.2847 | 3.4636 | 3.4636 | 550.1369 | 2.8526 | 0 | 1507.4456 | 0 | 0 | 0 | 2.8526 | 0 | 0 | 1507.4456
9 | 14 | 13 | 63.0839 | 57.8267 | 120.9105 | 28.6956 | 7.8202 | 115.5945 | 115.5945 | 550.9097 | 120.9105 | 0 | 63141.1745 | 0 | 0 | 0 | 120.9105 | 0 | 0 | 63141.1745
9 | 14 | 14 | 103.2939 | 31.0014 | 134.2953 | 19.5413 | 7.6568 | 119.4542 | 119.4542 | 554.2533 | 134.2953 | 0 | 71809.3034 | 0 | 0 | 0 | 134.2953 | 0 | 0 | 71809.3034
9 | 14 | 15 | 73.3889 | 23.1667 | 96.5556 | 19.8775 | 7.7256 | 88.4782 | 88.4782 | 557.3599 | 96.5556 | 0 | 51896.9312 | 0 | 0 | 0 | 96.5556 | 0 | 0 | 51896.9312
9 | 14 | 16 | 60.0069 | 76.1414 | 136.1483 | 31.6924 | 7.3729 | 108.0411 | 108.0411 | 560.5281 | 136.1483 | 0 | 72000.1003 | 0 | 0 | 0 | 136.1483 | 0 | 0 | 72000.1003
9 | 14 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 564.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 569.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 556.3677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 531.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 505.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 484.3925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 476.7266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 470.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 468.8044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 471.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 508.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 521.7509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 521.1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 528.4435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 536.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 541.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 9 | 2.51 | 84.8644 | 87.3744 | 46.9371 | 7.6998 | 79.1687 | 79.1687 | 541.1607 | 87.3744 | 0 | 43182.5034 | 0 | 0 | 0 | 87.3744 | 0 | 0 | 43182.5034
9 | 15 | 10 | 10.285 | 47.6641 | 57.9491 | 41.4331 | 7.8632 | 56.5139 | 56.5139 | 542.75 | 57.9491 | 0 | 29050.8689 | 0 | 0 | 0 | 57.9491 | 0 | 0 | 29050.8689
9 | 15 | 11 | 6.2842 | 213.8548 | 220.139 | 46.9438 | 7.6051 | 191.5997 | 191.5997 | 544.2345 | 220.139 | 0 | 109473.0778 | 0 | 0 | 0 | 220.139 | 0 | 0 | 109473.0778
9 | 15 | 12 | 1.5267 | 2.0682 | 3.5949 | 32.2869 | 8.2589 | 4.3004 | 4.3004 | 550.5167 | 3.5949 | 0 | 1862.9726 | 0 | 0 | 0 | 3.5949 | 0 | 0 | 1862.9726
9 | 15 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 552.1458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 551.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 15 | 0 | 0.27167 | 0.27167 | 48 | 7.803 | 0.25769 | 0.25769 | 557.9289 | 0.27167 | 0 | 138.5307 | 0 | 0 | 0 | 0.27167 | 0 | 0 | 138.5307
9 | 15 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 553.4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 558.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 545.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 518.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 493.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 463.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 451.2337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 448.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 444.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 443.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 454.7631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 484.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 508.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 514.3689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 522.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 531.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 544.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 9 | 2.8742 | 45.8494 | 48.7236 | 45.8174 | 7.5707 | 41.8075 | 41.8075 | 540.4976 | 48.7236 | 0 | 24102.6027 | 0 | 0 | 0 | 48.7236 | 0 | 0 | 24102.6027
9 | 16 | 10 | 10.9808 | 4.6734 | 15.6542 | 22.0459 | 7.4159 | 12.6288 | 12.6288 | 536.6247 | 15.6542 | 0 | 8055.3198 | 0 | 0 | 0 | 15.6542 | 0 | 0 | 8055.3198
9 | 16 | 11 | 12.7183 | 76.372 | 89.0903 | 42.718 | 7.5879 | 76.9885 | 76.9885 | 528.2208 | 89.0903 | 0 | 43253.5895 | 0 | 0 | 0 | 89.0903 | 0 | 0 | 43253.5895
9 | 16 | 12 | 1.3292 | 0.12583 | 1.455 | 14.1999 | 8.3192 | 1.8027 | 1.8027 | 520.625 | 1.455 | 0 | 736.8485 | 0 | 0 | 0 | 1.455 | 0 | 0 | 736.8485
9 | 16 | 13 | 5.1458 | 5.0316 | 10.1774 | 29.2923 | 8.6546 | 15.7426 | 15.7426 | 521.8606 | 10.1774 | 0 | 5013.0576 | 0 | 0 | 0 | 10.1774 | 0 | 0 | 5013.0576
9 | 16 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 526.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 531.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 541.2719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 546.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 539.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 536.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 526.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 505.5523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 489.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 483.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 476.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 469.9097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 469.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 480.3368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 485.1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 496.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 512.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 533.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 542.939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 548.2466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 543.4105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 542.6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 536.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 533.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 534.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 535.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 544.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 545.9951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 544.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 534.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 514.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 485.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 477.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 460.6835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 453.419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 449.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 453.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 461.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 471.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 485.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 509.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 533.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 8 | 6.4197 | 397.014 | 403.4337 | 47.4112 | 5.8502 | 202.8183 | 202.8183 | 549.8793 | 403.4337 | 0 | 202712.5202 | 0 | 0 | 0 | 403.4337 | 0 | 0 | 202712.5202
9 | 18 | 9 | 0.94667 | 822.5294 | 823.4761 | 47.9575 | 6.7707 | 531.8058 | 288 | 550.3838 | 445.9543 | 377.5218 | 224059.1962 | 37.7334 | 0 | 0 | 445.9543 | 377.5218 | 0 | 224059.1962
9 | 18 | 10 | 0.03 | 725.4362 | 725.4662 | 47.9985 | 8.9987 | 1505.9092 | 288 | 548.7191 | 138.7429 | 586.7233 | 69471.4476 | 58.6432 | 0 | 0 | 138.7429 | 586.7233 | 0 | 69471.4476
9 | 18 | 11 | 30.1372 | 726.0495 | 756.1868 | 46.5254 | 10.0569 | 0 | 0 | 540.9687 | 0 | 756.1868 | 0 | 75.5811 | 0 | 0 | 0 | 756.1868 | 0 | 0
9 | 18 | 12 | 10.9013 | 204.2925 | 215.1938 | 46.1257 | 10.1343 | 0 | 0 | 541.0511 | 0 | 215.1938 | 0 | 21.5087 | 0 | 0 | 0 | 215.1938 | 0 | 0
9 | 18 | 13 | 0.33833 | 1.7067 | 2.045 | 41.8786 | 10.2117 | 0 | 0 | 542.8817 | 0 | 2.045 | 0 | 0.2044 | 0 | 0 | 0 | 2.045 | 0 | 0
9 | 18 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 542.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 544.6394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 542.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 545.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 551.4009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 555.7732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 20 | 115.9275 | 0 | 115.9275 | 11 | 12.6978 | 0 | 0 | 548.0962 | 0 | 115.9275 | 0 | 11.587 | 0 | 0 | 0 | 115.9275 | 0 | 0
9 | 18 | 21 | 193.47 | 0 | 193.47 | 11 | 9.8762 | 3138.0234 | 288 | 533.4785 | 17.7562 | 175.7138 | 9277.2327 | 17.5626 | 0 | 0 | 17.7562 | 175.7138 | 0 | 9277.2327
9 | 18 | 22 | 204.5875 | 0 | 204.5875 | 11 | 6.1771 | 111.6358 | 111.6358 | 508.7305 | 204.5875 | 0 | 101829.4489 | 0 | 0 | 0 | 204.5875 | 0 | 0 | 101829.4489
9 | 18 | 23 | 183.3333 | 0 | 183.3333 | 11 | 4.6373 | 71.34 | 71.34 | 499.7049 | 183.3333 | 0 | 89595.8927 | 0 | 0 | 0 | 183.3333 | 0 | 0 | 89595.8927
9 | 19 | 0 | 176.1518 | 0 | 176.1518 | 11 | 3.9577 | 60.8423 | 60.8423 | 490.809 | 176.1518 | 0 | 84519.2356 | 0 | 0 | 0 | 176.1518 | 0 | 0 | 84519.2356
9 | 19 | 1 | 158.4836 | 0 | 158.4836 | 11 | 3.6394 | 52.0026 | 52.0026 | 486.7611 | 158.4836 | 0 | 75400.3166 | 0 | 0 | 0 | 158.4836 | 0 | 0 | 75400.3166
9 | 19 | 2 | 100.5303 | 0 | 100.5303 | 11 | 3.5276 | 32.4171 | 32.4171 | 508.7944 | 100.5303 | 0 | 50043.4269 | 0 | 0 | 0 | 100.5303 | 0 | 0 | 50043.4269
9 | 19 | 3 | 108.2406 | 0 | 108.2406 | 11 | 3.562 | 35.0898 | 35.0898 | 540.8311 | 108.2406 | 0 | 57349.2555 | 0 | 0 | 0 | 108.2406 | 0 | 0 | 57349.2555
9 | 19 | 4 | 49.2279 | 0 | 49.2279 | 11 | 3.5878 | 16.0231 | 16.0231 | 553.9991 | 49.2279 | 0 | 26730.7156 | 0 | 0 | 0 | 49.2279 | 0 | 0 | 26730.7156
9 | 19 | 5 | 173.9084 | 0 | 173.9084 | 11 | 4.1814 | 62.3744 | 62.3744 | 553.6255 | 173.9084 | 0 | 94367.144 | 0 | 0 | 0 | 173.9084 | 0 | 0 | 94367.144
9 | 19 | 6 | 79.3812 | 0 | 79.3812 | 11 | 5.3513 | 35.6287 | 35.6287 | 554.3891 | 79.3812 | 0 | 43134.8733 | 0 | 0 | 0 | 79.3812 | 0 | 0 | 43134.8733
9 | 19 | 7 | 0 | 15.526 | 15.526 | 48 | 5.6008 | 7.3633 | 7.3633 | 558.7681 | 15.526 | 0 | 7930.2057 | 0 | 0 | 0 | 15.526 | 0 | 0 | 7930.2057
9 | 19 | 8 | 2.2858 | 775.8206 | 778.1065 | 47.8913 | 6.5729 | 473.5371 | 288 | 560.5198 | 473.2357 | 304.8708 | 242594.0778 | 30.4719 | 0 | 0 | 473.2357 | 304.8708 | 0 | 242594.0778
9 | 19 | 9 | 0.83667 | 812.4571 | 813.2938 | 47.9619 | 7.7084 | 739.6742 | 288 | 553.6699 | 316.6646 | 496.6292 | 160139.8185 | 49.6382 | 0 | 0 | 316.6646 | 496.6292 | 0 | 160139.8185
9 | 19 | 10 | 8.628 | 701.6752 | 710.3032 | 47.5506 | 8.9471 | 1402.4929 | 288 | 549.0111 | 145.8598 | 564.4434 | 73142.935 | 56.4163 | 0 | 0 | 145.8598 | 564.4434 | 0 | 73142.935
9 | 19 | 11 | 20.3026 | 280.6493 | 300.952 | 45.5039 | 9.5923 | 1523.2995 | 288 | 548.1433 | 56.899 | 244.053 | 28599.6588 | 24.3932 | 0 | 0 | 56.899 | 244.053 | 0 | 28599.6588
9 | 19 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 543.8819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 546.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 547.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 552.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 16 | 0.0066101 | 0 | 0.0066101 | 11 | 12.3021 | 0 | 0 | 548.1201 | 0 | 0.0066101 | 0 | 0.00066068 | 0 | 0 | 0 | 0.0066101 | 0 | 0
9 | 19 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 558.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 561.7584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 555.366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 20 | 73.1302 | 0 | 73.1302 | 11 | 12.6806 | 0 | 0 | 533.329 | 0 | 73.1302 | 0 | 7.3094 | 0 | 0 | 0 | 73.1302 | 0 | 0
9 | 19 | 21 | 61.0901 | 0 | 61.0901 | 11 | 10.3235 | 0 | 0 | 507.1446 | 0 | 61.0901 | 0 | 6.106 | 0 | 0 | 0 | 61.0901 | 0 | 0
9 | 19 | 22 | 81.569 | 0 | 81.569 | 11 | 5.6868 | 39.4551 | 39.4551 | 485.81 | 81.569 | 0 | 38729.7874 | 0 | 0 | 0 | 81.569 | 0 | 0 | 38729.7874
9 | 19 | 23 | 3.648 | 0 | 3.648 | 11 | 4.5734 | 1.4029 | 1.4029 | 483.8829 | 3.648 | 0 | 1725.0965 | 0 | 0 | 0 | 3.648 | 0 | 0 | 1725.0965
9 | 20 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 479.4393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 482.841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 501.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 539.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 4 | 0.1927 | 0 | 0.1927 | 11 | 3.6222 | 0.063059 | 0.063059 | 555.6301 | 0.1927 | 0 | 104.9486 | 0 | 0 | 0 | 0.1927 | 0 | 0 | 104.9486
9 | 20 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 555.2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 6 | 11.3482 | 0 | 11.3482 | 11 | 5.1793 | 4.9118 | 4.9118 | 564.1689 | 11.3482 | 0 | 6277.4571 | 0 | 0 | 0 | 11.3482 | 0 | 0 | 6277.4571
9 | 20 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 570.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 8 | 3.2823 | 23.9692 | 27.2515 | 43.5435 | 6.5729 | 16.5846 | 16.5846 | 571.6229 | 27.2515 | 0 | 14390.9697 | 0 | 0 | 0 | 27.2515 | 0 | 0 | 14390.9697
9 | 20 | 9 | 0 | 104.683 | 104.683 | 48 | 7.6912 | 94.4991 | 94.4991 | 569.662 | 104.683 | 0 | 54609.1379 | 0 | 0 | 0 | 104.683 | 0 | 0 | 54609.1379
9 | 20 | 10 | 0 | 128.0277 | 128.0277 | 48 | 8.4482 | 171.7723 | 171.7723 | 563.0111 | 128.0277 | 0 | 65935.6825 | 0 | 0 | 0 | 128.0277 | 0 | 0 | 65935.6825
9 | 20 | 11 | 7.7551 | 111.3408 | 119.0959 | 45.5907 | 9.7214 | 877.0757 | 288 | 565.6407 | 39.1068 | 79.9891 | 20337.4918 | 7.9949 | 0 | 0 | 39.1068 | 79.9891 | 0 | 20337.4918
9 | 20 | 12 | 0 | 124.5271 | 124.5271 | 48 | 9.4117 | 438.3898 | 288 | 568.8635 | 81.808 | 42.7191 | 42610.8011 | 4.2698 | 0 | 0 | 81.808 | 42.7191 | 0 | 42610.8011
9 | 20 | 13 | 0.65927 | 88.7995 | 89.4588 | 47.7273 | 8.8869 | 167.1228 | 167.1228 | 574.72 | 89.4588 | 0 | 47144.1099 | 0 | 0 | 0 | 89.4588 | 0 | 0 | 47144.1099
9 | 20 | 14 | 0.85673 | 15.3374 | 16.1941 | 46.0426 | 9.3428 | 51.085 | 51.085 | 574.5388 | 16.1941 | 0 | 8558.541 | 0 | 0 | 0 | 16.1941 | 0 | 0 | 8558.541
9 | 20 | 15 | 0 | 53.1656 | 53.1656 | 48 | 10.0224 | 0 | 0 | 574.6237 | 0 | 53.1656 | 0 | 5.3139 | 0 | 0 | 0 | 53.1656 | 0 | 0
9 | 20 | 16 | 0 | 11.6142 | 11.6142 | 48 | 11.4074 | 0 | 0 | 564.8385 | 0 | 11.6142 | 0 | 1.1608 | 0 | 0 | 0 | 11.6142 | 0 | 0
9 | 20 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 571.8366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 568.6685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 567.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 551.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 518.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 497.5896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 485.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 479.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 477.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 495.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 527.7344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 549.0703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 548.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 553.5814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 7 | 0.091667 | 0 | 0.091667 | 11 | 4.99 | 0.038179 | 0.038179 | 555.3511 | 0.091667 | 0 | 49.8989 | 0 | 0 | 0 | 0.091667 | 0 | 0 | 49.8989
9 | 21 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 568.3401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 567.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 565.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 558.9275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 557.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 562.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 559.8877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 565.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 567.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 574.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 577.2956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 565.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 551.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 521.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 498.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 489.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 482.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 480.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 495.7324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 527.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 548.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 552.416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 563.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 578.8292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 582.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 581.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 577.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 11 | 8.241 | 0 | 8.241 | 11 | 7.6051 | 7.1726 | 7.1726 | 565.682 | 8.241 | 0 | 4571.1164 | 0 | 0 | 0 | 8.241 | 0 | 0 | 4571.1164
9 | 22 | 12 | 110.9298 | 0.0087083 | 110.9385 | 11.0029 | 8.2589 | 132.7107 | 132.7107 | 566.7121 | 110.9385 | 0 | 61649.5318 | 0 | 0 | 0 | 110.9385 | 0 | 0 | 61649.5318
9 | 22 | 13 | 161.0376 | 0.118 | 161.1556 | 11.0271 | 8.5686 | 234.3488 | 234.3488 | 566.0365 | 161.1556 | 0 | 89442.8772 | 0 | 0 | 0 | 161.1556 | 0 | 0 | 89442.8772
9 | 22 | 14 | 62.25 | 0.12225 | 62.3722 | 11.0725 | 8.6374 | 95.2647 | 95.2647 | 564.0903 | 62.3722 | 0 | 34492.9575 | 0 | 0 | 0 | 62.3722 | 0 | 0 | 34492.9575
9 | 22 | 15 | 0.083333 | 0 | 0.083333 | 11 | 7.803 | 0.079047 | 0.079047 | 570.8665 | 0.083333 | 0 | 46.6555 | 0 | 0 | 0 | 0.083333 | 0 | 0 | 46.6555
9 | 22 | 16 | 0.61667 | 0 | 0.61667 | 11 | 7.6998 | 0.55875 | 0.55875 | 567.6469 | 0.61667 | 0 | 343.2656 | 0 | 0 | 0 | 0.61667 | 0 | 0 | 343.2656
9 | 22 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 581.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 580.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 575.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 568.6281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 21 | 0.083179 | 0 | 0.083179 | 11 | 5.9879 | 0.04325 | 0.04325 | 534.7378 | 0.083179 | 0 | 43.5642 | 0 | 0 | 0 | 0.083179 | 0 | 0 | 43.5642
9 | 22 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 504.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 494.2294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 482.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 483.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 2 | 0.87639 | 0 | 0.87639 | 11 | 3.691 | 0.28992 | 0.28992 | 495.1633 | 0.87639 | 0 | 424.314 | 0 | 0 | 0 | 0.87639 | 0 | 0 | 424.314
9 | 23 | 3 | 1.6831 | 0 | 1.6831 | 11 | 3.6824 | 0.55602 | 0.55602 | 531.9367 | 1.6831 | 0 | 876.7799 | 0 | 0 | 0 | 1.6831 | 0 | 0 | 876.7799
9 | 23 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 549.3502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 553.7127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 562.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 572.6014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 575.0736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 9 | 4.9552 | 10.0201 | 14.9753 | 35.757 | 7.5707 | 12.8496 | 12.8496 | 570.2632 | 14.9753 | 0 | 8004.3876 | 0 | 0 | 0 | 14.9753 | 0 | 0 | 8004.3876
9 | 23 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 561.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 11 | 93.2918 | 219.7406 | 313.0324 | 36.973 | 7.5879 | 270.5109 | 270.5109 | 561.7824 | 313.0324 | 0 | 164282.3562 | 0 | 0 | 0 | 313.0324 | 0 | 0 | 164282.3562
9 | 23 | 12 | 54.0546 | 219.0269 | 273.0815 | 40.6761 | 8.3192 | 338.3438 | 288 | 558.6358 | 232.4483 | 40.6331 | 120398.878 | 4.0613 | 0 | 0 | 232.4483 | 40.6331 | 0 | 120398.878
9 | 23 | 13 | 138.3839 | 171.6184 | 310.0023 | 31.4833 | 8.6546 | 479.5171 | 288 | 558.4835 | 186.1887 | 123.8136 | 98121.4779 | 12.3752 | 0 | 0 | 186.1887 | 123.8136 | 0 | 98121.4779
9 | 23 | 14 | 73.6034 | 71.1563 | 144.7598 | 29.1873 | 8.9299 | 281.2536 | 281.2536 | 561.5239 | 144.7598 | 0 | 77060.9285 | 0 | 0 | 0 | 144.7598 | 0 | 0 | 77060.9285
9 | 23 | 15 | 0.79653 | 0 | 0.79653 | 11 | 8.8009 | 1.3817 | 1.3817 | 564.4774 | 0.79653 | 0 | 440.8624 | 0 | 0 | 0 | 0.79653 | 0 | 0 | 440.8624
9 | 23 | 16 | 6.4751 | 40.0958 | 46.5709 | 42.8556 | 9.5837 | 230.9099 | 230.9099 | 558.2265 | 46.5709 | 0 | 24001.2994 | 0 | 0 | 0 | 46.5709 | 0 | 0 | 24001.2994
9 | 23 | 17 | 1.5331 | 11.0425 | 12.5756 | 43.4892 | 9.0762 | 28.2803 | 28.2803 | 566.0213 | 12.5756 | 0 | 6571.1794 | 0 | 0 | 0 | 12.5756 | 0 | 0 | 6571.1794
9 | 23 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 570.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 567.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 561.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 21 | 12.3499 | 0 | 12.3499 | 11 | 9.1708 | 30.9232 | 30.9232 | 541.9726 | 12.3499 | 0 | 6557.484 | 0 | 0 | 0 | 12.3499 | 0 | 0 | 6557.484
9 | 23 | 22 | 144.224 | 0 | 144.224 | 11 | 5.4717 | 66.4518 | 66.4518 | 531.1847 | 144.224 | 0 | 75023.115 | 0 | 0 | 0 | 144.224 | 0 | 0 | 75023.115
9 | 23 | 23 | 46.6132 | 0 | 46.6132 | 11 | 4.8093 | 18.7391 | 18.7391 | 511.3179 | 46.6132 | 0 | 23321.4264 | 0 | 0 | 0 | 46.6132 | 0 | 0 | 23321.4264
9 | 24 | 0 | 29.7971 | 0 | 29.7971 | 11 | 3.3125 | 9.2996 | 9.2996 | 495.4416 | 29.7971 | 0 | 14434.939 | 0 | 0 | 0 | 29.7971 | 0 | 0 | 14434.939
9 | 24 | 1 | 1.3777 | 0 | 1.3777 | 11 | 3.2007 | 0.42291 | 0.42291 | 483.7406 | 1.3777 | 0 | 651.2867 | 0 | 0 | 0 | 1.3777 | 0 | 0 | 651.2867
9 | 24 | 2 | 23.0587 | 0 | 23.0587 | 11 | 3.1921 | 7.0694 | 7.0694 | 483.8238 | 23.0587 | 0 | 10902.7085 | 0 | 0 | 0 | 23.0587 | 0 | 0 | 10902.7085
9 | 24 | 3 | 17.95 | 0 | 17.95 | 11 | 3.3297 | 5.6166 | 5.6166 | 498.0606 | 17.95 | 0 | 8742.7355 | 0 | 0 | 0 | 17.95 | 0 | 0 | 8742.7355
9 | 24 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 508.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 514.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 522.5752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 535.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 8 | 0.53167 | 15.2153 | 15.7469 | 46.7508 | 5.1879 | 6.8279 | 6.8279 | 542.5785 | 15.7469 | 0 | 7807.7647 | 0 | 0 | 0 | 15.7469 | 0 | 0 | 7807.7647
9 | 24 | 9 | 47.5992 | 218.8367 | 266.4359 | 41.3899 | 6.7449 | 170.7038 | 170.7038 | 544.1983 | 266.4359 | 0 | 133966.2061 | 0 | 0 | 0 | 266.4359 | 0 | 0 | 133966.2061
9 | 24 | 10 | 29.7908 | 266.8182 | 296.609 | 44.2838 | 8.8783 | 549.8808 | 288 | 530.6064 | 155.349 | 141.2601 | 75549.7048 | 14.119 | 0 | 0 | 155.349 | 141.2601 | 0 | 75549.7048
9 | 24 | 11 | 84.8708 | 209.9201 | 294.7909 | 37.3476 | 9.8676 | 4482.0101 | 288 | 529.0247 | 18.9423 | 275.8486 | 9313.5166 | 27.5711 | 0 | 0 | 18.9423 | 275.8486 | 0 | 9313.5166
9 | 24 | 12 | 21.1459 | 51.0016 | 72.1475 | 37.1556 | 10.2547 | 0 | 0 | 527.1965 | 0 | 72.1475 | 0 | 7.2112 | 0 | 0 | 0 | 72.1475 | 0 | 0
9 | 24 | 13 | 162.0166 | 103.0599 | 265.0765 | 25.3853 | 10.031 | 0 | 0 | 527.6861 | 0 | 265.0765 | 0 | 26.4945 | 0 | 0 | 0 | 265.0765 | 0 | 0
9 | 24 | 14 | 153.1962 | 473.3669 | 626.5631 | 38.9534 | 9.9364 | 19088.816 | 288 | 527.1965 | 9.4532 | 617.1099 | 4615.4536 | 61.6803 | 0 | 0 | 9.4532 | 617.1099 | 0 | 4615.4536
9 | 24 | 15 | 115.4486 | 263.6813 | 379.1299 | 36.7332 | 11.1494 | 0 | 0 | 528.6414 | 0 | 379.1299 | 0 | 37.8941 | 0 | 0 | 0 | 379.1299 | 0 | 0
9 | 24 | 16 | 85.106 | 197.9911 | 283.0971 | 36.8769 | 12.5086 | 0 | 0 | 529.4475 | 0 | 283.0971 | 0 | 28.2956 | 0 | 0 | 0 | 283.0971 | 0 | 0
9 | 24 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 530.9849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 530.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 19 | 95.0732 | 0 | 95.0732 | 11 | 12.7322 | 0 | 0 | 509.8891 | 0 | 95.0732 | 0 | 9.5026 | 0 | 0 | 0 | 95.0732 | 0 | 0
9 | 24 | 20 | 94.1407 | 0 | 94.1407 | 11 | 13.3172 | 0 | 0 | 500.9149 | 0 | 94.1407 | 0 | 9.4094 | 0 | 0 | 0 | 94.1407 | 0 | 0
9 | 24 | 21 | 41.9947 | 0 | 41.9947 | 11 | 9.2568 | 117.2416 | 117.2416 | 480.6097 | 41.9947 | 0 | 19721.1225 | 0 | 0 | 0 | 41.9947 | 0 | 0 | 19721.1225
9 | 24 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 456.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 449.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 441.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 435.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 436.4568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 442.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 443.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 451.8913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 471.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 482.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 8 | 0.016667 | 228.3187 | 228.3353 | 47.9973 | 5.8502 | 114.7911 | 114.7911 | 502.6908 | 228.3353 | 0 | 103822.5934 | 0 | 0 | 0 | 228.3353 | 0 | 0 | 103822.5934
9 | 25 | 9 | 56.225 | 467.4155 | 523.6406 | 44.0272 | 6.7707 | 338.1702 | 288 | 515.166 | 445.9543 | 77.6862 | 210106.3859 | 7.7648 | 0 | 0 | 445.9543 | 77.6862 | 0 | 210106.3859
9 | 25 | 10 | 2.4211 | 444.9311 | 447.3523 | 47.7998 | 8.9987 | 928.6055 | 288 | 524.4146 | 138.7429 | 308.6093 | 66126.9424 | 30.8456 | 0 | 0 | 138.7429 | 308.6093 | 0 | 66126.9424
9 | 25 | 11 | 1.1658 | 300.9222 | 302.088 | 47.8572 | 10.0569 | 0 | 0 | 531.4696 | 0 | 302.088 | 0 | 30.1938 | 0 | 0 | 0 | 302.088 | 0 | 0
9 | 25 | 12 | 0.76583 | 120.9448 | 121.7106 | 47.7672 | 10.1343 | 0 | 0 | 534.1457 | 0 | 121.7106 | 0 | 12.165 | 0 | 0 | 0 | 121.7106 | 0 | 0
9 | 25 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 530.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 530.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 15 | 0 | 0.26696 | 0.26696 | 48 | 10.9601 | 0 | 0 | 527.2293 | 0 | 0.26696 | 0 | 0.026683 | 0 | 0 | 0 | 0.26696 | 0 | 0
9 | 25 | 16 | 15.9854 | 0.77775 | 16.7632 | 12.7167 | 11.5279 | 0 | 0 | 517.94 | 0 | 16.7632 | 0 | 1.6755 | 0 | 0 | 0 | 16.7632 | 0 | 0
9 | 25 | 17 | 2.3586 | 0.050792 | 2.4094 | 11.78 | 11.5451 | 0 | 0 | 529.6513 | 0 | 2.4094 | 0 | 0.24082 | 0 | 0 | 0 | 2.4094 | 0 | 0
9 | 25 | 18 | 0 | 0.89713 | 0.89713 | 48 | 11.9236 | 0 | 0 | 543.3473 | 0 | 0.89713 | 0 | 0.089668 | 0 | 0 | 0 | 0.89713 | 0 | 0
9 | 25 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 526.9634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 506.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 482.2662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 462.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 451.3664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 450.5984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 455.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 479.8797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 509.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 530.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 530.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 523.0236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 7 | 1.6155 | 1.4 | 3.0155 | 28.178 | 5.6008 | 1.4301 | 1.4301 | 526.1823 | 3.0155 | 0 | 1501.725 | 0 | 0 | 0 | 3.0155 | 0 | 0 | 1501.725
9 | 26 | 8 | 26.6967 | 764.7512 | 791.4479 | 46.7519 | 6.5729 | 481.6564 | 288 | 524.0184 | 473.2357 | 318.2122 | 225859.5295 | 31.8054 | 0 | 0 | 473.2357 | 318.2122 | 0 | 225859.5295
9 | 26 | 9 | 27.4597 | 1015.9522 | 1043.4119 | 47.0263 | 7.7084 | 948.9619 | 288 | 515.7856 | 316.6646 | 726.7473 | 148439.4821 | 72.6386 | 0 | 0 | 316.6646 | 726.7473 | 0 | 148439.4821
9 | 26 | 10 | 40.0017 | 702.1362 | 742.1379 | 46.0057 | 8.9471 | 1465.3504 | 288 | 512.165 | 145.8598 | 596.2781 | 67993.9008 | 59.5982 | 0 | 0 | 145.8598 | 596.2781 | 0 | 67993.9008
9 | 26 | 11 | 46.8383 | 373.7066 | 420.5449 | 43.8791 | 9.5923 | 2128.6318 | 288 | 509.6128 | 56.899 | 363.646 | 26499.7653 | 36.3465 | 0 | 0 | 56.899 | 363.646 | 0 | 26499.7653
9 | 26 | 12 | 10.7216 | 64.6227 | 75.3443 | 42.7349 | 10.2891 | 0 | 0 | 498.2562 | 0 | 75.3443 | 0 | 7.5307 | 0 | 0 | 0 | 75.3443 | 0 | 0
9 | 26 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 491.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 492.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 15 | 0.27333 | 0.59625 | 0.86958 | 36.3699 | 11.6655 | 0 | 0 | 498.4661 | 0 | 0.86958 | 0 | 0.086915 | 0 | 0 | 0 | 0.86958 | 0 | 0
9 | 26 | 16 | 0 | 1.8416 | 1.8416 | 48 | 12.3021 | 0 | 0 | 512.9649 | 0 | 1.8416 | 0 | 0.18407 | 0 | 0 | 0 | 1.8416 | 0 | 0
9 | 26 | 17 | 0 | 2.0251 | 2.0251 | 48 | 12.1989 | 0 | 0 | 529.3781 | 0 | 2.0251 | 0 | 0.20241 | 0 | 0 | 0 | 2.0251 | 0 | 0
9 | 26 | 18 | 0 | 1.1438 | 1.1438 | 48 | 12.9559 | 0 | 0 | 521.4429 | 0 | 1.1438 | 0 | 0.11433 | 0 | 0 | 0 | 1.1438 | 0 | 0
9 | 26 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 506.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 478.7637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 451.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 436.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 434.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 431.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 429.4612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 448.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 479.5951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 509.6817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 506.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 519.6544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 530.7707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 524.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 509.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 10 | 3.4025 | 406.8711 | 410.2736 | 47.6931 | 8.4482 | 550.4561 | 288 | 502.6975 | 214.6562 | 195.6174 | 97669.4936 | 19.552 | 0 | 0 | 214.6562 | 195.6174 | 0 | 97669.4936
9 | 27 | 11 | 8.3875 | 225.0315 | 233.419 | 46.6705 | 9.7214 | 1719.002 | 288 | 502.462 | 39.1068 | 194.3122 | 17824.5473 | 19.4216 | 0 | 0 | 39.1068 | 194.3122 | 0 | 17824.5473
9 | 27 | 12 | 4.6292 | 332.0884 | 336.7176 | 47.4913 | 9.4117 | 1185.3935 | 288 | 504.2103 | 81.808 | 254.9096 | 37363.2649 | 25.4783 | 0 | 0 | 81.808 | 254.9096 | 0 | 37363.2649
9 | 27 | 13 | 1.9067 | 297.0049 | 298.9116 | 47.764 | 8.8869 | 558.4132 | 288 | 506.7719 | 154.1628 | 144.7488 | 70761.9485 | 14.4677 | 0 | 0 | 154.1628 | 144.7488 | 0 | 70761.9485
9 | 27 | 14 | 0.63917 | 173.0162 | 173.6553 | 47.8638 | 9.3428 | 547.8017 | 288 | 512.0254 | 91.2972 | 82.3582 | 42376.6349 | 8.2317 | 0 | 0 | 91.2972 | 82.3582 | 0 | 42376.6349
9 | 27 | 15 | 6.5842 | 229.182 | 235.7662 | 46.9667 | 10.0224 | 0 | 0 | 512.7402 | 0 | 235.7662 | 0 | 23.5649 | 0 | 0 | 0 | 235.7662 | 0 | 0
9 | 27 | 16 | 33.0149 | 52.564 | 85.5789 | 33.726 | 11.4074 | 0 | 0 | 514.0113 | 0 | 85.5789 | 0 | 8.5536 | 0 | 0 | 0 | 85.5789 | 0 | 0
9 | 27 | 17 | 0.96667 | 0.99904 | 1.9657 | 29.8047 | 10.8053 | 0 | 0 | 530.025 | 0 | 1.9657 | 0 | 0.19647 | 0 | 0 | 0 | 1.9657 | 0 | 0
9 | 27 | 18 | 0.18333 | 1.1278 | 1.3112 | 42.8265 | 11.5107 | 0 | 0 | 539.0894 | 0 | 1.3112 | 0 | 0.13105 | 0 | 0 | 0 | 1.3112 | 0 | 0
9 | 27 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 525.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 503.441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 477.0283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 22 | 0.4425 | 0 | 0.4425 | 11 | 5.575 | 0.20863 | 0.20863 | 462.8007 | 0.4425 | 0 | 199.9218 | 0 | 0 | 0 | 0.4425 | 0 | 0 | 199.9218
9 | 27 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 454.9162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 451.6718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 452.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 464.7241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 492.6275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 516.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 518.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 523.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 522.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 525.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 526.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 10 | 0 | 0.20139 | 0.20139 | 48 | 7.3471 | 0.15826 | 0.15826 | 518.3607 | 0.20139 | 0 | 94.7241 | 0 | 0 | 0 | 0.20139 | 0 | 0 | 94.7241
9 | 28 | 11 | 57.1876 | 13.2484 | 70.436 | 17.9594 | 8.9643 | 141.3752 | 141.3752 | 515.1325 | 70.436 | 0 | 35018.9083 | 0 | 0 | 0 | 70.436 | 0 | 0 | 35018.9083
9 | 28 | 12 | 21.599 | 55.6736 | 77.2726 | 37.6579 | 8.2847 | 93.8245 | 93.8245 | 518.7842 | 77.2726 | 0 | 37177.8664 | 0 | 0 | 0 | 77.2726 | 0 | 0 | 37177.8664
9 | 28 | 13 | 4.7761 | 216.8885 | 221.6646 | 47.2028 | 7.8202 | 211.9187 | 211.9187 | 510.7818 | 221.6646 | 0 | 102759.0556 | 0 | 0 | 0 | 221.6646 | 0 | 0 | 102759.0556
9 | 28 | 14 | 15.1314 | 240.7237 | 255.8551 | 45.8118 | 7.6568 | 227.5802 | 227.5802 | 507.3627 | 255.8551 | 0 | 118090.1508 | 0 | 0 | 0 | 255.8551 | 0 | 0 | 118090.1508
9 | 28 | 15 | 0 | 240.5452 | 240.5452 | 48 | 7.7256 | 220.4223 | 220.4223 | 508.3727 | 240.5452 | 0 | 110740.466 | 0 | 0 | 0 | 240.5452 | 0 | 0 | 110740.466
9 | 28 | 16 | 0 | 230.5714 | 230.5714 | 48 | 7.3729 | 182.9709 | 182.9709 | 515.8643 | 230.5714 | 0 | 107876.1316 | 0 | 0 | 0 | 230.5714 | 0 | 0 | 107876.1316
9 | 28 | 17 | 0 | 1.9979 | 1.9979 | 48 | 7.5449 | 1.6963 | 1.6963 | 515.8643 | 1.9979 | 0 | 934.7344 | 0 | 0 | 0 | 1.9979 | 0 | 0 | 934.7344
9 | 28 | 18 | 0 | 0.99946 | 0.99946 | 48 | 7.0804 | 0.7138 | 0.7138 | 515.8643 | 0.99946 | 0 | 467.6109 | 0 | 0 | 0 | 0.99946 | 0 | 0 | 467.6109
9 | 28 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 515.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 515.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 465.9802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 448.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 444.6241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 434.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 438.3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 457.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 481.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 505.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 511.2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 521.6572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 522.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 505.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 508.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 10 | 0 | 1.4229 | 1.4229 | 48 | 7.8632 | 1.3877 | 1.3877 | 504.5166 | 1.4229 | 0 | 649.5851 | 0 | 0 | 0 | 1.4229 | 0 | 0 | 649.5851
9 | 29 | 11 | 0 | 1.6137 | 1.6137 | 48 | 7.6051 | 1.4045 | 1.4045 | 509.254 | 1.6137 | 0 | 744.3102 | 0 | 0 | 0 | 1.6137 | 0 | 0 | 744.3102
9 | 29 | 12 | 0 | 0.66525 | 0.66525 | 48 | 8.2589 | 0.79581 | 0.79581 | 503.7495 | 0.66525 | 0 | 303.1874 | 0 | 0 | 0 | 0.66525 | 0 | 0 | 303.1874
9 | 29 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 497.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 14 | 1.9104 | 0 | 1.9104 | 11 | 8.6374 | 2.9178 | 2.9178 | 500.5521 | 1.9104 | 0 | 935.2284 | 0 | 0 | 0 | 1.9104 | 0 | 0 | 935.2284
9 | 29 | 15 | 0 | 0.37142 | 0.37142 | 48 | 7.803 | 0.35231 | 0.35231 | 497.9519 | 0.37142 | 0 | 167.1196 | 0 | 0 | 0 | 0.37142 | 0 | 0 | 167.1196
9 | 29 | 16 | 0 | 1.3302 | 1.3302 | 48 | 7.6998 | 1.2053 | 1.2053 | 486.3406 | 1.3302 | 0 | 583.0843 | 0 | 0 | 0 | 1.3302 | 0 | 0 | 583.0843
9 | 29 | 17 | 0 | 1.3112 | 1.3112 | 48 | 7.6482 | 1.162 | 1.162 | 505.1619 | 1.3112 | 0 | 599.4155 | 0 | 0 | 0 | 1.3112 | 0 | 0 | 599.4155
9 | 29 | 18 | 0 | 0.294 | 0.294 | 48 | 7.3041 | 0.22736 | 0.22736 | 513.3207 | 0.294 | 0 | 136.8043 | 0 | 0 | 0 | 0.294 | 0 | 0 | 136.8043
9 | 29 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 504.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 475.0229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 451.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 438.8275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 435.7856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 0 | 2.1448 | 0 | 2.1448 | 11 | 3.9749 | 0.7429 | 0.7429 | 429.2889 | 2.1448 | 0 | 897.1254 | 0 | 0 | 0 | 2.1448 | 0 | 0 | 897.1254
9 | 30 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 427.5218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 449.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 475.6502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 496.6019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 500.8132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 508.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 510.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 499.3491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 9 | 0.066667 | 1.5762 | 1.6428 | 46.4985 | 7.5707 | 1.4097 | 1.4097 | 500.4813 | 1.6428 | 0 | 745.8244 | 0 | 0 | 0 | 1.6428 | 0 | 0 | 745.8244
9 | 30 | 10 | 0.19 | 45.0599 | 45.2499 | 47.8446 | 7.4159 | 36.5048 | 36.5048 | 498.7954 | 45.2499 | 0 | 20405.471 | 0 | 0 | 0 | 45.2499 | 0 | 0 | 20405.471
9 | 30 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 498.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 12 | 0 | 0.75746 | 0.75746 | 48 | 8.3192 | 0.93848 | 0.93848 | 495.3983 | 0.75746 | 0 | 338.8856 | 0 | 0 | 0 | 0.75746 | 0 | 0 | 338.8856
9 | 30 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 488.6936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 486.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 15 | 60.7939 | 0.86913 | 61.663 | 11.5215 | 8.8009 | 106.966 | 106.966 | 481.0824 | 61.663 | 0 | 28954.5413 | 0 | 0 | 0 | 61.663 | 0 | 0 | 28954.5413
9 | 30 | 16 | 0 | 0.83217 | 0.83217 | 48 | 9.5837 | 4.1261 | 4.1261 | 473.2934 | 0.83217 | 0 | 353.915 | 0 | 0 | 0 | 0.83217 | 0 | 0 | 353.915
9 | 30 | 17 | 0 | 1.0883 | 1.0883 | 48 | 9.0762 | 2.4474 | 2.4474 | 491.0433 | 1.0883 | 0 | 482.1603 | 0 | 0 | 0 | 1.0883 | 0 | 0 | 482.1603
9 | 30 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 502.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 19 | 59.2037 | 0 | 59.2037 | 11 | 8.0611 | 63.6142 | 63.6142 | 493.762 | 59.2037 | 0 | 28581.3172 | 0 | 0 | 0 | 59.2037 | 0 | 0 | 28581.3172
9 | 30 | 20 | 57.6867 | 0 | 57.6867 | 11 | 11.2698 | 0 | 0 | 478.8342 | 0 | 57.6867 | 0 | 5.7658 | 0 | 0 | 0 | 57.6867 | 0 | 0
9 | 30 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 452.5329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 446.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 23 | 1.5947 | 0 | 1.5947 | 11 | 4.8093 | 0.64107 | 0.64107 | 448.2885 | 1.5947 | 0 | 697.327 | 0 | 0 | 0 | 1.5947 | 0 | 0 | 697.327
10 | 1 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 443.4427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 443.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 445.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 452.8964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 467.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 477.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 495.1187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 7 | 3.0017 | 0 | 3.0017 | 11 | 5.2137 | 1.3086 | 1.3086 | 507.3664 | 3.0017 | 0 | 1489.9546 | 0 | 0 | 0 | 3.0017 | 0 | 0 | 1489.9546
10 | 1 | 8 | 96.1741 | 21.6671 | 117.8412 | 17.8031 | 5.1879 | 51.0961 | 51.0961 | 507.4997 | 117.8412 | 0 | 57706.426 | 0 | 0 | 0 | 117.8412 | 0 | 0 | 57706.426
10 | 1 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 506.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 511.8338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 511.8732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 12 | 0 | 0.10987 | 0.10987 | 48 | 10.2547 | 0 | 0 | 511.8057 | 0 | 0.10987 | 0 | 0.010982 | 0 | 0 | 0 | 0.10987 | 0 | 0
10 | 1 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 508.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 506.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 15 | 0.25547 | 0.09125 | 0.34672 | 20.7377 | 11.1494 | 0 | 0 | 512.021 | 0 | 0.34672 | 0 | 0.034655 | 0 | 0 | 0 | 0.34672 | 0 | 0
10 | 1 | 16 | 1.1729 | 1.5077 | 2.6806 | 31.8109 | 12.5086 | 0 | 0 | 500.9753 | 0 | 2.6806 | 0 | 0.26793 | 0 | 0 | 0 | 2.6806 | 0 | 0
10 | 1 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 518.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 511.415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 502.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 483.9912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 468.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 447.6904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 444.9395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 0 | 1.2035 | 0 | 1.2035 | 11 | 3.5706 | 0.39066 | 0.39066 | 436.7491 | 1.2035 | 0 | 512.3733 | 0 | 0 | 0 | 1.2035 | 0 | 0 | 512.3733
10 | 2 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 429.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 2 | 0.82734 | 0 | 0.82734 | 11 | 3.3555 | 0.25988 | 0.25988 | 430.6982 | 0.82734 | 0 | 347.2349 | 0 | 0 | 0 | 0.82734 | 0 | 0 | 347.2349
10 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 436.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 438.9379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 447.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 468.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 484.6807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 8 | 0 | 5.3076 | 5.3076 | 48 | 5.8502 | 2.6683 | 2.6683 | 487.59 | 5.3076 | 0 | 2333.1775 | 0 | 0 | 0 | 5.3076 | 0 | 0 | 2333.1775
10 | 2 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 493.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 10 | 0 | 0.019125 | 0.019125 | 48 | 8.9987 | 0.039699 | 0.039699 | 500.0946 | 0.019125 | 0 | 8.6463 | 0 | 0 | 0 | 0.019125 | 0 | 0 | 8.6463
10 | 2 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 507.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 500.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 502.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 14 | 0.33764 | 0 | 0.33764 | 11 | 9.8762 | 5.4763 | 5.4763 | 508.4882 | 0.33764 | 0 | 167.9697 | 0 | 0 | 0 | 0.33764 | 0 | 0 | 167.9697
10 | 2 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 511.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 16 | 0 | 1.0056 | 1.0056 | 48 | 11.5279 | 0 | 0 | 498.6899 | 0 | 1.0056 | 0 | 0.10051 | 0 | 0 | 0 | 1.0056 | 0 | 0
10 | 2 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 502.3503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 18 | 0 | 0.004125 | 0.004125 | 48 | 11.9236 | 0 | 0 | 507.4183 | 0 | 0.004125 | 0 | 0.00041229 | 0 | 0 | 0 | 0.004125 | 0 | 0
10 | 2 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 498.1974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 484.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 463.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 450.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 451.8444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 448.3494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 1 | 1.945 | 0 | 1.945 | 11 | 3.6394 | 0.63819 | 0.63819 | 454.3648 | 1.945 | 0 | 862.3261 | 0 | 0 | 0 | 1.945 | 0 | 0 | 862.3261
10 | 3 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 468.1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 508.6168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 528.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 536.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 536.2343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 538.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 8 | 0.42417 | 1.85 | 2.2742 | 41.0991 | 6.5729 | 1.384 | 1.384 | 525.4977 | 2.2742 | 0 | 1101.6233 | 0 | 0 | 0 | 2.2742 | 0 | 0 | 1101.6233
10 | 3 | 9 | 82.2507 | 208.3662 | 290.6169 | 37.5282 | 7.7084 | 264.3102 | 264.3102 | 528.8843 | 290.6169 | 0 | 142796.3923 | 0 | 0 | 0 | 290.6169 | 0 | 0 | 142796.3923
10 | 3 | 10 | 25.9863 | 9.8131 | 35.7994 | 21.1422 | 8.9471 | 70.6858 | 70.6858 | 523.3473 | 35.7994 | 0 | 17978.624 | 0 | 0 | 0 | 35.7994 | 0 | 0 | 17978.624
10 | 3 | 11 | 76.0075 | 26.0779 | 102.0854 | 20.4517 | 9.5923 | 516.7156 | 288 | 521.4709 | 56.899 | 45.1864 | 28507.4727 | 4.5164 | 0 | 0 | 56.899 | 45.1864 | 0 | 28507.4727
10 | 3 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 524.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 521.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 14 | 0.46558 | 0.16604 | 0.63162 | 20.7266 | 10.6934 | 0 | 0 | 524.7241 | 0 | 0.63162 | 0 | 0.063131 | 0 | 0 | 0 | 0.63162 | 0 | 0
10 | 3 | 15 | 97.4242 | 214.777 | 312.2012 | 36.4539 | 11.6655 | 0 | 0 | 529.9655 | 0 | 312.2012 | 0 | 31.2046 | 0 | 0 | 0 | 312.2012 | 0 | 0
10 | 3 | 16 | 62.0697 | 175.4973 | 237.567 | 38.3329 | 12.3021 | 0 | 0 | 521.0667 | 0 | 237.567 | 0 | 23.7449 | 0 | 0 | 0 | 237.567 | 0 | 0
10 | 3 | 17 | 0 | 1.5093 | 1.5093 | 48 | 12.1989 | 0 | 0 | 527.8353 | 0 | 1.5093 | 0 | 0.15085 | 0 | 0 | 0 | 1.5093 | 0 | 0
10 | 3 | 18 | 0 | 0.16642 | 0.16642 | 48 | 12.9559 | 0 | 0 | 540.0744 | 0 | 0.16642 | 0 | 0.016633 | 0 | 0 | 0 | 0.16642 | 0 | 0
10 | 3 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 524.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 501.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 477.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 463.8545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 464.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 0 | 0.027114 | 0 | 0.027114 | 11 | 3.8373 | 0.0091821 | 0.0091821 | 453.5988 | 0.027114 | 0 | 12.0005 | 0 | 0 | 0 | 0.027114 | 0 | 0 | 12.0005
10 | 4 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 456.9823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 483.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 516.0294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 530.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 525.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 529.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 532.3652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 8 | 0 | 0.14567 | 0.14567 | 48 | 6.5729 | 0.088649 | 0.088649 | 535.2845 | 0.14567 | 0 | 70.9811 | 0 | 0 | 0 | 0.14567 | 0 | 0 | 70.9811
10 | 4 | 9 | 79.8272 | 152.34 | 232.1672 | 35.2781 | 7.6912 | 209.5813 | 209.5813 | 528.8839 | 232.1672 | 0 | 114599.0714 | 0 | 0 | 0 | 232.1672 | 0 | 0 | 114599.0714
10 | 4 | 10 | 86.27 | 377.6451 | 463.9151 | 41.1195 | 8.4482 | 622.4258 | 288 | 528.1324 | 214.6562 | 249.2589 | 104540.3292 | 24.9135 | 0 | 0 | 214.6562 | 249.2589 | 0 | 104540.3292
10 | 4 | 11 | 85.3382 | 453.7417 | 539.0799 | 42.1428 | 9.7214 | 3970.0262 | 288 | 524.6029 | 39.1068 | 499.9731 | 18867.4726 | 49.9725 | 0 | 0 | 39.1068 | 499.9731 | 0 | 18867.4726
10 | 4 | 12 | 71.2775 | 498.03 | 569.3075 | 43.3676 | 9.4117 | 2004.2119 | 288 | 521.3636 | 81.808 | 487.4995 | 39103.8991 | 48.7257 | 0 | 0 | 81.808 | 487.4995 | 0 | 39103.8991
10 | 4 | 13 | 66.7063 | 485.8705 | 552.5769 | 43.5334 | 8.8869 | 1032.2992 | 288 | 515.2295 | 154.1628 | 398.4141 | 72717.9988 | 39.8216 | 0 | 0 | 154.1628 | 398.4141 | 0 | 72717.9988
10 | 4 | 14 | 71.65 | 471.1032 | 542.7532 | 43.1156 | 9.3428 | 1712.1336 | 288 | 517.9971 | 91.2972 | 451.456 | 43355.3302 | 45.1232 | 0 | 0 | 91.2972 | 451.456 | 0 | 43355.3302
10 | 4 | 15 | 48.7525 | 28.0735 | 76.826 | 24.5204 | 10.0224 | 0 | 0 | 509.6289 | 0 | 76.826 | 0 | 7.6788 | 0 | 0 | 0 | 76.826 | 0 | 0
10 | 4 | 16 | 18.1629 | 1.7432 | 19.9062 | 14.2401 | 11.4074 | 0 | 0 | 515.4698 | 0 | 19.9062 | 0 | 1.9896 | 0 | 0 | 0 | 19.9062 | 0 | 0
10 | 4 | 17 | 0 | 1.1655 | 1.1655 | 48 | 10.8053 | 0 | 0 | 517.9061 | 0 | 1.1655 | 0 | 0.11649 | 0 | 0 | 0 | 1.1655 | 0 | 0
10 | 4 | 18 | 0 | 0.1665 | 0.1665 | 48 | 11.5107 | 0 | 0 | 518.0557 | 0 | 0.1665 | 0 | 0.016642 | 0 | 0 | 0 | 0.1665 | 0 | 0
10 | 4 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 509.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 487.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 21 | 99.4376 | 0 | 99.4376 | 11 | 7.4847 | 82.4105 | 82.4105 | 465.0403 | 99.4376 | 0 | 45148.6521 | 0 | 0 | 0 | 99.4376 | 0 | 0 | 45148.6521
10 | 4 | 22 | 9.7311 | 0 | 9.7311 | 11 | 5.575 | 4.5881 | 4.5881 | 443.71 | 9.7311 | 0 | 4210.7454 | 0 | 0 | 0 | 9.7311 | 0 | 0 | 4210.7454
10 | 4 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 436.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 433.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 436.6407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 451.7784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 485.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 508.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 506.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 509.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 511.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 8 | 12.9925 | 334.2344 | 347.2269 | 46.6155 | 5.4889 | 160.5957 | 160.5957 | 515.7296 | 347.2269 | 0 | 162889.0201 | 0 | 0 | 0 | 347.2269 | 0 | 0 | 162889.0201
10 | 5 | 9 | 17.8056 | 1072.8385 | 1090.6441 | 47.3959 | 6.9858 | 754.5158 | 288 | 524.0183 | 416.3007 | 674.3434 | 198418.2193 | 67.4008 | 0 | 0 | 416.3007 | 674.3434 | 0 | 198418.2193
10 | 5 | 10 | 22.292 | 786.785 | 809.0769 | 46.9806 | 7.3471 | 635.8122 | 288 | 522.2907 | 366.4827 | 442.5943 | 174192.9283 | 44.2374 | 0 | 0 | 366.4827 | 442.5943 | 0 | 174192.9283
10 | 5 | 11 | 134.5001 | 801.67 | 936.1701 | 42.6842 | 8.9643 | 1879.0275 | 288 | 524.1514 | 143.4875 | 792.6825 | 69084.5232 | 79.2288 | 0 | 0 | 143.4875 | 792.6825 | 0 | 69084.5232
10 | 5 | 12 | 148.9952 | 816.3057 | 965.3008 | 42.289 | 8.2847 | 1172.0697 | 288 | 519.2143 | 237.1929 | 728.1079 | 113123.3049 | 72.7746 | 0 | 0 | 237.1929 | 728.1079 | 0 | 113123.3049
10 | 5 | 13 | 179.4158 | 955.2203 | 1134.6361 | 42.1493 | 7.8202 | 1084.75 | 288 | 513.075 | 301.2447 | 833.3914 | 141863.8773 | 83.2977 | 0 | 0 | 301.2447 | 833.3914 | 0 | 141863.8773
10 | 5 | 14 | 52.7559 | 1050.4435 | 1103.1994 | 46.2306 | 7.6568 | 981.2836 | 288 | 515.6376 | 323.7815 | 779.4179 | 151985.2625 | 77.903 | 0 | 0 | 323.7815 | 779.4179 | 0 | 151985.2625
10 | 5 | 15 | 27.085 | 576.9992 | 604.0842 | 46.3411 | 7.7256 | 553.5492 | 288 | 516.1986 | 314.2923 | 289.7919 | 147672.6159 | 28.9648 | 0 | 0 | 314.2923 | 289.7919 | 0 | 147672.6159
10 | 5 | 16 | 3.7192 | 159.3538 | 163.0729 | 47.1561 | 7.3729 | 129.4072 | 129.4072 | 515.6358 | 163.0729 | 0 | 76396.3472 | 0 | 0 | 0 | 163.0729 | 0 | 0 | 76396.3472
10 | 5 | 17 | 1.5408 | 71.6966 | 73.2374 | 47.2216 | 7.5449 | 62.1825 | 62.1825 | 512.9353 | 73.2374 | 0 | 34107.6631 | 0 | 0 | 0 | 73.2374 | 0 | 0 | 34107.6631
10 | 5 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 517.1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 512.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 500.6569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 478.2149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 460.1643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 455.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 450.8273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 454.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 474.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 505.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 516.6584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 512.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 507.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 7 | 1.2108 | 0 | 1.2108 | 11 | 6.5556 | 0.73318 | 0.73318 | 516.3156 | 1.2108 | 0 | 611.8319 | 0 | 0 | 0 | 1.2108 | 0 | 0 | 611.8319
10 | 6 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 510.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 9 | 56.0363 | 73.3999 | 129.4361 | 31.9817 | 7.6998 | 117.2802 | 117.2802 | 508.6648 | 129.4361 | 0 | 61700.0119 | 0 | 0 | 0 | 129.4361 | 0 | 0 | 61700.0119
10 | 6 | 10 | 59.3834 | 78.0464 | 137.4298 | 32.0123 | 7.8632 | 134.0261 | 134.0261 | 504.4807 | 137.4298 | 0 | 64931.2189 | 0 | 0 | 0 | 137.4298 | 0 | 0 | 64931.2189
10 | 6 | 11 | 45.4851 | 22.2797 | 67.7648 | 23.1648 | 7.6051 | 58.9796 | 58.9796 | 497.549 | 67.7648 | 0 | 32146.541 | 0 | 0 | 0 | 67.7648 | 0 | 0 | 32146.541
10 | 6 | 12 | 22.4713 | 3.4929 | 25.9642 | 15.9776 | 8.2589 | 31.0598 | 31.0598 | 490.6139 | 25.9642 | 0 | 12323.5607 | 0 | 0 | 0 | 25.9642 | 0 | 0 | 12323.5607
10 | 6 | 13 | 6.5246 | 2.6091 | 9.1337 | 21.5692 | 8.5686 | 13.282 | 13.282 | 489.3268 | 9.1337 | 0 | 4272.3578 | 0 | 0 | 0 | 9.1337 | 0 | 0 | 4272.3578
10 | 6 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 493.8577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 15 | 0 | 2.0911 | 2.0911 | 48 | 7.803 | 1.9835 | 1.9835 | 505.6398 | 2.0911 | 0 | 956.9607 | 0 | 0 | 0 | 2.0911 | 0 | 0 | 956.9607
10 | 6 | 16 | 0 | 0.19604 | 0.19604 | 48 | 7.6998 | 0.17763 | 0.17763 | 498.0087 | 0.19604 | 0 | 88.2205 | 0 | 0 | 0 | 0.19604 | 0 | 0 | 88.2205
10 | 6 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 498.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 18 | 0 | 0.0049167 | 0.0049167 | 48 | 7.3041 | 0.0038022 | 0.0038022 | 504.8745 | 0.0049167 | 0 | 2.2463 | 0 | 0 | 0 | 0.0049167 | 0 | 0 | 2.2463
10 | 6 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 497.9684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 487.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 473.1915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 463.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 458.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 448.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 450.8229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 469.8284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 495.4362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 501.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 499.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 501.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 504.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 502.3298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 9 | 0.63417 | 61.2464 | 61.8806 | 47.6208 | 7.5707 | 53.0969 | 53.0969 | 500.2002 | 61.8806 | 0 | 28005.8614 | 0 | 0 | 0 | 61.8806 | 0 | 0 | 28005.8614
10 | 7 | 10 | 29.543 | 98.9083 | 128.4513 | 39.4902 | 7.4159 | 103.6265 | 103.6265 | 498.9248 | 128.4513 | 0 | 59014.9831 | 0 | 0 | 0 | 128.4513 | 0 | 0 | 59014.9831
10 | 7 | 11 | 14.0621 | 17.6424 | 31.7045 | 31.5892 | 7.5879 | 27.3978 | 27.3978 | 501.345 | 31.7045 | 0 | 14893.3579 | 0 | 0 | 0 | 31.7045 | 0 | 0 | 14893.3579
10 | 7 | 12 | 25.9307 | 30.1217 | 56.0524 | 30.8832 | 8.3192 | 69.4481 | 69.4481 | 494.7336 | 56.0524 | 0 | 25999.9425 | 0 | 0 | 0 | 56.0524 | 0 | 0 | 25999.9425
10 | 7 | 13 | 11.6978 | 33.1497 | 44.8475 | 38.3491 | 8.6546 | 69.3709 | 69.3709 | 493.9933 | 44.8475 | 0 | 20434.5096 | 0 | 0 | 0 | 44.8475 | 0 | 0 | 20434.5096
10 | 7 | 14 | 0 | 10.1692 | 10.1692 | 48 | 8.9299 | 19.7578 | 19.7578 | 509.7927 | 10.1692 | 0 | 4696.0852 | 0 | 0 | 0 | 10.1692 | 0 | 0 | 4696.0852
10 | 7 | 15 | 0 | 0.74306 | 0.74306 | 48 | 8.8009 | 1.289 | 1.289 | 498.6473 | 0.74306 | 0 | 334.8592 | 0 | 0 | 0 | 0.74306 | 0 | 0 | 334.8592
10 | 7 | 16 | 0 | 1.3312 | 1.3312 | 48 | 9.5837 | 6.6002 | 6.6002 | 498.7068 | 1.3312 | 0 | 599.9658 | 0 | 0 | 0 | 1.3312 | 0 | 0 | 599.9658
10 | 7 | 17 | 0 | 0.33321 | 0.33321 | 48 | 9.0762 | 0.74932 | 0.74932 | 509.0978 | 0.33321 | 0 | 153.6416 | 0 | 0 | 0 | 0.33321 | 0 | 0 | 153.6416
10 | 7 | 18 | 0 | 0.034958 | 0.034958 | 48 | 9.4461 | 0.13065 | 0.13065 | 512.8579 | 0.034958 | 0 | 16.2507 | 0 | 0 | 0 | 0.034958 | 0 | 0 | 16.2507
10 | 7 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 507.7431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 495.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 470.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 456.7244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 440.0226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 434.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 427.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 432.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 451.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 471.0197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 478.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 495.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 7 | 1.0965 | 0 | 1.0965 | 11 | 5.2137 | 0.47799 | 0.47799 | 502.3473 | 1.0965 | 0 | 538.7447 | 0 | 0 | 0 | 1.0965 | 0 | 0 | 538.7447
10 | 8 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 498.7069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 9 | 0 | 0.16633 | 0.16633 | 48 | 6.7449 | 0.10657 | 0.10657 | 498.0314 | 0.16633 | 0 | 74.8552 | 0 | 0 | 0 | 0.16633 | 0 | 0 | 74.8552
10 | 8 | 10 | 0 | 0.078875 | 0.078875 | 48 | 8.8783 | 0.14623 | 0.14623 | 497.844 | 0.078875 | 0 | 35.4814 | 0 | 0 | 0 | 0.078875 | 0 | 0 | 35.4814
10 | 8 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 493.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 12 | 0 | 0.60764 | 0.60764 | 48 | 10.2547 | 0 | 0 | 490.657 | 0 | 0.60764 | 0 | 0.060734 | 0 | 0 | 0 | 0.60764 | 0 | 0
10 | 8 | 13 | 0 | 1.7698 | 1.7698 | 48 | 10.031 | 0 | 0 | 486.0945 | 0 | 1.7698 | 0 | 0.17689 | 0 | 0 | 0 | 1.7698 | 0 | 0
10 | 8 | 14 | 0.065829 | 57.1735 | 57.2394 | 47.9574 | 9.9364 | 1743.8492 | 288 | 487.092 | 9.4532 | 47.7862 | 4151.2214 | 4.7762 | 0 | 0 | 9.4532 | 47.7862 | 0 | 4151.2214
10 | 8 | 15 | 1.6316 | 0.15012 | 1.7818 | 14.1175 | 11.1494 | 0 | 0 | 490.7679 | 0 | 1.7818 | 0 | 0.17809 | 0 | 0 | 0 | 1.7818 | 0 | 0
10 | 8 | 16 | 32.3708 | 1.1273 | 33.4981 | 12.2452 | 12.5086 | 0 | 0 | 485.2243 | 0 | 33.4981 | 0 | 3.3481 | 0 | 0 | 0 | 33.4981 | 0 | 0
10 | 8 | 17 | 0.8134 | 1.332 | 2.1454 | 33.9719 | 12.2591 | 0 | 0 | 490.5331 | 0 | 2.1454 | 0 | 0.21443 | 0 | 0 | 0 | 2.1454 | 0 | 0
10 | 8 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 492.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 472.9495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 458.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 436.5679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 418.4511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 411.7527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 0 | 65.2617 | 0 | 65.2617 | 11 | 3.5706 | 21.185 | 21.185 | 410.8474 | 65.2617 | 0 | 26094.7117 | 0 | 0 | 0 | 65.2617 | 0 | 0 | 26094.7117
10 | 9 | 1 | 83.6036 | 0 | 83.6036 | 11 | 3.4588 | 26.6755 | 26.6755 | 413.5587 | 83.6036 | 0 | 33655.3551 | 0 | 0 | 0 | 83.6036 | 0 | 0 | 33655.3551
10 | 9 | 2 | 88.7489 | 0 | 88.7489 | 11 | 3.3555 | 27.8776 | 27.8776 | 415.5562 | 88.7489 | 0 | 35903.9085 | 0 | 0 | 0 | 88.7489 | 0 | 0 | 35903.9085
10 | 9 | 3 | 40.7843 | 0 | 40.7843 | 11 | 3.4416 | 12.979 | 12.979 | 419.5615 | 40.7843 | 0 | 16662.912 | 0 | 0 | 0 | 40.7843 | 0 | 0 | 16662.912
10 | 9 | 4 | 40.4879 | 0 | 40.4879 | 11 | 3.691 | 13.3937 | 13.3937 | 427.0341 | 40.4879 | 0 | 16844.3258 | 0 | 0 | 0 | 40.4879 | 0 | 0 | 16844.3258
10 | 9 | 5 | 0.21122 | 0 | 0.21122 | 11 | 3.9405 | 0.072749 | 0.072749 | 439.4998 | 0.21122 | 0 | 90.5095 | 0 | 0 | 0 | 0.21122 | 0 | 0 | 90.5095
10 | 9 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 451.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 459.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 462.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 9 | 0 | 46.2633 | 46.2633 | 48 | 6.7707 | 29.8771 | 29.8771 | 467.298 | 46.2633 | 0 | 19398.1102 | 0 | 0 | 0 | 46.2633 | 0 | 0 | 19398.1102
10 | 9 | 10 | 0 | 200.5609 | 200.5609 | 48 | 8.9987 | 416.3207 | 288 | 472.1191 | 138.7429 | 61.818 | 58843.5304 | 6.1787 | 0 | 0 | 138.7429 | 61.818 | 0 | 58843.5304
10 | 9 | 11 | 0 | 212.318 | 212.318 | 48 | 10.0569 | 0 | 0 | 472.0289 | 0 | 212.318 | 0 | 21.2212 | 0 | 0 | 0 | 212.318 | 0 | 0
10 | 9 | 12 | 0 | 215.8738 | 215.8738 | 48 | 10.1343 | 0 | 0 | 467.3738 | 0 | 215.8738 | 0 | 21.5766 | 0 | 0 | 0 | 215.8738 | 0 | 0
10 | 9 | 13 | 0 | 182.9291 | 182.9291 | 48 | 10.2117 | 0 | 0 | 472.2737 | 0 | 182.9291 | 0 | 18.2838 | 0 | 0 | 0 | 182.9291 | 0 | 0
10 | 9 | 14 | 0 | 175.3652 | 175.3652 | 48 | 9.8762 | 2844.3689 | 288 | 479.8473 | 17.7562 | 157.609 | 7667.9671 | 15.7531 | 0 | 0 | 17.7562 | 157.609 | 0 | 7667.9671
10 | 9 | 15 | 0 | 130.809 | 130.809 | 48 | 10.9601 | 0 | 0 | 484.4854 | 0 | 130.809 | 0 | 13.0744 | 0 | 0 | 0 | 130.809 | 0 | 0
10 | 9 | 16 | 0 | 27.8734 | 27.8734 | 48 | 11.5279 | 0 | 0 | 480.0137 | 0 | 27.8734 | 0 | 2.786 | 0 | 0 | 0 | 27.8734 | 0 | 0
10 | 9 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 488.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 480.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 461.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 454.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 434.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 420.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 420.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 422.8475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 435.4721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 2 | 0.15018 | 0 | 0.15018 | 11 | 3.5276 | 0.048428 | 0.048428 | 450.1499 | 0.15018 | 0 | 65.9531 | 0 | 0 | 0 | 0.15018 | 0 | 0 | 65.9531
10 | 10 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 456.4488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 490.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 499.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 509.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 7 | 2.8081 | 0 | 2.8081 | 11 | 5.6008 | 1.3318 | 1.3318 | 513.1054 | 2.8081 | 0 | 1409.9851 | 0 | 0 | 0 | 2.8081 | 0 | 0 | 1409.9851
10 | 10 | 8 | 0.20833 | 188.9741 | 189.1824 | 47.9593 | 6.5729 | 115.1319 | 115.1319 | 512.2814 | 189.1824 | 0 | 87841.5707 | 0 | 0 | 0 | 189.1824 | 0 | 0 | 87841.5707
10 | 10 | 9 | 0.041667 | 359.9055 | 359.9472 | 47.9957 | 7.7084 | 327.3646 | 288 | 516.1118 | 316.6646 | 43.2826 | 148235.785 | 4.3261 | 0 | 0 | 316.6646 | 43.2826 | 0 | 148235.785
10 | 10 | 10 | 0.84476 | 356.7097 | 357.5544 | 47.9126 | 8.9471 | 705.9908 | 288 | 520.0368 | 145.8598 | 211.6946 | 68863.9484 | 21.1589 | 0 | 0 | 145.8598 | 211.6946 | 0 | 68863.9484
10 | 10 | 11 | 0 | 317.2333 | 317.2333 | 48 | 9.5923 | 1605.7092 | 288 | 523.1883 | 56.899 | 260.3343 | 27037.7216 | 26.0205 | 0 | 0 | 56.899 | 260.3343 | 0 | 27037.7216
10 | 10 | 12 | 3.9634 | 235.7461 | 239.7095 | 47.3882 | 10.2891 | 0 | 0 | 526.1102 | 0 | 239.7095 | 0 | 23.959 | 0 | 0 | 0 | 239.7095 | 0 | 0
10 | 10 | 13 | 3.5218 | 113.0445 | 116.5662 | 46.8821 | 10.0827 | 0 | 0 | 527.1923 | 0 | 116.5662 | 0 | 11.6508 | 0 | 0 | 0 | 116.5662 | 0 | 0
10 | 10 | 14 | 0.44124 | 82.5916 | 83.0328 | 47.8034 | 10.6934 | 0 | 0 | 523.185 | 0 | 83.0328 | 0 | 8.2992 | 0 | 0 | 0 | 83.0328 | 0 | 0
10 | 10 | 15 | 0 | 13.2617 | 13.2617 | 48 | 11.6655 | 0 | 0 | 505.7748 | 0 | 13.2617 | 0 | 1.3255 | 0 | 0 | 0 | 13.2617 | 0 | 0
10 | 10 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 504.1393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 506.8953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 509.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 499.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 487.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 467.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 22 | 3.6468 | 0 | 3.6468 | 11 | 5.6868 | 1.7639 | 1.7639 | 455.6584 | 3.6468 | 0 | 1621.559 | 0 | 0 | 0 | 3.6468 | 0 | 0 | 1621.559
10 | 10 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 460.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 454.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 454.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 457.814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 463.0967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 487.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 503.7862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 516.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 515.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 8 | 0 | 0.10473 | 0.10473 | 48 | 6.5729 | 0.063734 | 0.063734 | 514.6177 | 0.10473 | 0 | 48.8674 | 0 | 0 | 0 | 0.10473 | 0 | 0 | 48.8674
10 | 11 | 9 | 100.3742 | 0 | 100.3742 | 11 | 7.6912 | 90.6095 | 90.6095 | 521.7663 | 100.3742 | 0 | 51267.7611 | 0 | 0 | 0 | 100.3742 | 0 | 0 | 51267.7611
10 | 11 | 10 | 139.2747 | 0 | 139.2747 | 11 | 8.4482 | 186.8622 | 186.8622 | 519.8602 | 139.2747 | 0 | 70871.3515 | 0 | 0 | 0 | 139.2747 | 0 | 0 | 70871.3515
10 | 11 | 11 | 114.87 | 0 | 114.87 | 11 | 9.7214 | 845.9542 | 288 | 516.7773 | 39.1068 | 75.7632 | 19779.3293 | 7.5726 | 0 | 0 | 39.1068 | 75.7632 | 0 | 19779.3293
10 | 11 | 12 | 130.2311 | 0 | 130.2311 | 11 | 9.4117 | 458.4705 | 288 | 515.1639 | 81.808 | 48.4231 | 41244.6397 | 4.8399 | 0 | 0 | 81.808 | 48.4231 | 0 | 41244.6397
10 | 11 | 13 | 123.6845 | 0 | 123.6845 | 11 | 8.8869 | 231.0617 | 231.0617 | 519.6833 | 123.6845 | 0 | 62916.2273 | 0 | 0 | 0 | 123.6845 | 0 | 0 | 62916.2273
10 | 11 | 14 | 133.6017 | 0 | 133.6017 | 11 | 9.3428 | 421.4511 | 288 | 516.0609 | 91.2972 | 42.3045 | 46110.6238 | 4.2284 | 0 | 0 | 91.2972 | 42.3045 | 0 | 46110.6238
10 | 11 | 15 | 103.829 | 0 | 103.829 | 11 | 10.0224 | 0 | 0 | 508.6152 | 0 | 103.829 | 0 | 10.3777 | 0 | 0 | 0 | 103.829 | 0 | 0
10 | 11 | 16 | 39.1976 | 0 | 39.1976 | 11 | 11.4074 | 0 | 0 | 499.8354 | 0 | 39.1976 | 0 | 3.9178 | 0 | 0 | 0 | 39.1976 | 0 | 0
10 | 11 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 497.9112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 500.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 496.2591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 480.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 456.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 435.8611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 431.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 431.0882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 444.5682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 450.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 445.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 479.8121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 479.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 495.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 503.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 8 | 0 | 8.3148 | 8.3148 | 48 | 5.4889 | 3.8457 | 3.8457 | 501.0676 | 8.3148 | 0 | 3767.1459 | 0 | 0 | 0 | 8.3148 | 0 | 0 | 3767.1459
10 | 12 | 9 | 0 | 39.0892 | 39.0892 | 48 | 6.9858 | 27.0422 | 27.0422 | 508.0077 | 39.0892 | 0 | 17981.3182 | 0 | 0 | 0 | 39.0892 | 0 | 0 | 17981.3182
10 | 12 | 10 | 0 | 15.652 | 15.652 | 48 | 7.3471 | 12.3001 | 12.3001 | 514.8023 | 15.652 | 0 | 7306.3953 | 0 | 0 | 0 | 15.652 | 0 | 0 | 7306.3953
10 | 12 | 11 | 0 | 0.20283 | 0.20283 | 48 | 8.9643 | 0.40712 | 0.40712 | 503.9572 | 0.20283 | 0 | 92.4833 | 0 | 0 | 0 | 0.20283 | 0 | 0 | 92.4833
10 | 12 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 513.5213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 13 | 0 | 0.48788 | 0.48788 | 48 | 7.8202 | 0.46642 | 0.46642 | 514.4306 | 0.48788 | 0 | 227.5598 | 0 | 0 | 0 | 0.48788 | 0 | 0 | 227.5598
10 | 12 | 14 | 0 | 0.31067 | 0.31067 | 48 | 7.6568 | 0.27633 | 0.27633 | 523.5147 | 0.31067 | 0 | 147.7266 | 0 | 0 | 0 | 0.31067 | 0 | 0 | 147.7266
10 | 12 | 15 | 0 | 0.33271 | 0.33271 | 48 | 7.7256 | 0.30488 | 0.30488 | 520.7423 | 0.33271 | 0 | 157.2853 | 0 | 0 | 0 | 0.33271 | 0 | 0 | 157.2853
10 | 12 | 16 | 0 | 1.2754 | 1.2754 | 48 | 7.3729 | 1.0121 | 1.0121 | 509.7263 | 1.2754 | 0 | 588.8935 | 0 | 0 | 0 | 1.2754 | 0 | 0 | 588.8935
10 | 12 | 17 | 0 | 1.3656 | 1.3656 | 48 | 7.5449 | 1.1595 | 1.1595 | 507.641 | 1.3656 | 0 | 627.6973 | 0 | 0 | 0 | 1.3656 | 0 | 0 | 627.6973
10 | 12 | 18 | 0 | 0.12071 | 0.12071 | 48 | 7.0804 | 0.086209 | 0.086209 | 516.6241 | 0.12071 | 0 | 56.5668 | 0 | 0 | 0 | 0.12071 | 0 | 0 | 56.5668
10 | 12 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 507.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 488.2687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 467.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 454.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 457.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 453.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 459.7753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 462.6202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 474.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 497.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 504.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 515.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 528.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 524.3229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 525.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 528.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 519.6148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 524.7621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 521.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 523.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 517.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 510.4483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 518.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 530.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 526.5932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 510.9492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 492.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 487.5187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 480.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 472.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 475.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 494.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 507.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 510.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 506.8423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 500.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 7 | 0 | 6.8514 | 6.8514 | 48 | 6.3664 | 3.933 | 3.933 | 511.975 | 6.8514 | 0 | 3178.8884 | 0 | 0 | 0 | 6.8514 | 0 | 0 | 3178.8884
10 | 14 | 8 | 0 | 28.04 | 28.04 | 48 | 6.9944 | 19.4537 | 19.4537 | 521.7724 | 28.04 | 0 | 13284.5871 | 0 | 0 | 0 | 28.04 | 0 | 0 | 13284.5871
10 | 14 | 9 | 0 | 141.9028 | 141.9028 | 48 | 7.5707 | 121.7604 | 121.7604 | 516.4586 | 141.9028 | 0 | 66475.592 | 0 | 0 | 0 | 141.9028 | 0 | 0 | 66475.592
10 | 14 | 10 | 0.2025 | 251.9314 | 252.1339 | 47.9703 | 7.4159 | 203.4059 | 203.4059 | 519.1371 | 252.1339 | 0 | 118797.1268 | 0 | 0 | 0 | 252.1339 | 0 | 0 | 118797.1268
10 | 14 | 11 | 0 | 155.6114 | 155.6114 | 48 | 7.5879 | 134.4735 | 134.4735 | 516.8478 | 155.6114 | 0 | 72958.0471 | 0 | 0 | 0 | 155.6114 | 0 | 0 | 72958.0471
10 | 14 | 12 | 0 | 65.2509 | 65.2509 | 48 | 8.3192 | 80.8449 | 80.8449 | 519.4868 | 65.2509 | 0 | 30764.9444 | 0 | 0 | 0 | 65.2509 | 0 | 0 | 30764.9444
10 | 14 | 13 | 0 | 42.2984 | 42.2984 | 48 | 8.6546 | 65.4279 | 65.4279 | 517.3924 | 42.2984 | 0 | 19854.5363 | 0 | 0 | 0 | 42.2984 | 0 | 0 | 19854.5363
10 | 14 | 14 | 0 | 65.8753 | 65.8753 | 48 | 8.9299 | 127.989 | 127.989 | 519.183 | 65.8753 | 0 | 31039.3134 | 0 | 0 | 0 | 65.8753 | 0 | 0 | 31039.3134
10 | 14 | 15 | 0 | 44.7462 | 44.7462 | 48 | 8.8009 | 77.6206 | 77.6206 | 518.4554 | 44.7462 | 0 | 21051.082 | 0 | 0 | 0 | 44.7462 | 0 | 0 | 21051.082
10 | 14 | 16 | 0 | 98.3043 | 98.3043 | 48 | 9.5837 | 487.4166 | 288 | 521.1096 | 58.0851 | 40.2192 | 27480.6209 | 4.0199 | 0 | 0 | 58.0851 | 40.2192 | 0 | 27480.6209
10 | 14 | 17 | 0 | 1.1648 | 1.1648 | 48 | 9.0762 | 2.6194 | 2.6194 | 510.2221 | 1.1648 | 0 | 538.3924 | 0 | 0 | 0 | 1.1648 | 0 | 0 | 538.3924
10 | 14 | 18 | 0 | 0.034792 | 0.034792 | 48 | 9.4461 | 0.13002 | 0.13002 | 495.0892 | 0.034792 | 0 | 15.555 | 0 | 0 | 0 | 0.034792 | 0 | 0 | 15.555
10 | 14 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 482.4358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 469.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 444.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 440.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 440.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 445.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 451.6854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 458.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 3 | 1.9546 | 0 | 1.9546 | 11 | 3.3297 | 0.61161 | 0.61161 | 464.2481 | 1.9546 | 0 | 885.9331 | 0 | 0 | 0 | 1.9546 | 0 | 0 | 885.9331
10 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 478.7821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 481.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 484.8656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 7 | 0 | 0.69755 | 0.69755 | 48 | 5.2137 | 0.30409 | 0.30409 | 493.3169 | 0.69755 | 0 | 310.6298 | 0 | 0 | 0 | 0.69755 | 0 | 0 | 310.6298
10 | 15 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 486.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 9 | 0.24496 | 0.12992 | 0.37487 | 23.8227 | 6.7449 | 0.24018 | 0.24018 | 486.3917 | 0.37487 | 0 | 173.4056 | 0 | 0 | 0 | 0.37487 | 0 | 0 | 173.4056
10 | 15 | 10 | 4.075 | 4.778 | 8.853 | 30.9689 | 8.8783 | 16.4126 | 16.4126 | 479.6954 | 8.853 | 0 | 3972.593 | 0 | 0 | 0 | 8.853 | 0 | 0 | 3972.593
10 | 15 | 11 | 10.046 | 0.16654 | 10.2126 | 11.6034 | 9.8676 | 155.2724 | 155.2724 | 477.6342 | 10.2126 | 0 | 4759.3788 | 0 | 0 | 0 | 10.2126 | 0 | 0 | 4759.3788
10 | 15 | 12 | 12.1804 | 0 | 12.1804 | 11 | 10.2547 | 0 | 0 | 478.4997 | 0 | 12.1804 | 0 | 1.2174 | 0 | 0 | 0 | 12.1804 | 0 | 0
10 | 15 | 13 | 130.3305 | 0 | 130.3305 | 11 | 10.031 | 0 | 0 | 481.2523 | 0 | 130.3305 | 0 | 13.0266 | 0 | 0 | 0 | 130.3305 | 0 | 0
10 | 15 | 14 | 125.9526 | 0 | 125.9526 | 11 | 9.9364 | 3837.2606 | 288 | 481.4195 | 9.4532 | 116.4994 | 4446.9648 | 11.6441 | 0 | 0 | 9.4532 | 116.4994 | 0 | 4446.9648
10 | 15 | 15 | 69.6482 | 0.41892 | 70.0671 | 11.2212 | 11.1494 | 0 | 0 | 482.3722 | 0 | 70.0671 | 0 | 7.0032 | 0 | 0 | 0 | 70.0671 | 0 | 0
10 | 15 | 16 | 79.5395 | 0.66596 | 80.2055 | 11.3072 | 12.5086 | 0 | 0 | 481.7967 | 0 | 80.2055 | 0 | 8.0166 | 0 | 0 | 0 | 80.2055 | 0 | 0
10 | 15 | 17 | 6.7784 | 0.97092 | 7.7493 | 15.6357 | 12.2591 | 0 | 0 | 486.5694 | 0 | 7.7493 | 0 | 0.77455 | 0 | 0 | 0 | 7.7493 | 0 | 0
10 | 15 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 482.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 472.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 460.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 436.3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 22 | 0.35413 | 0 | 0.35413 | 11 | 5.3857 | 0.16013 | 0.16013 | 418.744 | 0.35412 | 0 | 144.3923 | 0 | 0 | 0 | 0.35412 | 0 | 0 | 144.3923
10 | 15 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 404.3123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 403.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 398.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 401.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 415.2752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 438.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 443.8031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 454.1621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 474.8134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 8 | 0 | 0.49942 | 0.49942 | 48 | 5.8502 | 0.25107 | 0.25107 | 483.5529 | 0.49942 | 0 | 217.5224 | 0 | 0 | 0 | 0.49942 | 0 | 0 | 217.5224
10 | 16 | 9 | 39.4474 | 52.4388 | 91.8862 | 32.1156 | 6.7707 | 59.3407 | 59.3407 | 492.3672 | 91.8862 | 0 | 42290.7573 | 0 | 0 | 0 | 91.8862 | 0 | 0 | 42290.7573
10 | 16 | 10 | 83.5517 | 110.8576 | 194.4093 | 32.0984 | 8.9987 | 403.5512 | 288 | 498.0122 | 138.7429 | 55.6664 | 64642.2471 | 5.5639 | 0 | 0 | 138.7429 | 55.6664 | 0 | 64642.2471
10 | 16 | 11 | 44.9597 | 85.6821 | 130.6418 | 35.2666 | 10.0569 | 0 | 0 | 498.4038 | 0 | 130.6418 | 0 | 13.0577 | 0 | 0 | 0 | 130.6418 | 0 | 0
10 | 16 | 12 | 61.3665 | 52.2794 | 113.6459 | 28.0207 | 10.1343 | 0 | 0 | 500.6727 | 0 | 113.6459 | 0 | 11.3589 | 0 | 0 | 0 | 113.6459 | 0 | 0
10 | 16 | 13 | 44.21 | 56.8163 | 101.0263 | 31.8085 | 10.2117 | 0 | 0 | 509.5271 | 0 | 101.0263 | 0 | 10.0976 | 0 | 0 | 0 | 101.0263 | 0 | 0
10 | 16 | 14 | 47.7052 | 47.3219 | 95.027 | 29.4254 | 9.8762 | 1541.309 | 288 | 517.0557 | 17.7562 | 77.2708 | 8658.4613 | 7.7232 | 0 | 0 | 17.7562 | 77.2708 | 0 | 8658.4613
10 | 16 | 15 | 0 | 0.66567 | 0.66567 | 48 | 10.9601 | 0 | 0 | 505.8152 | 0 | 0.66567 | 0 | 0.066534 | 0 | 0 | 0 | 0.66567 | 0 | 0
10 | 16 | 16 | 0 | 0.33292 | 0.33292 | 48 | 11.5279 | 0 | 0 | 503.7882 | 0 | 0.33292 | 0 | 0.033275 | 0 | 0 | 0 | 0.33292 | 0 | 0
10 | 16 | 17 | 0 | 0.99854 | 0.99854 | 48 | 11.5451 | 0 | 0 | 514.8502 | 0 | 0.99854 | 0 | 0.099805 | 0 | 0 | 0 | 0.99854 | 0 | 0
10 | 16 | 18 | 0 | 0.14246 | 0.14246 | 48 | 11.9236 | 0 | 0 | 506.5507 | 0 | 0.14246 | 0 | 0.014239 | 0 | 0 | 0 | 0.14246 | 0 | 0
10 | 16 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 489.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 472.2151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 21 | 6.9031 | 0 | 6.9031 | 11 | 9.8762 | 111.9667 | 111.9667 | 450.8458 | 6.9031 | 0 | 3036.3135 | 0 | 0 | 0 | 6.9031 | 0 | 0 | 3036.3135
10 | 16 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 431.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 423.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 411.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 419.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 430.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 460.8657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 480.3897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 489.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 497.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 496.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 499.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 503.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 498.9966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 494.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 505.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 505.7467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 506.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 501.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 505.2224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 514.4475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 518.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 503.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 494.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 460.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 442.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 435.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 421.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 419.9622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 438.7918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 464.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 493.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 487.1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 497.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 504.2288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 511.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 513.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 518.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 519.8995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 526.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 530.9096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 534.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 534.5694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 542.5772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 541.268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 546.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 544.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 533.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 505.7472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 493.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 480.2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 478.0581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 481.1242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 501.8131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 529.4839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 546.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 546.7383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 544.7014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 550.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 552.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 9 | 0 | 0 | 0 | 0 | 6.9858 | 0 | 0 | 544.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 548.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 11 | 0 | 0 | 0 | 0 | 8.9643 | 0 | 0 | 551.6036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 551.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 548.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 14 | 0 | 0 | 0 | 0 | 7.6568 | 0 | 0 | 550.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 541.6598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 540.1809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 547.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 538.554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 537.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 536.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 500.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 484.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 471.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 468.7527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 467.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 484.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 509.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 532.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 527.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 526.9705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 534.6285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 531.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 535.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 535.4934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 530.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 528.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 527.0499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 527.0404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 519.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 523.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 524.9201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 528.4912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 521.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 502.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 476.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 452.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 458.7478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 449.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 447.5719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 461.3001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 493.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 515.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 512.6253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 513.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 509.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 522.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 523.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 524.9426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 523.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 522.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 520.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 513.7301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 510.3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 514.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 507.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 513.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 500.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 480.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 471.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 453.9684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 446.5536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 439.4386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 439.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 447.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 457.7238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 473.2505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 476.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 487.8553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 485.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 8 | 0 | 55.867 | 55.867 | 48 | 5.1879 | 24.224 | 24.224 | 489.2569 | 55.867 | 0 | 24651.7081 | 0 | 0 | 0 | 55.867 | 0 | 0 | 24651.7081
10 | 22 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 488.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 481.2655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 477.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 470.5224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 466.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 471.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 472.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 486.4646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 484.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 487.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 470.0372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 458.3683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 444.6962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 424.8918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 414.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 0 | 0.44334 | 0 | 0.44334 | 11 | 3.5706 | 0.14392 | 0.14392 | 407.0165 | 0.44334 | 0 | 175.5714 | 0 | 0 | 0 | 0.44334 | 0 | 0 | 175.5714
10 | 23 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 404.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 409.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 423.2753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 445.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 451.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 452.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 459.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 8 | 0.98417 | 139.8206 | 140.8048 | 47.7414 | 5.8502 | 70.7868 | 70.7868 | 455.9974 | 140.8048 | 0 | 57484.4024 | 0 | 0 | 0 | 140.8048 | 0 | 0 | 57484.4024
10 | 23 | 9 | 14.98 | 1092.9872 | 1107.9672 | 47.4998 | 6.7707 | 715.5319 | 288 | 450.9959 | 445.9543 | 662.0128 | 179940.848 | 66.1684 | 0 | 0 | 445.9543 | 662.0128 | 0 | 179940.848
10 | 23 | 10 | 0.635 | 974.4074 | 975.0424 | 47.9759 | 8.9987 | 2023.9748 | 288 | 440.3448 | 138.7429 | 836.2994 | 54438.4094 | 83.5884 | 0 | 0 | 138.7429 | 836.2994 | 0 | 54438.4094
10 | 23 | 11 | 2.0642 | 758.599 | 760.6632 | 47.8996 | 10.0569 | 0 | 0 | 426.6029 | 0 | 760.6632 | 0 | 76.0285 | 0 | 0 | 0 | 760.6632 | 0 | 0
10 | 23 | 12 | 8.14 | 332.9019 | 341.0419 | 47.1169 | 10.1343 | 0 | 0 | 427.7471 | 0 | 341.0419 | 0 | 34.0872 | 0 | 0 | 0 | 341.0419 | 0 | 0
10 | 23 | 13 | 7.025 | 156.0387 | 163.0637 | 46.406 | 10.2117 | 0 | 0 | 437.9092 | 0 | 163.0637 | 0 | 16.2983 | 0 | 0 | 0 | 163.0637 | 0 | 0
10 | 23 | 14 | 0 | 42.2453 | 42.2453 | 48 | 9.8762 | 685.2052 | 288 | 453.2308 | 17.7562 | 24.4891 | 7195.358 | 2.4477 | 0 | 0 | 17.7562 | 24.4891 | 0 | 7195.358
10 | 23 | 15 | 0 | 0.55961 | 0.55961 | 48 | 10.9601 | 0 | 0 | 451.2309 | 0 | 0.55961 | 0 | 0.055933 | 0 | 0 | 0 | 0.55961 | 0 | 0
10 | 23 | 16 | 1.25 | 0 | 1.25 | 11 | 11.5279 | 0 | 0 | 472.7603 | 0 | 1.25 | 0 | 0.12493 | 0 | 0 | 0 | 1.25 | 0 | 0
10 | 23 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 468.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 473.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 19 | 16.4406 | 0 | 16.4406 | 11 | 13.1107 | 0 | 0 | 452.0832 | 0 | 16.4406 | 0 | 1.6432 | 0 | 0 | 0 | 16.4406 | 0 | 0
10 | 23 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 438.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 423.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 418.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 422.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 422.3431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 423.3815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 449.4095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 469.8943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 498.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 502.6413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 505.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 510.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 8 | 0 | 17.0062 | 17.0062 | 48 | 6.5729 | 10.3496 | 10.3496 | 511.4463 | 17.0062 | 0 | 7881.4545 | 0 | 0 | 0 | 17.0062 | 0 | 0 | 7881.4545
10 | 24 | 9 | 0 | 15.9987 | 15.9987 | 48 | 7.7084 | 14.5505 | 14.5505 | 510.8949 | 15.9987 | 0 | 7405.7051 | 0 | 0 | 0 | 15.9987 | 0 | 0 | 7405.7051
10 | 24 | 10 | 0 | 73.1222 | 73.1222 | 48 | 8.9471 | 144.3796 | 144.3796 | 512.2249 | 73.1222 | 0 | 33945.1204 | 0 | 0 | 0 | 73.1222 | 0 | 0 | 33945.1204
10 | 24 | 11 | 0 | 14.5552 | 14.5552 | 48 | 9.5923 | 73.6724 | 73.6724 | 517.2119 | 14.5552 | 0 | 6829.452 | 0 | 0 | 0 | 14.5552 | 0 | 0 | 6829.452
10 | 24 | 12 | 0 | 1.834 | 1.834 | 48 | 10.2891 | 0 | 0 | 519.003 | 0 | 1.834 | 0 | 0.18331 | 0 | 0 | 0 | 1.834 | 0 | 0
10 | 24 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 516.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 14 | 0 | 0.82514 | 0.82514 | 48 | 10.6934 | 0 | 0 | 514.414 | 0 | 0.82514 | 0 | 0.082473 | 0 | 0 | 0 | 0.82514 | 0 | 0
10 | 24 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 495.2628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 502.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 509.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 516.4716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 19 | 0.40996 | 0 | 0.40996 | 11 | 13.2054 | 0 | 0 | 517.8884 | 0 | 0.40996 | 0 | 0.040975 | 0 | 0 | 0 | 0.40996 | 0 | 0
10 | 24 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 517.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 466.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 451.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 445.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 443.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 444.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 458.5156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 479.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 490.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 501.4431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 507.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 511.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 8 | 0 | 0.52826 | 0.52826 | 48 | 6.5729 | 0.32149 | 0.32149 | 515.4104 | 0.52826 | 0 | 246.914 | 0 | 0 | 0 | 0.52826 | 0 | 0 | 246.914
10 | 25 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 512.5483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 511.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 514.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 512.5623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 514.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 515.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 498.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 500.5789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 507.6155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 516.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 510.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 20 | 8.5471 | 0 | 8.5471 | 11 | 8.4138 | 11.2195 | 11.2195 | 493.0556 | 8.5471 | 0 | 4120.1877 | 0 | 0 | 0 | 8.5471 | 0 | 0 | 4120.1877
10 | 25 | 21 | 0.78795 | 0 | 0.78795 | 11 | 7.4847 | 0.65303 | 0.65303 | 474.9844 | 0.78795 | 0 | 365.5966 | 0 | 0 | 0 | 0.78795 | 0 | 0 | 365.5966
10 | 25 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 464.8252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 463.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 456.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 460.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 464.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 477.6902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 490.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 495.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 6 | 5.6604 | 0 | 5.6604 | 11 | 4.7319 | 2.2421 | 2.2421 | 498.0873 | 5.6604 | 0 | 2757.1037 | 0 | 0 | 0 | 5.6604 | 0 | 0 | 2757.1037
10 | 26 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 494.7204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 8 | 0.46167 | 5.8534 | 6.315 | 45.2951 | 5.4889 | 2.9208 | 2.9208 | 498.6384 | 6.315 | 0 | 2862.8792 | 0 | 0 | 0 | 6.315 | 0 | 0 | 2862.8792
10 | 26 | 9 | 0.985 | 118.7374 | 119.7224 | 47.6956 | 6.9858 | 82.8249 | 82.8249 | 501.8281 | 119.7224 | 0 | 54369.833 | 0 | 0 | 0 | 119.7224 | 0 | 0 | 54369.833
10 | 26 | 10 | 2.3825 | 67.7347 | 70.1172 | 46.7428 | 7.3471 | 55.1015 | 55.1015 | 506.2851 | 70.1172 | 0 | 32221.8135 | 0 | 0 | 0 | 70.1172 | 0 | 0 | 32221.8135
10 | 26 | 11 | 2.6625 | 73.5009 | 76.1634 | 46.7066 | 8.9643 | 152.8709 | 152.8709 | 507.9946 | 76.1634 | 0 | 35133.2716 | 0 | 0 | 0 | 76.1634 | 0 | 0 | 35133.2716
10 | 26 | 12 | 0 | 0.2565 | 0.2565 | 48 | 8.2847 | 0.31144 | 0.31144 | 511.3157 | 0.2565 | 0 | 118.8405 | 0 | 0 | 0 | 0.2565 | 0 | 0 | 118.8405
10 | 26 | 13 | 0.051667 | 0.25237 | 0.30404 | 41.7125 | 7.8202 | 0.29067 | 0.29067 | 514.7881 | 0.30404 | 0 | 143.8347 | 0 | 0 | 0 | 0.30404 | 0 | 0 | 143.8347
10 | 26 | 14 | 0 | 0.33275 | 0.33275 | 48 | 7.6568 | 0.29598 | 0.29598 | 512.0835 | 0.33275 | 0 | 154.4238 | 0 | 0 | 0 | 0.33275 | 0 | 0 | 154.4238
10 | 26 | 15 | 0 | 0.52025 | 0.52025 | 48 | 7.7256 | 0.47673 | 0.47673 | 500.2023 | 0.52025 | 0 | 235.2583 | 0 | 0 | 0 | 0.52025 | 0 | 0 | 235.2583
10 | 26 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 499.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 500.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 18 | 0.18333 | 0 | 0.18333 | 11 | 7.0804 | 0.13094 | 0.13094 | 508.6984 | 0.18333 | 0 | 91.2447 | 0 | 0 | 0 | 0.18333 | 0 | 0 | 91.2447
10 | 26 | 19 | 1.075 | 0 | 1.075 | 11 | 7.7772 | 1.0079 | 1.0079 | 497.6154 | 1.075 | 0 | 523.1115 | 0 | 0 | 0 | 1.075 | 0 | 0 | 523.1115
10 | 26 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 471.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 448.7866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 437.1778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 426.356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 425.5734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 431.5951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 404.3374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 415.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 449.3176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 460.0859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 464.8622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 465.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 472.3166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 472.5911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 473.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 471.6705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 471.5849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 471.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 475.3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 462.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 463.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 473.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 478.7454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 471.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 453.5032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 456.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 437.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 434.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 432.6655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 440.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 444.3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 455.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 470.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 468.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 477.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 478.7751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 8 | 0 | 8.6768 | 8.6768 | 48 | 6.9944 | 6.0198 | 6.0198 | 486.309 | 8.6768 | 0 | 3803.1087 | 0 | 0 | 0 | 8.6768 | 0 | 0 | 3803.1087
10 | 28 | 9 | 0 | 5.764 | 5.764 | 48 | 7.5707 | 4.9458 | 4.9458 | 484.0357 | 5.764 | 0 | 2513.2884 | 0 | 0 | 0 | 5.764 | 0 | 0 | 2513.2884
10 | 28 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 481.6981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 481.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 12 | 0.28297 | 6.0845 | 6.3675 | 46.3557 | 8.3192 | 7.8892 | 7.8892 | 482.579 | 6.3675 | 0 | 2777.6508 | 0 | 0 | 0 | 6.3675 | 0 | 0 | 2777.6508
10 | 28 | 13 | 0.076667 | 0 | 0.076667 | 11 | 8.6546 | 0.11859 | 0.11859 | 486.7077 | 0.076667 | 0 | 36.4709 | 0 | 0 | 0 | 0.076667 | 0 | 0 | 36.4709
10 | 28 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 486.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 477.1821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 16 | 0.65417 | 0.3506 | 1.0048 | 23.9107 | 9.5837 | 4.9819 | 4.9819 | 483.0532 | 1.0048 | 0 | 461.3316 | 0 | 0 | 0 | 1.0048 | 0 | 0 | 461.3316
10 | 28 | 17 | 0 | 0.17115 | 0.17115 | 48 | 9.0762 | 0.38488 | 0.38488 | 472.751 | 0.17115 | 0 | 72.6947 | 0 | 0 | 0 | 0.17115 | 0 | 0 | 72.6947
10 | 28 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 481.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 19 | 51.1045 | 0 | 51.1045 | 11 | 8.0611 | 54.9115 | 54.9115 | 464.2245 | 51.1045 | 0 | 23161.79 | 0 | 0 | 0 | 51.1045 | 0 | 0 | 23161.79
10 | 28 | 20 | 33.6093 | 0 | 33.6093 | 11 | 11.2698 | 0 | 0 | 445.6497 | 0 | 33.6093 | 0 | 3.3593 | 0 | 0 | 0 | 33.6093 | 0 | 0
10 | 28 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 435.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 22 | 67.4868 | 0 | 67.4868 | 11 | 5.4717 | 31.0948 | 31.0948 | 426.5211 | 67.4868 | 0 | 28042.1965 | 0 | 0 | 0 | 67.4868 | 0 | 0 | 28042.1965
10 | 28 | 23 | 55.725 | 0 | 55.725 | 11 | 4.8093 | 22.4022 | 22.4022 | 419.1181 | 55.725 | 0 | 22742.3778 | 0 | 0 | 0 | 55.725 | 0 | 0 | 22742.3778
10 | 29 | 0 | 5.5181 | 0 | 5.5181 | 11 | 3.3125 | 1.7222 | 1.7222 | 402.0976 | 5.5181 | 0 | 2158.1219 | 0 | 0 | 0 | 5.5181 | 0 | 0 | 2158.1219
10 | 29 | 1 | 33.6421 | 0 | 33.6421 | 11 | 3.2007 | 10.3271 | 10.3271 | 401.2562 | 33.6421 | 0 | 13129.0201 | 0 | 0 | 0 | 33.6421 | 0 | 0 | 13129.0201
10 | 29 | 2 | 3.5519 | 0 | 3.5519 | 11 | 3.1921 | 1.0889 | 1.0889 | 409.1336 | 3.5519 | 0 | 1414.1201 | 0 | 0 | 0 | 3.5519 | 0 | 0 | 1414.1201
10 | 29 | 3 | 5.2541 | 0 | 5.2541 | 11 | 3.3297 | 1.644 | 1.644 | 423.2446 | 5.2541 | 0 | 2165.9616 | 0 | 0 | 0 | 5.2541 | 0 | 0 | 2165.9616
10 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 437.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 5 | 47.7048 | 0 | 47.7048 | 11 | 3.7857 | 16.0213 | 16.0213 | 451.583 | 47.7048 | 0 | 21017.9356 | 0 | 0 | 0 | 47.7048 | 0 | 0 | 21017.9356
10 | 29 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 454.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 457.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 461.1967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 457.2932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 10 | 0 | 27.7192 | 27.7192 | 48 | 8.8783 | 51.3884 | 51.3884 | 465.0508 | 27.7192 | 0 | 11560.3172 | 0 | 0 | 0 | 27.7192 | 0 | 0 | 11560.3172
10 | 29 | 11 | 23.3194 | 26.8596 | 50.1791 | 30.8052 | 9.8676 | 762.9239 | 288 | 470.5197 | 18.9423 | 31.2367 | 8329.2241 | 3.1221 | 0 | 0 | 18.9423 | 31.2367 | 0 | 8329.2241
10 | 29 | 12 | 0 | 61.2451 | 61.2451 | 48 | 10.2547 | 0 | 0 | 475.8508 | 0 | 61.2451 | 0 | 6.1215 | 0 | 0 | 0 | 61.2451 | 0 | 0
10 | 29 | 13 | 1.25 | 11.7741 | 13.024 | 44.449 | 10.031 | 0 | 0 | 483.1732 | 0 | 13.024 | 0 | 1.3018 | 0 | 0 | 0 | 13.024 | 0 | 0
10 | 29 | 14 | 16.2813 | 7.393 | 23.6744 | 22.5544 | 9.9364 | 721.2619 | 288 | 490.4636 | 9.4532 | 14.2212 | 4423.2344 | 1.4214 | 0 | 0 | 9.4532 | 14.2212 | 0 | 4423.2344
10 | 29 | 15 | 7.8703 | 72.3386 | 80.2089 | 44.3695 | 11.1494 | 0 | 0 | 487.2671 | 0 | 80.2089 | 0 | 8.0169 | 0 | 0 | 0 | 80.2089 | 0 | 0
10 | 29 | 16 | 0 | 12.2995 | 12.2995 | 48 | 12.5086 | 0 | 0 | 486.5584 | 0 | 12.2995 | 0 | 1.2293 | 0 | 0 | 0 | 12.2995 | 0 | 0
10 | 29 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 480.3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 475.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 469.8504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 469.8504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 432.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 410.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 403.8042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 402.391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 401.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 398.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 402.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 406.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 426.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 441.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 454.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 461.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 9 | 0 | 32.5205 | 32.5205 | 48 | 6.7707 | 21.0019 | 21.0019 | 469.6079 | 32.5205 | 0 | 13710.8862 | 0 | 0 | 0 | 32.5205 | 0 | 0 | 13710.8862
10 | 30 | 10 | 0 | 90.9588 | 90.9588 | 48 | 8.9987 | 188.8106 | 188.8106 | 484.1509 | 90.9588 | 0 | 39671.77 | 0 | 0 | 0 | 90.9588 | 0 | 0 | 39671.77
10 | 30 | 11 | 0 | 35.5215 | 35.5215 | 48 | 10.0569 | 0 | 0 | 491.2905 | 0 | 35.5215 | 0 | 3.5504 | 0 | 0 | 0 | 35.5215 | 0 | 0
10 | 30 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 492.4303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 490.4324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 495.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 15 | 0 | 0 | 0 | 0 | 10.9601 | 0 | 0 | 487.5298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 491.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 499.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 496.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 481.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 457.2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 450.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 449.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 440.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 435.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 435.5464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 453.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 462.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 488.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 497.9058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 506.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 505.1574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 507.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 9 | 0 | 7.9567 | 7.9567 | 48 | 7.7084 | 7.2364 | 7.2364 | 511.0138 | 7.9567 | 0 | 3684.054 | 0 | 0 | 0 | 7.9567 | 0 | 0 | 3684.054
10 | 31 | 10 | 0 | 35.7732 | 35.7732 | 48 | 8.9471 | 70.6341 | 70.6341 | 510.7321 | 35.7732 | 0 | 16553.4018 | 0 | 0 | 0 | 35.7732 | 0 | 0 | 16553.4018
10 | 31 | 11 | 1.425 | 0 | 1.425 | 11 | 9.5923 | 7.2128 | 7.2128 | 513.2143 | 1.425 | 0 | 715.6554 | 0 | 0 | 0 | 1.425 | 0 | 0 | 715.6554
10 | 31 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 508.693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 13 | 0.87573 | 0 | 0.87573 | 11 | 10.0827 | 0 | 0 | 505.391 | 0 | 0.87573 | 0 | 0.08753 | 0 | 0 | 0 | 0.87573 | 0 | 0
10 | 31 | 14 | 0 | 0 | 0 | 0 | 10.6934 | 0 | 0 | 508.9923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 479.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 485.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 489.9615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 18 | 0.033333 | 0 | 0.033333 | 11 | 12.9559 | 0 | 0 | 497.7842 | 0 | 0.033333 | 0 | 0.0033317 | 0 | 0 | 0 | 0.033333 | 0 | 0
10 | 31 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 493.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 471.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 455.5035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 22 | 2.4032 | 0 | 2.4032 | 11 | 5.6868 | 1.1624 | 1.1624 | 441.5633 | 2.4032 | 0 | 1034.7284 | 0 | 0 | 0 | 2.4032 | 0 | 0 | 1034.7284
10 | 31 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 436.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 0 | 7.5119 | 0 | 7.5119 | 11 | 3.8373 | 2.5439 | 2.5439 | 434.9752 | 7.5119 | 0 | 3184.8553 | 0 | 0 | 0 | 7.5119 | 0 | 0 | 3184.8553
11 | 1 | 1 | 73.7484 | 0 | 73.7484 | 11 | 3.605 | 24.0687 | 24.0687 | 439.4941 | 73.7484 | 0 | 31600.7457 | 0 | 0 | 0 | 73.7484 | 0 | 0 | 31600.7457
11 | 1 | 2 | 80.2565 | 0 | 80.2565 | 11 | 3.5018 | 25.7769 | 25.7769 | 443.5777 | 80.2565 | 0 | 34717.1486 | 0 | 0 | 0 | 80.2565 | 0 | 0 | 34717.1486
11 | 1 | 3 | 19.2693 | 0 | 19.2693 | 11 | 3.4416 | 6.1322 | 6.1322 | 456.0852 | 19.2693 | 0 | 8576.4999 | 0 | 0 | 0 | 19.2693 | 0 | 0 | 8576.4999
11 | 1 | 4 | 30.4761 | 0 | 30.4761 | 11 | 3.6222 | 9.9731 | 9.9731 | 474.6173 | 30.4761 | 0 | 14129.2623 | 0 | 0 | 0 | 30.4761 | 0 | 0 | 14129.2623
11 | 1 | 5 | 57.0469 | 0 | 57.0469 | 11 | 4.0351 | 19.9594 | 19.9594 | 496.5088 | 57.0469 | 0 | 27696.7736 | 0 | 0 | 0 | 57.0469 | 0 | 0 | 27696.7736
11 | 1 | 6 | 97.2903 | 0 | 97.2903 | 11 | 5.1793 | 42.11 | 42.11 | 498.4378 | 97.2903 | 0 | 47422.962 | 0 | 0 | 0 | 97.2903 | 0 | 0 | 47422.962
11 | 1 | 7 | 194.4531 | 0.36333 | 194.8165 | 11.069 | 5.3599 | 87.6014 | 87.6014 | 501.3778 | 194.8165 | 0 | 95520.2304 | 0 | 0 | 0 | 194.8165 | 0 | 0 | 95520.2304
11 | 1 | 8 | 279.794 | 351.6693 | 631.4633 | 31.6057 | 6.5729 | 384.2936 | 288 | 502.1671 | 473.2357 | 158.2276 | 222686.3975 | 15.8149 | 0 | 0 | 473.2357 | 158.2276 | 0 | 222686.3975
11 | 1 | 9 | 227.0346 | 410.7493 | 637.7838 | 34.829 | 7.6912 | 575.7383 | 288 | 508.7955 | 319.0369 | 318.747 | 151212.8128 | 31.8588 | 0 | 0 | 319.0369 | 318.747 | 0 | 151212.8128
11 | 1 | 10 | 246.7883 | 160.2252 | 407.0136 | 25.5654 | 8.4482 | 546.0822 | 288 | 510.099 | 214.6562 | 192.3574 | 104008.1159 | 19.2262 | 0 | 0 | 214.6562 | 192.3574 | 0 | 104008.1159
11 | 1 | 11 | 244.375 | 722.9153 | 967.2902 | 38.6524 | 9.7214 | 7123.5589 | 288 | 515.9042 | 39.1068 | 928.1834 | 18663.7931 | 92.7722 | 0 | 0 | 39.1068 | 928.1834 | 0 | 18663.7931
11 | 1 | 12 | 247.9231 | 458.6916 | 706.6147 | 35.0182 | 9.4117 | 2487.5934 | 288 | 513.3177 | 81.808 | 624.8067 | 39128.7261 | 62.4496 | 0 | 0 | 81.808 | 624.8067 | 0 | 39128.7261
11 | 1 | 13 | 298.0856 | 937.3411 | 1235.4267 | 39.0726 | 8.8869 | 2307.9684 | 288 | 514.8675 | 154.1628 | 1081.2639 | 73349.8811 | 108.0726 | 0 | 0 | 154.1628 | 1081.2639 | 0 | 73349.8811
11 | 1 | 14 | 269.7355 | 869.6708 | 1139.4064 | 39.2409 | 9.3428 | 3594.2965 | 288 | 511.2843 | 91.2972 | 1048.1092 | 43096.2242 | 104.7588 | 0 | 0 | 91.2972 | 1048.1092 | 0 | 43096.2242
11 | 1 | 15 | 267.6276 | 502.7885 | 770.416 | 35.1469 | 10.0224 | 0 | 0 | 502.2965 | 0 | 770.416 | 0 | 77.0033 | 0 | 0 | 0 | 770.416 | 0 | 0
11 | 1 | 16 | 213.7569 | 9.1096 | 222.8665 | 12.5124 | 11.4074 | 0 | 0 | 502.1497 | 0 | 222.8665 | 0 | 22.2756 | 0 | 0 | 0 | 222.8665 | 0 | 0
11 | 1 | 17 | 200.002 | 1.7417 | 201.7436 | 11.3194 | 10.8053 | 0 | 0 | 509.3812 | 0 | 201.7436 | 0 | 20.1643 | 0 | 0 | 0 | 201.7436 | 0 | 0
11 | 1 | 18 | 200.0016 | 0 | 200.0016 | 11 | 11.5107 | 0 | 0 | 518.5837 | 0 | 200.0016 | 0 | 19.9902 | 0 | 0 | 0 | 200.0016 | 0 | 0
11 | 1 | 19 | 173.3933 | 0 | 173.3933 | 11 | 10.8913 | 0 | 0 | 503.8263 | 0 | 173.3933 | 0 | 17.3307 | 0 | 0 | 0 | 173.3933 | 0 | 0
11 | 1 | 20 | 195.9442 | 0 | 195.9442 | 11 | 8.4138 | 257.2094 | 257.2094 | 481.0256 | 195.9442 | 0 | 92098.7988 | 0 | 0 | 0 | 195.9442 | 0 | 0 | 92098.7988
11 | 1 | 21 | 197.9639 | 0 | 197.9639 | 11 | 7.4847 | 164.0658 | 164.0658 | 451.4173 | 197.9639 | 0 | 87186.6962 | 0 | 0 | 0 | 197.9639 | 0 | 0 | 87186.6962
11 | 1 | 22 | 122.1188 | 0 | 122.1188 | 11 | 5.575 | 57.5779 | 57.5779 | 436.9563 | 122.1188 | 0 | 52017.2652 | 0 | 0 | 0 | 122.1188 | 0 | 0 | 52017.2652
11 | 1 | 23 | 72.8728 | 0 | 72.8728 | 11 | 4.5599 | 27.9536 | 27.9536 | 423.0802 | 72.8728 | 0 | 30029.4576 | 0 | 0 | 0 | 72.8728 | 0 | 0 | 30029.4576
11 | 2 | 0 | 21.3397 | 0 | 21.3397 | 11 | 4.5083 | 8.1089 | 8.1089 | 420.914 | 21.3397 | 0 | 8747.4336 | 0 | 0 | 0 | 21.3397 | 0 | 0 | 8747.4336
11 | 2 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 417.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 2 | 57.5011 | 0 | 57.5011 | 11 | 4.147 | 20.5023 | 20.5023 | 434.7209 | 57.5011 | 0 | 24364.4038 | 0 | 0 | 0 | 57.5011 | 0 | 0 | 24364.4038
11 | 2 | 3 | 69.7598 | 0 | 69.7598 | 11 | 3.7857 | 23.4283 | 23.4283 | 459.1957 | 69.7598 | 0 | 31266.0546 | 0 | 0 | 0 | 69.7598 | 0 | 0 | 31266.0546
11 | 2 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 489.3806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 499.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 507.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 7 | 2.8556 | 0 | 2.8556 | 11 | 4.99 | 1.1893 | 1.1893 | 509.7195 | 2.8556 | 0 | 1424.1392 | 0 | 0 | 0 | 2.8556 | 0 | 0 | 1424.1392
11 | 2 | 8 | 2.6892 | 19.3657 | 22.0549 | 43.4886 | 5.4889 | 10.2006 | 10.2006 | 515.9208 | 22.0549 | 0 | 10419.4369 | 0 | 0 | 0 | 22.0549 | 0 | 0 | 10419.4369
11 | 2 | 9 | 0 | 97.2961 | 97.2961 | 48 | 6.9858 | 67.3102 | 67.3102 | 515.5977 | 97.2961 | 0 | 45495.4512 | 0 | 0 | 0 | 97.2961 | 0 | 0 | 45495.4512
11 | 2 | 10 | 34.3308 | 266.266 | 300.5968 | 43.7743 | 7.3471 | 236.2237 | 236.2237 | 512.2812 | 300.5968 | 0 | 140831.6831 | 0 | 0 | 0 | 300.5968 | 0 | 0 | 140831.6831
11 | 2 | 11 | 78.4843 | 426.2144 | 504.6987 | 42.2462 | 8.9643 | 1013.0026 | 288 | 514.5615 | 143.4875 | 361.2112 | 67771.3455 | 36.1032 | 0 | 0 | 143.4875 | 361.2112 | 0 | 67771.3455
11 | 2 | 12 | 59.3017 | 416.7663 | 476.068 | 43.3911 | 8.2847 | 578.0425 | 288 | 517.2194 | 237.1929 | 238.8751 | 112388.7164 | 23.8756 | 0 | 0 | 237.1929 | 238.8751 | 0 | 112388.7164
11 | 2 | 13 | 59.2933 | 596.5341 | 655.8275 | 44.6548 | 7.8202 | 626.9929 | 288 | 511.2601 | 301.2447 | 354.5828 | 140562.3844 | 35.4406 | 0 | 0 | 301.2447 | 354.5828 | 0 | 140562.3844
11 | 2 | 14 | 46.8776 | 530.2712 | 577.1488 | 44.9948 | 7.6568 | 513.3674 | 288 | 512.8334 | 323.7815 | 253.3674 | 151477.4802 | 25.3241 | 0 | 0 | 323.7815 | 253.3674 | 0 | 151477.4802
11 | 2 | 15 | 65.4652 | 215.9362 | 281.4014 | 39.3923 | 7.7256 | 257.8606 | 257.8606 | 499.7682 | 281.4014 | 0 | 129550.4205 | 0 | 0 | 0 | 281.4014 | 0 | 0 | 129550.4205
11 | 2 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 497.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 507.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 521.6603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 19 | 3.0583 | 0 | 3.0583 | 11 | 7.7772 | 2.8674 | 2.8674 | 504.4476 | 3.0583 | 0 | 1509.1272 | 0 | 0 | 0 | 3.0583 | 0 | 0 | 1509.1272
11 | 2 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 480.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 452.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 22 | 2.0825 | 0 | 2.0825 | 11 | 4.9212 | 0.85559 | 0.85559 | 437.8914 | 2.0825 | 0 | 888.9854 | 0 | 0 | 0 | 2.0825 | 0 | 0 | 888.9854
11 | 2 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 434.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 0 | 19.6612 | 0 | 19.6612 | 11 | 3.8459 | 6.6676 | 6.6676 | 425.1184 | 19.6612 | 0 | 8142.0844 | 0 | 0 | 0 | 19.6612 | 0 | 0 | 8142.0844
11 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 425.1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 442.2638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 467.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 496.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 5 | 7.5962 | 0 | 7.5962 | 11 | 3.4071 | 2.4048 | 2.4048 | 504.001 | 7.5962 | 0 | 3744.9136 | 0 | 0 | 0 | 7.5962 | 0 | 0 | 3744.9136
11 | 3 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 503.1683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 508.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 8 | 0 | 123.8045 | 123.8045 | 48 | 7.2524 | 93.9469 | 93.9469 | 519.4904 | 123.8045 | 0 | 58372.6512 | 0 | 0 | 0 | 123.8045 | 0 | 0 | 58372.6512
11 | 3 | 9 | 3.3825 | 164.0583 | 167.4408 | 47.2526 | 7.6998 | 151.7157 | 151.7157 | 523.3493 | 167.4408 | 0 | 79718.0302 | 0 | 0 | 0 | 167.4408 | 0 | 0 | 79718.0302
11 | 3 | 10 | 0 | 89.3024 | 89.3024 | 48 | 7.8632 | 87.0907 | 87.0907 | 527.3609 | 89.3024 | 0 | 42808.0874 | 0 | 0 | 0 | 89.3024 | 0 | 0 | 42808.0874
11 | 3 | 11 | 1.3608 | 143.9036 | 145.2644 | 47.6534 | 7.6051 | 126.432 | 126.432 | 521.9131 | 145.2644 | 0 | 68893.0601 | 0 | 0 | 0 | 145.2644 | 0 | 0 | 68893.0601
11 | 3 | 12 | 9.0525 | 421.2551 | 430.3076 | 47.2216 | 8.2589 | 514.7577 | 288 | 514.5966 | 240.7514 | 189.5563 | 112521.1492 | 18.9462 | 0 | 0 | 240.7514 | 189.5563 | 0 | 112521.1492
11 | 3 | 13 | 1.1725 | 395.7648 | 396.9373 | 47.8907 | 8.5686 | 577.2171 | 288 | 511.6022 | 198.0502 | 198.8871 | 91838.1292 | 19.8788 | 0 | 0 | 198.0502 | 198.8871 | 0 | 91838.1292
11 | 3 | 14 | 19.7075 | 299.818 | 319.5255 | 45.7179 | 8.6374 | 488.0296 | 288 | 516.7258 | 188.561 | 130.9645 | 88813.7211 | 13.0899 | 0 | 0 | 188.561 | 130.9645 | 0 | 88813.7211
11 | 3 | 15 | 0 | 79.5731 | 79.5731 | 48 | 7.803 | 75.4801 | 75.4801 | 505.6711 | 79.5731 | 0 | 36418.3095 | 0 | 0 | 0 | 79.5731 | 0 | 0 | 36418.3095
11 | 3 | 16 | 8.315 | 115.9358 | 124.2508 | 45.5239 | 7.6998 | 112.5818 | 112.5818 | 510.3588 | 124.2508 | 0 | 57756.0827 | 0 | 0 | 0 | 124.2508 | 0 | 0 | 57756.0827
11 | 3 | 17 | 5.4286 | 0 | 5.4286 | 11 | 7.6482 | 4.8111 | 4.8111 | 517.7322 | 5.4286 | 0 | 2750.8462 | 0 | 0 | 0 | 5.4286 | 0 | 0 | 2750.8462
11 | 3 | 18 | 56.8006 | 0 | 56.8006 | 11 | 7.3041 | 43.9258 | 43.9258 | 518.0972 | 56.8006 | 0 | 28803.4021 | 0 | 0 | 0 | 56.8006 | 0 | 0 | 28803.4021
11 | 3 | 19 | 47.6118 | 0 | 47.6118 | 11 | 7.3127 | 36.9375 | 36.9375 | 491.5866 | 47.6118 | 0 | 22881.5765 | 0 | 0 | 0 | 47.6118 | 0 | 0 | 22881.5765
11 | 3 | 20 | 120.8296 | 0 | 120.8296 | 11 | 6.6417 | 75.0387 | 75.0387 | 467.127 | 120.8296 | 0 | 55113.6419 | 0 | 0 | 0 | 120.8296 | 0 | 0 | 55113.6419
11 | 3 | 21 | 97.6797 | 0 | 97.6797 | 11 | 5.9879 | 50.7891 | 50.7891 | 441.3922 | 97.6797 | 0 | 42040.562 | 0 | 0 | 0 | 97.6797 | 0 | 0 | 42040.562
11 | 3 | 22 | 58.215 | 0 | 58.215 | 11 | 5.0846 | 24.7125 | 24.7125 | 424.7582 | 58.215 | 0 | 24086.9402 | 0 | 0 | 0 | 58.215 | 0 | 0 | 24086.9402
11 | 3 | 23 | 66.4089 | 0 | 66.4089 | 11 | 4.4566 | 25.0001 | 25.0001 | 415.7099 | 66.4089 | 0 | 26876.3297 | 0 | 0 | 0 | 66.4089 | 0 | 0 | 26876.3297
11 | 4 | 0 | 113.9196 | 0 | 113.9196 | 11 | 3.9749 | 39.4597 | 39.4597 | 415.6392 | 113.9196 | 0 | 46096.351 | 0 | 0 | 0 | 113.9196 | 0 | 0 | 46096.351
11 | 4 | 1 | 131.6501 | 0 | 131.6501 | 11 | 3.7598 | 44.0309 | 44.0309 | 416.7519 | 131.6501 | 0 | 53417.2645 | 0 | 0 | 0 | 131.6501 | 0 | 0 | 53417.2645
11 | 4 | 2 | 48.3726 | 0 | 48.3726 | 11 | 3.691 | 16.0021 | 16.0021 | 428.6111 | 48.3726 | 0 | 20200.9141 | 0 | 0 | 0 | 48.3726 | 0 | 0 | 20200.9141
11 | 4 | 3 | 50.4914 | 0 | 50.4914 | 11 | 3.6824 | 16.6803 | 16.6803 | 443.1141 | 50.4914 | 0 | 21818.0306 | 0 | 0 | 0 | 50.4914 | 0 | 0 | 21818.0306
11 | 4 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 472.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 5 | 35.57 | 0 | 35.57 | 11 | 3.691 | 11.7669 | 11.7669 | 497.7806 | 35.57 | 0 | 17314.7672 | 0 | 0 | 0 | 35.57 | 0 | 0 | 17314.7672
11 | 4 | 6 | 0.22275 | 0 | 0.22275 | 11 | 4.8007 | 0.089401 | 0.089401 | 502.6058 | 0.22275 | 0 | 109.5061 | 0 | 0 | 0 | 0.22275 | 0 | 0 | 109.5061
11 | 4 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 508.8537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 8 | 0.075 | 2.3858 | 2.4608 | 46.8723 | 6.9944 | 1.7073 | 1.7073 | 516.0216 | 2.4608 | 0 | 1154.4806 | 0 | 0 | 0 | 2.4608 | 0 | 0 | 1154.4806
11 | 4 | 9 | 0 | 1.4667 | 1.4667 | 48 | 7.5707 | 1.2585 | 1.2585 | 512.2266 | 1.4667 | 0 | 680.8726 | 0 | 0 | 0 | 1.4667 | 0 | 0 | 680.8726
11 | 4 | 10 | 0 | 78.4215 | 78.4215 | 48 | 7.4159 | 63.2656 | 63.2656 | 515.0449 | 78.4215 | 0 | 36626.3571 | 0 | 0 | 0 | 78.4215 | 0 | 0 | 36626.3571
11 | 4 | 11 | 0 | 0.84712 | 0.84712 | 48 | 7.5879 | 0.73205 | 0.73205 | 512.8498 | 0.84712 | 0 | 393.7859 | 0 | 0 | 0 | 0.84712 | 0 | 0 | 393.7859
11 | 4 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 511.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 13 | 0 | 0.97567 | 0.97567 | 48 | 8.6546 | 1.5092 | 1.5092 | 509.4668 | 0.97567 | 0 | 450.2378 | 0 | 0 | 0 | 0.97567 | 0 | 0 | 450.2378
11 | 4 | 14 | 0 | 1.2258 | 1.2258 | 48 | 8.9299 | 2.3816 | 2.3816 | 512.0668 | 1.2258 | 0 | 568.8492 | 0 | 0 | 0 | 1.2258 | 0 | 0 | 568.8492
11 | 4 | 15 | 0 | 1.1573 | 1.1573 | 48 | 8.8009 | 2.0075 | 2.0075 | 501.8786 | 1.1573 | 0 | 525.2699 | 0 | 0 | 0 | 1.1573 | 0 | 0 | 525.2699
11 | 4 | 16 | 0 | 0.33321 | 0.33321 | 48 | 9.5837 | 1.6521 | 1.6521 | 502.3634 | 0.33321 | 0 | 151.3977 | 0 | 0 | 0 | 0.33321 | 0 | 0 | 151.3977
11 | 4 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 505.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 505.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 496.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 465.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 446.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 444.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 430.7532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 422.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 421.2656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 426.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 444.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 465.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 475.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 480.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 483.4633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 8 | 0.285 | 13.928 | 14.213 | 47.2581 | 5.1879 | 6.1628 | 6.1628 | 484.8368 | 14.213 | 0 | 6219.3135 | 0 | 0 | 0 | 14.213 | 0 | 0 | 6219.3135
11 | 5 | 9 | 0.45 | 232.6144 | 233.0644 | 47.9286 | 6.7449 | 149.3229 | 149.3229 | 479.366 | 233.0644 | 0 | 100552.694 | 0 | 0 | 0 | 233.0644 | 0 | 0 | 100552.694
11 | 5 | 10 | 0.28667 | 138.2309 | 138.5176 | 47.9234 | 8.8783 | 256.7965 | 256.7965 | 473.0033 | 138.5176 | 0 | 58881.043 | 0 | 0 | 0 | 138.5176 | 0 | 0 | 58881.043
11 | 5 | 11 | 0 | 22.0706 | 22.0706 | 48 | 9.8676 | 335.5619 | 288 | 462.5483 | 18.9423 | 3.1282 | 7852.5166 | 0.31267 | 0 | 0 | 18.9423 | 3.1282 | 0 | 7852.5166
11 | 5 | 12 | 0 | 12.5482 | 12.5482 | 48 | 10.2547 | 0 | 0 | 463.4118 | 0 | 12.5482 | 0 | 1.2542 | 0 | 0 | 0 | 12.5482 | 0 | 0
11 | 5 | 13 | 0 | 2.3032 | 2.3032 | 48 | 10.031 | 0 | 0 | 468.2896 | 0 | 2.3032 | 0 | 0.2302 | 0 | 0 | 0 | 2.3032 | 0 | 0
11 | 5 | 14 | 0 | 2.3311 | 2.3311 | 48 | 9.9364 | 71.0186 | 71.0186 | 473.9217 | 2.3311 | 0 | 992.8589 | 0 | 0 | 0 | 2.3311 | 0 | 0 | 992.8589
11 | 5 | 15 | 0 | 0.49921 | 0.49921 | 48 | 11.1494 | 0 | 0 | 469.7256 | 0 | 0.49921 | 0 | 0.049896 | 0 | 0 | 0 | 0.49921 | 0 | 0
11 | 5 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 482.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 17 | 0 | 0.42646 | 0.42646 | 48 | 12.2591 | 0 | 0 | 472.8578 | 0 | 0.42646 | 0 | 0.042625 | 0 | 0 | 0 | 0.42646 | 0 | 0
11 | 5 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 468.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 457.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 440.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 427.3046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 418.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 421.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 423.8518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 424.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 425.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 431.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 437.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 452.9045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 461.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 457.7527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 453.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 9 | 0.2075 | 427.9023 | 428.1098 | 47.9821 | 6.7707 | 276.4759 | 276.4759 | 455.4744 | 428.1098 | 0 | 174451.4652 | 0 | 0 | 0 | 428.1098 | 0 | 0 | 174451.4652
11 | 6 | 10 | 0.43417 | 273.4599 | 273.8941 | 47.9413 | 8.9987 | 568.5443 | 288 | 453.4937 | 138.7429 | 135.1512 | 56267.5219 | 13.5084 | 0 | 0 | 138.7429 | 135.1512 | 0 | 56267.5219
11 | 6 | 11 | 0.40083 | 194.9043 | 195.3051 | 47.9241 | 10.0569 | 0 | 0 | 450.7254 | 0 | 195.3051 | 0 | 19.5208 | 0 | 0 | 0 | 195.3051 | 0 | 0
11 | 6 | 12 | 0.1575 | 0 | 0.1575 | 11 | 10.1343 | 0 | 0 | 454.0495 | 0 | 0.1575 | 0 | 0.015742 | 0 | 0 | 0 | 0.1575 | 0 | 0
11 | 6 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 458.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 481.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 15 | 0 | 31.8627 | 31.8627 | 48 | 10.9601 | 0 | 0 | 497.7461 | 0 | 31.8627 | 0 | 3.1847 | 0 | 0 | 0 | 31.8627 | 0 | 0
11 | 6 | 16 | 0 | 0.58881 | 0.58881 | 48 | 11.5279 | 0 | 0 | 489.159 | 0 | 0.58881 | 0 | 0.058851 | 0 | 0 | 0 | 0.58881 | 0 | 0
11 | 6 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 485.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 478.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 458.947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 443.1779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 432.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 427.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 23 | 1.2166 | 0 | 1.2166 | 11 | 4.6373 | 0.47342 | 0.47342 | 426.3521 | 1.2166 | 0 | 505.3277 | 0 | 0 | 0 | 1.2166 | 0 | 0 | 505.3277
11 | 7 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 430.9296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 1 | 5.939 | 0 | 5.939 | 11 | 3.6394 | 1.9487 | 1.9487 | 434.9348 | 5.939 | 0 | 2517.7402 | 0 | 0 | 0 | 5.939 | 0 | 0 | 2517.7402
11 | 7 | 2 | 12.4035 | 0 | 12.4035 | 11 | 3.5276 | 3.9996 | 3.9996 | 442.1565 | 12.4035 | 0 | 5347.8408 | 0 | 0 | 0 | 12.4035 | 0 | 0 | 5347.8408
11 | 7 | 3 | 19.0007 | 0 | 19.0007 | 11 | 3.562 | 6.1597 | 6.1597 | 472.6797 | 19.0007 | 0 | 8772.2531 | 0 | 0 | 0 | 19.0007 | 0 | 0 | 8772.2531
11 | 7 | 4 | 31.132 | 0 | 31.132 | 11 | 3.5878 | 10.133 | 10.133 | 501.3707 | 31.132 | 0 | 15266.2009 | 0 | 0 | 0 | 31.132 | 0 | 0 | 15266.2009
11 | 7 | 5 | 20.525 | 0 | 20.525 | 11 | 4.1814 | 7.3615 | 7.3615 | 498.5789 | 20.525 | 0 | 10007.5574 | 0 | 0 | 0 | 20.525 | 0 | 0 | 10007.5574
11 | 7 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 511.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 7 | 60.8114 | 293.6152 | 354.4267 | 41.6517 | 5.6008 | 168.0881 | 168.0881 | 515.4422 | 354.4267 | 0 | 167924.0082 | 0 | 0 | 0 | 354.4267 | 0 | 0 | 167924.0082
11 | 7 | 8 | 97.2811 | 153.9148 | 251.1959 | 33.6709 | 6.5729 | 152.8719 | 152.8719 | 520.9054 | 251.1959 | 0 | 122391.3165 | 0 | 0 | 0 | 251.1959 | 0 | 0 | 122391.3165
11 | 7 | 9 | 216.5175 | 204.3839 | 420.9014 | 28.9667 | 7.7084 | 382.8013 | 288 | 525.477 | 316.6646 | 104.2368 | 157227.2317 | 10.4185 | 0 | 0 | 316.6646 | 104.2368 | 0 | 157227.2317
11 | 7 | 10 | 172.4882 | 169.078 | 341.5661 | 29.3153 | 8.9471 | 674.422 | 288 | 526.4246 | 145.8598 | 195.7064 | 72508.2597 | 19.5609 | 0 | 0 | 145.8598 | 195.7064 | 0 | 72508.2597
11 | 7 | 11 | 125.7844 | 140.2212 | 266.0056 | 30.504 | 9.5923 | 1346.4147 | 288 | 525.8046 | 56.899 | 209.1066 | 28182.0882 | 20.9003 | 0 | 0 | 56.899 | 209.1066 | 0 | 28182.0882
11 | 7 | 12 | 114.8172 | 120.266 | 235.0832 | 29.9288 | 10.2891 | 0 | 0 | 524.8338 | 0 | 235.0832 | 0 | 23.4966 | 0 | 0 | 0 | 235.0832 | 0 | 0
11 | 7 | 13 | 90.3748 | 96.0515 | 186.4263 | 30.0633 | 10.0827 | 0 | 0 | 524.094 | 0 | 186.4263 | 0 | 18.6334 | 0 | 0 | 0 | 186.4263 | 0 | 0
11 | 7 | 14 | 133.1943 | 38.4389 | 171.6332 | 19.2865 | 10.6934 | 0 | 0 | 511.549 | 0 | 171.6332 | 0 | 17.1548 | 0 | 0 | 0 | 171.6332 | 0 | 0
11 | 7 | 15 | 63.4281 | 0 | 63.4281 | 11 | 11.6655 | 0 | 0 | 517.3704 | 0 | 63.4281 | 0 | 6.3397 | 0 | 0 | 0 | 63.4281 | 0 | 0
11 | 7 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 505.789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 506.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 505.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 489.458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 463.162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 449.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 443.5406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 438.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 435.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 443.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 463.0771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 475.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 506.3078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 507.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 510.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 7 | 0.22417 | 124.1906 | 124.4147 | 47.9333 | 5.3599 | 55.9445 | 55.9445 | 508.9182 | 124.4147 | 0 | 57353.3056 | 0 | 0 | 0 | 124.4147 | 0 | 0 | 57353.3056
11 | 8 | 8 | 0.58127 | 393.5945 | 394.1758 | 47.9454 | 6.5729 | 239.886 | 239.886 | 509.434 | 394.1758 | 0 | 181907.606 | 0 | 0 | 0 | 394.1758 | 0 | 0 | 181907.606
11 | 8 | 9 | 0.58083 | 148.2588 | 148.8397 | 47.8556 | 7.6912 | 134.3601 | 134.3601 | 504.6409 | 148.8397 | 0 | 67987.7632 | 0 | 0 | 0 | 148.8397 | 0 | 0 | 67987.7632
11 | 8 | 10 | 0.13833 | 142.0182 | 142.1565 | 47.964 | 8.4482 | 190.7286 | 190.7286 | 503.4529 | 142.1565 | 0 | 64750.6944 | 0 | 0 | 0 | 142.1565 | 0 | 0 | 64750.6944
11 | 8 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 502.3875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 504.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 13 | 0 | 54.087 | 54.087 | 48 | 8.8869 | 101.043 | 101.043 | 504.1058 | 54.087 | 0 | 24669.4175 | 0 | 0 | 0 | 54.087 | 0 | 0 | 24669.4175
11 | 8 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 495.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 490.2945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 504.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 506.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 495.1589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 475.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 447.8847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 431.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 421.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 418.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 418.2634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 422.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 433.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 448.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 491.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 492.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 504.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 7 | 0.38167 | 121.7453 | 122.127 | 47.8844 | 4.99 | 50.8652 | 50.8652 | 512.845 | 122.127 | 0 | 56784.2201 | 0 | 0 | 0 | 122.127 | 0 | 0 | 56784.2201
11 | 9 | 8 | 1.4875 | 81.5474 | 83.0349 | 47.3372 | 5.4889 | 38.4044 | 38.4044 | 513.9273 | 83.0349 | 0 | 38743.2597 | 0 | 0 | 0 | 83.0349 | 0 | 0 | 38743.2597
11 | 9 | 9 | 0 | 0.40413 | 0.40413 | 48 | 6.9858 | 0.27958 | 0.27958 | 516.3799 | 0.40413 | 0 | 189.284 | 0 | 0 | 0 | 0.40413 | 0 | 0 | 189.284
11 | 9 | 10 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 516.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 11 | 0 | 1.0408 | 1.0408 | 48 | 8.9643 | 2.089 | 2.089 | 512.3951 | 1.0408 | 0 | 483.3386 | 0 | 0 | 0 | 1.0408 | 0 | 0 | 483.3386
11 | 9 | 12 | 6.0583 | 0 | 6.0583 | 11 | 8.2847 | 7.356 | 7.356 | 511.7079 | 6.0583 | 0 | 3033.4553 | 0 | 0 | 0 | 6.0583 | 0 | 0 | 3033.4553
11 | 9 | 13 | 0 | 0 | 0 | 0 | 7.8202 | 0 | 0 | 510.5568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 14 | 0.52917 | 0 | 0.52917 | 11 | 7.6568 | 0.47069 | 0.47069 | 497.0153 | 0.52917 | 0 | 257.1831 | 0 | 0 | 0 | 0.52917 | 0 | 0 | 257.1831
11 | 9 | 15 | 0 | 0 | 0 | 0 | 7.7256 | 0 | 0 | 499.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 500.9377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 508.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 511.4573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 488.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 467.0175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 449.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 436.3985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 426.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 427.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 429.6162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 440.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 449.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 4 | 0.066667 | 0 | 0.066667 | 11 | 3.2609 | 0.020647 | 0.020647 | 488.6316 | 0.066667 | 0 | 31.8421 | 0 | 0 | 0 | 0.066667 | 0 | 0 | 31.8421
11 | 10 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 499.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 6 | 0.11667 | 0 | 0.11667 | 11 | 4.9556 | 0.04826 | 0.04826 | 494.2855 | 0.11667 | 0 | 56.3833 | 0 | 0 | 0 | 0.11667 | 0 | 0 | 56.3833
11 | 10 | 7 | 0 | 73.5257 | 73.5257 | 48 | 6.5556 | 44.5228 | 44.5228 | 494.7157 | 73.5257 | 0 | 32845.0804 | 0 | 0 | 0 | 73.5257 | 0 | 0 | 32845.0804
11 | 10 | 8 | 2.6542 | 270.3339 | 272.988 | 47.6403 | 7.2524 | 207.1523 | 207.1523 | 480.6871 | 272.988 | 0 | 118216.5903 | 0 | 0 | 0 | 272.988 | 0 | 0 | 118216.5903
11 | 10 | 9 | 0.0525 | 53.0054 | 53.0579 | 47.9634 | 7.6998 | 48.075 | 48.075 | 477.7024 | 53.0579 | 0 | 22801.0527 | 0 | 0 | 0 | 53.0579 | 0 | 0 | 22801.0527
11 | 10 | 10 | 0 | 36.3292 | 36.3292 | 48 | 7.8632 | 35.4294 | 35.4294 | 474.6464 | 36.3292 | 0 | 15499.7074 | 0 | 0 | 0 | 36.3292 | 0 | 0 | 15499.7074
11 | 10 | 11 | 0 | 3.0672 | 3.0672 | 48 | 7.6051 | 2.6695 | 2.6695 | 477.5326 | 3.0672 | 0 | 1317.4523 | 0 | 0 | 0 | 3.0672 | 0 | 0 | 1317.4523
11 | 10 | 12 | 0 | 4.3624 | 4.3624 | 48 | 8.2589 | 5.2185 | 5.2185 | 472.2889 | 4.3624 | 0 | 1850.9074 | 0 | 0 | 0 | 4.3624 | 0 | 0 | 1850.9074
11 | 10 | 13 | 3.4061 | 157.5074 | 160.9135 | 47.2168 | 8.5686 | 233.9967 | 233.9967 | 471.8731 | 160.9135 | 0 | 68332.9325 | 0 | 0 | 0 | 160.9135 | 0 | 0 | 68332.9325
11 | 10 | 14 | 0.76917 | 191.5858 | 192.3549 | 47.852 | 8.6374 | 293.7947 | 288 | 465.7127 | 188.561 | 3.7939 | 78792.2283 | 0.37921 | 0 | 0 | 188.561 | 3.7939 | 0 | 78792.2283
11 | 10 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 481.8435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 487.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 486.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 483.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 463.8508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 440.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 428.8623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 412.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 404.3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 405.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 1 | 0.61841 | 0 | 0.61841 | 11 | 3.7598 | 0.20683 | 0.20683 | 412.0726 | 0.61841 | 0 | 248.0254 | 0 | 0 | 0 | 0.61841 | 0 | 0 | 248.0254
11 | 11 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 429.3309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 440.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 470.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 483.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 482.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 480.198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 8 | 0.055 | 0.044958 | 0.099958 | 27.6415 | 6.9944 | 0.06935 | 0.06935 | 467.6043 | 0.099958 | 0 | 43.9779 | 0 | 0 | 0 | 0.099958 | 0 | 0 | 43.9779
11 | 11 | 9 | 0 | 0.48608 | 0.48608 | 48 | 7.5707 | 0.41709 | 0.41709 | 464.5502 | 0.48608 | 0 | 202.4777 | 0 | 0 | 0 | 0.48608 | 0 | 0 | 202.4777
11 | 11 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 452.8484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 11 | 0 | 0.17471 | 0.17471 | 48 | 7.5879 | 0.15098 | 0.15098 | 452.7661 | 0.17471 | 0 | 70.716 | 0 | 0 | 0 | 0.17471 | 0 | 0 | 70.716
11 | 11 | 12 | 0 | 0.15992 | 0.15992 | 48 | 8.3192 | 0.19813 | 0.19813 | 451.7001 | 0.15992 | 0 | 64.5584 | 0 | 0 | 0 | 0.15992 | 0 | 0 | 64.5584
11 | 11 | 13 | 0 | 0.26604 | 0.26604 | 48 | 8.6546 | 0.41152 | 0.41152 | 451.6109 | 0.26604 | 0 | 107.3773 | 0 | 0 | 0 | 0.26604 | 0 | 0 | 107.3773
11 | 11 | 14 | 0 | 3.7313 | 3.7313 | 48 | 8.9299 | 7.2496 | 7.2496 | 455.2767 | 3.7313 | 0 | 1519.6897 | 0 | 0 | 0 | 3.7313 | 0 | 0 | 1519.6897
11 | 11 | 15 | 6.8833 | 0.83192 | 7.7153 | 14.9896 | 8.8009 | 13.3835 | 13.3835 | 469.8633 | 7.7153 | 0 | 3509.464 | 0 | 0 | 0 | 7.7153 | 0 | 0 | 3509.464
11 | 11 | 16 | 0 | 0.36954 | 0.36954 | 48 | 9.5837 | 1.8323 | 1.8323 | 470.7294 | 0.36954 | 0 | 156.2161 | 0 | 0 | 0 | 0.36954 | 0 | 0 | 156.2161
11 | 11 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 472.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 470.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 454.423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 436.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 426.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 431.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 425.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 426.8517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 435.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 446.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 459.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 483.6892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 488.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 493.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 7 | 0.013333 | 0 | 0.013333 | 11 | 5.2137 | 0.0058125 | 0.0058125 | 489.2342 | 0.013333 | 0 | 6.3765 | 0 | 0 | 0 | 0.013333 | 0 | 0 | 6.3765
11 | 12 | 8 | 0.38833 | 40.9543 | 41.3426 | 47.6525 | 5.1879 | 17.9262 | 17.9262 | 476.709 | 41.3426 | 0 | 17738.3151 | 0 | 0 | 0 | 41.3426 | 0 | 0 | 17738.3151
11 | 12 | 9 | 0.48 | 1.5055 | 1.9855 | 39.0551 | 6.7449 | 1.2721 | 1.2721 | 459.5586 | 1.9855 | 0 | 834.9019 | 0 | 0 | 0 | 1.9855 | 0 | 0 | 834.9019
11 | 12 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 448.9899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 11 | 0.0375 | 0 | 0.0375 | 11 | 9.8676 | 0.57015 | 0.57015 | 443.8749 | 0.0375 | 0 | 16.2328 | 0 | 0 | 0 | 0.0375 | 0 | 0 | 16.2328
11 | 12 | 12 | 0.07 | 34.4295 | 34.4995 | 47.9249 | 10.2547 | 0 | 0 | 438.5382 | 0 | 34.4995 | 0 | 3.4482 | 0 | 0 | 0 | 34.4995 | 0 | 0
11 | 12 | 13 | 0.87083 | 0 | 0.87083 | 11 | 10.031 | 0 | 0 | 449.1041 | 0 | 0.87083 | 0 | 0.08704 | 0 | 0 | 0 | 0.87083 | 0 | 0
11 | 12 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 475.705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 15 | 0.20255 | 0 | 0.20255 | 11 | 11.1494 | 0 | 0 | 489.8288 | 0 | 0.20255 | 0 | 0.020245 | 0 | 0 | 0 | 0.20255 | 0 | 0
11 | 12 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 485.7465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 478.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 480.8833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 464.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 446.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 419.1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 406.9143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 397.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 399.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 400.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 415.5671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 419.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 4 | 3.73 | 0 | 3.73 | 11 | 3.691 | 1.2339 | 1.2339 | 428.6991 | 3.73 | 0 | 1558.0367 | 0 | 0 | 0 | 3.73 | 0 | 0 | 1558.0367
11 | 13 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 427.9906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 427.8399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 428.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 419.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 9 | 33.2833 | 0 | 33.2833 | 11 | 6.7707 | 21.4946 | 21.4946 | 409.86 | 33.2833 | 0 | 13275.3804 | 0 | 0 | 0 | 33.2833 | 0 | 0 | 13275.3804
11 | 13 | 10 | 72.5511 | 0 | 72.5511 | 11 | 8.9987 | 150.6001 | 150.6001 | 406.6324 | 72.5511 | 0 | 28703.5512 | 0 | 0 | 0 | 72.5511 | 0 | 0 | 28703.5512
11 | 13 | 11 | 108.1561 | 0 | 108.1561 | 11 | 10.0569 | 0 | 0 | 402.1398 | 0 | 108.1561 | 0 | 10.8102 | 0 | 0 | 0 | 108.1561 | 0 | 0
11 | 13 | 12 | 114.3938 | 0 | 114.3938 | 11 | 10.1343 | 0 | 0 | 400.5244 | 0 | 114.3938 | 0 | 11.4337 | 0 | 0 | 0 | 114.3938 | 0 | 0
11 | 13 | 13 | 148.3217 | 0 | 148.3217 | 11 | 10.2117 | 0 | 0 | 407.4433 | 0 | 148.3217 | 0 | 14.8248 | 0 | 0 | 0 | 148.3217 | 0 | 0
11 | 13 | 14 | 127.6263 | 0 | 127.6263 | 11 | 9.8762 | 2070.0591 | 288 | 431.8994 | 17.7562 | 109.8701 | 7473.5736 | 10.9815 | 0 | 0 | 17.7562 | 109.8701 | 0 | 7473.5736
11 | 13 | 15 | 13.6093 | 0 | 13.6093 | 11 | 10.9601 | 0 | 0 | 446.5366 | 0 | 13.6093 | 0 | 1.3603 | 0 | 0 | 0 | 13.6093 | 0 | 0
11 | 13 | 16 | 15.6773 | 0 | 15.6773 | 11 | 11.5279 | 0 | 0 | 441.7116 | 0 | 15.6773 | 0 | 1.5669 | 0 | 0 | 0 | 15.6773 | 0 | 0
11 | 13 | 17 | 15.2671 | 0 | 15.2671 | 11 | 11.5451 | 0 | 0 | 440.1443 | 0 | 15.2671 | 0 | 1.5259 | 0 | 0 | 0 | 15.2671 | 0 | 0
11 | 13 | 18 | 73.5599 | 0 | 73.5599 | 11 | 11.9236 | 0 | 0 | 426.7123 | 0 | 73.5599 | 0 | 7.3523 | 0 | 0 | 0 | 73.5599 | 0 | 0
11 | 13 | 19 | 124.3337 | 0 | 124.3337 | 11 | 13.1107 | 0 | 0 | 408.3246 | 0 | 124.3337 | 0 | 12.4272 | 0 | 0 | 0 | 124.3337 | 0 | 0
11 | 13 | 20 | 109.1859 | 0 | 109.1859 | 11 | 12.6978 | 0 | 0 | 393.4594 | 0 | 109.1859 | 0 | 10.9132 | 0 | 0 | 0 | 109.1859 | 0 | 0
11 | 13 | 21 | 90.8526 | 0 | 90.8526 | 11 | 9.8762 | 1473.6007 | 288 | 379.1573 | 17.7562 | 73.0964 | 6537.0735 | 7.306 | 0 | 0 | 17.7562 | 73.0964 | 0 | 6537.0735
11 | 13 | 22 | 92.6353 | 0 | 92.6353 | 11 | 6.1771 | 50.5477 | 50.5477 | 381.2727 | 92.6353 | 0 | 34300.3341 | 0 | 0 | 0 | 92.6353 | 0 | 0 | 34300.3341
11 | 13 | 23 | 59.014 | 0 | 59.014 | 11 | 4.6373 | 22.964 | 22.964 | 385.7054 | 59.014 | 0 | 22112.8725 | 0 | 0 | 0 | 59.014 | 0 | 0 | 22112.8725
11 | 14 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 391.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 404.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 434.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 452.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 469.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 478.2489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 479.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 7 | 0.016667 | 0 | 0.016667 | 11 | 5.6008 | 0.0079042 | 0.0079042 | 489.0169 | 0.016667 | 0 | 7.9669 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 7.9669
11 | 14 | 8 | 0.2075 | 311.257 | 311.4645 | 47.9754 | 6.5729 | 189.5499 | 189.5499 | 487.8292 | 311.4645 | 0 | 136998.8463 | 0 | 0 | 0 | 311.4645 | 0 | 0 | 136998.8463
11 | 14 | 9 | 4.9483 | 440.2478 | 445.1962 | 47.5887 | 7.7084 | 404.8969 | 288 | 490.8066 | 316.6646 | 128.5316 | 140351.3952 | 12.8468 | 0 | 0 | 316.6646 | 128.5316 | 0 | 140351.3952
11 | 14 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 484.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 484.1207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 485.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 483.6894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 14 | 0.091667 | 0 | 0.091667 | 11 | 10.6934 | 0 | 0 | 488.5676 | 0 | 0.091667 | 0 | 0.0091621 | 0 | 0 | 0 | 0.091667 | 0 | 0
11 | 14 | 15 | 0 | 0 | 0 | 0 | 11.6655 | 0 | 0 | 488.8946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 478.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 489.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 485.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 469.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 442.7205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 417.7875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 409.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 23 | 0.35 | 0 | 0.35 | 11 | 4.5734 | 0.13459 | 0.13459 | 405.4715 | 0.35 | 0 | 138.065 | 0 | 0 | 0 | 0.35 | 0 | 0 | 138.065
11 | 15 | 0 | 7.975 | 0 | 7.975 | 11 | 3.8373 | 2.7008 | 2.7008 | 405.5548 | 7.975 | 0 | 3146.5745 | 0 | 0 | 0 | 7.975 | 0 | 0 | 3146.5745
11 | 15 | 1 | 5.4833 | 0 | 5.4833 | 11 | 3.605 | 1.7896 | 1.7896 | 414.5037 | 5.4833 | 0 | 2212.5454 | 0 | 0 | 0 | 5.4833 | 0 | 0 | 2212.5454
11 | 15 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 434.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 456.5294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 4 | 49.9842 | 0 | 49.9842 | 11 | 3.6222 | 16.3569 | 16.3569 | 479.2562 | 49.9842 | 0 | 23405.4266 | 0 | 0 | 0 | 49.9842 | 0 | 0 | 23405.4266
11 | 15 | 5 | 71.3656 | 0 | 71.3656 | 11 | 4.0351 | 24.9691 | 24.9691 | 486.0988 | 71.3656 | 0 | 33905.702 | 0 | 0 | 0 | 71.3656 | 0 | 0 | 33905.702
11 | 15 | 6 | 83.9678 | 0 | 83.9678 | 11 | 5.1793 | 36.3436 | 36.3436 | 483.6577 | 83.9678 | 0 | 39688.024 | 0 | 0 | 0 | 83.9678 | 0 | 0 | 39688.024
11 | 15 | 7 | 46.1858 | 0 | 46.1858 | 11 | 5.3599 | 20.768 | 20.768 | 485.0627 | 46.1858 | 0 | 21894.951 | 0 | 0 | 0 | 46.1858 | 0 | 0 | 21894.951
11 | 15 | 8 | 40.5943 | 82.9093 | 123.5036 | 35.8385 | 6.5729 | 75.1614 | 75.1614 | 488.0099 | 123.5036 | 0 | 55844.799 | 0 | 0 | 0 | 123.5036 | 0 | 0 | 55844.799
11 | 15 | 9 | 73.0653 | 0.34446 | 73.4097 | 11.1736 | 7.6912 | 66.2682 | 66.2682 | 483.7717 | 73.4097 | 0 | 34693.2942 | 0 | 0 | 0 | 73.4097 | 0 | 0 | 34693.2942
11 | 15 | 10 | 100.6239 | 0.74817 | 101.3721 | 11.2731 | 8.4482 | 136.009 | 136.009 | 481.7716 | 101.3721 | 0 | 47695.4194 | 0 | 0 | 0 | 101.3721 | 0 | 0 | 47695.4194
11 | 15 | 11 | 64.7368 | 0.45387 | 65.1907 | 11.2576 | 9.7214 | 480.0932 | 288 | 475.3013 | 39.1068 | 26.0839 | 18147.2646 | 2.6071 | 0 | 0 | 39.1068 | 26.0839 | 0 | 18147.2646
11 | 15 | 12 | 36.3111 | 0.028208 | 36.3393 | 11.0287 | 9.4117 | 127.9302 | 127.9302 | 467.8631 | 36.3393 | 0 | 16601.0306 | 0 | 0 | 0 | 36.3393 | 0 | 0 | 16601.0306
11 | 15 | 13 | 62.0732 | 35.0626 | 97.1359 | 24.3557 | 8.8869 | 181.4649 | 181.4649 | 463.9073 | 97.1359 | 0 | 42696.2287 | 0 | 0 | 0 | 97.1359 | 0 | 0 | 42696.2287
11 | 15 | 14 | 56.9729 | 13.3605 | 70.3334 | 18.0285 | 9.3428 | 221.869 | 221.869 | 468.0146 | 70.3334 | 0 | 31649.0325 | 0 | 0 | 0 | 70.3334 | 0 | 0 | 31649.0325
11 | 15 | 15 | 77.3952 | 0.017458 | 77.4127 | 11.0083 | 10.0224 | 0 | 0 | 470.4696 | 0 | 77.4127 | 0 | 7.7374 | 0 | 0 | 0 | 77.4127 | 0 | 0
11 | 15 | 16 | 0.77433 | 0 | 0.77433 | 11 | 11.4074 | 0 | 0 | 479.3085 | 0 | 0.77433 | 0 | 0.077395 | 0 | 0 | 0 | 0.77433 | 0 | 0
11 | 15 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 479.9673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 477.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 457.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 423.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 409.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 404.3641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 401.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 400.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 409.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 431.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 444.5479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 464.7102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 477.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 483.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 484.0643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 8 | 40.7056 | 41.7138 | 82.4194 | 29.7263 | 5.4889 | 38.1198 | 38.1198 | 487.3793 | 82.4194 | 0 | 37719.4815 | 0 | 0 | 0 | 82.4194 | 0 | 0 | 37719.4815
11 | 16 | 9 | 0.0575 | 0.14429 | 0.20179 | 37.4569 | 6.9858 | 0.1396 | 0.1396 | 483.0268 | 0.20179 | 0 | 89.9123 | 0 | 0 | 0 | 0.20179 | 0 | 0 | 89.9123
11 | 16 | 10 | 0 | 0.079125 | 0.079125 | 48 | 7.3471 | 0.06218 | 0.06218 | 489.0158 | 0.079125 | 0 | 34.8954 | 0 | 0 | 0 | 0.079125 | 0 | 0 | 34.8954
11 | 16 | 11 | 24.3392 | 0 | 24.3392 | 11 | 8.9643 | 48.8522 | 48.8522 | 485.5296 | 24.3392 | 0 | 11549.6591 | 0 | 0 | 0 | 24.3392 | 0 | 0 | 11549.6591
11 | 16 | 12 | 57.804 | 0 | 57.804 | 11 | 8.2847 | 70.1857 | 70.1857 | 482.3604 | 57.804 | 0 | 27246.5154 | 0 | 0 | 0 | 57.804 | 0 | 0 | 27246.5154
11 | 16 | 13 | 11.7069 | 0 | 11.7069 | 11 | 7.8202 | 11.1922 | 11.1922 | 479.0332 | 11.7069 | 0 | 5479.241 | 0 | 0 | 0 | 11.7069 | 0 | 0 | 5479.241
11 | 16 | 14 | 12.1883 | 0.47687 | 12.6652 | 12.3931 | 7.6568 | 11.2656 | 11.2656 | 472.4428 | 12.6652 | 0 | 5826.6248 | 0 | 0 | 0 | 12.6652 | 0 | 0 | 5826.6248
11 | 16 | 15 | 0 | 0.20237 | 0.20237 | 48 | 7.7256 | 0.18545 | 0.18545 | 483.696 | 0.20237 | 0 | 88.174 | 0 | 0 | 0 | 0.20237 | 0 | 0 | 88.174
11 | 16 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 481.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 484.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 470.579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 451.1045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 20 | 30.1993 | 0 | 30.1993 | 11 | 7.3471 | 23.7321 | 23.7321 | 419.0859 | 30.1993 | 0 | 12323.9235 | 0 | 0 | 0 | 30.1993 | 0 | 0 | 12323.9235
11 | 16 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 411.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 399.8991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 396.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 400.3137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 410.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 415.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 433.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 455.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 5 | 0.46436 | 0 | 0.46436 | 11 | 3.4071 | 0.147 | 0.147 | 462.434 | 0.46436 | 0 | 209.6257 | 0 | 0 | 0 | 0.46436 | 0 | 0 | 209.6257
11 | 17 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 462.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 7 | 34.2414 | 0 | 34.2414 | 11 | 6.5556 | 20.7346 | 20.7346 | 465.4921 | 34.2414 | 0 | 15562.4541 | 0 | 0 | 0 | 34.2414 | 0 | 0 | 15562.4541
11 | 17 | 8 | 0 | 58.4886 | 58.4886 | 48 | 7.2524 | 44.3831 | 44.3831 | 460.4891 | 58.4886 | 0 | 24125.9207 | 0 | 0 | 0 | 58.4886 | 0 | 0 | 24125.9207
11 | 17 | 9 | 8.7813 | 0.26417 | 9.0455 | 12.0806 | 7.6998 | 8.196 | 8.196 | 455.9295 | 9.0455 | 0 | 4014.8173 | 0 | 0 | 0 | 9.0455 | 0 | 0 | 4014.8173
11 | 17 | 10 | 6.6576 | 2.9889 | 9.6466 | 22.4643 | 7.8632 | 9.4077 | 9.4077 | 449.4589 | 9.6466 | 0 | 4119.0356 | 0 | 0 | 0 | 9.6466 | 0 | 0 | 4119.0356
11 | 17 | 11 | 3.4441 | 0 | 3.4441 | 11 | 7.6051 | 2.9976 | 2.9976 | 445.5716 | 3.4441 | 0 | 1496.7188 | 0 | 0 | 0 | 3.4441 | 0 | 0 | 1496.7188
11 | 17 | 12 | 0 | 0.016583 | 0.016583 | 48 | 8.2589 | 0.019838 | 0.019838 | 445.1261 | 0.016583 | 0 | 6.5857 | 0 | 0 | 0 | 0.016583 | 0 | 0 | 6.5857
11 | 17 | 13 | 23.239 | 0.11829 | 23.3573 | 11.1874 | 8.5686 | 33.9656 | 33.9656 | 437.4525 | 23.3573 | 0 | 9956.3824 | 0 | 0 | 0 | 23.3573 | 0 | 0 | 9956.3824
11 | 17 | 14 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 427.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 15 | 0 | 0 | 0 | 0 | 7.803 | 0 | 0 | 441.9813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 449.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 452.1793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 448.2137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 431.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 413.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 388.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 393.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 386.6579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 0 | 2.6206 | 0 | 2.6206 | 11 | 3.9749 | 0.90772 | 0.90772 | 383.3722 | 2.6206 | 0 | 975.8263 | 0 | 0 | 0 | 2.6206 | 0 | 0 | 975.8263
11 | 18 | 1 | 2.6122 | 0 | 2.6122 | 11 | 3.7598 | 0.87366 | 0.87366 | 384.8478 | 2.6122 | 0 | 976.563 | 0 | 0 | 0 | 2.6122 | 0 | 0 | 976.563
11 | 18 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 401.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 402.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 439.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 446.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 442.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 7 | 0 | 90.795 | 90.795 | 48 | 6.3664 | 52.1204 | 52.1204 | 441.8466 | 90.795 | 0 | 35759.2954 | 0 | 0 | 0 | 90.795 | 0 | 0 | 35759.2954
11 | 18 | 8 | 25.1728 | 165.7343 | 190.9071 | 43.1212 | 6.9944 | 132.4484 | 132.4484 | 439.2635 | 190.9071 | 0 | 75626.3813 | 0 | 0 | 0 | 190.9071 | 0 | 0 | 75626.3813
11 | 18 | 9 | 52.825 | 651.4956 | 704.3206 | 45.2249 | 7.5707 | 604.3457 | 288 | 436.6106 | 335.6429 | 368.6777 | 131365.8026 | 36.8494 | 0 | 0 | 335.6429 | 368.6777 | 0 | 131365.8026
11 | 18 | 10 | 60.7475 | 436.4603 | 497.2078 | 43.4794 | 7.4159 | 401.1161 | 288 | 431.6627 | 356.9935 | 140.2143 | 138578.8942 | 14.0145 | 0 | 0 | 356.9935 | 140.2143 | 0 | 138578.8942
11 | 18 | 11 | 57.3467 | 332.0578 | 389.4045 | 42.5511 | 7.5879 | 336.5088 | 288 | 431.6555 | 333.2706 | 56.1339 | 129677.0751 | 5.6106 | 0 | 0 | 333.2706 | 56.1339 | 0 | 129677.0751
11 | 18 | 12 | 32.6933 | 14.7581 | 47.4515 | 22.5076 | 8.3192 | 58.7916 | 58.7916 | 432.7694 | 47.4515 | 0 | 19467.5244 | 0 | 0 | 0 | 47.4515 | 0 | 0 | 19467.5244
11 | 18 | 13 | 14.5974 | 0.42218 | 15.0196 | 12.04 | 8.6546 | 23.2325 | 23.2325 | 430.9668 | 15.0196 | 0 | 6292.1021 | 0 | 0 | 0 | 15.0196 | 0 | 0 | 6292.1021
11 | 18 | 14 | 0.63583 | 76.8806 | 77.5165 | 47.6965 | 8.9299 | 150.6067 | 150.6067 | 422.2011 | 77.5165 | 0 | 29030.2727 | 0 | 0 | 0 | 77.5165 | 0 | 0 | 29030.2727
11 | 18 | 15 | 0 | 2.8888 | 2.8888 | 48 | 8.8009 | 5.0111 | 5.0111 | 435.9625 | 2.8888 | 0 | 1120.7387 | 0 | 0 | 0 | 2.8888 | 0 | 0 | 1120.7387
11 | 18 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 433.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 427.8343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 422.8062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 405.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 390.1331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 375.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 365.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 362.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 360.7583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 363.4292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 369.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 372.5546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 4 | 5.9231 | 0 | 5.9231 | 11 | 3.3469 | 1.8581 | 1.8581 | 383.0416 | 5.9231 | 0 | 2203.6393 | 0 | 0 | 0 | 5.9231 | 0 | 0 | 2203.6393
11 | 19 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 396.6563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 405.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 7 | 0 | 14.616 | 14.616 | 48 | 5.2137 | 6.3717 | 6.3717 | 419.2442 | 14.616 | 0 | 5426.1159 | 0 | 0 | 0 | 14.616 | 0 | 0 | 5426.1159
11 | 19 | 8 | 10.4617 | 270.0521 | 280.5138 | 46.6201 | 5.1879 | 121.6311 | 121.6311 | 405.6057 | 280.5138 | 0 | 100700.4127 | 0 | 0 | 0 | 280.5138 | 0 | 0 | 100700.4127
11 | 19 | 9 | 13.6175 | 298.8863 | 312.5038 | 46.3877 | 6.7449 | 200.2192 | 200.2192 | 404.5873 | 312.5038 | 0 | 111938.7343 | 0 | 0 | 0 | 312.5038 | 0 | 0 | 111938.7343
11 | 19 | 10 | 21.9567 | 61.6659 | 83.6226 | 38.285 | 8.8783 | 155.0272 | 155.0272 | 405.9759 | 83.6226 | 0 | 30747.274 | 0 | 0 | 0 | 83.6226 | 0 | 0 | 30747.274
11 | 19 | 11 | 24.0833 | 91.0694 | 115.1528 | 40.2617 | 9.8676 | 1750.7861 | 288 | 406.5496 | 18.9423 | 96.2104 | 6938.3517 | 9.6163 | 0 | 0 | 18.9423 | 96.2104 | 0 | 6938.3517
11 | 19 | 12 | 18.6267 | 29.6907 | 48.3173 | 33.7362 | 10.2547 | 0 | 0 | 407.5231 | 0 | 48.3173 | 0 | 4.8293 | 0 | 0 | 0 | 48.3173 | 0 | 0
11 | 19 | 13 | 5.7823 | 10.348 | 16.1303 | 34.7365 | 10.031 | 0 | 0 | 407.0339 | 0 | 16.1303 | 0 | 1.6122 | 0 | 0 | 0 | 16.1303 | 0 | 0
11 | 19 | 14 | 2.0233 | 40.1331 | 42.1564 | 46.2242 | 9.9364 | 1284.333 | 288 | 415.7212 | 9.4532 | 32.7032 | 3492.9257 | 3.2687 | 0 | 0 | 9.4532 | 32.7032 | 0 | 3492.9257
11 | 19 | 15 | 0 | 0 | 0 | 0 | 11.1494 | 0 | 0 | 441.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 448.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 448.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 447.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 440.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 419.8416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 403.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 398.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 397.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 395.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 404.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 413.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 422.7958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 431.9251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 454.4189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 468.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 7 | 0.3375 | 113.512 | 113.8495 | 47.8903 | 5.1706 | 49.1896 | 49.1896 | 466.2952 | 113.8495 | 0 | 47635.1783 | 0 | 0 | 0 | 113.8495 | 0 | 0 | 47635.1783
11 | 20 | 8 | 1.8433 | 280.8293 | 282.6726 | 47.7587 | 5.8502 | 142.1081 | 142.1081 | 470.9904 | 282.6726 | 0 | 119636.0108 | 0 | 0 | 0 | 282.6726 | 0 | 0 | 119636.0108
11 | 20 | 9 | 0.93833 | 36.8758 | 37.8141 | 47.0819 | 6.7707 | 24.4206 | 24.4206 | 469.4583 | 37.8141 | 0 | 15971.7875 | 0 | 0 | 0 | 37.8141 | 0 | 0 | 15971.7875
11 | 20 | 10 | 0.074167 | 0.024958 | 0.099125 | 20.3161 | 8.9987 | 0.20576 | 0.20576 | 467.0824 | 0.099125 | 0 | 44.2857 | 0 | 0 | 0 | 0.099125 | 0 | 0 | 44.2857
11 | 20 | 11 | 3.979 | 0 | 3.979 | 11 | 10.0569 | 0 | 0 | 465.8128 | 0 | 3.979 | 0 | 0.39771 | 0 | 0 | 0 | 3.979 | 0 | 0
11 | 20 | 12 | 12.6535 | 0.898 | 13.5515 | 13.4518 | 10.1343 | 0 | 0 | 473.2688 | 0 | 13.5515 | 0 | 1.3545 | 0 | 0 | 0 | 13.5515 | 0 | 0
11 | 20 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 477.8256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 481.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 15 | 0 | 0.33238 | 0.33238 | 48 | 10.9601 | 0 | 0 | 490.8893 | 0 | 0.33238 | 0 | 0.033221 | 0 | 0 | 0 | 0.33238 | 0 | 0
11 | 20 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 498.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 507.9513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 507.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 496.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 483.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 470.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 465.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 461.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 467.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 474.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 477.6999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 483.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 504.9342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 510.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 517.2614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 521.4369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 515.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 9 | 0 | 0 | 0 | 0 | 7.7084 | 0 | 0 | 514.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 10 | 0 | 0 | 0 | 0 | 8.9471 | 0 | 0 | 510.0888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 11 | 0 | 0 | 0 | 0 | 9.5923 | 0 | 0 | 501.8474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 12 | 0 | 0 | 0 | 0 | 10.2891 | 0 | 0 | 501.7708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 13 | 0 | 0 | 0 | 0 | 10.0827 | 0 | 0 | 505.2922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 14 | 0 | 0.70652 | 0.70652 | 48 | 10.6934 | 0 | 0 | 499.6062 | 0 | 0.70652 | 0 | 0.070616 | 0 | 0 | 0 | 0.70652 | 0 | 0
11 | 21 | 15 | 0.058449 | 0.85575 | 0.9142 | 45.6344 | 11.6655 | 0 | 0 | 511.7548 | 0 | 0.9142 | 0 | 0.091374 | 0 | 0 | 0 | 0.9142 | 0 | 0
11 | 21 | 16 | 25.5905 | 0 | 25.5905 | 11 | 12.3021 | 0 | 0 | 512.0612 | 0 | 25.5905 | 0 | 2.5578 | 0 | 0 | 0 | 25.5905 | 0 | 0
11 | 21 | 17 | 0.275 | 0 | 0.275 | 11 | 12.1989 | 0 | 0 | 517.6455 | 0 | 0.275 | 0 | 0.027486 | 0 | 0 | 0 | 0.275 | 0 | 0
11 | 21 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 521.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 515.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 497.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 21 | 0.10833 | 0 | 0.10833 | 11 | 10.3235 | 0 | 0 | 480.4748 | 0 | 0.10833 | 0 | 0.010828 | 0 | 0 | 0 | 0.10833 | 0 | 0
11 | 21 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 473.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 468.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 467.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 480.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 496.6134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 3 | 77.0927 | 0 | 77.0927 | 11 | 3.4416 | 24.5336 | 24.5336 | 496.1053 | 77.0927 | 0 | 37398.0653 | 0 | 0 | 0 | 77.0927 | 0 | 0 | 37398.0653
11 | 22 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 501.2229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 501.4726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 505.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 509.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 8 | 0 | 1.674 | 1.674 | 48 | 6.5729 | 1.0188 | 1.0188 | 506.4336 | 1.674 | 0 | 767.4132 | 0 | 0 | 0 | 1.674 | 0 | 0 | 767.4132
11 | 22 | 9 | 0 | 0.43668 | 0.43668 | 48 | 7.6912 | 0.3942 | 0.3942 | 503.3597 | 0.43668 | 0 | 198.8474 | 0 | 0 | 0 | 0.43668 | 0 | 0 | 198.8474
11 | 22 | 10 | 0 | 0.0074583 | 0.0074583 | 48 | 8.4482 | 0.010007 | 0.010007 | 496.4615 | 0.0074583 | 0 | 3.3448 | 0 | 0 | 0 | 0.0074583 | 0 | 0 | 3.3448
11 | 22 | 11 | 0.75462 | 0.56375 | 1.3184 | 26.8216 | 9.7214 | 9.7091 | 9.7091 | 493.9455 | 1.3184 | 0 | 615.8415 | 0 | 0 | 0 | 1.3184 | 0 | 0 | 615.8415
11 | 22 | 12 | 12.7127 | 0.021583 | 12.7342 | 11.0627 | 9.4117 | 44.8301 | 44.8301 | 495.4526 | 12.7342 | 0 | 6168.335 | 0 | 0 | 0 | 12.7342 | 0 | 0 | 6168.335
11 | 22 | 13 | 0 | 0.063042 | 0.063042 | 48 | 8.8869 | 0.11777 | 0.11777 | 500.379 | 0.063042 | 0 | 28.5187 | 0 | 0 | 0 | 0.063042 | 0 | 0 | 28.5187
11 | 22 | 14 | 0 | 0.45196 | 0.45196 | 48 | 9.3428 | 1.4257 | 1.4257 | 492.4976 | 0.45196 | 0 | 200.8944 | 0 | 0 | 0 | 0.45196 | 0 | 0 | 200.8944
11 | 22 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 499.6724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 500.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 503.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 506.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 504.0771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 484.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 477.9343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 476.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 469.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 467.9796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 478.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 481.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 480.9998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 494.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 500.5608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 503.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 7 | 0 | 31.2532 | 31.2532 | 48 | 4.99 | 13.0168 | 13.0168 | 509.5381 | 31.2532 | 0 | 14424.5448 | 0 | 0 | 0 | 31.2532 | 0 | 0 | 14424.5448
11 | 23 | 8 | 0.44333 | 21.8565 | 22.2999 | 47.2644 | 5.4889 | 10.3139 | 10.3139 | 517.0869 | 22.2999 | 0 | 10476.9855 | 0 | 0 | 0 | 22.2999 | 0 | 0 | 10476.9855
11 | 23 | 9 | 0.625 | 42.4374 | 43.0624 | 47.463 | 6.9858 | 29.7909 | 29.7909 | 514.6127 | 43.0624 | 0 | 20116.6 | 0 | 0 | 0 | 43.0624 | 0 | 0 | 20116.6
11 | 23 | 10 | 0.11083 | 54.3342 | 54.445 | 47.9247 | 7.3471 | 42.7856 | 42.7856 | 515.6334 | 54.445 | 0 | 25464.4198 | 0 | 0 | 0 | 54.445 | 0 | 0 | 25464.4198
11 | 23 | 11 | 0 | 0.41171 | 0.41171 | 48 | 8.9643 | 0.82636 | 0.82636 | 511.1011 | 0.41171 | 0 | 190.6626 | 0 | 0 | 0 | 0.41171 | 0 | 0 | 190.6626
11 | 23 | 12 | 0 | 0 | 0 | 0 | 8.2847 | 0 | 0 | 514.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 13 | 0 | 18.9129 | 18.9129 | 48 | 7.8202 | 18.0814 | 18.0814 | 514.0964 | 18.9129 | 0 | 8815.2555 | 0 | 0 | 0 | 18.9129 | 0 | 0 | 8815.2555
11 | 23 | 14 | 0 | 20.5777 | 20.5777 | 48 | 7.6568 | 18.3036 | 18.3036 | 508.5589 | 20.5777 | 0 | 9477.2305 | 0 | 0 | 0 | 20.5777 | 0 | 0 | 9477.2305
11 | 23 | 15 | 0 | 0.66629 | 0.66629 | 48 | 7.7256 | 0.61055 | 0.61055 | 515.1333 | 0.66629 | 0 | 311.247 | 0 | 0 | 0 | 0.66629 | 0 | 0 | 311.247
11 | 23 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 518.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 501.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 498.6069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 476.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 452.3935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 433.583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 421.1651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 408.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 406.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 404.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 403.8351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 408.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 4 | 35.7305 | 0 | 35.7305 | 11 | 3.2609 | 11.0661 | 11.0661 | 419.3936 | 35.7305 | 0 | 14592.0917 | 0 | 0 | 0 | 35.7305 | 0 | 0 | 14592.0917
11 | 24 | 5 | 39.4295 | 0 | 39.4295 | 11 | 3.4071 | 12.4824 | 12.4824 | 444.7109 | 39.4295 | 0 | 17100.995 | 0 | 0 | 0 | 39.4295 | 0 | 0 | 17100.995
11 | 24 | 6 | 19.1771 | 0 | 19.1771 | 11 | 4.9556 | 7.9327 | 7.9327 | 461.6616 | 19.1771 | 0 | 8642.3977 | 0 | 0 | 0 | 19.1771 | 0 | 0 | 8642.3977
11 | 24 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 477.4371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 8 | 31.6543 | 6.1515 | 37.8058 | 17.0204 | 7.2524 | 28.6883 | 28.6883 | 484.1084 | 37.8058 | 0 | 17658.6312 | 0 | 0 | 0 | 37.8058 | 0 | 0 | 17658.6312
11 | 24 | 9 | 36.723 | 176.4727 | 213.1956 | 41.6267 | 7.6998 | 193.1735 | 193.1735 | 477.4262 | 213.1956 | 0 | 92910.5486 | 0 | 0 | 0 | 213.1956 | 0 | 0 | 92910.5486
11 | 24 | 10 | 139.9327 | 414.5668 | 554.4995 | 38.6627 | 7.8632 | 540.7663 | 288 | 459.0543 | 295.314 | 259.1855 | 124147.5076 | 25.9057 | 0 | 0 | 295.314 | 259.1855 | 0 | 124147.5076
11 | 24 | 11 | 60.076 | 188.7309 | 248.8069 | 39.0661 | 7.6051 | 216.5511 | 216.5511 | 448.608 | 248.8069 | 0 | 101896.8349 | 0 | 0 | 0 | 248.8069 | 0 | 0 | 101896.8349
11 | 24 | 12 | 124.9134 | 319.0207 | 443.9341 | 37.589 | 8.2589 | 531.0584 | 288 | 437.8429 | 240.7514 | 203.1828 | 96361.6616 | 20.3082 | 0 | 0 | 240.7514 | 203.1828 | 0 | 96361.6616
11 | 24 | 13 | 75.5587 | 793.6518 | 869.2105 | 44.7837 | 8.5686 | 1263.986 | 288 | 426.9197 | 198.0502 | 671.1603 | 75682.0964 | 67.0827 | 0 | 0 | 198.0502 | 671.1603 | 0 | 75682.0964
11 | 24 | 14 | 30.3166 | 95.3464 | 125.663 | 39.0736 | 8.6374 | 191.9323 | 191.9323 | 425.9185 | 125.663 | 0 | 48612.103 | 0 | 0 | 0 | 125.663 | 0 | 0 | 48612.103
11 | 24 | 15 | 6.7876 | 0.11408 | 6.9017 | 11.6116 | 7.803 | 6.5467 | 6.5467 | 426.2592 | 6.9017 | 0 | 2861.7582 | 0 | 0 | 0 | 6.9017 | 0 | 0 | 2861.7582
11 | 24 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 426.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 422.9635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 431.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 436.1671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 421.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 410.5503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 22 | 96.9837 | 0 | 96.9837 | 11 | 5.0846 | 41.17 | 41.17 | 408.1174 | 96.9837 | 0 | 38513.8909 | 0 | 0 | 0 | 96.9837 | 0 | 0 | 38513.8909
11 | 24 | 23 | 44.0851 | 0 | 44.0851 | 11 | 4.4566 | 16.5961 | 16.5961 | 403.6714 | 44.0851 | 0 | 17310.9463 | 0 | 0 | 0 | 44.0851 | 0 | 0 | 17310.9463
11 | 25 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 403.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 406.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 414.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 420.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 440.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 5 | 25.8171 | 0 | 25.8171 | 11 | 3.691 | 8.5405 | 8.5405 | 451.0027 | 25.8171 | 0 | 11359.5796 | 0 | 0 | 0 | 25.8171 | 0 | 0 | 11359.5796
11 | 25 | 6 | 14.3376 | 0 | 14.3376 | 11 | 4.8007 | 5.7544 | 5.7544 | 467.7519 | 14.3376 | 0 | 6548.7475 | 0 | 0 | 0 | 14.3376 | 0 | 0 | 6548.7475
11 | 25 | 7 | 1.1657 | 0 | 1.1657 | 11 | 6.3664 | 0.66919 | 0.66919 | 475.4537 | 1.1657 | 0 | 541.4319 | 0 | 0 | 0 | 1.1657 | 0 | 0 | 541.4319
11 | 25 | 8 | 18.4298 | 3.4164 | 21.8461 | 16.7861 | 6.9944 | 15.1565 | 15.1565 | 471.195 | 21.8461 | 0 | 9927.0834 | 0 | 0 | 0 | 21.8461 | 0 | 0 | 9927.0834
11 | 25 | 9 | 19.4609 | 54.4733 | 73.9342 | 38.2609 | 7.5707 | 63.4396 | 63.4396 | 465.9562 | 73.9342 | 0 | 31621.3098 | 0 | 0 | 0 | 73.9342 | 0 | 0 | 31621.3098
11 | 25 | 10 | 26.7965 | 48.3734 | 75.17 | 34.8103 | 7.4159 | 60.6424 | 60.6424 | 458.841 | 75.17 | 0 | 31874.3828 | 0 | 0 | 0 | 75.17 | 0 | 0 | 31874.3828
11 | 25 | 11 | 104.4244 | 30.5876 | 135.012 | 19.3825 | 7.5879 | 116.6723 | 116.6723 | 454.7003 | 135.012 | 0 | 58773.132 | 0 | 0 | 0 | 135.012 | 0 | 0 | 58773.132
11 | 25 | 12 | 165.9773 | 46.2719 | 212.2492 | 19.0663 | 8.3192 | 262.9735 | 262.9735 | 453.1236 | 212.2492 | 0 | 92128.3106 | 0 | 0 | 0 | 212.2492 | 0 | 0 | 92128.3106
11 | 25 | 13 | 137.9503 | 62.561 | 200.5113 | 22.5443 | 8.6546 | 310.1544 | 288 | 461.3271 | 186.1887 | 14.3226 | 81696.416 | 1.4315 | 0 | 0 | 186.1887 | 14.3226 | 0 | 81696.416
11 | 25 | 14 | 201.62 | 41.0705 | 242.6904 | 17.2615 | 8.9299 | 471.523 | 288 | 469.6466 | 148.2321 | 94.4583 | 67057.9853 | 9.4411 | 0 | 0 | 148.2321 | 94.4583 | 0 | 67057.9853
11 | 25 | 15 | 199.5567 | 13.6824 | 213.239 | 13.3741 | 8.8009 | 369.9028 | 288 | 475.8972 | 166.0243 | 47.2148 | 76790.0591 | 4.7191 | 0 | 0 | 166.0243 | 47.2148 | 0 | 76790.0591
11 | 25 | 16 | 199.9007 | 0 | 199.9007 | 11 | 9.5837 | 991.1558 | 288 | 471.2553 | 58.0851 | 141.8156 | 26733.9786 | 14.1745 | 0 | 0 | 58.0851 | 141.8156 | 0 | 26733.9786
11 | 25 | 17 | 199.4273 | 0 | 199.4273 | 11 | 9.0762 | 448.4746 | 288 | 467.3655 | 128.0676 | 71.3597 | 58445.6517 | 7.1324 | 0 | 0 | 128.0676 | 71.3597 | 0 | 58445.6517
11 | 25 | 18 | 162.7195 | 0 | 162.7195 | 11 | 9.4461 | 608.1122 | 288 | 465.0194 | 77.0634 | 85.656 | 34988.2879 | 8.5613 | 0 | 0 | 77.0634 | 85.656 | 0 | 34988.2879
11 | 25 | 19 | 124.5054 | 0 | 124.5054 | 11 | 8.0611 | 133.7805 | 133.7805 | 453.7241 | 124.5054 | 0 | 55121.5297 | 0 | 0 | 0 | 124.5054 | 0 | 0 | 55121.5297
11 | 25 | 20 | 130.237 | 0 | 130.237 | 11 | 11.2698 | 0 | 0 | 437.1364 | 0 | 130.237 | 0 | 13.0172 | 0 | 0 | 0 | 130.237 | 0 | 0
11 | 25 | 21 | 103.7199 | 0 | 103.7199 | 11 | 9.1708 | 259.7054 | 259.7054 | 413.5416 | 103.7199 | 0 | 41751.5694 | 0 | 0 | 0 | 103.7199 | 0 | 0 | 41751.5694
11 | 25 | 22 | 24.2243 | 0 | 24.2243 | 11 | 5.4717 | 11.1615 | 11.1615 | 401.1944 | 24.2243 | 0 | 9452.2046 | 0 | 0 | 0 | 24.2243 | 0 | 0 | 9452.2046
11 | 25 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 395.5512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 0 | 42.0098 | 0 | 42.0098 | 11 | 3.3125 | 13.1112 | 13.1112 | 395.8696 | 42.0098 | 0 | 16168.2916 | 0 | 0 | 0 | 42.0098 | 0 | 0 | 16168.2916
11 | 26 | 1 | 3.437 | 0 | 3.437 | 11 | 3.2007 | 1.055 | 1.055 | 396.7549 | 3.437 | 0 | 1325.8324 | 0 | 0 | 0 | 3.437 | 0 | 0 | 1325.8324
11 | 26 | 2 | 12.9724 | 0 | 12.9724 | 11 | 3.1921 | 3.9771 | 3.9771 | 406.9503 | 12.9724 | 0 | 5136.4197 | 0 | 0 | 0 | 12.9724 | 0 | 0 | 5136.4197
11 | 26 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 419.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 426.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 445.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 455.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 460.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 8 | 1.2825 | 49.8485 | 51.131 | 47.0719 | 5.1879 | 22.1705 | 22.1705 | 461.8933 | 51.131 | 0 | 21210.2269 | 0 | 0 | 0 | 51.131 | 0 | 0 | 21210.2269
11 | 26 | 9 | 2.9725 | 208.0222 | 210.9947 | 47.4787 | 6.7449 | 135.1829 | 135.1829 | 460.2435 | 210.9947 | 0 | 87091.1678 | 0 | 0 | 0 | 210.9947 | 0 | 0 | 87091.1678
11 | 26 | 10 | 6.145 | 263.841 | 269.986 | 47.1579 | 8.8783 | 500.5246 | 288 | 447.764 | 155.349 | 114.6371 | 62233.7487 | 11.458 | 0 | 0 | 155.349 | 114.6371 | 0 | 62233.7487
11 | 26 | 11 | 5.8892 | 158.1322 | 164.0213 | 46.6715 | 9.8676 | 2493.7853 | 288 | 435.3587 | 18.9423 | 145.079 | 7362.6463 | 14.5007 | 0 | 0 | 18.9423 | 145.079 | 0 | 7362.6463
11 | 26 | 12 | 3.2408 | 213.9174 | 217.1582 | 47.4478 | 10.2547 | 0 | 0 | 427.8729 | 0 | 217.1582 | 0 | 21.705 | 0 | 0 | 0 | 217.1582 | 0 | 0
11 | 26 | 13 | 3.1758 | 293.028 | 296.2038 | 47.6033 | 10.031 | 0 | 0 | 438.4621 | 0 | 296.2038 | 0 | 29.6057 | 0 | 0 | 0 | 296.2038 | 0 | 0
11 | 26 | 14 | 1.16 | 62.8456 | 64.0056 | 47.3294 | 9.9364 | 1949.9886 | 288 | 448.4622 | 9.4532 | 54.5524 | 3791.9837 | 5.4525 | 0 | 0 | 9.4532 | 54.5524 | 0 | 3791.9837
11 | 26 | 15 | 0 | 23.2863 | 23.2863 | 48 | 11.1494 | 0 | 0 | 457.64 | 0 | 23.2863 | 0 | 2.3275 | 0 | 0 | 0 | 23.2863 | 0 | 0
11 | 26 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 457.2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 459.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 462.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 452.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 433.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 428.7384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 22 | 2.0378 | 0 | 2.0378 | 11 | 5.3857 | 0.92145 | 0.92145 | 417.7325 | 2.0378 | 0 | 828.8467 | 0 | 0 | 0 | 2.0378 | 0 | 0 | 828.8467
11 | 26 | 23 | 30.9377 | 0 | 30.9377 | 11 | 3.6704 | 10.2012 | 10.2012 | 413.9248 | 30.9377 | 0 | 12465.5752 | 0 | 0 | 0 | 30.9377 | 0 | 0 | 12465.5752
11 | 27 | 0 | 30.0035 | 0 | 30.0035 | 11 | 3.5706 | 9.7396 | 9.7396 | 420.2584 | 30.0035 | 0 | 12279.1973 | 0 | 0 | 0 | 30.0035 | 0 | 0 | 12279.1973
11 | 27 | 1 | 1.3812 | 0 | 1.3812 | 11 | 3.4588 | 0.44071 | 0.44071 | 419.7711 | 1.3812 | 0 | 564.603 | 0 | 0 | 0 | 1.3812 | 0 | 0 | 564.603
11 | 27 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 425.4236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 430.7498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 447.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 453.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 456.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 454.0162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 444.9849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 9 | 0 | 16.7016 | 16.7016 | 48 | 6.7707 | 10.786 | 10.786 | 440.7414 | 16.7016 | 0 | 6559.4062 | 0 | 0 | 0 | 16.7016 | 0 | 0 | 6559.4062
11 | 27 | 10 | 0 | 17.8494 | 17.8494 | 48 | 8.9987 | 37.0515 | 37.0515 | 430.983 | 17.8494 | 0 | 6836.026 | 0 | 0 | 0 | 17.8494 | 0 | 0 | 6836.026
11 | 27 | 11 | 0 | 11.5464 | 11.5464 | 48 | 10.0569 | 0 | 0 | 429.1541 | 0 | 11.5464 | 0 | 1.1541 | 0 | 0 | 0 | 11.5464 | 0 | 0
11 | 27 | 12 | 0 | 3.1201 | 3.1201 | 48 | 10.1343 | 0 | 0 | 431.6084 | 0 | 3.1201 | 0 | 0.31185 | 0 | 0 | 0 | 3.1201 | 0 | 0
11 | 27 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 437.5319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 14 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 446.4098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 15 | 0 | 1.3587 | 1.3587 | 48 | 10.9601 | 0 | 0 | 454.3109 | 0 | 1.3587 | 0 | 0.13581 | 0 | 0 | 0 | 1.3587 | 0 | 0
11 | 27 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 459.9559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 463.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 467.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 449.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 429.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 405.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 397.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 397.1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 0 | 8.1409 | 0 | 8.1409 | 11 | 3.9577 | 2.8118 | 2.8118 | 403.1865 | 8.1409 | 0 | 3192.744 | 0 | 0 | 0 | 8.1409 | 0 | 0 | 3192.744
11 | 28 | 1 | 21.8448 | 0 | 21.8448 | 11 | 3.6394 | 7.1678 | 7.1678 | 412.0369 | 21.8448 | 0 | 8760.5572 | 0 | 0 | 0 | 21.8448 | 0 | 0 | 8760.5572
11 | 28 | 2 | 21.2271 | 0 | 21.2271 | 11 | 3.5276 | 6.8449 | 6.8449 | 426.0665 | 21.2271 | 0 | 8810.6523 | 0 | 0 | 0 | 21.2271 | 0 | 0 | 8810.6523
11 | 28 | 3 | 50 | 0 | 50 | 11 | 3.562 | 16.2092 | 16.2092 | 438.2711 | 50 | 0 | 21363.557 | 0 | 0 | 0 | 50 | 0 | 0 | 21363.557
11 | 28 | 4 | 15.153 | 0 | 15.153 | 11 | 3.5878 | 4.9321 | 4.9321 | 450.9568 | 15.153 | 0 | 6666.6749 | 0 | 0 | 0 | 15.153 | 0 | 0 | 6666.6749
11 | 28 | 5 | 35.114 | 0 | 35.114 | 11 | 4.1814 | 12.5941 | 12.5941 | 455.0033 | 35.114 | 0 | 15590.7295 | 0 | 0 | 0 | 35.114 | 0 | 0 | 15590.7295
11 | 28 | 6 | 47.8661 | 0 | 47.8661 | 11 | 5.3513 | 21.4838 | 21.4838 | 460.9917 | 47.8661 | 0 | 21539.3631 | 0 | 0 | 0 | 47.8661 | 0 | 0 | 21539.3631
11 | 28 | 7 | 71.7339 | 0 | 71.7339 | 11 | 5.6008 | 34.02 | 34.02 | 463.428 | 71.7339 | 0 | 32454.4114 | 0 | 0 | 0 | 71.7339 | 0 | 0 | 32454.4114
11 | 28 | 8 | 15.5478 | 0 | 15.5478 | 11 | 6.5729 | 9.462 | 9.462 | 465.9798 | 15.5478 | 0 | 7073.9127 | 0 | 0 | 0 | 15.5478 | 0 | 0 | 7073.9127
11 | 28 | 9 | 202.9661 | 0 | 202.9661 | 11 | 7.7084 | 184.5936 | 184.5936 | 469.7442 | 202.9661 | 0 | 93109.5344 | 0 | 0 | 0 | 202.9661 | 0 | 0 | 93109.5344
11 | 28 | 10 | 128.4666 | 0 | 128.4666 | 11 | 8.9471 | 253.6572 | 253.6572 | 462.0147 | 128.4666 | 0 | 57940.3222 | 0 | 0 | 0 | 128.4666 | 0 | 0 | 57940.3222
11 | 28 | 11 | 135.5467 | 0 | 135.5467 | 11 | 9.5923 | 686.0837 | 288 | 461.8004 | 56.899 | 78.6477 | 25650.0785 | 7.8609 | 0 | 0 | 56.899 | 78.6477 | 0 | 25650.0785
11 | 28 | 12 | 125.6171 | 0.52806 | 126.1452 | 11.1549 | 10.2891 | 0 | 0 | 457.9795 | 0 | 126.1452 | 0 | 12.6082 | 0 | 0 | 0 | 126.1452 | 0 | 0
11 | 28 | 13 | 89.9443 | 1.219 | 91.1633 | 11.4947 | 10.0827 | 0 | 0 | 458.1912 | 0 | 91.1633 | 0 | 9.1118 | 0 | 0 | 0 | 91.1633 | 0 | 0
11 | 28 | 14 | 32.3796 | 10.8435 | 43.2231 | 20.2823 | 10.6934 | 0 | 0 | 451.2486 | 0 | 43.2231 | 0 | 4.3202 | 0 | 0 | 0 | 43.2231 | 0 | 0
11 | 28 | 15 | 1.2999 | 1.5601 | 2.86 | 31.1832 | 11.6655 | 0 | 0 | 455.3195 | 0 | 2.86 | 0 | 0.28586 | 0 | 0 | 0 | 2.86 | 0 | 0
11 | 28 | 16 | 0 | 0.33283 | 0.33283 | 48 | 12.3021 | 0 | 0 | 462.5798 | 0 | 0.33283 | 0 | 0.033267 | 0 | 0 | 0 | 0.33283 | 0 | 0
11 | 28 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 464.2626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 18 | 0.7089 | 0 | 0.7089 | 11 | 12.9559 | 0 | 0 | 461.9151 | 0 | 0.7089 | 0 | 0.070854 | 0 | 0 | 0 | 0.7089 | 0 | 0
11 | 28 | 19 | 4.0554 | 0 | 4.0554 | 11 | 13.2054 | 0 | 0 | 437.3318 | 0 | 4.0554 | 0 | 0.40534 | 0 | 0 | 0 | 4.0554 | 0 | 0
11 | 28 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 411.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 21 | 2.8415 | 0 | 2.8415 | 11 | 10.3235 | 0 | 0 | 398.8104 | 0 | 2.8415 | 0 | 0.28401 | 0 | 0 | 0 | 2.8415 | 0 | 0
11 | 28 | 22 | 7.3731 | 0 | 7.3731 | 11 | 5.6868 | 3.5664 | 3.5664 | 392.2922 | 7.3731 | 0 | 2811.2979 | 0 | 0 | 0 | 7.3731 | 0 | 0 | 2811.2979
11 | 28 | 23 | 61.3288 | 0 | 61.3288 | 11 | 4.5734 | 23.584 | 23.584 | 385.4932 | 61.3288 | 0 | 22967.2052 | 0 | 0 | 0 | 61.3288 | 0 | 0 | 22967.2052
11 | 29 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 382.3571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 399.1701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 401.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 420.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 446.7285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 458.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 457.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 466.6404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 479.2204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 9 | 0 | 1.13 | 1.13 | 48 | 7.6912 | 1.02 | 1.02 | 479.4429 | 1.13 | 0 | 487.517 | 0 | 0 | 0 | 1.13 | 0 | 0 | 487.517
11 | 29 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 474.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 11 | 0 | 0 | 0 | 0 | 9.7214 | 0 | 0 | 469.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 12 | 0 | 0 | 0 | 0 | 9.4117 | 0 | 0 | 472.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 473.2289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 462.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 458.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 466.1936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 468.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 471.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 461.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 430.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 414.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 398.098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 396.8682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 396.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 1 | 40.7235 | 0 | 40.7235 | 11 | 4.2072 | 14.671 | 14.671 | 402.5241 | 40.7235 | 0 | 15944.247 | 0 | 0 | 0 | 40.7235 | 0 | 0 | 15944.247
11 | 30 | 2 | 94.3966 | 0 | 94.3966 | 11 | 4.147 | 33.6576 | 33.6576 | 420.8157 | 94.3966 | 0 | 38685.2138 | 0 | 0 | 0 | 94.3966 | 0 | 0 | 38685.2138
11 | 30 | 3 | 147.2304 | 0 | 147.2304 | 11 | 3.7857 | 49.4461 | 49.4461 | 443.4854 | 147.2304 | 0 | 63675.0041 | 0 | 0 | 0 | 147.2304 | 0 | 0 | 63675.0041
11 | 30 | 4 | 94.4742 | 0 | 94.4742 | 11 | 3.7254 | 31.4241 | 31.4241 | 469.5484 | 94.4742 | 0 | 43320.9925 | 0 | 0 | 0 | 94.4742 | 0 | 0 | 43320.9925
11 | 30 | 5 | 104.6604 | 0 | 104.6604 | 11 | 3.9663 | 36.2009 | 36.2009 | 476.0325 | 104.6604 | 0 | 48670.4677 | 0 | 0 | 0 | 104.6604 | 0 | 0 | 48670.4677
11 | 30 | 6 | 48.1204 | 0 | 48.1204 | 11 | 4.7319 | 19.061 | 19.061 | 481.9531 | 48.1204 | 0 | 22662.4311 | 0 | 0 | 0 | 48.1204 | 0 | 0 | 22662.4311
11 | 30 | 7 | 0 | 2.0417 | 2.0417 | 48 | 4.99 | 0.85034 | 0.85034 | 486.1986 | 2.0417 | 0 | 894.6484 | 0 | 0 | 0 | 2.0417 | 0 | 0 | 894.6484
11 | 30 | 8 | 43.2153 | 259.2985 | 302.5137 | 42.7144 | 5.4889 | 139.9155 | 139.9155 | 486.4147 | 302.5137 | 0 | 134225.4103 | 0 | 0 | 0 | 302.5137 | 0 | 0 | 134225.4103
11 | 30 | 9 | 4.9014 | 415.051 | 419.9524 | 47.5682 | 6.9858 | 290.5263 | 288 | 480.3981 | 416.3007 | 3.6517 | 180187.4019 | 0.36499 | 0 | 0 | 416.3007 | 3.6517 | 0 | 180187.4019
11 | 30 | 10 | 60.6531 | 403.0367 | 463.6898 | 43.1602 | 7.3471 | 364.3901 | 288 | 482.9319 | 366.4827 | 97.2071 | 161168.7186 | 9.7159 | 0 | 0 | 366.4827 | 97.2071 | 0 | 161168.7186
11 | 30 | 11 | 108.7113 | 471.1773 | 579.8885 | 41.0636 | 8.9643 | 1163.9194 | 288 | 479.6269 | 143.4875 | 436.401 | 62928.3513 | 43.6184 | 0 | 0 | 143.4875 | 436.401 | 0 | 62928.3513
11 | 30 | 12 | 92.2569 | 516.0545 | 608.3114 | 42.3886 | 8.2847 | 738.6126 | 288 | 476.4106 | 237.1929 | 371.1185 | 102946.9476 | 37.0934 | 0 | 0 | 237.1929 | 371.1185 | 0 | 102946.9476
11 | 30 | 13 | 59.2513 | 465.355 | 524.6064 | 43.8211 | 7.8202 | 501.5412 | 288 | 474.9641 | 301.2447 | 223.3617 | 129879.5542 | 22.3251 | 0 | 0 | 301.2447 | 223.3617 | 0 | 129879.5542
11 | 30 | 14 | 21.4668 | 240.2471 | 261.7139 | 44.9651 | 7.6568 | 232.7916 | 232.7916 | 467.9189 | 261.7139 | 0 | 110692.8859 | 0 | 0 | 0 | 261.7139 | 0 | 0 | 110692.8859
11 | 30 | 15 | 14.1335 | 86.8592 | 100.9926 | 42.822 | 7.7256 | 92.544 | 92.544 | 468.8567 | 100.9926 | 0 | 43026.3655 | 0 | 0 | 0 | 100.9926 | 0 | 0 | 43026.3655
11 | 30 | 16 | 5.8199 | 2.2208 | 8.0408 | 21.2193 | 7.3729 | 6.3808 | 6.3808 | 471.8392 | 8.0408 | 0 | 3623.3328 | 0 | 0 | 0 | 8.0408 | 0 | 0 | 3623.3328
11 | 30 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 476.6626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 479.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 451.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 419.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 403.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 394.6374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 23 | 0.033333 | 0 | 0.033333 | 11 | 4.5954 | 0.012871 | 0.012871 | 390.3939 | 0.033333 | 0 | 12.6465 | 0 | 0 | 0 | 0.033333 | 0 | 0 | 12.6465
12 | 1 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 392.3247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 394.6624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 407.0891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 3 | 87.7652 | 0 | 87.7652 | 11 | 3.3039 | 27.3563 | 27.3563 | 423.9221 | 87.7652 | 0 | 36240.2078 | 0 | 0 | 0 | 87.7652 | 0 | 0 | 36240.2078
12 | 1 | 4 | 115.4848 | 0 | 115.4848 | 11 | 3.2609 | 35.7668 | 35.7668 | 453.3997 | 115.4848 | 0 | 51090.4294 | 0 | 0 | 0 | 115.4848 | 0 | 0 | 51090.4294
12 | 1 | 5 | 100.1618 | 0 | 100.1618 | 11 | 3.4071 | 31.7087 | 31.7087 | 465.8957 | 100.1618 | 0 | 45563.153 | 0 | 0 | 0 | 100.1618 | 0 | 0 | 45563.153
12 | 1 | 6 | 108.812 | 0 | 108.812 | 11 | 4.9556 | 45.0107 | 45.0107 | 466.8912 | 108.812 | 0 | 49606.4389 | 0 | 0 | 0 | 108.812 | 0 | 0 | 49606.4389
12 | 1 | 7 | 158.8391 | 89.4871 | 248.3263 | 24.3334 | 6.5556 | 150.3717 | 150.3717 | 468.6706 | 248.3263 | 0 | 110340.5979 | 0 | 0 | 0 | 248.3263 | 0 | 0 | 110340.5979
12 | 1 | 8 | 200.2883 | 340.4768 | 540.7652 | 34.296 | 7.2524 | 410.3503 | 288 | 467.8748 | 379.5302 | 161.2349 | 164556.2752 | 16.1155 | 0 | 0 | 379.5302 | 161.2349 | 0 | 164556.2752
12 | 1 | 9 | 215.7625 | 894.1783 | 1109.9408 | 40.8075 | 7.6998 | 1005.7014 | 288 | 463.4699 | 317.8507 | 792.09 | 134343.5451 | 79.1696 | 0 | 0 | 317.8507 | 792.09 | 0 | 134343.5451
12 | 1 | 10 | 185.0033 | 855.19 | 1040.1934 | 41.4194 | 7.8632 | 1014.4311 | 288 | 471.5125 | 295.314 | 744.8794 | 127012.5166 | 74.4509 | 0 | 0 | 295.314 | 744.8794 | 0 | 127012.5166
12 | 1 | 11 | 201.6917 | 647.8227 | 849.5143 | 39.2155 | 7.6051 | 739.3816 | 288 | 473.3907 | 330.8983 | 518.616 | 143667.865 | 51.8358 | 0 | 0 | 330.8983 | 518.616 | 0 | 143667.865
12 | 1 | 12 | 201.6417 | 491.4688 | 693.1105 | 37.2359 | 8.2589 | 829.1368 | 288 | 469.4808 | 240.7514 | 452.3591 | 104063.5429 | 45.2134 | 0 | 0 | 240.7514 | 452.3591 | 0 | 104063.5429
12 | 1 | 13 | 218.9337 | 597.1576 | 816.0913 | 38.074 | 8.5686 | 1186.7414 | 288 | 472.3855 | 198.0502 | 618.0412 | 86015.473 | 61.7734 | 0 | 0 | 198.0502 | 618.0412 | 0 | 86015.473
12 | 1 | 14 | 115.8846 | 308.5501 | 424.4347 | 37.8978 | 8.6374 | 648.2634 | 288 | 471.4264 | 188.561 | 235.8737 | 81746.5812 | 23.5756 | 0 | 0 | 188.561 | 235.8737 | 0 | 81746.5812
12 | 1 | 15 | 0 | 71.2034 | 71.2034 | 48 | 7.803 | 67.5409 | 67.5409 | 474.2205 | 71.2034 | 0 | 30348.3372 | 0 | 0 | 0 | 71.2034 | 0 | 0 | 30348.3372
12 | 1 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 472.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 477.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 482.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 487.0256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 472.7909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 460.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 460.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 456.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 454.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 459.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 469.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 474.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 474.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 5 | 4.25 | 0 | 4.25 | 11 | 3.691 | 1.4059 | 1.4059 | 476.924 | 4.25 | 0 | 1980.1769 | 0 | 0 | 0 | 4.25 | 0 | 0 | 1980.1769
12 | 2 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 479.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 483.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 8 | 0.10917 | 101.1132 | 101.2224 | 47.9601 | 6.9944 | 70.2265 | 70.2265 | 484.7275 | 101.2224 | 0 | 44210.6303 | 0 | 0 | 0 | 101.2224 | 0 | 0 | 44210.6303
12 | 2 | 9 | 0 | 266.8997 | 266.8997 | 48 | 7.5707 | 229.0146 | 229.0146 | 485.3132 | 266.8997 | 0 | 116718.7731 | 0 | 0 | 0 | 266.8997 | 0 | 0 | 116718.7731
12 | 2 | 10 | 4.3117 | 301.8216 | 306.1332 | 47.4789 | 7.4159 | 246.9691 | 246.9691 | 484.5264 | 306.1332 | 0 | 133794.7682 | 0 | 0 | 0 | 306.1332 | 0 | 0 | 133794.7682
12 | 2 | 11 | 2.6817 | 244.8332 | 247.5149 | 47.5991 | 7.5879 | 213.8931 | 213.8931 | 484.9046 | 247.5149 | 0 | 108239.6075 | 0 | 0 | 0 | 247.5149 | 0 | 0 | 108239.6075
12 | 2 | 12 | 3.5508 | 237.0696 | 240.6204 | 47.454 | 8.3192 | 298.1251 | 288 | 480.2876 | 232.4483 | 8.1721 | 100611.4487 | 0.8168 | 0 | 0 | 232.4483 | 8.1721 | 0 | 100611.4487
12 | 2 | 13 | 1.734 | 244.641 | 246.375 | 47.7396 | 8.6546 | 381.0972 | 288 | 482.5632 | 186.1887 | 60.1862 | 80959.2521 | 6.0156 | 0 | 0 | 186.1887 | 60.1862 | 0 | 80959.2521
12 | 2 | 14 | 0 | 212.876 | 212.876 | 48 | 8.9299 | 413.5966 | 288 | 472.8261 | 148.2321 | 64.6439 | 62972.8584 | 6.4612 | 0 | 0 | 148.2321 | 64.6439 | 0 | 62972.8584
12 | 2 | 15 | 0 | 71.2938 | 71.2938 | 48 | 8.8009 | 123.6725 | 123.6725 | 475.2787 | 71.2938 | 0 | 30462.3381 | 0 | 0 | 0 | 71.2938 | 0 | 0 | 30462.3381
12 | 2 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 480.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 485.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 486.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 484.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 479.3835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 470.2137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 467.9343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 464.3976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 460.7803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 459.8062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 464.9321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 471.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 479.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 481.6089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 6 | 3.325 | 0 | 3.325 | 11 | 4.5255 | 1.2674 | 1.2674 | 485.1067 | 3.325 | 0 | 1576.4048 | 0 | 0 | 0 | 3.325 | 0 | 0 | 1576.4048
12 | 3 | 7 | 1.5104 | 14.6629 | 16.1733 | 44.5446 | 5.2137 | 7.0505 | 7.0505 | 489.0843 | 16.1733 | 0 | 7189.6728 | 0 | 0 | 0 | 16.1733 | 0 | 0 | 7189.6728
12 | 3 | 8 | 0.70257 | 163.4601 | 164.1626 | 47.8417 | 5.1879 | 71.1811 | 71.1811 | 491.1373 | 164.1626 | 0 | 72772.5809 | 0 | 0 | 0 | 164.1626 | 0 | 0 | 72772.5809
12 | 3 | 9 | 2.5067 | 177.4595 | 179.9662 | 47.4846 | 6.7449 | 115.3032 | 115.3032 | 489.6568 | 179.9662 | 0 | 79576.0291 | 0 | 0 | 0 | 179.9662 | 0 | 0 | 79576.0291
12 | 3 | 10 | 0 | 240.8792 | 240.8792 | 48 | 8.8783 | 446.5637 | 288 | 489.3351 | 155.349 | 85.5302 | 68560.942 | 8.5488 | 0 | 0 | 155.349 | 85.5302 | 0 | 68560.942
12 | 3 | 11 | 42.7942 | 184.9011 | 227.6952 | 41.046 | 9.8676 | 3461.8856 | 288 | 488.8948 | 18.9423 | 208.7529 | 8483.3048 | 20.8649 | 0 | 0 | 18.9423 | 208.7529 | 0 | 8483.3048
12 | 3 | 12 | 103.5193 | 296.3167 | 399.836 | 38.4205 | 10.2547 | 0 | 0 | 487.7111 | 0 | 399.836 | 0 | 39.9637 | 0 | 0 | 0 | 399.836 | 0 | 0
12 | 3 | 13 | 17.2453 | 195.0799 | 212.3253 | 44.9948 | 10.031 | 0 | 0 | 488.8213 | 0 | 212.3253 | 0 | 21.222 | 0 | 0 | 0 | 212.3253 | 0 | 0
12 | 3 | 14 | 71.6561 | 337.3235 | 408.9796 | 41.5173 | 9.9364 | 12459.936 | 288 | 482.6598 | 9.4532 | 399.5264 | 4170.2032 | 39.9328 | 0 | 0 | 9.4532 | 399.5264 | 0 | 4170.2032
12 | 3 | 15 | 0 | 50.2509 | 50.2509 | 48 | 11.1494 | 0 | 0 | 483.3671 | 0 | 50.2509 | 0 | 5.0226 | 0 | 0 | 0 | 50.2509 | 0 | 0
12 | 3 | 16 | 0.93821 | 0 | 0.93821 | 11 | 12.5086 | 0 | 0 | 490.273 | 0 | 0.93821 | 0 | 0.093774 | 0 | 0 | 0 | 0.93821 | 0 | 0
12 | 3 | 17 | 0.2375 | 0 | 0.2375 | 11 | 12.2591 | 0 | 0 | 496.3028 | 0 | 0.2375 | 0 | 0.023738 | 0 | 0 | 0 | 0.2375 | 0 | 0
12 | 3 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 496.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 497.6741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 501.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 496.1575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 494.944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 484.1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 480.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 1 | 13.9515 | 0 | 13.9515 | 11 | 3.4588 | 4.4515 | 4.4515 | 483.8412 | 13.9515 | 0 | 6596.8598 | 0 | 0 | 0 | 13.9515 | 0 | 0 | 6596.8598
12 | 4 | 2 | 22.4888 | 0 | 22.4888 | 11 | 3.3555 | 7.0641 | 7.0641 | 483.7452 | 22.4888 | 0 | 10631.4645 | 0 | 0 | 0 | 22.4888 | 0 | 0 | 10631.4645
12 | 4 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 484.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 493.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 497.484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 503.6471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 7 | 3.5223 | 1.5393 | 5.0616 | 22.252 | 5.1706 | 2.1869 | 2.1869 | 505.6499 | 5.0616 | 0 | 2446.7479 | 0 | 0 | 0 | 5.0616 | 0 | 0 | 2446.7479
12 | 4 | 8 | 0.91758 | 94.175 | 95.0926 | 47.643 | 5.8502 | 47.8059 | 47.8059 | 506.2786 | 95.0926 | 0 | 43612.8419 | 0 | 0 | 0 | 95.0926 | 0 | 0 | 43612.8419
12 | 4 | 9 | 0 | 171.1182 | 171.1182 | 48 | 6.7707 | 110.5092 | 110.5092 | 507.9976 | 171.1182 | 0 | 78713.9562 | 0 | 0 | 0 | 171.1182 | 0 | 0 | 78713.9562
12 | 4 | 10 | 0 | 254.9921 | 254.9921 | 48 | 8.9987 | 529.3078 | 288 | 510.3847 | 138.7429 | 116.2491 | 64152.6116 | 11.6191 | 0 | 0 | 138.7429 | 116.2491 | 0 | 64152.6116
12 | 4 | 11 | 0 | 295.3957 | 295.3957 | 48 | 10.0569 | 0 | 0 | 509.2469 | 0 | 295.3957 | 0 | 29.5249 | 0 | 0 | 0 | 295.3957 | 0 | 0
12 | 4 | 12 | 0 | 309.8115 | 309.8115 | 48 | 10.1343 | 0 | 0 | 510.246 | 0 | 309.8115 | 0 | 30.9657 | 0 | 0 | 0 | 309.8115 | 0 | 0
12 | 4 | 13 | 0.33174 | 325.572 | 325.9038 | 47.9623 | 10.2117 | 0 | 0 | 513.7443 | 0 | 325.9038 | 0 | 32.5742 | 0 | 0 | 0 | 325.9038 | 0 | 0
12 | 4 | 14 | 0 | 293.6449 | 293.6449 | 48 | 9.8762 | 4762.8285 | 288 | 506.5124 | 17.7562 | 275.8887 | 8141.437 | 27.5752 | 0 | 0 | 17.7562 | 275.8887 | 0 | 8141.437
12 | 4 | 15 | 0 | 15.5431 | 15.5431 | 48 | 10.9601 | 0 | 0 | 505.548 | 0 | 15.5431 | 0 | 1.5535 | 0 | 0 | 0 | 15.5431 | 0 | 0
12 | 4 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 508.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 516.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 507.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 502.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 20 | 16.5053 | 0 | 16.5053 | 11 | 12.6978 | 0 | 0 | 484.8852 | 0 | 16.5053 | 0 | 1.6497 | 0 | 0 | 0 | 16.5053 | 0 | 0
12 | 4 | 21 | 99.5254 | 0 | 99.5254 | 11 | 9.8762 | 1614.2704 | 288 | 479.4267 | 17.7562 | 81.7692 | 8317.4778 | 8.1729 | 0 | 0 | 17.7562 | 81.7692 | 0 | 8317.4778
12 | 4 | 22 | 80.5342 | 0 | 80.5342 | 11 | 6.1771 | 43.9445 | 43.9445 | 473.3319 | 80.5342 | 0 | 37233.5335 | 0 | 0 | 0 | 80.5342 | 0 | 0 | 37233.5335
12 | 4 | 23 | 58.3051 | 0 | 58.3051 | 11 | 4.6373 | 22.6881 | 22.6881 | 469.1436 | 58.3051 | 0 | 26712.0863 | 0 | 0 | 0 | 58.3051 | 0 | 0 | 26712.0863
12 | 5 | 0 | 19.2074 | 0 | 19.2074 | 11 | 3.9577 | 6.6342 | 6.6342 | 474.2512 | 19.2074 | 0 | 8897.829 | 0 | 0 | 0 | 19.2074 | 0 | 0 | 8897.829
12 | 5 | 1 | 44.1079 | 0 | 44.1079 | 11 | 3.6394 | 14.473 | 14.473 | 486.3703 | 44.1079 | 0 | 20967.5755 | 0 | 0 | 0 | 44.1079 | 0 | 0 | 20967.5755
12 | 5 | 2 | 47.2289 | 0 | 47.2289 | 11 | 3.5276 | 15.2295 | 15.2295 | 499.24 | 47.2289 | 0 | 23059.0321 | 0 | 0 | 0 | 47.2289 | 0 | 0 | 23059.0321
12 | 5 | 3 | 34.5188 | 0 | 34.5188 | 11 | 3.562 | 11.1904 | 11.1904 | 497.955 | 34.5188 | 0 | 16809.1059 | 0 | 0 | 0 | 34.5188 | 0 | 0 | 16809.1059
12 | 5 | 4 | 6.9919 | 0 | 6.9919 | 11 | 3.5878 | 2.2758 | 2.2758 | 514.5914 | 6.9919 | 0 | 3521.0389 | 0 | 0 | 0 | 6.9919 | 0 | 0 | 3521.0389
12 | 5 | 5 | 82.8241 | 0 | 82.8241 | 11 | 4.1814 | 29.7059 | 29.7059 | 520.3828 | 82.8241 | 0 | 42189.1717 | 0 | 0 | 0 | 82.8241 | 0 | 0 | 42189.1717
12 | 5 | 6 | 150.7736 | 0 | 150.7736 | 11 | 5.3513 | 67.6717 | 67.6717 | 516.8658 | 150.7736 | 0 | 76271.224 | 0 | 0 | 0 | 150.7736 | 0 | 0 | 76271.224
12 | 5 | 7 | 126.2985 | 28.8064 | 155.1049 | 17.8717 | 5.6008 | 73.5591 | 73.5591 | 517.9195 | 155.1049 | 0 | 77559.8745 | 0 | 0 | 0 | 155.1049 | 0 | 0 | 77559.8745
12 | 5 | 8 | 174.8391 | 255.1019 | 429.941 | 32.9536 | 6.5729 | 261.6519 | 261.6519 | 518.1537 | 429.941 | 0 | 208607.4176 | 0 | 0 | 0 | 429.941 | 0 | 0 | 208607.4176
12 | 5 | 9 | 129.4748 | 223.7789 | 353.2537 | 34.4387 | 7.7084 | 321.2771 | 288 | 512.9995 | 316.6646 | 36.5891 | 151543.2635 | 3.6571 | 0 | 0 | 316.6646 | 36.5891 | 0 | 151543.2635
12 | 5 | 10 | 104.4602 | 268.1889 | 372.6491 | 37.6282 | 8.9471 | 735.7952 | 288 | 514.728 | 145.8598 | 226.7893 | 69589.6805 | 22.6677 | 0 | 0 | 145.8598 | 226.7893 | 0 | 69589.6805
12 | 5 | 11 | 97.9052 | 209.3352 | 307.2404 | 36.2096 | 9.5923 | 1555.1292 | 288 | 513.9931 | 56.899 | 250.3414 | 27185.3847 | 25.0217 | 0 | 0 | 56.899 | 250.3414 | 0 | 27185.3847
12 | 5 | 12 | 137.7659 | 179.6631 | 317.429 | 31.9418 | 10.2891 | 0 | 0 | 513.5755 | 0 | 317.429 | 0 | 31.7271 | 0 | 0 | 0 | 317.429 | 0 | 0
12 | 5 | 13 | 131.0916 | 215.8791 | 346.9707 | 34.0207 | 10.0827 | 0 | 0 | 521.4972 | 0 | 346.9707 | 0 | 34.6798 | 0 | 0 | 0 | 346.9707 | 0 | 0
12 | 5 | 14 | 102.361 | 125.1321 | 227.4931 | 31.3518 | 10.6934 | 0 | 0 | 511.6456 | 0 | 227.4931 | 0 | 22.738 | 0 | 0 | 0 | 227.4931 | 0 | 0
12 | 5 | 15 | 73.4044 | 4.3629 | 77.7673 | 13.0758 | 11.6655 | 0 | 0 | 516.4315 | 0 | 77.7673 | 0 | 7.7729 | 0 | 0 | 0 | 77.7673 | 0 | 0
12 | 5 | 16 | 35.7772 | 0 | 35.7772 | 11 | 12.3021 | 0 | 0 | 520.1361 | 0 | 35.7772 | 0 | 3.5759 | 0 | 0 | 0 | 35.7772 | 0 | 0
12 | 5 | 17 | 51.4539 | 0 | 51.4539 | 11 | 12.1989 | 0 | 0 | 528.0095 | 0 | 51.4539 | 0 | 5.1428 | 0 | 0 | 0 | 51.4539 | 0 | 0
12 | 5 | 18 | 50.4334 | 0 | 50.4334 | 11 | 12.9559 | 0 | 0 | 528.2682 | 0 | 50.4334 | 0 | 5.0408 | 0 | 0 | 0 | 50.4334 | 0 | 0
12 | 5 | 19 | 56.2882 | 0 | 56.2882 | 11 | 13.2054 | 0 | 0 | 520.1424 | 0 | 56.2882 | 0 | 5.626 | 0 | 0 | 0 | 56.2882 | 0 | 0
12 | 5 | 20 | 101.9512 | 0 | 101.9512 | 11 | 12.6806 | 0 | 0 | 510.4586 | 0 | 101.9512 | 0 | 10.19 | 0 | 0 | 0 | 101.9512 | 0 | 0
12 | 5 | 21 | 100.323 | 0 | 100.323 | 11 | 10.3235 | 0 | 0 | 502.7077 | 0 | 100.323 | 0 | 10.0273 | 0 | 0 | 0 | 100.323 | 0 | 0
12 | 5 | 22 | 117.8531 | 0 | 117.8531 | 11 | 5.6868 | 57.0057 | 57.0057 | 496.6712 | 117.8531 | 0 | 57237.8581 | 0 | 0 | 0 | 117.8531 | 0 | 0 | 57237.8581
12 | 5 | 23 | 90.1677 | 0 | 90.1677 | 11 | 4.5734 | 34.674 | 34.674 | 488.0201 | 90.1677 | 0 | 43011.8275 | 0 | 0 | 0 | 90.1677 | 0 | 0 | 43011.8275
12 | 6 | 0 | 96.6547 | 0 | 96.6547 | 11 | 3.8373 | 32.7323 | 32.7323 | 488.0501 | 96.6547 | 0 | 46109.1383 | 0 | 0 | 0 | 96.6547 | 0 | 0 | 46109.1383
12 | 6 | 1 | 103.0906 | 0 | 103.0906 | 11 | 3.605 | 33.6449 | 33.6449 | 494.1634 | 103.0906 | 0 | 49809.5999 | 0 | 0 | 0 | 103.0906 | 0 | 0 | 49809.5999
12 | 6 | 2 | 103.556 | 0 | 103.556 | 11 | 3.5018 | 33.2603 | 33.2603 | 505.7937 | 103.556 | 0 | 51238.8357 | 0 | 0 | 0 | 103.556 | 0 | 0 | 51238.8357
12 | 6 | 3 | 10.6939 | 0 | 10.6939 | 11 | 3.4416 | 3.4032 | 3.4032 | 513.6227 | 10.6939 | 0 | 5374.9831 | 0 | 0 | 0 | 10.6939 | 0 | 0 | 5374.9831
12 | 6 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 519.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 522.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 528.7517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 537.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 8 | 0 | 72.4645 | 72.4645 | 48 | 6.5729 | 44.1002 | 44.1002 | 539.3838 | 72.4645 | 0 | 35607.8622 | 0 | 0 | 0 | 72.4645 | 0 | 0 | 35607.8622
12 | 6 | 9 | 150.0383 | 143.5862 | 293.6245 | 29.0935 | 7.6912 | 265.0598 | 265.0598 | 537.7702 | 293.6245 | 0 | 149359.9463 | 0 | 0 | 0 | 293.6245 | 0 | 0 | 149359.9463
12 | 6 | 10 | 167.3458 | 156.4703 | 323.8161 | 28.8787 | 8.4482 | 434.4578 | 288 | 535.9871 | 214.6562 | 109.1599 | 108853.9537 | 10.9106 | 0 | 0 | 214.6562 | 109.1599 | 0 | 108853.9537
12 | 6 | 11 | 129.6986 | 120.5712 | 250.2698 | 28.8253 | 9.7214 | 1843.0991 | 288 | 525.6664 | 39.1068 | 211.163 | 19429.8661 | 21.1058 | 0 | 0 | 39.1068 | 211.163 | 0 | 19429.8661
12 | 6 | 12 | 63.784 | 78.4554 | 142.2395 | 31.4082 | 9.4117 | 500.7453 | 288 | 518.8438 | 81.808 | 60.4315 | 39876.1301 | 6.0401 | 0 | 0 | 81.808 | 60.4315 | 0 | 39876.1301
12 | 6 | 13 | 0 | 70.9825 | 70.9825 | 48 | 8.8869 | 132.6062 | 132.6062 | 522.9071 | 70.9825 | 0 | 33710.0718 | 0 | 0 | 0 | 70.9825 | 0 | 0 | 33710.0718
12 | 6 | 14 | 0 | 26.2182 | 26.2182 | 48 | 9.3428 | 82.7062 | 82.7062 | 519.8668 | 26.2182 | 0 | 12371.489 | 0 | 0 | 0 | 26.2182 | 0 | 0 | 12371.489
12 | 6 | 15 | 0.23333 | 0.030792 | 0.26412 | 15.3135 | 10.0224 | 0 | 0 | 515.3481 | 0 | 0.26412 | 0 | 0.026399 | 0 | 0 | 0 | 0.26412 | 0 | 0
12 | 6 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 521.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 530.1575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 527.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 519.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 505.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 491.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 488.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 486.6096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 491.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 503.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 509.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 514.7812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 523.8384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 534.8444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 530.6289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 525.0051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 8 | 0 | 20.8358 | 20.8358 | 48 | 5.4889 | 9.6368 | 9.6368 | 524.6255 | 20.8358 | 0 | 9930.8913 | 0 | 0 | 0 | 20.8358 | 0 | 0 | 9930.8913
12 | 7 | 9 | 0 | 60.9934 | 60.9934 | 48 | 6.9858 | 42.1957 | 42.1957 | 527.6478 | 60.9934 | 0 | 29255.3742 | 0 | 0 | 0 | 60.9934 | 0 | 0 | 29255.3742
12 | 7 | 10 | 0 | 47.8689 | 47.8689 | 48 | 7.3471 | 37.6177 | 37.6177 | 523.5737 | 47.8689 | 0 | 22765.1948 | 0 | 0 | 0 | 47.8689 | 0 | 0 | 22765.1948
12 | 7 | 11 | 0 | 43.8332 | 43.8332 | 48 | 8.9643 | 87.9795 | 87.9795 | 522.9551 | 43.8332 | 0 | 20818.7898 | 0 | 0 | 0 | 43.8332 | 0 | 0 | 20818.7898
12 | 7 | 12 | 68.0923 | 120.2713 | 188.3636 | 34.6247 | 8.2847 | 228.7114 | 228.7114 | 519.837 | 188.3636 | 0 | 91396.3333 | 0 | 0 | 0 | 188.3636 | 0 | 0 | 91396.3333
12 | 7 | 13 | 0 | 100.8745 | 100.8745 | 48 | 7.8202 | 96.4394 | 96.4394 | 525.1552 | 100.8745 | 0 | 48132.7988 | 0 | 0 | 0 | 100.8745 | 0 | 0 | 48132.7988
12 | 7 | 14 | 0 | 29.118 | 29.118 | 48 | 7.6568 | 25.9001 | 25.9001 | 513.9149 | 29.118 | 0 | 13566.489 | 0 | 0 | 0 | 29.118 | 0 | 0 | 13566.489
12 | 7 | 15 | 0 | 0.40517 | 0.40517 | 48 | 7.7256 | 0.37127 | 0.37127 | 525.8989 | 0.40517 | 0 | 193.6287 | 0 | 0 | 0 | 0.40517 | 0 | 0 | 193.6287
12 | 7 | 16 | 0 | 0.11388 | 0.11388 | 48 | 7.3729 | 0.090366 | 0.090366 | 530.9121 | 0.11387 | 0 | 54.9916 | 0 | 0 | 0 | 0.11387 | 0 | 0 | 54.9916
12 | 7 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 534.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 537.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 527.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 515.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 505.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 504.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 497.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 499.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 502.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 2 | 0.77253 | 0 | 0.77253 | 11 | 3.3383 | 0.24204 | 0.24204 | 513.342 | 0.77253 | 0 | 388.0743 | 0 | 0 | 0 | 0.77253 | 0 | 0 | 388.0743
12 | 8 | 3 | 51.9381 | 0 | 51.9381 | 11 | 3.3039 | 16.189 | 16.189 | 513.0601 | 51.9381 | 0 | 26076.0549 | 0 | 0 | 0 | 51.9381 | 0 | 0 | 26076.0549
12 | 8 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 521.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 531.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 537.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 7 | 0 | 2.7053 | 2.7053 | 48 | 6.5556 | 1.6382 | 1.6382 | 530.4852 | 2.7053 | 0 | 1305.2728 | 0 | 0 | 0 | 2.7053 | 0 | 0 | 1305.2728
12 | 8 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 529.7512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 9 | 0 | 0.16629 | 0.16629 | 48 | 7.6998 | 0.15067 | 0.15067 | 522.882 | 0.16629 | 0 | 78.9689 | 0 | 0 | 0 | 0.16629 | 0 | 0 | 78.9689
12 | 8 | 10 | 0 | 21.3946 | 21.3946 | 48 | 7.8632 | 20.8647 | 20.8647 | 521.0189 | 21.3946 | 0 | 10120.0532 | 0 | 0 | 0 | 21.3946 | 0 | 0 | 10120.0532
12 | 8 | 11 | 0 | 72.4281 | 72.4281 | 48 | 7.6051 | 63.0383 | 63.0383 | 520.3613 | 72.4281 | 0 | 34212.2185 | 0 | 0 | 0 | 72.4281 | 0 | 0 | 34212.2185
12 | 8 | 12 | 0 | 56.634 | 56.634 | 48 | 8.2589 | 67.7487 | 67.7487 | 519.2267 | 56.634 | 0 | 26687.4527 | 0 | 0 | 0 | 56.634 | 0 | 0 | 26687.4527
12 | 8 | 13 | 0.43333 | 0.83997 | 1.2733 | 35.4081 | 8.5686 | 1.8516 | 1.8516 | 525.7656 | 1.2733 | 0 | 624.3734 | 0 | 0 | 0 | 1.2733 | 0 | 0 | 624.3734
12 | 8 | 14 | 0 | 0.16633 | 0.16633 | 48 | 8.6374 | 0.25405 | 0.25405 | 517.3089 | 0.16633 | 0 | 78.0617 | 0 | 0 | 0 | 0.16633 | 0 | 0 | 78.0617
12 | 8 | 15 | 0 | 0.34371 | 0.34371 | 48 | 7.803 | 0.32603 | 0.32603 | 519.1487 | 0.34371 | 0 | 161.9377 | 0 | 0 | 0 | 0.34371 | 0 | 0 | 161.9377
12 | 8 | 16 | 0 | 0.059875 | 0.059875 | 48 | 7.6998 | 0.054252 | 0.054252 | 524.6886 | 0.059875 | 0 | 28.5417 | 0 | 0 | 0 | 0.059875 | 0 | 0 | 28.5417
12 | 8 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 532.587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 540.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 541.3084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 537.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 534.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 540.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 540.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 544.4447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 549.7454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 552.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 537.3943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 541.5024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 545.0958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 551.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 559.2097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 8 | 0 | 10.3664 | 10.3664 | 48 | 6.9944 | 7.192 | 7.192 | 561.2575 | 10.3664 | 0 | 5320.6292 | 0 | 0 | 0 | 10.3664 | 0 | 0 | 5320.6292
12 | 9 | 9 | 0 | 92.9671 | 92.9671 | 48 | 7.5707 | 79.7709 | 79.7709 | 564.7388 | 92.9671 | 0 | 48039.705 | 0 | 0 | 0 | 92.9671 | 0 | 0 | 48039.705
12 | 9 | 10 | 0 | 110.0284 | 110.0284 | 48 | 7.4159 | 88.764 | 88.764 | 566.5874 | 110.0284 | 0 | 57059.3494 | 0 | 0 | 0 | 110.0284 | 0 | 0 | 57059.3494
12 | 9 | 11 | 0 | 62.8338 | 62.8338 | 48 | 7.5879 | 54.2987 | 54.2987 | 565.3437 | 62.8338 | 0 | 32506.696 | 0 | 0 | 0 | 62.8338 | 0 | 0 | 32506.696
12 | 9 | 12 | 0 | 11.1131 | 11.1131 | 48 | 8.3192 | 13.7689 | 13.7689 | 564.6492 | 11.1131 | 0 | 5741.5503 | 0 | 0 | 0 | 11.1131 | 0 | 0 | 5741.5503
12 | 9 | 13 | 0 | 0 | 0 | 0 | 8.6546 | 0 | 0 | 563.1599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 553.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 15 | 0 | 0.98342 | 0.98342 | 48 | 8.8009 | 1.7059 | 1.7059 | 554.9859 | 0.98342 | 0 | 498.5784 | 0 | 0 | 0 | 0.98342 | 0 | 0 | 498.5784
12 | 9 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 558.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 565.0292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 573.1645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 573.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 568.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 21 | 0.053333 | 0 | 0.053333 | 11 | 9.1708 | 0.13354 | 0.13354 | 563.4083 | 0.053333 | 0 | 29.4618 | 0 | 0 | 0 | 0.053333 | 0 | 0 | 29.4618
12 | 9 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 557.7471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 554.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 554.4907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 556.8928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 560.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 563.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 563.5075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 561.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 560.8113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 568.5005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 564.3807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 9 | 0 | 0 | 0 | 0 | 6.7449 | 0 | 0 | 561.5361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 10 | 0 | 0 | 0 | 0 | 8.8783 | 0 | 0 | 559.1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 11 | 0 | 0.052083 | 0.052083 | 48 | 9.8676 | 0.79188 | 0.79188 | 557.0023 | 0.052083 | 0 | 26.5105 | 0 | 0 | 0 | 0.052083 | 0 | 0 | 26.5105
12 | 10 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 555.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 13 | 0 | 0.051167 | 0.051167 | 48 | 10.031 | 0 | 0 | 557.6092 | 0 | 0.051167 | 0 | 0.0051141 | 0 | 0 | 0 | 0.051167 | 0 | 0
12 | 10 | 14 | 0 | 0.66592 | 0.66592 | 48 | 9.9364 | 20.2878 | 20.2878 | 549.7652 | 0.66592 | 0 | 334.1338 | 0 | 0 | 0 | 0.66592 | 0 | 0 | 334.1338
12 | 10 | 15 | 0 | 0.49938 | 0.49938 | 48 | 11.1494 | 0 | 0 | 556.5028 | 0 | 0.49938 | 0 | 0.049913 | 0 | 0 | 0 | 0.49938 | 0 | 0
12 | 10 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 560.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 567.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 571.7273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 569.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 559.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 553.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 549.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 541.6842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 539.7681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 538.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3555 | 0 | 0 | 538.7961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 3 | 2.1199 | 0 | 2.1199 | 11 | 3.4416 | 0.67461 | 0.67461 | 538.6722 | 2.1199 | 0 | 1118.5896 | 0 | 0 | 0 | 2.1199 | 0 | 0 | 1118.5896
12 | 11 | 4 | 53.5321 | 0 | 53.5321 | 11 | 3.691 | 17.7089 | 17.7089 | 539.2312 | 53.5321 | 0 | 28277.3002 | 0 | 0 | 0 | 53.5321 | 0 | 0 | 28277.3002
12 | 11 | 5 | 21.6102 | 0 | 21.6102 | 11 | 3.9405 | 7.4429 | 7.4429 | 537.3859 | 21.6102 | 0 | 11375.312 | 0 | 0 | 0 | 21.6102 | 0 | 0 | 11375.312
12 | 11 | 6 | 29.043 | 0 | 29.043 | 11 | 4.8093 | 11.6757 | 11.6757 | 543.3063 | 29.043 | 0 | 15459.7694 | 0 | 0 | 0 | 29.043 | 0 | 0 | 15459.7694
12 | 11 | 7 | 22.4729 | 0 | 22.4729 | 11 | 5.1706 | 9.7096 | 9.7096 | 548.4224 | 22.4729 | 0 | 12077.4376 | 0 | 0 | 0 | 22.4729 | 0 | 0 | 12077.4376
12 | 11 | 8 | 0 | 0.19667 | 0.19667 | 48 | 5.8502 | 0.09887 | 0.09887 | 551.3595 | 0.19667 | 0 | 98.994 | 0 | 0 | 0 | 0.19667 | 0 | 0 | 98.994
12 | 11 | 9 | 0 | 0 | 0 | 0 | 6.7707 | 0 | 0 | 548.9345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 10 | 0 | 0.16621 | 0.16621 | 48 | 8.9987 | 0.34501 | 0.34501 | 545.8054 | 0.16621 | 0 | 82.7394 | 0 | 0 | 0 | 0.16621 | 0 | 0 | 82.7394
12 | 11 | 11 | 0 | 0 | 0 | 0 | 10.0569 | 0 | 0 | 538.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 12 | 0 | 0 | 0 | 0 | 10.1343 | 0 | 0 | 539.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 13 | 0 | 0 | 0 | 0 | 10.2117 | 0 | 0 | 537.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 14 | 7.5666 | 0 | 7.5666 | 11 | 9.8762 | 122.7276 | 122.7276 | 541.1011 | 7.5666 | 0 | 4011.0539 | 0 | 0 | 0 | 7.5666 | 0 | 0 | 4011.0539
12 | 11 | 15 | 0 | 1.2834 | 1.2834 | 48 | 10.9601 | 0 | 0 | 545.8442 | 0 | 1.2834 | 0 | 0.12828 | 0 | 0 | 0 | 1.2834 | 0 | 0
12 | 11 | 16 | 7.0658 | 0 | 7.0658 | 11 | 11.5279 | 0 | 0 | 548.0727 | 0 | 7.0658 | 0 | 0.70623 | 0 | 0 | 0 | 7.0658 | 0 | 0
12 | 11 | 17 | 57.1056 | 0 | 57.1056 | 11 | 11.5451 | 0 | 0 | 548.2386 | 0 | 57.1056 | 0 | 5.7077 | 0 | 0 | 0 | 57.1056 | 0 | 0
12 | 11 | 18 | 71.2831 | 0 | 71.2831 | 11 | 11.9236 | 0 | 0 | 546.8237 | 0 | 71.2831 | 0 | 7.1248 | 0 | 0 | 0 | 71.2831 | 0 | 0
12 | 11 | 19 | 57.5284 | 0 | 57.5284 | 11 | 13.1107 | 0 | 0 | 534.6678 | 0 | 57.5284 | 0 | 5.75 | 0 | 0 | 0 | 57.5284 | 0 | 0
12 | 11 | 20 | 15.3391 | 0 | 15.3391 | 11 | 12.6978 | 0 | 0 | 512.281 | 0 | 15.3391 | 0 | 1.5332 | 0 | 0 | 0 | 15.3391 | 0 | 0
12 | 11 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 504.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 501.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 494.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 488.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 490.5694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 495.5936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 510.3239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 527.3019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 544.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 547.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 554.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 8 | 3.9229 | 0 | 3.9229 | 11 | 6.5729 | 2.3874 | 2.3874 | 561.6534 | 3.9229 | 0 | 2160.1722 | 0 | 0 | 0 | 3.9229 | 0 | 0 | 2160.1722
12 | 12 | 9 | 24.965 | 10.4212 | 35.3862 | 21.8964 | 7.7084 | 32.183 | 32.183 | 558.0792 | 35.3862 | 0 | 18973.4697 | 0 | 0 | 0 | 35.3862 | 0 | 0 | 18973.4697
12 | 12 | 10 | 72.2245 | 22.2952 | 94.5197 | 19.7275 | 8.9471 | 186.6291 | 186.6291 | 552.9597 | 94.5197 | 0 | 50400.9703 | 0 | 0 | 0 | 94.5197 | 0 | 0 | 50400.9703
12 | 12 | 11 | 117.9067 | 554.3562 | 672.2629 | 41.5107 | 9.5923 | 3402.7281 | 288 | 549.4865 | 56.899 | 615.3639 | 28903.2972 | 61.5058 | 0 | 0 | 56.899 | 615.3639 | 0 | 28903.2972
12 | 12 | 12 | 82.9394 | 310.6384 | 393.5778 | 40.2029 | 10.2891 | 0 | 0 | 544.3749 | 0 | 393.5778 | 0 | 39.3382 | 0 | 0 | 0 | 393.5778 | 0 | 0
12 | 12 | 13 | 97.55 | 308.2507 | 405.8007 | 39.1056 | 10.0827 | 0 | 0 | 540.2198 | 0 | 405.8007 | 0 | 40.5599 | 0 | 0 | 0 | 405.8007 | 0 | 0
12 | 12 | 14 | 105.7808 | 240.5206 | 346.3014 | 36.698 | 10.6934 | 0 | 0 | 540.8028 | 0 | 346.3014 | 0 | 34.6129 | 0 | 0 | 0 | 346.3014 | 0 | 0
12 | 12 | 15 | 15.4846 | 0.33279 | 15.8174 | 11.7785 | 11.6655 | 0 | 0 | 543.5454 | 0 | 15.8174 | 0 | 1.581 | 0 | 0 | 0 | 15.8174 | 0 | 0
12 | 12 | 16 | 15.0135 | 0.024833 | 15.0383 | 11.0611 | 12.3021 | 0 | 0 | 547.2734 | 0 | 15.0383 | 0 | 1.5031 | 0 | 0 | 0 | 15.0383 | 0 | 0
12 | 12 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 553.7956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 558.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 555.3706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 542.9054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 523.5791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 529.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 528.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 531.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 538.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 2 | 0.64079 | 0 | 0.64079 | 11 | 3.5018 | 0.20581 | 0.20581 | 550.2487 | 0.64079 | 0 | 345.5461 | 0 | 0 | 0 | 0.64079 | 0 | 0 | 345.5461
12 | 13 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 557.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 558.1566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 562.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 564.7071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 560.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 8 | 0 | 0 | 0 | 0 | 6.5729 | 0 | 0 | 559.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 9 | 0 | 0 | 0 | 0 | 7.6912 | 0 | 0 | 560.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 10 | 0 | 0 | 0 | 0 | 8.4482 | 0 | 0 | 560.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 11 | 35.7303 | 5.1647 | 40.8949 | 15.6728 | 9.7214 | 301.1687 | 288 | 560.7117 | 39.1068 | 1.7881 | 21314.7259 | 0.17873 | 0 | 0 | 39.1068 | 1.7881 | 0 | 21314.7259
12 | 13 | 12 | 152.7294 | 9.2087 | 161.9381 | 13.104 | 9.4117 | 570.0931 | 288 | 559.4868 | 81.808 | 80.1301 | 44698.4793 | 8.009 | 0 | 0 | 81.808 | 80.1301 | 0 | 44698.4793
12 | 13 | 13 | 0 | 0 | 0 | 0 | 8.8869 | 0 | 0 | 558.3887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 14 | 0 | 0 | 0 | 0 | 9.3428 | 0 | 0 | 549.431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 15 | 0 | 0.37483 | 0.37483 | 48 | 10.0224 | 0 | 0 | 551.4523 | 0 | 0.37483 | 0 | 0.037465 | 0 | 0 | 0 | 0.37483 | 0 | 0
12 | 13 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 554.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 560.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 568.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 561.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 542.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 530.773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 522.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 518.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 522.7104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 520.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 528.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 534.5815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 542.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 553.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 6 | 0.39167 | 0 | 0.39167 | 11 | 4.7319 | 0.15514 | 0.15514 | 554.1353 | 0.39167 | 0 | 212.728 | 0 | 0 | 0 | 0.39167 | 0 | 0 | 212.728
12 | 14 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 550.5847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 8 | 0 | 0 | 0 | 0 | 5.4889 | 0 | 0 | 546.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 9 | 8.5183 | 207.915 | 216.4334 | 46.5438 | 6.9858 | 149.7303 | 149.7303 | 543.5667 | 216.4334 | 0 | 107572.3447 | 0 | 0 | 0 | 216.4334 | 0 | 0 | 107572.3447
12 | 14 | 10 | 13.5558 | 285.862 | 299.4178 | 46.3249 | 7.3471 | 235.2972 | 235.2972 | 543.1879 | 299.4178 | 0 | 148769.663 | 0 | 0 | 0 | 299.4178 | 0 | 0 | 148769.663
12 | 14 | 11 | 35.3024 | 167.0549 | 202.3573 | 41.5451 | 8.9643 | 406.1601 | 288 | 540.4876 | 143.4875 | 58.8698 | 71592.0102 | 5.884 | 0 | 0 | 143.4875 | 58.8698 | 0 | 71592.0102
12 | 14 | 12 | 124.3097 | 115.496 | 239.8057 | 28.8201 | 8.2847 | 291.1725 | 288 | 537.7124 | 237.1929 | 2.6128 | 120705.6525 | 0.26115 | 0 | 0 | 237.1929 | 2.6128 | 0 | 120705.6525
12 | 14 | 13 | 82.3604 | 0.51549 | 82.8759 | 11.2301 | 7.8202 | 79.2322 | 79.2322 | 533.2923 | 82.8759 | 0 | 43266.386 | 0 | 0 | 0 | 82.8759 | 0 | 0 | 43266.386
12 | 14 | 14 | 118.9084 | 73.923 | 192.8314 | 25.1842 | 7.6568 | 171.5213 | 171.5213 | 529.1908 | 192.8314 | 0 | 97188.2835 | 0 | 0 | 0 | 192.8314 | 0 | 0 | 97188.2835
12 | 14 | 15 | 40.1041 | 0.052458 | 40.1566 | 11.0483 | 7.7256 | 36.7972 | 36.7972 | 537.3794 | 40.1566 | 0 | 21135.6411 | 0 | 0 | 0 | 40.1566 | 0 | 0 | 21135.6411
12 | 14 | 16 | 26.1839 | 0 | 26.1839 | 11 | 7.3729 | 20.7783 | 20.7783 | 540.0587 | 26.1839 | 0 | 13852.7989 | 0 | 0 | 0 | 26.1839 | 0 | 0 | 13852.7989
12 | 14 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 543.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 546.8321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 540.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 532.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 21 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 522.3726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 22 | 0 | 0 | 0 | 0 | 4.9212 | 0 | 0 | 516.9312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 23 | 0 | 0 | 0 | 0 | 4.5954 | 0 | 0 | 517.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 518.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 522.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 533.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 539.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 553.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 560.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 571.1662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 577.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 583.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 9 | 0.5575 | 3.2584 | 3.8159 | 42.5943 | 7.6998 | 3.4575 | 3.4575 | 587.4977 | 3.8159 | 0 | 2079.3009 | 0 | 0 | 0 | 3.8159 | 0 | 0 | 2079.3009
12 | 15 | 10 | 0 | 0.23392 | 0.23392 | 48 | 7.8632 | 0.22812 | 0.22812 | 585.0143 | 0.23392 | 0 | 125.6166 | 0 | 0 | 0 | 0.23392 | 0 | 0 | 125.6166
12 | 15 | 11 | 0 | 0 | 0 | 0 | 7.6051 | 0 | 0 | 583.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 12 | 0 | 0 | 0 | 0 | 8.2589 | 0 | 0 | 586.5647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 13 | 0.39163 | 0.15242 | 0.54404 | 21.3658 | 8.5686 | 0.79113 | 0.79113 | 581.8062 | 0.54404 | 0 | 304.903 | 0 | 0 | 0 | 0.54404 | 0 | 0 | 304.903
12 | 15 | 14 | 43.544 | 0.49917 | 44.0432 | 11.4193 | 8.6374 | 67.2697 | 67.2697 | 567.0967 | 44.0432 | 0 | 24473.7977 | 0 | 0 | 0 | 44.0432 | 0 | 0 | 24473.7977
12 | 15 | 15 | 33.0841 | 0.88262 | 33.9668 | 11.9614 | 7.803 | 32.2196 | 32.2196 | 564.8851 | 33.9668 | 0 | 18781.0306 | 0 | 0 | 0 | 33.9668 | 0 | 0 | 18781.0306
12 | 15 | 16 | 7.2795 | 0 | 7.2795 | 11 | 7.6998 | 6.5959 | 6.5959 | 566.9619 | 7.2795 | 0 | 4047.1403 | 0 | 0 | 0 | 7.2795 | 0 | 0 | 4047.1403
12 | 15 | 17 | 3.3667 | 0 | 3.3667 | 11 | 7.6482 | 2.9837 | 2.9837 | 571.8415 | 3.3667 | 0 | 1888.1663 | 0 | 0 | 0 | 3.3667 | 0 | 0 | 1888.1663
12 | 15 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 578.7809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 589.8886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 598.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 600.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 600.8879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 595.9003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 596.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 591.5057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 583.9771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 571.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 572.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 570.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 573.6767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 582.3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 8 | 0 | 0 | 0 | 0 | 6.9944 | 0 | 0 | 588.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 9 | 0 | 0 | 0 | 0 | 7.5707 | 0 | 0 | 592.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 10 | 0 | 0 | 0 | 0 | 7.4159 | 0 | 0 | 592.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 11 | 0 | 0 | 0 | 0 | 7.5879 | 0 | 0 | 590.7804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 12 | 0 | 0 | 0 | 0 | 8.3192 | 0 | 0 | 590.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 13 | 0.28395 | 0 | 0.28395 | 11 | 8.6546 | 0.43921 | 0.43921 | 586.2242 | 0.28395 | 0 | 163.3331 | 0 | 0 | 0 | 0.28395 | 0 | 0 | 163.3331
12 | 16 | 14 | 0 | 0 | 0 | 0 | 8.9299 | 0 | 0 | 576.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 575.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 581.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 17 | 23.9762 | 0 | 23.9762 | 11 | 9.0762 | 53.918 | 53.918 | 586.2966 | 23.9762 | 0 | 13793.4297 | 0 | 0 | 0 | 23.9762 | 0 | 0 | 13793.4297
12 | 16 | 18 | 61.7439 | 0 | 61.7439 | 11 | 9.4461 | 230.748 | 230.748 | 592.2347 | 61.7439 | 0 | 35887.6725 | 0 | 0 | 0 | 61.7439 | 0 | 0 | 35887.6725
12 | 16 | 19 | 40.6401 | 0 | 40.6401 | 11 | 8.0611 | 43.6676 | 43.6676 | 598.1687 | 40.6401 | 0 | 23862.5994 | 0 | 0 | 0 | 40.6401 | 0 | 0 | 23862.5994
12 | 16 | 20 | 0.71287 | 0 | 0.71287 | 11 | 11.2698 | 0 | 0 | 595.2071 | 0 | 0.71287 | 0 | 0.071251 | 0 | 0 | 0 | 0.71287 | 0 | 0
12 | 16 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 589.4521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 22 | 0 | 0 | 0 | 0 | 5.4717 | 0 | 0 | 585.9317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 23 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 573.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 0 | 0 | 0 | 0 | 0 | 3.3125 | 0 | 0 | 567.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 1 | 0 | 0 | 0 | 0 | 3.2007 | 0 | 0 | 572.0842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 2 | 0 | 0 | 0 | 0 | 3.1921 | 0 | 0 | 578.6229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3297 | 0 | 0 | 577.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3469 | 0 | 0 | 581.1593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 5 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 587.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 6 | 0 | 0 | 0 | 0 | 4.5255 | 0 | 0 | 590.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 7 | 0 | 0 | 0 | 0 | 5.2137 | 0 | 0 | 592.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 8 | 0 | 0.053083 | 0.053083 | 48 | 5.1879 | 0.023017 | 0.023017 | 591.329 | 0.053083 | 0 | 28.8417 | 0 | 0 | 0 | 0.053083 | 0 | 0 | 28.8417
12 | 17 | 9 | 15.7055 | 16.209 | 31.9146 | 29.7919 | 6.7449 | 20.4475 | 20.4475 | 588.1439 | 31.9146 | 0 | 17819.5613 | 0 | 0 | 0 | 31.9146 | 0 | 0 | 17819.5613
12 | 17 | 10 | 19.6467 | 3.4673 | 23.1139 | 16.5503 | 8.8783 | 42.8507 | 42.8507 | 585.2369 | 23.1139 | 0 | 13144.5758 | 0 | 0 | 0 | 23.1139 | 0 | 0 | 13144.5758
12 | 17 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 581.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 12 | 54.5672 | 52.5359 | 107.1032 | 29.1491 | 10.2547 | 0 | 0 | 571.1947 | 0 | 107.1032 | 0 | 10.705 | 0 | 0 | 0 | 107.1032 | 0 | 0
12 | 17 | 13 | 12.9075 | 0.20662 | 13.1142 | 11.583 | 10.031 | 0 | 0 | 574.0371 | 0 | 13.1142 | 0 | 1.3108 | 0 | 0 | 0 | 13.1142 | 0 | 0
12 | 17 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 575.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 15 | 0 | 0.33275 | 0.33275 | 48 | 11.1494 | 0 | 0 | 576.3682 | 0 | 0.33275 | 0 | 0.033258 | 0 | 0 | 0 | 0.33275 | 0 | 0
12 | 17 | 16 | 0 | 0.33308 | 0.33308 | 48 | 12.5086 | 0 | 0 | 575.3225 | 0 | 0.33308 | 0 | 0.033292 | 0 | 0 | 0 | 0.33308 | 0 | 0
12 | 17 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 570.1757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 566.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 559.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 548.0893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 528.4965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 526.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 508.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 500.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4588 | 0 | 0 | 500.5889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 2 | 2.6717 | 0 | 2.6717 | 11 | 3.3555 | 0.83924 | 0.83924 | 495.5891 | 2.6717 | 0 | 1294.6903 | 0 | 0 | 0 | 2.6717 | 0 | 0 | 1294.6903
12 | 18 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 505.4131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 512.4226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 524.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 533.8473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 541.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 8 | 0 | 44.4244 | 44.4244 | 48 | 5.8502 | 22.3335 | 22.3335 | 543.8005 | 44.4244 | 0 | 22025.6497 | 0 | 0 | 0 | 44.4244 | 0 | 0 | 22025.6497
12 | 18 | 9 | 19.9083 | 197.4048 | 217.3131 | 44.6104 | 6.7707 | 140.3421 | 140.3421 | 551.6521 | 217.3131 | 0 | 110186.8055 | 0 | 0 | 0 | 217.3131 | 0 | 0 | 110186.8055
12 | 18 | 10 | 33.1158 | 363.3779 | 396.4937 | 44.9097 | 8.9987 | 823.0343 | 288 | 556.6272 | 138.7429 | 257.7508 | 70997.1882 | 25.7623 | 0 | 0 | 138.7429 | 257.7508 | 0 | 70997.1882
12 | 18 | 11 | 11.5252 | 165.0192 | 176.5444 | 45.5846 | 10.0569 | 0 | 0 | 558.7547 | 0 | 176.5444 | 0 | 17.6457 | 0 | 0 | 0 | 176.5444 | 0 | 0
12 | 18 | 12 | 6.1775 | 122.2055 | 128.383 | 46.2196 | 10.1343 | 0 | 0 | 557.7827 | 0 | 128.383 | 0 | 12.8319 | 0 | 0 | 0 | 128.383 | 0 | 0
12 | 18 | 13 | 5.4308 | 462.0128 | 467.4436 | 47.5701 | 10.2117 | 0 | 0 | 566.6116 | 0 | 467.4436 | 0 | 46.7211 | 0 | 0 | 0 | 467.4436 | 0 | 0
12 | 18 | 14 | 7.8408 | 576.9859 | 584.8267 | 47.5039 | 9.8762 | 9485.7069 | 288 | 564.4075 | 17.7562 | 567.0705 | 9178.2423 | 56.6789 | 0 | 0 | 17.7562 | 567.0705 | 0 | 9178.2423
12 | 18 | 15 | 28.4891 | 204.8336 | 233.3228 | 43.4822 | 10.9601 | 0 | 0 | 568.5839 | 0 | 233.3228 | 0 | 23.3207 | 0 | 0 | 0 | 233.3228 | 0 | 0
12 | 18 | 16 | 0.20244 | 0 | 0.20244 | 11 | 11.5279 | 0 | 0 | 572.2441 | 0 | 0.20244 | 0 | 0.020234 | 0 | 0 | 0 | 0.20244 | 0 | 0
12 | 18 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 574.5722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 579.2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 579.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 572.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 557.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 554.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 555.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 554.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 562.2988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 567.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 566.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 561.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 560.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 562.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 563.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 8 | 15.95 | 49.2449 | 65.1949 | 38.9479 | 6.5729 | 39.6761 | 39.6761 | 569.5297 | 65.1949 | 0 | 34591.2137 | 0 | 0 | 0 | 65.1949 | 0 | 0 | 34591.2137
12 | 19 | 9 | 35.96 | 7.9303 | 43.8903 | 17.6853 | 7.7084 | 39.9174 | 39.9174 | 569.9821 | 43.8903 | 0 | 24240.4843 | 0 | 0 | 0 | 43.8903 | 0 | 0 | 24240.4843
12 | 19 | 10 | 22.9614 | 12.2799 | 35.2413 | 23.8927 | 8.9471 | 69.5838 | 69.5838 | 570.3034 | 35.2413 | 0 | 19256.1991 | 0 | 0 | 0 | 35.2413 | 0 | 0 | 19256.1991
12 | 19 | 11 | 63.8883 | 210.332 | 274.2204 | 39.3797 | 9.5923 | 1387.9948 | 288 | 568.7692 | 56.899 | 217.3214 | 30121.7173 | 21.7213 | 0 | 0 | 56.899 | 217.3214 | 0 | 30121.7173
12 | 19 | 12 | 53.1167 | 741.1034 | 794.2201 | 45.5255 | 10.2891 | 0 | 0 | 567.0873 | 0 | 794.2201 | 0 | 79.3825 | 0 | 0 | 0 | 794.2201 | 0 | 0
12 | 19 | 13 | 45.3908 | 340.3546 | 385.7455 | 43.6462 | 10.0827 | 0 | 0 | 564.9807 | 0 | 385.7455 | 0 | 38.5554 | 0 | 0 | 0 | 385.7455 | 0 | 0
12 | 19 | 14 | 40.6208 | 182.2546 | 222.8754 | 41.2565 | 10.6934 | 0 | 0 | 554.2589 | 0 | 222.8754 | 0 | 22.2765 | 0 | 0 | 0 | 222.8754 | 0 | 0
12 | 19 | 15 | 21.015 | 179.8619 | 200.8769 | 44.1292 | 11.6655 | 0 | 0 | 551.0602 | 0 | 200.8769 | 0 | 20.0777 | 0 | 0 | 0 | 200.8769 | 0 | 0
12 | 19 | 16 | 0 | 0 | 0 | 0 | 12.3021 | 0 | 0 | 553.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 555.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 560.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 19 | 0 | 0 | 0 | 0 | 13.2054 | 0 | 0 | 565.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 558.5833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 555.1977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 22 | 0 | 0 | 0 | 0 | 5.6868 | 0 | 0 | 553.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 23 | 0 | 0 | 0 | 0 | 4.5734 | 0 | 0 | 551.8649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 551.3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 554.5284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 557.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4416 | 0 | 0 | 553.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 4 | 0 | 0 | 0 | 0 | 3.6222 | 0 | 0 | 547.3153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 5 | 0 | 0 | 0 | 0 | 4.0351 | 0 | 0 | 549.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 6 | 0 | 0 | 0 | 0 | 5.1793 | 0 | 0 | 551.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 7 | 0 | 0 | 0 | 0 | 5.3599 | 0 | 0 | 560.6308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 8 | 3.5522 | 0.066667 | 3.6189 | 11.6816 | 6.5729 | 2.2024 | 2.2024 | 560.4775 | 3.6189 | 0 | 1986.0206 | 0 | 0 | 0 | 3.6189 | 0 | 0 | 1986.0206
12 | 20 | 9 | 0.012432 | 13.6864 | 13.6988 | 47.9664 | 7.6912 | 12.3662 | 12.3662 | 553.0747 | 13.6988 | 0 | 6919.3881 | 0 | 0 | 0 | 13.6988 | 0 | 0 | 6919.3881
12 | 20 | 10 | 3.1708 | 110.3444 | 113.5153 | 46.9665 | 8.4482 | 152.3012 | 152.3012 | 550.7077 | 113.5153 | 0 | 57182.309 | 0 | 0 | 0 | 113.5153 | 0 | 0 | 57182.309
12 | 20 | 11 | 19.0108 | 227.1418 | 246.1526 | 45.1424 | 9.7214 | 1812.7781 | 288 | 548.9283 | 39.1068 | 207.0458 | 19701.4534 | 20.6943 | 0 | 0 | 39.1068 | 207.0458 | 0 | 19701.4534
12 | 20 | 12 | 10.4333 | 89.1505 | 99.5839 | 44.1235 | 9.4117 | 350.5788 | 288 | 548.2474 | 81.808 | 17.7759 | 41241.3653 | 1.7767 | 0 | 0 | 81.808 | 17.7759 | 0 | 41241.3653
12 | 20 | 13 | 2.2032 | 16.4274 | 18.6306 | 43.6244 | 8.8869 | 34.8049 | 34.8049 | 547.4391 | 18.6306 | 0 | 9386.381 | 0 | 0 | 0 | 18.6306 | 0 | 0 | 9386.381
12 | 20 | 14 | 0 | 12.9776 | 12.9776 | 48 | 9.3428 | 40.9382 | 40.9382 | 542.6033 | 12.9776 | 0 | 6418.7485 | 0 | 0 | 0 | 12.9776 | 0 | 0 | 6418.7485
12 | 20 | 15 | 0 | 0.23251 | 0.23251 | 48 | 10.0224 | 0 | 0 | 549.7083 | 0 | 0.23251 | 0 | 0.02324 | 0 | 0 | 0 | 0.23251 | 0 | 0
12 | 20 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 553.2761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 557.6435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 564.6464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 560.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 549.485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 21 | 101.5805 | 0 | 101.5805 | 11 | 7.4847 | 84.1865 | 84.1865 | 537.9647 | 101.5805 | 0 | 53529.3298 | 0 | 0 | 0 | 101.5805 | 0 | 0 | 53529.3298
12 | 20 | 22 | 93.8477 | 0 | 93.8477 | 11 | 5.575 | 44.2483 | 44.2483 | 537.5455 | 93.8477 | 0 | 49415.0601 | 0 | 0 | 0 | 93.8477 | 0 | 0 | 49415.0601
12 | 20 | 23 | 49.0348 | 0 | 49.0348 | 11 | 4.5599 | 18.8095 | 18.8095 | 535.9187 | 49.0348 | 0 | 25739.2742 | 0 | 0 | 0 | 49.0348 | 0 | 0 | 25739.2742
12 | 21 | 0 | 69.287 | 0 | 69.287 | 11 | 4.5083 | 26.3285 | 26.3285 | 542.9005 | 69.287 | 0 | 36853.8098 | 0 | 0 | 0 | 69.287 | 0 | 0 | 36853.8098
12 | 21 | 1 | 24.5648 | 0 | 24.5648 | 11 | 4.2072 | 8.8497 | 8.8497 | 548.2702 | 24.5648 | 0 | 13197.9149 | 0 | 0 | 0 | 24.5648 | 0 | 0 | 13197.9149
12 | 21 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 549.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 534.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 535.0909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 542.3412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 554.5889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 560.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 8 | 2.8378 | 0.9767 | 3.8145 | 20.4739 | 5.4889 | 1.7642 | 1.7642 | 557.3947 | 3.8145 | 0 | 2048.0694 | 0 | 0 | 0 | 3.8145 | 0 | 0 | 2048.0694
12 | 21 | 9 | 41.3084 | 1.6498 | 42.9582 | 12.421 | 6.9858 | 29.7188 | 29.7188 | 552.2516 | 42.9582 | 0 | 23190.1372 | 0 | 0 | 0 | 42.9582 | 0 | 0 | 23190.1372
12 | 21 | 10 | 0 | 0.025792 | 0.025792 | 48 | 7.3471 | 0.020268 | 0.020268 | 548.2693 | 0.025792 | 0 | 12.9028 | 0 | 0 | 0 | 0.025792 | 0 | 0 | 12.9028
12 | 21 | 11 | 3.2883 | 16.5924 | 19.8807 | 41.8801 | 8.9643 | 39.9034 | 39.9034 | 543.1482 | 19.8807 | 0 | 9965.5567 | 0 | 0 | 0 | 19.8807 | 0 | 0 | 9965.5567
12 | 21 | 12 | 47.2616 | 174.6514 | 221.9129 | 40.12 | 8.2847 | 269.447 | 269.447 | 542.6504 | 221.9129 | 0 | 111517.9929 | 0 | 0 | 0 | 221.9129 | 0 | 0 | 111517.9929
12 | 21 | 13 | 3.2851 | 187.6044 | 190.8895 | 47.3632 | 7.8202 | 182.4967 | 182.4967 | 541.285 | 190.8895 | 0 | 94284.4802 | 0 | 0 | 0 | 190.8895 | 0 | 0 | 94284.4802
12 | 21 | 14 | 5.244 | 18.992 | 24.2361 | 39.9942 | 7.6568 | 21.5577 | 21.5577 | 529.9139 | 24.2361 | 0 | 11873.7308 | 0 | 0 | 0 | 24.2361 | 0 | 0 | 11873.7308
12 | 21 | 15 | 33.3321 | 0 | 33.3321 | 11 | 7.7256 | 30.5436 | 30.5436 | 537.5471 | 33.3321 | 0 | 17550.8992 | 0 | 0 | 0 | 33.3321 | 0 | 0 | 17550.8992
12 | 21 | 16 | 1.6684 | 0 | 1.6684 | 11 | 7.3729 | 1.324 | 1.324 | 544.5449 | 1.6684 | 0 | 890.1819 | 0 | 0 | 0 | 1.6684 | 0 | 0 | 890.1819
12 | 21 | 17 | 0 | 0 | 0 | 0 | 7.5449 | 0 | 0 | 543.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 539.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 529.8819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 20 | 0 | 0 | 0 | 0 | 7.3471 | 0 | 0 | 509.2871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 21 | 21 | 32.0435 | 0 | 32.0435 | 11 | 6.5556 | 19.4037 | 19.4037 | 496.9721 | 32.0435 | 0 | 15572.2572 | 0 | 0 | 0 | 32.0435 | 0 | 0 | 15572.2572
12 | 21 | 22 | 100.7746 | 0 | 100.7746 | 11 | 4.9212 | 41.4038 | 41.4038 | 482.063 | 100.7746 | 0 | 47471.1709 | 0 | 0 | 0 | 100.7746 | 0 | 0 | 47471.1709
12 | 21 | 23 | 102.1442 | 0 | 102.1442 | 11 | 4.5954 | 39.4395 | 39.4395 | 472.2443 | 102.1442 | 0 | 47113.4487 | 0 | 0 | 0 | 102.1442 | 0 | 0 | 47113.4487
12 | 22 | 0 | 100.8677 | 0 | 100.8677 | 11 | 3.8459 | 34.2068 | 34.2068 | 466.3892 | 100.8677 | 0 | 45934.0463 | 0 | 0 | 0 | 100.8677 | 0 | 0 | 45934.0463
12 | 22 | 1 | 98.6009 | 0 | 98.6009 | 11 | 3.4243 | 31.2962 | 31.2962 | 473.6889 | 98.6009 | 0 | 45621.5609 | 0 | 0 | 0 | 98.6009 | 0 | 0 | 45621.5609
12 | 22 | 2 | 39.9888 | 0 | 39.9888 | 11 | 3.3383 | 12.5288 | 12.5288 | 482.0648 | 39.9888 | 0 | 18837.2913 | 0 | 0 | 0 | 39.9888 | 0 | 0 | 18837.2913
12 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 494.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 509.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 5 | 0 | 0 | 0 | 0 | 3.4071 | 0 | 0 | 525.2469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 6 | 0 | 0 | 0 | 0 | 4.9556 | 0 | 0 | 525.1758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 7 | 0 | 0 | 0 | 0 | 6.5556 | 0 | 0 | 530.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 8 | 0 | 0 | 0 | 0 | 7.2524 | 0 | 0 | 533.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 9 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 526.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 10 | 0 | 0 | 0 | 0 | 7.8632 | 0 | 0 | 523.5236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 11 | 0 | 0.024083 | 0.024083 | 48 | 7.6051 | 0.020961 | 0.020961 | 522.7666 | 0.024083 | 0 | 11.434 | 0 | 0 | 0 | 0.024083 | 0 | 0 | 11.434
12 | 22 | 12 | 0 | 0.13983 | 0.13983 | 48 | 8.2589 | 0.16728 | 0.16728 | 520.3428 | 0.13983 | 0 | 66.0493 | 0 | 0 | 0 | 0.13983 | 0 | 0 | 66.0493
12 | 22 | 13 | 0 | 0 | 0 | 0 | 8.5686 | 0 | 0 | 530.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 14 | 0 | 0.43262 | 0.43262 | 48 | 8.6374 | 0.66077 | 0.66077 | 525.6023 | 0.43262 | 0 | 206.6227 | 0 | 0 | 0 | 0.43262 | 0 | 0 | 206.6227
12 | 22 | 15 | 0 | 0.19217 | 0.19217 | 48 | 7.803 | 0.18228 | 0.18228 | 540.1949 | 0.19217 | 0 | 94.5835 | 0 | 0 | 0 | 0.19217 | 0 | 0 | 94.5835
12 | 22 | 16 | 0 | 0 | 0 | 0 | 7.6998 | 0 | 0 | 544.4009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 17 | 0 | 0 | 0 | 0 | 7.6482 | 0 | 0 | 545.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 18 | 0 | 0 | 0 | 0 | 7.3041 | 0 | 0 | 546.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 535.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 20 | 0 | 0 | 0 | 0 | 6.6417 | 0 | 0 | 517.7356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 21 | 0 | 0 | 0 | 0 | 5.9879 | 0 | 0 | 504.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 22 | 0 | 0 | 0 | 0 | 5.0846 | 0 | 0 | 493.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 22 | 23 | 0 | 0 | 0 | 0 | 4.4566 | 0 | 0 | 491.4699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 0 | 0 | 0 | 0 | 0 | 3.9749 | 0 | 0 | 499.3922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 1 | 0 | 0 | 0 | 0 | 3.7598 | 0 | 0 | 508.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 2 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 515.8314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 3 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 517.9099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 4 | 0 | 0 | 0 | 0 | 3.6824 | 0 | 0 | 516.2619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 5 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 520.3323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 6 | 0 | 0 | 0 | 0 | 4.8007 | 0 | 0 | 528.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 7 | 0 | 0 | 0 | 0 | 6.3664 | 0 | 0 | 528.3716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 8 | 0 | 0.49908 | 0.49908 | 48 | 6.9944 | 0.34626 | 0.34626 | 522.8759 | 0.49908 | 0 | 237.0027 | 0 | 0 | 0 | 0.49908 | 0 | 0 | 237.0027
12 | 23 | 9 | 0 | 0.45167 | 0.45167 | 48 | 7.5707 | 0.38755 | 0.38755 | 520.5656 | 0.45167 | 0 | 213.4421 | 0 | 0 | 0 | 0.45167 | 0 | 0 | 213.4421
12 | 23 | 10 | 0 | 5.5837 | 5.5837 | 48 | 7.4159 | 4.5046 | 4.5046 | 518.1411 | 5.5837 | 0 | 2625.1307 | 0 | 0 | 0 | 5.5837 | 0 | 0 | 2625.1307
12 | 23 | 11 | 0 | 23.1086 | 23.1086 | 48 | 7.5879 | 19.9696 | 19.9696 | 508.8882 | 23.1086 | 0 | 10650.4621 | 0 | 0 | 0 | 23.1086 | 0 | 0 | 10650.4621
12 | 23 | 12 | 0 | 0.23888 | 0.23888 | 48 | 8.3192 | 0.29597 | 0.29597 | 512.4733 | 0.23888 | 0 | 110.9525 | 0 | 0 | 0 | 0.23888 | 0 | 0 | 110.9525
12 | 23 | 13 | 0 | 4.4678 | 4.4678 | 48 | 8.6546 | 6.9108 | 6.9108 | 521.0509 | 4.4678 | 0 | 2113.4784 | 0 | 0 | 0 | 4.4678 | 0 | 0 | 2113.4784
12 | 23 | 14 | 0 | 0.77804 | 0.77804 | 48 | 8.9299 | 1.5117 | 1.5117 | 523.7022 | 0.77804 | 0 | 370.1161 | 0 | 0 | 0 | 0.77804 | 0 | 0 | 370.1161
12 | 23 | 15 | 0 | 0 | 0 | 0 | 8.8009 | 0 | 0 | 532.4071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 16 | 0 | 0 | 0 | 0 | 9.5837 | 0 | 0 | 525.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 17 | 0 | 0 | 0 | 0 | 9.0762 | 0 | 0 | 523.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 18 | 0 | 0 | 0 | 0 | 9.4461 | 0 | 0 | 523.7942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 19 | 0 | 0 | 0 | 0 | 8.0611 | 0 | 0 | 518.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 20 | 0 | 0 | 0 | 0 | 11.2698 | 0 | 0 | 500.4873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 21 | 0 | 0 | 0 | 0 | 9.1708 | 0 | 0 | 486.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 23 | 22 | 48.3918 | 0 | 48.3918 | 11 | 5.4717 | 22.2967 | 22.2967 | 493.3857 | 48.3918 | 0 | 23343.4888 | 0 | 0 | 0 | 48.3918 | 0 | 0 | 23343.4888
12 | 23 | 23 | 98.8869 | 0 | 98.8869 | 11 | 4.8093 | 39.7538 | 39.7538 | 485.1664 | 98.8869 | 0 | 46888.8294 | 0 | 0 | 0 | 98.8869 | 0 | 0 | 46888.8294
12 | 24 | 0 | 74.2264 | 0 | 74.2264 | 11 | 3.3125 | 23.166 | 23.166 | 476.5464 | 74.2264 | 0 | 34555.817 | 0 | 0 | 0 | 74.2264 | 0 | 0 | 34555.817
12 | 24 | 1 | 125.0336 | 0 | 125.0336 | 11 | 3.2007 | 38.3815 | 38.3815 | 480.2687 | 125.0336 | 0 | 58674.3659 | 0 | 0 | 0 | 125.0336 | 0 | 0 | 58674.3659
12 | 24 | 2 | 116.4392 | 0 | 116.4392 | 11 | 3.1921 | 35.6981 | 35.6981 | 482.1252 | 116.4392 | 0 | 54857.4338 | 0 | 0 | 0 | 116.4392 | 0 | 0 | 54857.4338
12 | 24 | 3 | 118.2286 | 0 | 118.2286 | 11 | 3.3297 | 36.9941 | 36.9941 | 482.8231 | 118.2286 | 0 | 55782.9845 | 0 | 0 | 0 | 118.2286 | 0 | 0 | 55782.9845
12 | 24 | 4 | 152.8573 | 0 | 152.8573 | 11 | 3.3469 | 47.9532 | 47.9532 | 497.9594 | 152.8573 | 0 | 74435.3112 | 0 | 0 | 0 | 152.8573 | 0 | 0 | 74435.3112
12 | 24 | 5 | 153.3275 | 0 | 153.3275 | 11 | 3.7857 | 51.4938 | 51.4938 | 517.0172 | 153.3275 | 0 | 77586.3443 | 0 | 0 | 0 | 153.3275 | 0 | 0 | 77586.3443
12 | 24 | 6 | 151.6278 | 0 | 151.6278 | 11 | 4.5255 | 57.7983 | 57.7983 | 533.4788 | 151.6278 | 0 | 79222.2923 | 0 | 0 | 0 | 151.6278 | 0 | 0 | 79222.2923
12 | 24 | 7 | 88.7804 | 0 | 88.7804 | 11 | 5.2137 | 38.7026 | 38.7026 | 541.1312 | 88.7804 | 0 | 47065.2525 | 0 | 0 | 0 | 88.7804 | 0 | 0 | 47065.2525
12 | 24 | 8 | 0 | 0 | 0 | 0 | 5.1879 | 0 | 0 | 540.6787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 9 | 0 | 5.7881 | 5.7881 | 48 | 6.7449 | 3.7084 | 3.7084 | 533.4086 | 5.7881 | 0 | 2809.6056 | 0 | 0 | 0 | 5.7881 | 0 | 0 | 2809.6056
12 | 24 | 10 | 0 | 0.22913 | 0.22913 | 48 | 8.8783 | 0.42477 | 0.42477 | 532.0458 | 0.22912 | 0 | 110.907 | 0 | 0 | 0 | 0.22912 | 0 | 0 | 110.907
12 | 24 | 11 | 0 | 0 | 0 | 0 | 9.8676 | 0 | 0 | 524.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 12 | 0 | 0 | 0 | 0 | 10.2547 | 0 | 0 | 511.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 13 | 0 | 0 | 0 | 0 | 10.031 | 0 | 0 | 515.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 14 | 0 | 0 | 0 | 0 | 9.9364 | 0 | 0 | 525.6899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 15 | 0 | 0.16654 | 0.16654 | 48 | 11.1494 | 0 | 0 | 522.4836 | 0 | 0.16654 | 0 | 0.016646 | 0 | 0 | 0 | 0.16654 | 0 | 0
12 | 24 | 16 | 0 | 0 | 0 | 0 | 12.5086 | 0 | 0 | 515.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 523.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 18 | 0 | 0 | 0 | 0 | 12.801 | 0 | 0 | 520.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 19 | 0 | 0 | 0 | 0 | 12.7322 | 0 | 0 | 516.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 505.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 479.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 460.6692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 24 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 456.5868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 0 | 0 | 0 | 0 | 0 | 3.5706 | 0 | 0 | 459.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 1 | 9.4949 | 0 | 9.4949 | 11 | 3.4588 | 3.0296 | 3.0296 | 461.1345 | 9.4949 | 0 | 4273.9874 | 0 | 0 | 0 | 9.4949 | 0 | 0 | 4273.9874
12 | 25 | 2 | 13.6357 | 0 | 13.6357 | 11 | 3.3555 | 4.2832 | 4.2832 | 466.5703 | 13.6357 | 0 | 6212.0279 | 0 | 0 | 0 | 13.6357 | 0 | 0 | 6212.0279
12 | 25 | 3 | 21.1914 | 0 | 21.1914 | 11 | 3.4416 | 6.7439 | 6.7439 | 468.6481 | 21.1914 | 0 | 9698.2195 | 0 | 0 | 0 | 21.1914 | 0 | 0 | 9698.2195
12 | 25 | 4 | 0 | 0 | 0 | 0 | 3.691 | 0 | 0 | 482.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 5 | 0 | 0 | 0 | 0 | 3.9405 | 0 | 0 | 489.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 6 | 0 | 0 | 0 | 0 | 4.8093 | 0 | 0 | 483.3079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 7 | 0 | 0 | 0 | 0 | 5.1706 | 0 | 0 | 478.3982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 8 | 0 | 0 | 0 | 0 | 5.8502 | 0 | 0 | 465.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 9 | 0 | 0.43675 | 0.43675 | 48 | 6.7707 | 0.28206 | 0.28206 | 463.2268 | 0.43675 | 0 | 181.3503 | 0 | 0 | 0 | 0.43675 | 0 | 0 | 181.3503
12 | 25 | 10 | 0 | 3.174 | 3.174 | 48 | 8.9987 | 6.5885 | 6.5885 | 455.9042 | 3.174 | 0 | 1294.6881 | 0 | 0 | 0 | 3.174 | 0 | 0 | 1294.6881
12 | 25 | 11 | 8.3648 | 0.39829 | 8.763 | 12.6817 | 10.0569 | 0 | 0 | 443.9824 | 0 | 8.763 | 0 | 0.87587 | 0 | 0 | 0 | 8.763 | 0 | 0
12 | 25 | 12 | 1.6403 | 0 | 1.6403 | 11 | 10.1343 | 0 | 0 | 436.3934 | 0 | 1.6403 | 0 | 0.16395 | 0 | 0 | 0 | 1.6403 | 0 | 0
12 | 25 | 13 | 2.62 | 0.12662 | 2.7466 | 12.7058 | 10.2117 | 0 | 0 | 440.6064 | 0 | 2.7466 | 0 | 0.27452 | 0 | 0 | 0 | 2.7466 | 0 | 0
12 | 25 | 14 | 0.15 | 4.9657 | 5.1157 | 46.9151 | 9.8762 | 82.9759 | 82.9759 | 463.2943 | 5.1157 | 0 | 2130.092 | 0 | 0 | 0 | 5.1157 | 0 | 0 | 2130.092
12 | 25 | 15 | 0 | 0.23612 | 0.23612 | 48 | 10.9601 | 0 | 0 | 473.9575 | 0 | 0.23612 | 0 | 0.023601 | 0 | 0 | 0 | 0.23612 | 0 | 0
12 | 25 | 16 | 0 | 0 | 0 | 0 | 11.5279 | 0 | 0 | 466.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 17 | 0 | 0 | 0 | 0 | 11.5451 | 0 | 0 | 470.2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 18 | 0 | 0 | 0 | 0 | 11.9236 | 0 | 0 | 475.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 19 | 0 | 0 | 0 | 0 | 13.1107 | 0 | 0 | 463.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 20 | 0 | 0 | 0 | 0 | 12.6978 | 0 | 0 | 447.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 21 | 0 | 0 | 0 | 0 | 9.8762 | 0 | 0 | 425.3903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 22 | 0 | 0 | 0 | 0 | 6.1771 | 0 | 0 | 416.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 25 | 23 | 0 | 0 | 0 | 0 | 4.6373 | 0 | 0 | 408.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 0 | 0 | 0 | 0 | 0 | 3.9577 | 0 | 0 | 404.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 1 | 0 | 0 | 0 | 0 | 3.6394 | 0 | 0 | 406.5675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 2 | 0 | 0 | 0 | 0 | 3.5276 | 0 | 0 | 410.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 3 | 0 | 0 | 0 | 0 | 3.562 | 0 | 0 | 424.6005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 4 | 0 | 0 | 0 | 0 | 3.5878 | 0 | 0 | 435.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 5 | 0 | 0 | 0 | 0 | 4.1814 | 0 | 0 | 445.6913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 6 | 0 | 0 | 0 | 0 | 5.3513 | 0 | 0 | 459.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 7 | 0 | 0 | 0 | 0 | 5.6008 | 0 | 0 | 469.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 8 | 5.293 | 0.045833 | 5.3388 | 11.3176 | 6.5729 | 3.2491 | 3.2491 | 477.4431 | 5.3388 | 0 | 2488.5723 | 0 | 0 | 0 | 5.3388 | 0 | 0 | 2488.5723
12 | 26 | 9 | 7.9467 | 0.27667 | 8.2233 | 12.2448 | 7.7084 | 7.479 | 7.479 | 478.4853 | 8.2233 | 0 | 3834.0506 | 0 | 0 | 0 | 8.2233 | 0 | 0 | 3834.0506
12 | 26 | 10 | 14.4557 | 106.5772 | 121.0329 | 43.5809 | 8.9471 | 238.9793 | 238.9793 | 473.7371 | 121.0329 | 0 | 52063.054 | 0 | 0 | 0 | 121.0329 | 0 | 0 | 52063.054
12 | 26 | 11 | 58.5995 | 645.8496 | 704.4491 | 44.9222 | 9.5923 | 3565.6419 | 288 | 465.5184 | 56.899 | 647.5501 | 23931.4922 | 64.7228 | 0 | 0 | 56.899 | 647.5501 | 0 | 23931.4922
12 | 26 | 12 | 41.5194 | 388.3863 | 429.9057 | 44.4266 | 10.2891 | 0 | 0 | 456.481 | 0 | 429.9057 | 0 | 42.9692 | 0 | 0 | 0 | 429.9057 | 0 | 0
12 | 26 | 13 | 17.43 | 214.2253 | 231.6553 | 45.2161 | 10.0827 | 0 | 0 | 458.9349 | 0 | 231.6553 | 0 | 23.154 | 0 | 0 | 0 | 231.6553 | 0 | 0
12 | 26 | 14 | 8.0724 | 148.5493 | 156.6217 | 46.093 | 10.6934 | 0 | 0 | 466.9641 | 0 | 156.6217 | 0 | 15.6544 | 0 | 0 | 0 | 156.6217 | 0 | 0
12 | 26 | 15 | 0 | 0.7105 | 0.7105 | 48 | 11.6655 | 0 | 0 | 480.9293 | 0 | 0.7105 | 0 | 0.071015 | 0 | 0 | 0 | 0.7105 | 0 | 0
12 | 26 | 16 | 1.1242 | 0 | 1.1242 | 11 | 12.3021 | 0 | 0 | 478.6661 | 0 | 1.1242 | 0 | 0.11236 | 0 | 0 | 0 | 1.1242 | 0 | 0
12 | 26 | 17 | 0 | 0 | 0 | 0 | 12.1989 | 0 | 0 | 480.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 18 | 0 | 0 | 0 | 0 | 12.9559 | 0 | 0 | 476.2699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 19 | 0.0575 | 0 | 0.0575 | 11 | 13.2054 | 0 | 0 | 465.5436 | 0 | 0.0575 | 0 | 0.0057471 | 0 | 0 | 0 | 0.0575 | 0 | 0
12 | 26 | 20 | 0 | 0 | 0 | 0 | 12.6806 | 0 | 0 | 436.378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 21 | 0 | 0 | 0 | 0 | 10.3235 | 0 | 0 | 416.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 26 | 22 | 18.7271 | 0 | 18.7271 | 11 | 5.6868 | 9.0583 | 9.0583 | 403.857 | 18.7271 | 0 | 7357.0529 | 0 | 0 | 0 | 18.7271 | 0 | 0 | 7357.0529
12 | 26 | 23 | 48.0174 | 0 | 48.0174 | 11 | 4.5734 | 18.4651 | 18.4651 | 406.4628 | 48.0174 | 0 | 18989.1004 | 0 | 0 | 0 | 48.0174 | 0 | 0 | 18989.1004
12 | 27 | 0 | 0 | 0 | 0 | 0 | 3.8373 | 0 | 0 | 408.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 1 | 0 | 0 | 0 | 0 | 3.605 | 0 | 0 | 417.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 2 | 0 | 0 | 0 | 0 | 3.5018 | 0 | 0 | 420.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 3 | 2.5946 | 0 | 2.5946 | 11 | 3.4416 | 0.82569 | 0.82569 | 434.9376 | 2.5946 | 0 | 1099.9478 | 0 | 0 | 0 | 2.5946 | 0 | 0 | 1099.9478
12 | 27 | 4 | 52.8743 | 0 | 52.8743 | 11 | 3.6222 | 17.3027 | 17.3027 | 478.4656 | 52.8743 | 0 | 24716.9067 | 0 | 0 | 0 | 52.8743 | 0 | 0 | 24716.9067
12 | 27 | 5 | 113.8708 | 0 | 113.8708 | 11 | 4.0351 | 39.8407 | 39.8407 | 481.8123 | 113.8708 | 0 | 53611.7545 | 0 | 0 | 0 | 113.8708 | 0 | 0 | 53611.7545
12 | 27 | 6 | 117.4977 | 0 | 117.4977 | 11 | 5.1793 | 50.8563 | 50.8563 | 500.104 | 117.4977 | 0 | 57468.5688 | 0 | 0 | 0 | 117.4977 | 0 | 0 | 57468.5688
12 | 27 | 7 | 149.8748 | 0 | 149.8748 | 11 | 5.3599 | 67.3929 | 67.3929 | 498.1559 | 149.8748 | 0 | 73012.4055 | 0 | 0 | 0 | 149.8748 | 0 | 0 | 73012.4055
12 | 27 | 8 | 158.1101 | 66.9426 | 225.0527 | 22.0058 | 6.5729 | 136.9617 | 136.9617 | 506.766 | 225.0527 | 0 | 109096.5982 | 0 | 0 | 0 | 225.0527 | 0 | 0 | 109096.5982
12 | 27 | 9 | 123.2577 | 25.8268 | 149.0845 | 17.4097 | 7.6912 | 134.5811 | 134.5811 | 502.2358 | 149.0845 | 0 | 72280.0429 | 0 | 0 | 0 | 149.0845 | 0 | 0 | 72280.0429
12 | 27 | 10 | 93.2522 | 0.1875 | 93.4397 | 11.0742 | 8.4482 | 125.3662 | 125.3662 | 492.7107 | 93.4397 | 0 | 45003.9602 | 0 | 0 | 0 | 93.4397 | 0 | 0 | 45003.9602
12 | 27 | 11 | 33.8742 | 1.7714 | 35.6457 | 12.8388 | 9.7214 | 262.5105 | 262.5105 | 483.4509 | 35.6457 | 0 | 16775.2742 | 0 | 0 | 0 | 35.6457 | 0 | 0 | 16775.2742
12 | 27 | 12 | 16.2068 | 69.0247 | 85.2315 | 40.9644 | 9.4117 | 300.0523 | 288 | 480.9645 | 81.808 | 3.4235 | 35995.5252 | 0.34218 | 0 | 0 | 81.808 | 3.4235 | 0 | 35995.5252
12 | 27 | 13 | 6.3392 | 21.6212 | 27.9603 | 39.6114 | 8.8869 | 52.2342 | 52.2342 | 480.3576 | 27.9603 | 0 | 12323.4098 | 0 | 0 | 0 | 27.9603 | 0 | 0 | 12323.4098
12 | 27 | 14 | 0 | 1.3243 | 1.3243 | 48 | 9.3428 | 4.1775 | 4.1775 | 485.2497 | 1.3243 | 0 | 579.036 | 0 | 0 | 0 | 1.3243 | 0 | 0 | 579.036
12 | 27 | 15 | 0 | 0 | 0 | 0 | 10.0224 | 0 | 0 | 514.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 16 | 0 | 0 | 0 | 0 | 11.4074 | 0 | 0 | 522.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 17 | 0 | 0 | 0 | 0 | 10.8053 | 0 | 0 | 516.7522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 18 | 0 | 0 | 0 | 0 | 11.5107 | 0 | 0 | 514.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 19 | 0 | 0 | 0 | 0 | 10.8913 | 0 | 0 | 508.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 20 | 0 | 0 | 0 | 0 | 8.4138 | 0 | 0 | 494.5703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 21 | 0 | 0 | 0 | 0 | 7.4847 | 0 | 0 | 485.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 22 | 0 | 0 | 0 | 0 | 5.575 | 0 | 0 | 483.1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 27 | 23 | 0 | 0 | 0 | 0 | 4.5599 | 0 | 0 | 481.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 0 | 0 | 0 | 0 | 0 | 4.5083 | 0 | 0 | 477.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 1 | 0 | 0 | 0 | 0 | 4.2072 | 0 | 0 | 484.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 2 | 0 | 0 | 0 | 0 | 4.147 | 0 | 0 | 495.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 3 | 0 | 0 | 0 | 0 | 3.7857 | 0 | 0 | 496.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 4 | 0 | 0 | 0 | 0 | 3.7254 | 0 | 0 | 505.8576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 5 | 0 | 0 | 0 | 0 | 3.9663 | 0 | 0 | 515.3866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 6 | 0 | 0 | 0 | 0 | 4.7319 | 0 | 0 | 513.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 7 | 0 | 0 | 0 | 0 | 4.99 | 0 | 0 | 514.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 8 | 7.0875 | 13.6781 | 20.7656 | 35.3715 | 5.4889 | 9.6043 | 9.6043 | 512.6883 | 20.7656 | 0 | 9911.7643 | 0 | 0 | 0 | 20.7656 | 0 | 0 | 9911.7643
12 | 28 | 9 | 9.311 | 112.0312 | 121.3423 | 45.1609 | 6.9858 | 83.9455 | 83.9455 | 510.1724 | 121.3423 | 0 | 56425.5538 | 0 | 0 | 0 | 121.3423 | 0 | 0 | 56425.5538
12 | 28 | 10 | 16.0258 | 130.1016 | 146.1273 | 43.9422 | 7.3471 | 114.834 | 114.834 | 505.1084 | 146.1273 | 0 | 67388.9889 | 0 | 0 | 0 | 146.1273 | 0 | 0 | 67388.9889
12 | 28 | 11 | 18.6175 | 502.099 | 520.7165 | 46.6771 | 8.9643 | 1045.1527 | 288 | 502.928 | 143.4875 | 377.229 | 65466.3022 | 37.7041 | 0 | 0 | 143.4875 | 377.229 | 0 | 65466.3022
12 | 28 | 12 | 9.7258 | 32.0006 | 41.7265 | 39.3758 | 8.2847 | 50.6644 | 50.6644 | 502.1403 | 41.7265 | 0 | 19309.5313 | 0 | 0 | 0 | 41.7265 | 0 | 0 | 19309.5313
12 | 28 | 13 | 10.2158 | 156.8811 | 167.0969 | 45.7379 | 7.8202 | 159.7502 | 159.7502 | 514.6828 | 167.0969 | 0 | 78359.2219 | 0 | 0 | 0 | 167.0969 | 0 | 0 | 78359.2219
12 | 28 | 14 | 9.8108 | 226.5438 | 236.3546 | 46.4642 | 7.6568 | 210.2348 | 210.2348 | 502.7435 | 236.3546 | 0 | 107843.7416 | 0 | 0 | 0 | 236.3546 | 0 | 0 | 107843.7416
12 | 28 | 15 | 4.34 | 87.8845 | 92.2245 | 46.2588 | 7.7256 | 84.5094 | 84.5094 | 509.1757 | 92.2245 | 0 | 42692.2775 | 0 | 0 | 0 | 92.2245 | 0 | 0 | 42692.2775
12 | 28 | 16 | 0 | 0 | 0 | 0 | 7.3729 | 0 | 0 | 514.2711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 17 | 0.29537 | 0 | 0.29537 | 11 | 7.5449 | 0.25079 | 0.25079 | 522.494 | 0.29537 | 0 | 151.0812 | 0 | 0 | 0 | 0.29537 | 0 | 0 | 151.0812
12 | 28 | 18 | 0 | 0 | 0 | 0 | 7.0804 | 0 | 0 | 515.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 19 | 0 | 0 | 0 | 0 | 7.7772 | 0 | 0 | 516.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 28 | 20 | 20.8295 | 0 | 20.8295 | 11 | 7.3471 | 16.3689 | 16.3689 | 493.819 | 20.8295 | 0 | 10056.9006 | 0 | 0 | 0 | 20.8295 | 0 | 0 | 10056.9006
12 | 28 | 21 | 41.9686 | 0 | 41.9686 | 11 | 6.5556 | 25.4137 | 25.4137 | 479.0731 | 41.9686 | 0 | 19644.3813 | 0 | 0 | 0 | 41.9686 | 0 | 0 | 19644.3813
12 | 28 | 22 | 48.9083 | 0 | 48.9083 | 11 | 4.9212 | 20.0943 | 20.0943 | 472.1831 | 48.9083 | 0 | 22555.6855 | 0 | 0 | 0 | 48.9083 | 0 | 0 | 22555.6855
12 | 28 | 23 | 6.7505 | 0 | 6.7505 | 11 | 4.5954 | 2.6065 | 2.6065 | 471.7456 | 6.7505 | 0 | 3110.248 | 0 | 0 | 0 | 6.7505 | 0 | 0 | 3110.248
12 | 29 | 0 | 0 | 0 | 0 | 0 | 3.8459 | 0 | 0 | 471.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 1 | 0 | 0 | 0 | 0 | 3.4243 | 0 | 0 | 474.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 2 | 0 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 480.4979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 3 | 0 | 0 | 0 | 0 | 3.3039 | 0 | 0 | 478.0727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 4 | 0 | 0 | 0 | 0 | 3.2609 | 0 | 0 | 480.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 5 | 15.989 | 0 | 15.989 | 11 | 3.4071 | 5.0617 | 5.0617 | 492.884 | 15.989 | 0 | 7704.8259 | 0 | 0 | 0 | 15.989 | 0 | 0 | 7704.8259
12 | 29 | 6 | 36.6772 | 0 | 36.6772 | 11 | 4.9556 | 15.1717 | 15.1717 | 496.7202 | 36.6772 | 0 | 17814.8524 | 0 | 0 | 0 | 36.6772 | 0 | 0 | 17814.8524
12 | 29 | 7 | 45.9262 | 0 | 45.9262 | 11 | 6.5556 | 27.8102 | 27.8102 | 501.9489 | 45.9262 | 0 | 22547.4273 | 0 | 0 | 0 | 45.9262 | 0 | 0 | 22547.4273
12 | 29 | 8 | 27.813 | 0 | 27.813 | 11 | 7.2524 | 21.1054 | 21.1054 | 496.729 | 27.813 | 0 | 13509.5839 | 0 | 0 | 0 | 27.813 | 0 | 0 | 13509.5839
12 | 29 | 9 | 44.9116 | 0.7195 | 45.6311 | 11.5834 | 7.6998 | 41.3457 | 41.3457 | 498.8816 | 45.6311 | 0 | 22235.9436 | 0 | 0 | 0 | 45.6311 | 0 | 0 | 22235.9436
12 | 29 | 10 | 15.8858 | 3.2649 | 19.1507 | 17.3079 | 7.8632 | 18.6764 | 18.6764 | 498.4294 | 19.1507 | 0 | 9213.8187 | 0 | 0 | 0 | 19.1507 | 0 | 0 | 9213.8187
12 | 29 | 11 | 9.2332 | 136.317 | 145.5501 | 45.6529 | 7.6051 | 126.6807 | 126.6807 | 494.5465 | 145.5501 | 0 | 65336.5369 | 0 | 0 | 0 | 145.5501 | 0 | 0 | 65336.5369
12 | 29 | 12 | 10.04 | 124.8027 | 134.8427 | 45.2451 | 8.2589 | 161.3063 | 161.3063 | 487.6198 | 134.8427 | 0 | 59651.0044 | 0 | 0 | 0 | 134.8427 | 0 | 0 | 59651.0044
12 | 29 | 13 | 8.8642 | 92.4822 | 101.3464 | 44.7638 | 8.5686 | 147.3756 | 147.3756 | 476.3817 | 101.3464 | 0 | 43742.9043 | 0 | 0 | 0 | 101.3464 | 0 | 0 | 43742.9043
12 | 29 | 14 | 0 | 10.2373 | 10.2373 | 48 | 8.6374 | 15.636 | 15.636 | 474.35 | 10.2373 | 0 | 4364.6559 | 0 | 0 | 0 | 10.2373 | 0 | 0 | 4364.6559
12 | 29 | 15 | 0 | 0.026625 | 0.026625 | 48 | 7.803 | 0.025256 | 0.025256 | 490.5643 | 0.026625 | 0 | 11.7833 | 0 | 0 | 0 | 0.026625 | 0 | 0 | 11.7833
12 | 29 | 16 | 0.020516 | 0 | 0.020516 | 11 | 7.6998 | 0.018589 | 0.018589 | 499.1213 | 0.020516 | 0 | 10.0143 | 0 | 0 | 0 | 0.020516 | 0 | 0 | 10.0143
12 | 29 | 17 | 13.3563 | 0 | 13.3563 | 11 | 7.6482 | 11.8369 | 11.8369 | 498.199 | 13.3563 | 0 | 6507.1908 | 0 | 0 | 0 | 13.3563 | 0 | 0 | 6507.1908
12 | 29 | 18 | 1.3196 | 0 | 1.3196 | 11 | 7.3041 | 1.0205 | 1.0205 | 507.1038 | 1.3196 | 0 | 654.681 | 0 | 0 | 0 | 1.3196 | 0 | 0 | 654.681
12 | 29 | 19 | 0 | 0 | 0 | 0 | 7.3127 | 0 | 0 | 507.1047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 29 | 20 | 36.5006 | 0 | 36.5006 | 11 | 6.6417 | 22.668 | 22.668 | 495.304 | 36.5006 | 0 | 17677.4069 | 0 | 0 | 0 | 36.5006 | 0 | 0 | 17677.4069
12 | 29 | 21 | 82.785 | 0 | 82.785 | 11 | 5.9879 | 43.0445 | 43.0445 | 478.8835 | 82.785 | 0 | 38733.7325 | 0 | 0 | 0 | 82.785 | 0 | 0 | 38733.7325
12 | 29 | 22 | 101.6298 | 0 | 101.6298 | 11 | 5.0846 | 43.1423 | 43.1423 | 469.1536 | 101.6298 | 0 | 46562.0556 | 0 | 0 | 0 | 101.6298 | 0 | 0 | 46562.0556
12 | 29 | 23 | 101.2806 | 0 | 101.2806 | 11 | 4.4566 | 38.1278 | 38.1278 | 462.2892 | 101.2806 | 0 | 45706.8363 | 0 | 0 | 0 | 101.2806 | 0 | 0 | 45706.8363
12 | 30 | 0 | 147.2753 | 0 | 147.2753 | 11 | 3.9749 | 51.0135 | 51.0135 | 469.0929 | 147.2753 | 0 | 67465.7511 | 0 | 0 | 0 | 147.2753 | 0 | 0 | 67465.7511
12 | 30 | 1 | 104.2013 | 0 | 104.2013 | 11 | 3.7598 | 34.8505 | 34.8505 | 474.1714 | 104.2013 | 0 | 48263.0496 | 0 | 0 | 0 | 104.2013 | 0 | 0 | 48263.0496
12 | 30 | 2 | 103.3726 | 0 | 103.3726 | 11 | 3.691 | 34.1966 | 34.1966 | 486.189 | 103.3726 | 0 | 49121.5458 | 0 | 0 | 0 | 103.3726 | 0 | 0 | 49121.5458
12 | 30 | 3 | 126.8256 | 0 | 126.8256 | 11 | 3.6824 | 41.8979 | 41.8979 | 485.8907 | 126.8256 | 0 | 60228.3114 | 0 | 0 | 0 | 126.8256 | 0 | 0 | 60228.3114
12 | 30 | 4 | 108.2372 | 0 | 108.2372 | 11 | 3.6824 | 35.7571 | 35.7571 | 500.2842 | 108.2372 | 0 | 52958.7264 | 0 | 0 | 0 | 108.2372 | 0 | 0 | 52958.7264
12 | 30 | 5 | 117.6851 | 0 | 117.6851 | 11 | 3.691 | 38.9312 | 38.9312 | 514.9546 | 117.6851 | 0 | 59307.9189 | 0 | 0 | 0 | 117.6851 | 0 | 0 | 59307.9189
12 | 30 | 6 | 123.9797 | 0 | 123.9797 | 11 | 4.8007 | 49.759 | 49.759 | 509.0336 | 123.9797 | 0 | 61746.0547 | 0 | 0 | 0 | 123.9797 | 0 | 0 | 61746.0547
12 | 30 | 7 | 91.7853 | 0 | 91.7853 | 11 | 6.3664 | 52.6889 | 52.6889 | 512.1476 | 91.7853 | 0 | 45997.9865 | 0 | 0 | 0 | 91.7853 | 0 | 0 | 45997.9865
12 | 30 | 8 | 64.7285 | 0.12583 | 64.8544 | 11.0718 | 6.9944 | 44.9949 | 44.9949 | 522.0606 | 64.8544 | 0 | 33139.8572 | 0 | 0 | 0 | 64.8544 | 0 | 0 | 33139.8572
12 | 30 | 9 | 25.5197 | 6.3122 | 31.8319 | 18.337 | 7.5707 | 27.3135 | 27.3135 | 529.2022 | 31.8319 | 0 | 16261.8218 | 0 | 0 | 0 | 31.8319 | 0 | 0 | 16261.8218
12 | 30 | 10 | 120.0359 | 125.483 | 245.5189 | 29.9104 | 7.4159 | 198.0693 | 198.0693 | 522.3685 | 245.5189 | 0 | 120907.7667 | 0 | 0 | 0 | 245.5189 | 0 | 0 | 120907.7667
12 | 30 | 11 | 156.493 | 274.2645 | 430.7575 | 34.558 | 7.5879 | 372.2445 | 288 | 513.022 | 333.2706 | 97.4869 | 159457.9852 | 9.7438 | 0 | 0 | 333.2706 | 97.4869 | 0 | 159457.9852
12 | 30 | 12 | 108.6385 | 0.60586 | 109.2444 | 11.2052 | 8.3192 | 135.3521 | 135.3521 | 513.13 | 109.2444 | 0 | 54832.454 | 0 | 0 | 0 | 109.2444 | 0 | 0 | 54832.454
12 | 30 | 13 | 94.9055 | 1.7285 | 96.634 | 11.6618 | 8.6546 | 149.4752 | 149.4752 | 508.2651 | 96.634 | 0 | 47988.7466 | 0 | 0 | 0 | 96.634 | 0 | 0 | 47988.7466
12 | 30 | 14 | 96.811 | 0.049256 | 96.8603 | 11.0188 | 8.9299 | 188.1898 | 188.1898 | 501.6294 | 96.8603 | 0 | 47520.6761 | 0 | 0 | 0 | 96.8603 | 0 | 0 | 47520.6761
12 | 30 | 15 | 83.167 | 0.99846 | 84.1654 | 11.4389 | 8.8009 | 146.0006 | 146.0006 | 501.3146 | 84.1654 | 0 | 41230.597 | 0 | 0 | 0 | 84.1654 | 0 | 0 | 41230.597
12 | 30 | 16 | 48.8379 | 0 | 48.8379 | 11 | 9.5837 | 242.1501 | 242.1501 | 490.9132 | 48.8379 | 0 | 23437.9534 | 0 | 0 | 0 | 48.8379 | 0 | 0 | 23437.9534
12 | 30 | 17 | 55.2299 | 0 | 55.2299 | 11 | 9.0762 | 124.2016 | 124.2016 | 490.0121 | 55.2299 | 0 | 26455.7886 | 0 | 0 | 0 | 55.2299 | 0 | 0 | 26455.7886
12 | 30 | 18 | 94.0642 | 0 | 94.0642 | 11 | 9.4461 | 351.535 | 288 | 507.4959 | 77.0634 | 17.0008 | 38261.673 | 1.6992 | 0 | 0 | 77.0634 | 17.0008 | 0 | 38261.673
12 | 30 | 19 | 142.9144 | 0 | 142.9144 | 11 | 8.0611 | 153.5609 | 153.5609 | 508.9989 | 142.9144 | 0 | 71171.2102 | 0 | 0 | 0 | 142.9144 | 0 | 0 | 71171.2102
12 | 30 | 20 | 132.1095 | 0 | 132.1095 | 11 | 11.2698 | 0 | 0 | 498.8783 | 0 | 132.1095 | 0 | 13.2044 | 0 | 0 | 0 | 132.1095 | 0 | 0
12 | 30 | 21 | 198.184 | 0 | 198.184 | 11 | 9.1708 | 496.2351 | 288 | 501.6121 | 115.02 | 83.1639 | 56430.2242 | 8.3123 | 0 | 0 | 115.02 | 83.1639 | 0 | 56430.2242
12 | 30 | 22 | 157.7022 | 0 | 157.7022 | 11 | 5.4717 | 72.6619 | 72.6619 | 495.9436 | 157.7022 | 0 | 76476.6702 | 0 | 0 | 0 | 157.7022 | 0 | 0 | 76476.6702
12 | 30 | 23 | 153.4767 | 0 | 153.4767 | 11 | 4.8093 | 61.6996 | 61.6996 | 499.5715 | 153.4767 | 0 | 74984.3666 | 0 | 0 | 0 | 153.4767 | 0 | 0 | 74984.3666
12 | 31 | 0 | 173.237 | 0 | 173.237 | 11 | 3.3125 | 54.0671 | 54.0671 | 503.562 | 173.237 | 0 | 85329.9435 | 0 | 0 | 0 | 173.237 | 0 | 0 | 85329.9435
12 | 31 | 1 | 98.6254 | 0 | 98.6254 | 11 | 3.2007 | 30.275 | 30.275 | 505.9937 | 98.6254 | 0 | 48818.9381 | 0 | 0 | 0 | 98.6254 | 0 | 0 | 48818.9381
12 | 31 | 2 | 50.3277 | 0 | 50.3277 | 11 | 3.1921 | 15.4295 | 15.4295 | 498.2921 | 50.3277 | 0 | 24524.2664 | 0 | 0 | 0 | 50.3277 | 0 | 0 | 24524.2664
12 | 31 | 3 | 82.7227 | 0 | 82.7227 | 11 | 3.3297 | 25.8842 | 25.8842 | 493.1194 | 82.7227 | 0 | 39882.2378 | 0 | 0 | 0 | 82.7227 | 0 | 0 | 39882.2378
12 | 31 | 4 | 80.6543 | 0 | 80.6543 | 11 | 3.3469 | 25.3022 | 25.3022 | 500.2843 | 80.6543 | 0 | 39462.8776 | 0 | 0 | 0 | 80.6543 | 0 | 0 | 39462.8776
12 | 31 | 5 | 40.4969 | 0 | 40.4969 | 11 | 3.7857 | 13.6005 | 13.6005 | 500.7046 | 40.4969 | 0 | 19831.5048 | 0 | 0 | 0 | 40.4969 | 0 | 0 | 19831.5048
12 | 31 | 6 | 38.2403 | 0 | 38.2403 | 11 | 4.5255 | 14.5766 | 14.5766 | 498.3275 | 38.2403 | 0 | 18635.5311 | 0 | 0 | 0 | 38.2403 | 0 | 0 | 18635.5311
12 | 31 | 7 | 105.781 | 0 | 105.781 | 11 | 5.2137 | 46.1138 | 46.1138 | 503.439 | 105.781 | 0 | 52090.6647 | 0 | 0 | 0 | 105.781 | 0 | 0 | 52090.6647
12 | 31 | 8 | 119.1806 | 0.45446 | 119.6351 | 11.1406 | 5.1879 | 51.8739 | 51.8739 | 505.8363 | 119.6351 | 0 | 59182.9579 | 0 | 0 | 0 | 119.6351 | 0 | 0 | 59182.9579
12 | 31 | 9 | 100.5723 | 0.73508 | 101.3074 | 11.2685 | 6.7449 | 64.907 | 64.907 | 496.7876 | 101.3074 | 0 | 49186.6977 | 0 | 0 | 0 | 101.3074 | 0 | 0 | 49186.6977
12 | 31 | 10 | 150.8181 | 0.20238 | 151.0205 | 11.0496 | 8.8783 | 279.9756 | 279.9756 | 502.7538 | 151.0205 | 0 | 74257.4289 | 0 | 0 | 0 | 151.0205 | 0 | 0 | 74257.4289
12 | 31 | 11 | 136.5091 | 0 | 136.5091 | 11 | 9.8676 | 2075.4892 | 288 | 499.3077 | 18.9423 | 117.5668 | 9249.6934 | 11.7508 | 0 | 0 | 18.9423 | 117.5668 | 0 | 9249.6934
12 | 31 | 12 | 140.9041 | 0.037458 | 140.9416 | 11.0098 | 10.2547 | 0 | 0 | 506.3671 | 0 | 140.9416 | 0 | 14.0871 | 0 | 0 | 0 | 140.9416 | 0 | 0
12 | 31 | 13 | 149.5623 | 0 | 149.5623 | 11 | 10.031 | 0 | 0 | 506.5928 | 0 | 149.5623 | 0 | 14.9488 | 0 | 0 | 0 | 149.5623 | 0 | 0
12 | 31 | 14 | 117.816 | 0.52258 | 118.3386 | 11.1634 | 9.9364 | 3605.2921 | 288 | 508.4561 | 9.4532 | 108.8854 | 4701.0023 | 10.8831 | 0 | 0 | 9.4532 | 108.8854 | 0 | 4701.0023
12 | 31 | 15 | 71.4584 | 0.64917 | 72.1076 | 11.3331 | 11.1494 | 0 | 0 | 515.6531 | 0 | 72.1076 | 0 | 7.2072 | 0 | 0 | 0 | 72.1076 | 0 | 0
12 | 31 | 16 | 1.6314 | 0 | 1.6314 | 11 | 12.5086 | 0 | 0 | 522.4916 | 0 | 1.6314 | 0 | 0.16306 | 0 | 0 | 0 | 1.6314 | 0 | 0
12 | 31 | 17 | 0 | 0 | 0 | 0 | 12.2591 | 0 | 0 | 525.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 31 | 18 | 81.8051 | 0 | 81.8051 | 11 | 12.801 | 0 | 0 | 523.3743 | 0 | 81.8051 | 0 | 8.1764 | 0 | 0 | 0 | 81.8051 | 0 | 0
12 | 31 | 19 | 108.4343 | 0 | 108.4343 | 11 | 12.7322 | 0 | 0 | 522.9603 | 0 | 108.4343 | 0 | 10.838 | 0 | 0 | 0 | 108.4343 | 0 | 0
12 | 31 | 20 | 0 | 0 | 0 | 0 | 13.3172 | 0 | 0 | 513.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 31 | 21 | 0 | 0 | 0 | 0 | 9.2568 | 0 | 0 | 509.5493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 31 | 22 | 0 | 0 | 0 | 0 | 5.3857 | 0 | 0 | 506.9471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 31 | 23 | 0 | 0 | 0 | 0 | 3.6704 | 0 | 0 | 499.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2017
Month | Day | Hour (PDT) | Wind_curtail (MWh) | Solar_curtail (MWh) | Total_curtail (MWh) | GHG_intensity (kgCO2e/MWh) | CA_DC_load (MW) | #_ExistingDCs_needed | #_ExistingDCs_allowed | PJM_intensity (kgCO2e/MWh) | ExistingDCs_absorption (MWh) | Remaining_curtailment (MWh) | ExistingDCs_GHG_reduction (kgCO2e) | #_NewDCs_needed | #_NewDCs_allowed | NewDCs_absorption (MWh) | Total_absorption (MWh) | Final_curtailment (MWh) | NewDCs_GHG_reduction (kgCO2e) | Total_GHG_reduction (kgCO2e)
1 | 1 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 495.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 496.6658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 498.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 501.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 4 | 26.5936 | 0 | 26.5936 | 11 | 3.0317 | 8.4693 | 8.4693 | 510.8279 | 26.5936 | 0 | 13292.2166 | 0 | 0 | 0 | 26.5936 | 0 | 0 | 13292.2166
1 | 1 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 514.3379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 6 | 33.2246 | 0 | 33.2246 | 11 | 4.1926 | 12.8568 | 12.8568 | 519.4008 | 33.2246 | 0 | 16891.4315 | 0 | 0 | 0 | 33.2246 | 0 | 0 | 16891.4315
1 | 1 | 7 | 2.3883 | 0.35621 | 2.7445 | 15.8022 | 4.8705 | 1.2146 | 1.2146 | 518.9199 | 2.7445 | 0 | 1380.8065 | 0 | 0 | 0 | 2.7445 | 0 | 0 | 1380.8065
1 | 1 | 8 | 46.1692 | 88.4993 | 134.6685 | 35.3151 | 4.8451 | 59.278 | 59.278 | 509.1835 | 134.6685 | 0 | 63815.1313 | 0 | 0 | 0 | 134.6685 | 0 | 0 | 63815.1313
1 | 1 | 9 | 176.3099 | 516.2844 | 692.5943 | 38.5811 | 6.3789 | 450.471 | 288 | 507.8645 | 442.7969 | 249.7974 | 207797.2455 | 26.047 | 0 | 0 | 442.7969 | 249.7974 | 0 | 207797.2455
1 | 1 | 10 | 233.228 | 799.5618 | 1032.7899 | 39.6445 | 8.4804 | 1943.7195 | 288 | 507.1325 | 153.028 | 879.7619 | 71538.7378 | 91.7351 | 0 | 0 | 153.028 | 879.7619 | 0 | 71538.7378
1 | 1 | 11 | 39.6976 | 164.1471 | 203.8447 | 40.7945 | 9.4549 | 3146.2669 | 288 | 503.7391 | 18.6593 | 185.1853 | 8638.2406 | 19.3098 | 0 | 0 | 18.6593 | 185.1853 | 0 | 8638.2406
1 | 1 | 12 | 103.3283 | 251.5478 | 354.8761 | 37.2268 | 9.8362 | 0 | 0 | 502.5333 | 0 | 354.8761 | 0 | 37.0039 | 0 | 0 | 0 | 354.8761 | 0 | 0
1 | 1 | 13 | 101.2523 | 284.6628 | 385.9151 | 38.2923 | 9.6159 | 0 | 0 | 501.9162 | 0 | 385.9151 | 0 | 40.2404 | 0 | 0 | 0 | 385.9151 | 0 | 0
1 | 1 | 14 | 78.2839 | 121.4452 | 199.729 | 33.4978 | 9.5227 | 6177.2164 | 288 | 515.5186 | 9.312 | 190.4171 | 4488.5553 | 19.8553 | 0 | 0 | 9.312 | 190.4171 | 0 | 4488.5553
1 | 1 | 15 | 1.7833 | 3.5551 | 5.3384 | 35.6402 | 10.7175 | 0 | 0 | 526.3138 | 0 | 5.3384 | 0 | 0.55665 | 0 | 0 | 0 | 5.3384 | 0 | 0
1 | 1 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 524.3307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 511.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 504.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 496.2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 492.9938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 476.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 467.4242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 1 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 461.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 457.7572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 457.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 472.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 33.4824 | 0 | 33.4824 | 11 | 3.1249 | 10.8169 | 10.8169 | 489.3359 | 33.4824 | 0 | 16015.8571 | 0 | 0 | 0 | 33.4824 | 0 | 0 | 16015.8571
1 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 497.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 509.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 519.1535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 524.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 527.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 9 | 0 | 1.4199 | 1.4199 | 48 | 6.4043 | 0.9309 | 0.9309 | 526.8372 | 1.4199 | 0 | 679.9089 | 0 | 0 | 0 | 1.4199 | 0 | 0 | 679.9089
1 | 2 | 10 | 0 | 0.33317 | 0.33317 | 48 | 8.5991 | 0.70207 | 0.70207 | 530.4638 | 0.33317 | 0 | 160.7409 | 0 | 0 | 0 | 0.33317 | 0 | 0 | 160.7409
1 | 2 | 11 | 0 | 0.31054 | 0.31054 | 48 | 9.6413 | 0 | 0 | 529.8759 | 0 | 0.31054 | 0 | 0.032381 | 0 | 0 | 0 | 0.31054 | 0 | 0
1 | 2 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 529.2749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 13 | 0 | 0.66558 | 0.66558 | 48 | 9.7939 | 0 | 0 | 527.6396 | 0 | 0.66558 | 0 | 0.069402 | 0 | 0 | 0 | 0.66558 | 0 | 0
1 | 2 | 14 | 0 | 0.33288 | 0.33288 | 48 | 9.4634 | 5.481 | 5.481 | 513.2713 | 0.33288 | 0 | 154.8772 | 0 | 0 | 0 | 0.33288 | 0 | 0 | 154.8772
1 | 2 | 15 | 0 | 0.58004 | 0.58004 | 48 | 10.5311 | 0 | 0 | 514.9365 | 0 | 0.58004 | 0 | 0.060482 | 0 | 0 | 0 | 0.58004 | 0 | 0
1 | 2 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 525.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 526.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 524.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 522.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 506.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 497.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 493.9565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 489.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 484.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 491.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 499.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 515.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 523.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 527.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 531.1072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 7 | 0 | 0.60621 | 0.60621 | 48 | 5.2518 | 0.29186 | 0.29186 | 531.4007 | 0.60621 | 0 | 293.0415 | 0 | 0 | 0 | 0.60621 | 0 | 0 | 293.0415
1 | 3 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 528.0801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 9 | 0 | 0.10742 | 0.10742 | 48 | 7.328 | 0.099175 | 0.099175 | 528.8193 | 0.10742 | 0 | 51.648 | 0 | 0 | 0 | 0.10742 | 0 | 0 | 51.648
1 | 3 | 10 | 0 | 0.16633 | 0.16633 | 48 | 8.5482 | 0.33341 | 0.33341 | 529.0995 | 0.16633 | 0 | 80.0229 | 0 | 0 | 0 | 0.16633 | 0 | 0 | 80.0229
1 | 3 | 11 | 0 | 0.47654 | 0.47654 | 48 | 9.1838 | 2.4486 | 2.4486 | 528.9494 | 0.47654 | 0 | 229.1924 | 0 | 0 | 0 | 0.47654 | 0 | 0 | 229.1924
1 | 3 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 528.6713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 13 | 0 | 0.85404 | 0.85404 | 48 | 9.6668 | 0 | 0 | 514.0425 | 0 | 0.85404 | 0 | 0.089053 | 0 | 0 | 0 | 0.85404 | 0 | 0
1 | 3 | 14 | 0 | 1.0057 | 1.0057 | 48 | 10.2684 | 0 | 0 | 496.2449 | 0 | 1.0057 | 0 | 0.10486 | 0 | 0 | 0 | 1.0057 | 0 | 0
1 | 3 | 15 | 0 | 1.3539 | 1.3539 | 48 | 11.226 | 0 | 0 | 502.3067 | 0 | 1.3539 | 0 | 0.14118 | 0 | 0 | 0 | 1.3539 | 0 | 0
1 | 3 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 513.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 511.6951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 509.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 499.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 480.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 457.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 457.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 452.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 453.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 451.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 453.9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 472.9305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 494.1926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 502.7844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 507.8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 7 | 0 | 0.60621 | 0.60621 | 48 | 5.0146 | 0.27672 | 0.27672 | 506.9251 | 0.60621 | 0 | 278.2042 | 0 | 0 | 0 | 0.60621 | 0 | 0 | 278.2042
1 | 4 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 504.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 505.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 500.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 11 | 0 | 0 | 0 | 0 | 9.3109 | 0 | 0 | 494.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 491.3729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 489.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 14 | 0 | 0.10404 | 0.10404 | 48 | 8.938 | 0.33318 | 0.33318 | 486.7282 | 0.10404 | 0 | 45.646 | 0 | 0 | 0 | 0.10404 | 0 | 0 | 45.646
1 | 4 | 15 | 0 | 0.977 | 0.977 | 48 | 9.6075 | 0 | 0 | 509.0704 | 0 | 0.977 | 0 | 0.10187 | 0 | 0 | 0 | 0.977 | 0 | 0
1 | 4 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 516.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 528.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 528.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 521.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 516.3973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 517.5948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 516.2522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 509.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 513.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 520.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 532.8949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 532.4501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 531.4601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 540.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 551.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 7 | 0 | 0.60621 | 0.60621 | 48 | 4.6502 | 0.25631 | 0.25631 | 551.542 | 0.60621 | 0 | 305.2513 | 0 | 0 | 0 | 0.60621 | 0 | 0 | 305.2513
1 | 5 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 552.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 554.1237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 554.8242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 557.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 556.1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 13 | 15.7989 | 2.1773 | 17.9762 | 15.4814 | 7.4381 | 17.4465 | 17.4465 | 552.4386 | 17.9762 | 0 | 9652.4282 | 0 | 0 | 0 | 17.9762 | 0 | 0 | 9652.4282
1 | 5 | 14 | 51.2713 | 12.8462 | 64.1176 | 18.4131 | 7.2771 | 57.8969 | 57.8969 | 534.2155 | 64.1176 | 0 | 33072.0042 | 0 | 0 | 0 | 64.1176 | 0 | 0 | 33072.0042
1 | 5 | 15 | 0 | 0.20579 | 0.20579 | 48 | 7.3449 | 0.19144 | 0.19144 | 535.4345 | 0.20579 | 0 | 100.3099 | 0 | 0 | 0 | 0.20579 | 0 | 0 | 100.3099
1 | 5 | 16 | 0 | 0.12492 | 0.12492 | 48 | 6.9975 | 0.10063 | 0.10063 | 537.6125 | 0.12492 | 0 | 61.1608 | 0 | 0 | 0 | 0.12492 | 0 | 0 | 61.1608
1 | 5 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 544.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 553.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 556.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 553.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 546.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 542.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 539.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 0 | 10.6672 | 0 | 10.6672 | 11 | 3.5232 | 3.6724 | 3.6724 | 543.5777 | 10.6672 | 0 | 5681.1391 | 0 | 0 | 0 | 10.6672 | 0 | 0 | 5681.1391
1 | 6 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 549.5743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 547.4317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 539.8028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 537.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 550.5194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 556.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 564.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 8 | 4.5483 | 17.4483 | 21.9966 | 40.3493 | 6.8788 | 16.9449 | 16.9449 | 567.0249 | 21.9966 | 0 | 11585.0622 | 0 | 0 | 0 | 21.9966 | 0 | 0 | 11585.0622
1 | 6 | 9 | 9.5717 | 221.139 | 230.7107 | 46.465 | 7.3195 | 212.2142 | 212.2142 | 564.0663 | 230.7107 | 0 | 119416.1648 | 0 | 0 | 0 | 230.7107 | 0 | 0 | 119416.1648
1 | 6 | 10 | 14.6773 | 18.9169 | 33.5943 | 31.8347 | 7.4805 | 33.2591 | 33.2591 | 561.3966 | 33.5943 | 0 | 17790.2434 | 0 | 0 | 0 | 33.5943 | 0 | 0 | 17790.2434
1 | 6 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 562.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 12 | 0.59333 | 2.8311 | 3.4244 | 41.5892 | 7.8703 | 4.1586 | 4.1586 | 567.1446 | 3.4244 | 0 | 1799.7357 | 0 | 0 | 0 | 3.4244 | 0 | 0 | 1799.7357
1 | 6 | 13 | 1.4233 | 41.0384 | 42.4617 | 46.7597 | 8.1754 | 62.6834 | 62.6834 | 565.2374 | 42.4617 | 0 | 22015.4672 | 0 | 0 | 0 | 42.4617 | 0 | 0 | 22015.4672
1 | 6 | 14 | 0.15417 | 11.5563 | 11.7105 | 47.5129 | 8.2431 | 18.1574 | 18.1574 | 551.287 | 11.7105 | 0 | 5899.433 | 0 | 0 | 0 | 11.7105 | 0 | 0 | 5899.433
1 | 6 | 15 | 0 | 3.8119 | 3.8119 | 48 | 7.4212 | 3.6707 | 3.6707 | 549.8109 | 3.8119 | 0 | 1912.8476 | 0 | 0 | 0 | 3.8119 | 0 | 0 | 1912.8476
1 | 6 | 16 | 0 | 0.6665 | 0.6665 | 48 | 7.3195 | 0.61307 | 0.61307 | 551.183 | 0.6665 | 0 | 335.3715 | 0 | 0 | 0 | 0.6665 | 0 | 0 | 335.3715
1 | 6 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 560.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 568.7311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 570.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 566.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 571.9669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 574.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 573.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 574.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 577.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 577.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 576.7012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 576.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 577.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 569.4664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 7 | 0 | 0.022875 | 0.022875 | 48 | 6.006 | 0.01333 | 0.01333 | 572.7081 | 0.022875 | 0 | 12.0027 | 0 | 0 | 0 | 0.022875 | 0 | 0 | 12.0027
1 | 7 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 574.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 574.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 569.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 568.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 565.6345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 13 | 0 | 0.19246 | 0.19246 | 48 | 8.2601 | 0.30221 | 0.30221 | 564.4662 | 0.19246 | 0 | 99.3982 | 0 | 0 | 0 | 0.19246 | 0 | 0 | 99.3982
1 | 7 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 548.9594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 15 | 0 | 0.062458 | 0.062458 | 48 | 8.4041 | 0.10999 | 0.10999 | 550.9032 | 0.062458 | 0 | 31.4105 | 0 | 0 | 0 | 0.062458 | 0 | 0 | 31.4105
1 | 7 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 549.1561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 551.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 555.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 559.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 558.8653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 558.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 564.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 7 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 567.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 566.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 567.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 564.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 561.3189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 561.0814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 565.4677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 567.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 7 | 0 | 0.52288 | 0.52288 | 48 | 4.8705 | 0.2314 | 0.2314 | 572.0487 | 0.52288 | 0 | 274.0119 | 0 | 0 | 0 | 0.52288 | 0 | 0 | 274.0119
1 | 8 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 575.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 9 | 2.1025 | 9.5279 | 11.6304 | 41.3113 | 6.3789 | 7.5645 | 7.5645 | 575.6001 | 11.6304 | 0 | 6213.9917 | 0 | 0 | 0 | 11.6304 | 0 | 0 | 6213.9917
1 | 8 | 10 | 1.3667 | 70.525 | 71.8917 | 47.2966 | 8.4804 | 135.3008 | 135.3008 | 575.0087 | 71.8917 | 0 | 37938.1144 | 0 | 0 | 0 | 71.8917 | 0 | 0 | 37938.1144
1 | 8 | 11 | 1.07 | 3.5728 | 4.6428 | 39.4727 | 9.4549 | 71.6591 | 71.6591 | 573.1727 | 4.6428 | 0 | 2477.8364 | 0 | 0 | 0 | 4.6428 | 0 | 0 | 2477.8364
1 | 8 | 12 | 0.54583 | 124.5007 | 125.0465 | 47.8385 | 9.8362 | 0 | 0 | 567.5034 | 0 | 125.0465 | 0 | 13.0389 | 0 | 0 | 0 | 125.0465 | 0 | 0
1 | 8 | 13 | 1.4775 | 187.4388 | 188.9163 | 47.7106 | 9.6159 | 0 | 0 | 569.5948 | 0 | 188.9163 | 0 | 19.6988 | 0 | 0 | 0 | 188.9163 | 0 | 0
1 | 8 | 14 | 0 | 1.3438 | 1.3438 | 48 | 9.5227 | 41.5595 | 41.5595 | 561.0768 | 1.3438 | 0 | 689.4469 | 0 | 0 | 0 | 1.3438 | 0 | 0 | 689.4469
1 | 8 | 15 | 0 | 0.16654 | 0.16654 | 48 | 10.7175 | 0 | 0 | 559.4296 | 0 | 0.16654 | 0 | 0.017366 | 0 | 0 | 0 | 0.16654 | 0 | 0
1 | 8 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 552.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 552.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 553.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 556.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 550.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 551.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 551.6883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | 23 | 22.522 | 0 | 22.522 | 11 | 3.3504 | 7.5389 | 7.5389 | 552.4652 | 22.522 | 0 | 12194.8913 | 0 | 0 | 0 | 22.522 | 0 | 0 | 12194.8913
1 | 9 | 0 | 150.8046 | 0 | 150.8046 | 11 | 3.252 | 49.6962 | 49.6962 | 554.4244 | 150.8046 | 0 | 81950.8792 | 0 | 0 | 0 | 150.8046 | 0 | 0 | 81950.8792
1 | 9 | 1 | 61.6753 | 0 | 61.6753 | 11 | 3.1418 | 19.9773 | 19.9773 | 550.7863 | 61.6753 | 0 | 33291.4824 | 0 | 0 | 0 | 61.6753 | 0 | 0 | 33291.4824
1 | 9 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 546.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 538.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 4 | 12.1825 | 0 | 12.1825 | 11 | 3.3706 | 4.0912 | 4.0912 | 541.8963 | 12.1825 | 0 | 6467.6442 | 0 | 0 | 0 | 12.1825 | 0 | 0 | 6467.6442
1 | 9 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 545.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 552.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 7 | 0 | 0.10621 | 0.10621 | 48 | 4.8281 | 0.046584 | 0.046584 | 555.1826 | 0.10621 | 0 | 53.867 | 0 | 0 | 0 | 0.10621 | 0 | 0 | 53.867
1 | 9 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 563.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 567.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 569.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 11 | 0 | 0.403 | 0.403 | 48 | 9.6413 | 0 | 0 | 570.6272 | 0 | 0.403 | 0 | 0.042022 | 0 | 0 | 0 | 0.403 | 0 | 0
1 | 9 | 12 | 16.3773 | 12.5892 | 28.9665 | 27.0806 | 9.7176 | 0 | 0 | 569.6294 | 0 | 28.9665 | 0 | 3.0204 | 0 | 0 | 0 | 28.9665 | 0 | 0
1 | 9 | 13 | 19.8844 | 10.9721 | 30.8565 | 24.1567 | 9.7939 | 0 | 0 | 573.1646 | 0 | 30.8565 | 0 | 3.2175 | 0 | 0 | 0 | 30.8565 | 0 | 0
1 | 9 | 14 | 0 | 0.32846 | 0.32846 | 48 | 9.4634 | 5.4083 | 5.4083 | 559.5083 | 0.32846 | 0 | 168.0091 | 0 | 0 | 0 | 0.32846 | 0 | 0 | 168.0091
1 | 9 | 15 | 0 | 1.1612 | 1.1612 | 48 | 10.5311 | 0 | 0 | 553.7765 | 0 | 1.1612 | 0 | 0.12109 | 0 | 0 | 0 | 1.1612 | 0 | 0
1 | 9 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 549.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 543.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 548.2195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 554.9246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 546.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 542.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 22 | 45.2125 | 0 | 45.2125 | 11 | 5.8196 | 25.045 | 25.045 | 536.7922 | 45.2125 | 0 | 23772.4008 | 0 | 0 | 0 | 45.2125 | 0 | 0 | 23772.4008
1 | 9 | 23 | 35.7841 | 0 | 35.7841 | 11 | 4.3028 | 14.1358 | 14.1358 | 534.3607 | 35.7841 | 0 | 18727.9889 | 0 | 0 | 0 | 35.7841 | 0 | 0 | 18727.9889
1 | 10 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 527.3578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 532.5911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 534.1601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 523.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 528.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 529.7846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 533.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 540.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 8 | 6.683 | 0.42667 | 7.1096 | 13.2205 | 6.2094 | 4.3924 | 4.3924 | 534.2561 | 7.1096 | 0 | 3704.3694 | 0 | 0 | 0 | 7.1096 | 0 | 0 | 3704.3694
1 | 10 | 9 | 4.5481 | 0.033333 | 4.5815 | 11.2692 | 7.328 | 4.23 | 4.23 | 533.4854 | 4.5815 | 0 | 2392.5189 | 0 | 0 | 0 | 4.5815 | 0 | 0 | 2392.5189
1 | 10 | 10 | 9.2637 | 2.1692 | 11.4329 | 18.02 | 8.5482 | 22.9165 | 22.9165 | 528.8351 | 11.4329 | 0 | 5840.0723 | 0 | 0 | 0 | 11.4329 | 0 | 0 | 5840.0723
1 | 10 | 11 | 132.9817 | 232.2066 | 365.1883 | 34.5266 | 9.1838 | 1876.4734 | 288 | 525.9453 | 56.0489 | 309.1394 | 27543.4635 | 32.2348 | 0 | 0 | 56.0489 | 309.1394 | 0 | 27543.4635
1 | 10 | 12 | 129.9307 | 175.2058 | 305.1364 | 32.245 | 9.8701 | 0 | 0 | 527.3157 | 0 | 305.1364 | 0 | 31.8174 | 0 | 0 | 0 | 305.1364 | 0 | 0
1 | 10 | 13 | 5.0403 | 7.5402 | 12.5805 | 33.1761 | 9.6668 | 0 | 0 | 520.9658 | 0 | 12.5805 | 0 | 1.3118 | 0 | 0 | 0 | 12.5805 | 0 | 0
1 | 10 | 14 | 57.6054 | 42.9046 | 100.51 | 26.7942 | 10.2684 | 0 | 0 | 526.0058 | 0 | 100.51 | 0 | 10.4804 | 0 | 0 | 0 | 100.51 | 0 | 0
1 | 10 | 15 | 0 | 0.77858 | 0.77858 | 48 | 11.226 | 0 | 0 | 533.4191 | 0 | 0.77858 | 0 | 0.081185 | 0 | 0 | 0 | 0.77858 | 0 | 0
1 | 10 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 525.6365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 520.8209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 513.9708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 507.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 486.6243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 479.1797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 488.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 23 | 26.805 | 0 | 26.805 | 11 | 4.2398 | 10.4642 | 10.4642 | 489.4151 | 26.805 | 0 | 12823.9158 | 0 | 0 | 0 | 26.805 | 0 | 0 | 12823.9158
1 | 11 | 0 | 9.9561 | 0 | 9.9561 | 11 | 3.5147 | 3.4228 | 3.4228 | 496.3309 | 9.9561 | 0 | 4832.0142 | 0 | 0 | 0 | 9.9561 | 0 | 0 | 4832.0142
1 | 11 | 1 | 189.6775 | 0 | 189.6775 | 11 | 3.2859 | 62.8424 | 62.8424 | 498.3715 | 189.6775 | 0 | 92443.3992 | 0 | 0 | 0 | 189.6775 | 0 | 0 | 92443.3992
1 | 11 | 2 | 104.7055 | 0 | 104.7055 | 11 | 3.1842 | 34.1395 | 34.1395 | 497.4245 | 104.7055 | 0 | 50931.32 | 0 | 0 | 0 | 104.7055 | 0 | 0 | 50931.32
1 | 11 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 506.1242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 506.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 511.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 503.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 504.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 8 | 42.2883 | 72.8258 | 115.1141 | 34.4077 | 6.2094 | 71.1183 | 71.1183 | 495.0057 | 115.1141 | 0 | 53021.3459 | 0 | 0 | 0 | 115.1141 | 0 | 0 | 53021.3459
1 | 11 | 9 | 104.1566 | 339.7856 | 443.9422 | 39.3192 | 7.311 | 406.8324 | 288 | 483.8939 | 314.2704 | 129.6718 | 139716.676 | 13.5212 | 0 | 0 | 314.2704 | 129.6718 | 0 | 139716.676
1 | 11 | 10 | 136.1933 | 318.1424 | 454.3358 | 36.9087 | 8.0567 | 618.8188 | 288 | 483.3538 | 211.4491 | 242.8866 | 94400.4169 | 25.3264 | 0 | 0 | 211.4491 | 242.8866 | 0 | 94400.4169
1 | 11 | 11 | 132.0242 | 454.274 | 586.2981 | 39.6682 | 9.3109 | 4383.2494 | 288 | 480.4412 | 38.5225 | 547.7756 | 16979.691 | 57.118 | 0 | 0 | 38.5225 | 547.7756 | 0 | 16979.691
1 | 11 | 12 | 65.3008 | 73.0041 | 138.3048 | 30.5304 | 9.0058 | 494.2784 | 288 | 477.9428 | 80.5858 | 57.7191 | 36055.0662 | 6.0185 | 0 | 0 | 80.5858 | 57.7191 | 0 | 36055.0662
1 | 11 | 13 | 3.7661 | 9.8866 | 13.6527 | 37.7935 | 8.4889 | 25.8923 | 25.8923 | 485.4782 | 13.6527 | 0 | 6112.1246 | 0 | 0 | 0 | 13.6527 | 0 | 0 | 6112.1246
1 | 11 | 14 | 19.9921 | 10.0551 | 30.0473 | 23.3818 | 8.938 | 96.2228 | 96.2228 | 477.4607 | 30.0473 | 0 | 13643.8368 | 0 | 0 | 0 | 30.0473 | 0 | 0 | 13643.8368
1 | 11 | 15 | 0 | 0.83233 | 0.83233 | 48 | 9.6075 | 0 | 0 | 488.6469 | 0 | 0.83233 | 0 | 0.08679 | 0 | 0 | 0 | 0.83233 | 0 | 0
1 | 11 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 496.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 496.7395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 489.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 479.8925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 456.4449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 443.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 439.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 11 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 436.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 434.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 434.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 440.8951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 476.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 497.6682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 502.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 499.7975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 7 | 0 | 0.022875 | 0.022875 | 48 | 4.6502 | 0.0096718 | 0.0096718 | 498.9777 | 0.022875 | 0 | 10.3161 | 0 | 0 | 0 | 0.022875 | 0 | 0 | 10.3161
1 | 12 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 506.5515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 502.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 10 | 0 | 0.13704 | 0.13704 | 48 | 6.9721 | 0.10933 | 0.10933 | 501.9725 | 0.13704 | 0 | 62.2131 | 0 | 0 | 0 | 0.13704 | 0 | 0 | 62.2131
1 | 12 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 498.8119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 490.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 13 | 0 | 1.0204 | 1.0204 | 48 | 7.4381 | 0.99035 | 0.99035 | 487.2801 | 1.0204 | 0 | 448.2487 | 0 | 0 | 0 | 1.0204 | 0 | 0 | 448.2487
1 | 12 | 14 | 0 | 1.0854 | 1.0854 | 48 | 7.2771 | 0.98011 | 0.98011 | 470.5611 | 1.0854 | 0 | 458.6549 | 0 | 0 | 0 | 1.0854 | 0 | 0 | 458.6549
1 | 12 | 15 | 0 | 0.97317 | 0.97317 | 48 | 7.3449 | 0.90528 | 0.90528 | 496.7209 | 0.97317 | 0 | 436.6802 | 0 | 0 | 0 | 0.97317 | 0 | 0 | 436.6802
1 | 12 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 500.8277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 504.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 505.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 490.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 470.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 460.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 460.0305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 451.9078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 448.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 446.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 460.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 475.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 494.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 505.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 504.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 504.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 8 | 0 | 0.35621 | 0.35621 | 48 | 6.8788 | 0.2744 | 0.2744 | 506.3803 | 0.35621 | 0 | 163.2789 | 0 | 0 | 0 | 0.35621 | 0 | 0 | 163.2789
1 | 13 | 9 | 0 | 0.070375 | 0.070375 | 48 | 7.3195 | 0.064733 | 0.064733 | 507.2376 | 0.070375 | 0 | 32.3188 | 0 | 0 | 0 | 0.070375 | 0 | 0 | 32.3188
1 | 13 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 508.5205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 11 | 0 | 0.16658 | 0.16658 | 48 | 7.2263 | 0.14719 | 0.14719 | 503.1611 | 0.16658 | 0 | 75.8223 | 0 | 0 | 0 | 0.16658 | 0 | 0 | 75.8223
1 | 13 | 12 | 0 | 0.16662 | 0.16662 | 48 | 7.8703 | 0.20235 | 0.20235 | 498.3697 | 0.16662 | 0 | 75.0429 | 0 | 0 | 0 | 0.16662 | 0 | 0 | 75.0429
1 | 13 | 13 | 0 | 0.25383 | 0.25383 | 48 | 8.1754 | 0.37472 | 0.37472 | 492.0239 | 0.25383 | 0 | 112.7081 | 0 | 0 | 0 | 0.25383 | 0 | 0 | 112.7081
1 | 13 | 14 | 0 | 0.062458 | 0.062458 | 48 | 8.2431 | 0.096843 | 0.096843 | 477.3576 | 0.062458 | 0 | 26.817 | 0 | 0 | 0 | 0.062458 | 0 | 0 | 26.817
1 | 13 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 487.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 493.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 498.8606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 502.665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 500.3134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 489.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 476.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 474.8269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 470.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 469.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 467.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 468.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 468.5396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 475.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 486.2799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 484.7493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 7 | 0 | 0.85621 | 0.85621 | 48 | 6.006 | 0.49896 | 0.49896 | 484.4018 | 0.85621 | 0 | 373.6509 | 0 | 0 | 0 | 0.85621 | 0 | 0 | 373.6509
1 | 14 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 491.0277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 9 | 0 | 19.5892 | 19.5892 | 48 | 7.1924 | 17.0636 | 17.0636 | 499.3199 | 19.5892 | 0 | 8841.0186 | 0 | 0 | 0 | 19.5892 | 0 | 0 | 8841.0186
1 | 14 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 499.1677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 499.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 500.3633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 499.0301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 14 | 0 | 0.66492 | 0.66492 | 48 | 8.5313 | 1.3115 | 1.3115 | 485.3077 | 0.66492 | 0 | 290.7732 | 0 | 0 | 0 | 0.66492 | 0 | 0 | 290.7732
1 | 14 | 15 | 0 | 1.5106 | 1.5106 | 48 | 8.4041 | 2.6601 | 2.6601 | 486.4031 | 1.5106 | 0 | 662.2445 | 0 | 0 | 0 | 1.5106 | 0 | 0 | 662.2445
1 | 14 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 490.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 496.9478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 499.6195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 493.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 482.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 473.2041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 466.9416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 14 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 461.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 461.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 463.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 462.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 465.3919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 479.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 490.1289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 494.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 7 | 0 | 1.1062 | 1.1062 | 48 | 4.8705 | 0.48955 | 0.48955 | 491.7292 | 1.1062 | 0 | 490.8569 | 0 | 0 | 0 | 1.1062 | 0 | 0 | 490.8569
1 | 15 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 487.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 9 | 0 | 0.10783 | 0.10783 | 48 | 6.3789 | 0.070136 | 0.070136 | 484.5051 | 0.10783 | 0 | 47.0698 | 0 | 0 | 0 | 0.10783 | 0 | 0 | 47.0698
1 | 15 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 480.3783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 11 | 0 | 0.0315 | 0.0315 | 48 | 9.4549 | 0.48619 | 0.48619 | 477.5745 | 0.0315 | 0 | 13.5316 | 0 | 0 | 0 | 0.0315 | 0 | 0 | 13.5316
1 | 15 | 12 | 0 | 0.13847 | 0.13847 | 48 | 9.8362 | 0 | 0 | 481.9209 | 0 | 0.13847 | 0 | 0.014439 | 0 | 0 | 0 | 0.13847 | 0 | 0
1 | 15 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 489.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 488.9457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 15 | 0 | 0.044958 | 0.044958 | 48 | 10.7175 | 0 | 0 | 496.7564 | 0 | 0.044958 | 0 | 0.0046879 | 0 | 0 | 0 | 0.044958 | 0 | 0
1 | 15 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 498.7085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 499.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 502.5438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 493.2517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 482.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 474.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 462.8109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 462.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 464.2633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 470.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 473.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 484.2405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 484.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 487.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 487.1243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 7 | 0 | 0.85621 | 0.85621 | 48 | 4.8281 | 0.37554 | 0.37554 | 485.4321 | 0.85621 | 0 | 374.533 | 0 | 0 | 0 | 0.85621 | 0 | 0 | 374.533
1 | 16 | 8 | 0 | 2.0012 | 2.0012 | 48 | 5.4976 | 1.0213 | 1.0213 | 493.6405 | 2.0012 | 0 | 891.807 | 0 | 0 | 0 | 2.0012 | 0 | 0 | 891.807
1 | 16 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 501.9047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 498.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 11 | 0.88 | 109.2243 | 110.1043 | 47.7043 | 9.6413 | 0 | 0 | 495.6316 | 0 | 110.1043 | 0 | 11.4809 | 0 | 0 | 0 | 110.1043 | 0 | 0
1 | 16 | 12 | 2.0367 | 140.7091 | 142.7458 | 47.4721 | 9.7176 | 0 | 0 | 493.1499 | 0 | 142.7458 | 0 | 14.8845 | 0 | 0 | 0 | 142.7458 | 0 | 0
1 | 16 | 13 | 2.505 | 193.5022 | 196.0072 | 47.5271 | 9.7939 | 0 | 0 | 487.3763 | 0 | 196.0072 | 0 | 20.4382 | 0 | 0 | 0 | 196.0072 | 0 | 0
1 | 16 | 14 | 0.16333 | 6.7332 | 6.8966 | 47.1237 | 9.4634 | 113.5568 | 113.5568 | 469.1631 | 6.8966 | 0 | 2910.6252 | 0 | 0 | 0 | 6.8966 | 0 | 0 | 2910.6252
1 | 16 | 15 | 0 | 0.98633 | 0.98633 | 48 | 10.5311 | 0 | 0 | 471.4534 | 0 | 0.98633 | 0 | 0.10285 | 0 | 0 | 0 | 0.98633 | 0 | 0
1 | 16 | 16 | 0 | 0.33308 | 0.33308 | 48 | 11.0904 | 0 | 0 | 481.6387 | 0 | 0.33308 | 0 | 0.034731 | 0 | 0 | 0 | 0.33308 | 0 | 0
1 | 16 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 493.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 492.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 476.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 460.0905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 439.1957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 424.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 16 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 421.6135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 425.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 425.6612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 436.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 455.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 461.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 469.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 472.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 7 | 0 | 0.74038 | 0.74038 | 48 | 5.2518 | 0.35645 | 0.35645 | 473.8008 | 0.74038 | 0 | 315.2523 | 0 | 0 | 0 | 0.74038 | 0 | 0 | 315.2523
1 | 17 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 474.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 9 | 0 | 6.0426 | 6.0426 | 48 | 7.328 | 5.5789 | 5.5789 | 476.0817 | 6.0426 | 0 | 2586.7159 | 0 | 0 | 0 | 6.0426 | 0 | 0 | 2586.7159
1 | 17 | 10 | 0 | 8.7512 | 8.7512 | 48 | 8.5482 | 17.5414 | 17.5414 | 475.532 | 8.7512 | 0 | 3741.4285 | 0 | 0 | 0 | 8.7512 | 0 | 0 | 3741.4285
1 | 17 | 11 | 0 | 5.1607 | 5.1607 | 48 | 9.1838 | 26.5174 | 26.5174 | 471.4872 | 5.1607 | 0 | 2185.4747 | 0 | 0 | 0 | 5.1607 | 0 | 0 | 2185.4747
1 | 17 | 12 | 0.0066667 | 1.0844 | 1.0911 | 47.7739 | 9.8701 | 0 | 0 | 473.3752 | 0 | 1.0911 | 0 | 0.11377 | 0 | 0 | 0 | 1.0911 | 0 | 0
1 | 17 | 13 | 0 | 0.034875 | 0.034875 | 48 | 9.6668 | 0 | 0 | 476.7656 | 0 | 0.034875 | 0 | 0.0036365 | 0 | 0 | 0 | 0.034875 | 0 | 0
1 | 17 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 461.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 15 | 0 | 0.59942 | 0.59942 | 48 | 11.226 | 0 | 0 | 470.2934 | 0 | 0.59942 | 0 | 0.062503 | 0 | 0 | 0 | 0.59942 | 0 | 0
1 | 17 | 16 | 0 | 0.019125 | 0.019125 | 48 | 11.853 | 0 | 0 | 477.7457 | 0 | 0.019125 | 0 | 0.0019942 | 0 | 0 | 0 | 0.019125 | 0 | 0
1 | 17 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 477.4913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 477.2527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 465.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 449.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 424.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 409.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 17 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 404.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 408.7118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 416.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 424.8151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 442.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 461.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 475.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 483.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 483.5101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 8 | 6.5358 | 72.2245 | 78.7603 | 44.9296 | 6.2094 | 48.6586 | 48.6586 | 476.065 | 78.7603 | 0 | 33956.3538 | 0 | 0 | 0 | 78.7603 | 0 | 0 | 33956.3538
1 | 18 | 9 | 8.595 | 36.6198 | 45.2148 | 40.9666 | 7.311 | 41.4352 | 41.4352 | 475.5283 | 45.2148 | 0 | 19648.6201 | 0 | 0 | 0 | 45.2148 | 0 | 0 | 19648.6201
1 | 18 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 474.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 11 | 0 | 0 | 0 | 0 | 9.3109 | 0 | 0 | 477.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 474.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 480.1651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 469.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 15 | 0 | 0 | 0 | 0 | 9.6075 | 0 | 0 | 470.2447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 476.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 486.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 492.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 486.202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 464.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 449.5661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 441.5183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 18 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 441.4425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 442.7644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 442.6339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 447.8272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 441.7068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 456.7193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 466.1879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 478.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 483.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 485.1558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 9 | 0 | 0.74947 | 0.74947 | 48 | 6.6161 | 0.52635 | 0.52635 | 483.0747 | 0.74947 | 0 | 326.0735 | 0 | 0 | 0 | 0.74947 | 0 | 0 | 326.0735
1 | 19 | 10 | 0 | 2.1314 | 2.1314 | 48 | 6.9721 | 1.7004 | 1.7004 | 478.3435 | 2.1314 | 0 | 917.2331 | 0 | 0 | 0 | 2.1314 | 0 | 0 | 917.2331
1 | 19 | 11 | 2.1775 | 0.72635 | 2.9039 | 20.255 | 8.5652 | 5.9168 | 5.9168 | 474.8342 | 2.9039 | 0 | 1320.0312 | 0 | 0 | 0 | 2.9039 | 0 | 0 | 1320.0312
1 | 19 | 12 | 13.0917 | 23.6872 | 36.7789 | 34.8296 | 7.8957 | 45.3343 | 45.3343 | 475.3644 | 36.7789 | 0 | 16202.3864 | 0 | 0 | 0 | 36.7789 | 0 | 0 | 16202.3864
1 | 19 | 13 | 0 | 0.49033 | 0.49033 | 48 | 7.4381 | 0.47588 | 0.47588 | 477.2064 | 0.49033 | 0 | 210.4542 | 0 | 0 | 0 | 0.49033 | 0 | 0 | 210.4542
1 | 19 | 14 | 0 | 1.037 | 1.037 | 48 | 7.2771 | 0.93635 | 0.93635 | 463.2314 | 1.037 | 0 | 430.5777 | 0 | 0 | 0 | 1.037 | 0 | 0 | 430.5777
1 | 19 | 15 | 0 | 1.0853 | 1.0853 | 48 | 7.3449 | 1.0096 | 1.0096 | 470.4446 | 1.0853 | 0 | 458.4932 | 0 | 0 | 0 | 1.0853 | 0 | 0 | 458.4932
1 | 19 | 16 | 0 | 0.16658 | 0.16658 | 48 | 6.9975 | 0.1342 | 0.1342 | 467.8373 | 0.16658 | 0 | 69.9379 | 0 | 0 | 0 | 0.16658 | 0 | 0 | 69.9379
1 | 19 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 473.2601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 477.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 470.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 462.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 449.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 439.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 437.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 438.3569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 439.2113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 444.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 442.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 449.2956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 462.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 473.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 477.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 476.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 471.294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 10 | 0 | 0.80912 | 0.80912 | 48 | 7.4805 | 0.80105 | 0.80105 | 474.1392 | 0.80912 | 0 | 344.7999 | 0 | 0 | 0 | 0.80912 | 0 | 0 | 344.7999
1 | 20 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 471.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 469.5952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 13 | 0 | 0.6655 | 0.6655 | 48 | 8.1754 | 0.98243 | 0.98243 | 472.5331 | 0.6655 | 0 | 282.5268 | 0 | 0 | 0 | 0.6655 | 0 | 0 | 282.5268
1 | 20 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 463.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 15 | 0 | 0.34008 | 0.34008 | 48 | 7.4212 | 0.32748 | 0.32748 | 474.2571 | 0.34008 | 0 | 144.9629 | 0 | 0 | 0 | 0.34008 | 0 | 0 | 144.9629
1 | 20 | 16 | 0 | 0.33779 | 0.33779 | 48 | 7.3195 | 0.31071 | 0.31071 | 474.1487 | 0.33779 | 0 | 143.9495 | 0 | 0 | 0 | 0.33779 | 0 | 0 | 143.9495
1 | 20 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 465.7376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 458.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 446.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 429.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 414.5487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 401.7123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 20 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 397.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 393.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 390.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 392.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 396.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 401.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 421.8496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 429.1923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 440.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 8 | 46.6883 | 166.0731 | 212.7614 | 39.8807 | 6.6246 | 149.8493 | 149.8493 | 447.7043 | 212.7614 | 0 | 86769.1188 | 0 | 0 | 0 | 212.7614 | 0 | 0 | 86769.1188
1 | 21 | 9 | 204.0067 | 735.7197 | 939.7263 | 39.9676 | 7.1924 | 818.5663 | 288 | 439.7302 | 330.6283 | 609.098 | 132172.8271 | 63.5122 | 0 | 0 | 330.6283 | 609.098 | 0 | 132172.8271
1 | 21 | 10 | 457.5185 | 1251.9633 | 1709.4818 | 38.0975 | 7.0398 | 1400.0196 | 288 | 429.9421 | 351.6599 | 1357.8219 | 137796.0291 | 141.5836 | 0 | 0 | 351.6599 | 1357.8219 | 0 | 137796.0291
1 | 21 | 11 | 308.6385 | 818.6572 | 1127.2957 | 37.8699 | 7.2093 | 988.9419 | 288 | 427.7215 | 328.2914 | 799.0042 | 127984.9607 | 83.3143 | 0 | 0 | 328.2914 | 799.0042 | 0 | 127984.9607
1 | 21 | 12 | 85.9925 | 411.0082 | 497.0006 | 41.5982 | 7.9296 | 625.1158 | 288 | 427.6929 | 228.9755 | 268.0252 | 88406.2314 | 27.9477 | 0 | 0 | 228.9755 | 268.0252 | 0 | 88406.2314
1 | 21 | 13 | 66.9876 | 199.8893 | 266.8769 | 38.7128 | 8.2601 | 419.071 | 288 | 430.058 | 183.407 | 83.4699 | 71775.4515 | 8.7036 | 0 | 0 | 183.407 | 83.4699 | 0 | 71775.4515
1 | 21 | 14 | 15.7954 | 25.6603 | 41.4557 | 33.9023 | 8.5313 | 81.7659 | 81.7659 | 440.0127 | 41.4557 | 0 | 16835.607 | 0 | 0 | 0 | 41.4557 | 0 | 0 | 16835.607
1 | 21 | 15 | 0 | 6.2456 | 6.2456 | 48 | 8.4041 | 10.9986 | 10.9986 | 455.2455 | 6.2456 | 0 | 2543.513 | 0 | 0 | 0 | 6.2456 | 0 | 0 | 2543.513
1 | 21 | 16 | 0 | 0.027458 | 0.027458 | 48 | 9.1753 | 0.13821 | 0.13821 | 450.5659 | 0.027458 | 0 | 11.0538 | 0 | 0 | 0 | 0.027458 | 0 | 0 | 11.0538
1 | 21 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 453.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 448.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 438.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 422.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 414.5702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 413.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 21 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 410.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 417.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 414.9498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 418.3776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 417.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 419.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 424.8183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 431.9035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 444.6079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 455.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 451.3426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 10 | 0 | 0.20829 | 0.20829 | 48 | 8.4804 | 0.39201 | 0.39201 | 451.1266 | 0.20829 | 0 | 83.9679 | 0 | 0 | 0 | 0.20829 | 0 | 0 | 83.9679
1 | 22 | 11 | 0 | 0.060792 | 0.060792 | 48 | 9.4549 | 0.9383 | 0.9383 | 446.4545 | 0.060792 | 0 | 24.2227 | 0 | 0 | 0 | 0.060792 | 0 | 0 | 24.2227
1 | 22 | 12 | 0 | 0.35829 | 0.35829 | 48 | 9.8362 | 0 | 0 | 441.3021 | 0 | 0.35829 | 0 | 0.03736 | 0 | 0 | 0 | 0.35829 | 0 | 0
1 | 22 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 439.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 441.368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 15 | 0 | 0.94404 | 0.94404 | 48 | 10.7175 | 0 | 0 | 463.0491 | 0 | 0.94404 | 0 | 0.098438 | 0 | 0 | 0 | 0.94404 | 0 | 0
1 | 22 | 16 | 0 | 0.49979 | 0.49979 | 48 | 12.0564 | 0 | 0 | 452.9796 | 0 | 0.49979 | 0 | 0.052115 | 0 | 0 | 0 | 0.49979 | 0 | 0
1 | 22 | 17 | 0 | 0.083292 | 0.083292 | 48 | 11.8107 | 0 | 0 | 447.4649 | 0 | 0.083292 | 0 | 0.008685 | 0 | 0 | 0 | 0.083292 | 0 | 0
1 | 22 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 446.6352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 431.5525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 416.7716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 396.2098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 393.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 22 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 383.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 380.4886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 384.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 394.1769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 420.0694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 441.828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 452.6855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 474.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 471.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 8 | 0 | 2.8624 | 2.8624 | 48 | 5.4976 | 1.4609 | 1.4609 | 476.7748 | 2.8624 | 0 | 1227.3439 | 0 | 0 | 0 | 2.8624 | 0 | 0 | 1227.3439
1 | 23 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 489.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 10 | 0 | 1.9514 | 1.9514 | 48 | 8.5991 | 4.112 | 4.112 | 493.827 | 1.9514 | 0 | 869.9689 | 0 | 0 | 0 | 1.9514 | 0 | 0 | 869.9689
1 | 23 | 11 | 0 | 0.22575 | 0.22575 | 48 | 9.6413 | 0 | 0 | 492.3066 | 0 | 0.22575 | 0 | 0.02354 | 0 | 0 | 0 | 0.22575 | 0 | 0
1 | 23 | 12 | 3.8242 | 96.3836 | 100.2077 | 46.588 | 9.7176 | 0 | 0 | 490.2002 | 0 | 100.2077 | 0 | 10.4489 | 0 | 0 | 0 | 100.2077 | 0 | 0
1 | 23 | 13 | 0 | 0.33292 | 0.33292 | 48 | 9.7939 | 0 | 0 | 489.8628 | 0 | 0.33292 | 0 | 0.034714 | 0 | 0 | 0 | 0.33292 | 0 | 0
1 | 23 | 14 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 476.8084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 15 | 0 | 0.58237 | 0.58237 | 48 | 10.5311 | 0 | 0 | 487.1278 | 0 | 0.58237 | 0 | 0.060726 | 0 | 0 | 0 | 0.58237 | 0 | 0
1 | 23 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 493.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 499.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 504.5641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 503.5486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 490.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 480.9014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 487.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 23 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 479.9871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 479.9331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 486.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 501.2566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 501.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 512.3015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 512.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 513.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 514.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 511.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 9 | 1.7068 | 11.2381 | 12.9449 | 43.1214 | 7.328 | 11.9517 | 11.9517 | 510.92 | 12.9449 | 0 | 6055.6278 | 0 | 0 | 0 | 12.9449 | 0 | 0 | 6055.6278
1 | 24 | 10 | 8.3929 | 13.9372 | 22.3301 | 34.0933 | 8.5482 | 44.7595 | 44.7595 | 509.2338 | 22.3301 | 0 | 10609.9492 | 0 | 0 | 0 | 22.3301 | 0 | 0 | 10609.9492
1 | 24 | 11 | 36.0405 | 156.154 | 192.1945 | 41.0617 | 9.1838 | 987.5669 | 288 | 509.2212 | 56.0489 | 136.1456 | 26239.8136 | 14.1963 | 0 | 0 | 56.0489 | 136.1456 | 0 | 26239.8136
1 | 24 | 12 | 21.739 | 176.939 | 198.6781 | 43.9515 | 9.8701 | 0 | 0 | 507.2242 | 0 | 198.6781 | 0 | 20.7167 | 0 | 0 | 0 | 198.6781 | 0 | 0
1 | 24 | 13 | 0 | 0.28396 | 0.28396 | 48 | 9.6668 | 0 | 0 | 507.408 | 0 | 0.28396 | 0 | 0.029609 | 0 | 0 | 0 | 0.28396 | 0 | 0
1 | 24 | 14 | 0 | 0.024542 | 0.024542 | 48 | 10.2684 | 0 | 0 | 496.6027 | 0 | 0.024542 | 0 | 0.002559 | 0 | 0 | 0 | 0.024542 | 0 | 0
1 | 24 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 500.9768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 499.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 497.2151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 502.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 495.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 475.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 455.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 442.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 24 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 437.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 440.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 438.2171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 445.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 453.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 485.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 497.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 483.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 7 | 0 | 53.1075 | 53.1075 | 48 | 5.0146 | 24.2426 | 24.2426 | 479.4215 | 53.1075 | 0 | 22911.6981 | 0 | 0 | 0 | 53.1075 | 0 | 0 | 22911.6981
1 | 25 | 8 | 0.44167 | 418.1335 | 418.5752 | 47.961 | 6.2094 | 258.5985 | 258.5985 | 469.9411 | 418.5752 | 0 | 176630.427 | 0 | 0 | 0 | 418.5752 | 0 | 0 | 176630.427
1 | 25 | 9 | 0.2175 | 213.1607 | 213.3782 | 47.9623 | 7.311 | 195.5416 | 195.5416 | 461.869 | 213.3782 | 0 | 88318.6767 | 0 | 0 | 0 | 213.3782 | 0 | 0 | 88318.6767
1 | 25 | 10 | 0.46 | 117.5987 | 118.0587 | 47.8558 | 8.0567 | 160.7994 | 160.7994 | 458.2334 | 118.0587 | 0 | 48448.6393 | 0 | 0 | 0 | 118.0587 | 0 | 0 | 48448.6393
1 | 25 | 11 | 0.054167 | 119.3937 | 119.4479 | 47.9832 | 9.3109 | 893.0096 | 288 | 457.3526 | 38.5225 | 80.9253 | 15769.9461 | 8.4383 | 0 | 0 | 38.5225 | 80.9253 | 0 | 15769.9461
1 | 25 | 12 | 1.0167 | 224.3949 | 225.4115 | 47.8331 | 9.0058 | 805.5831 | 288 | 452.7789 | 80.5858 | 144.8258 | 32632.8671 | 15.1014 | 0 | 0 | 80.5858 | 144.8258 | 0 | 32632.8671
1 | 25 | 13 | 0.91 | 479.1999 | 480.1099 | 47.9299 | 8.4889 | 910.5232 | 288 | 454.9214 | 151.8596 | 328.2503 | 61805.5534 | 34.2275 | 0 | 0 | 151.8596 | 328.2503 | 0 | 61805.5534
1 | 25 | 14 | 0.75333 | 206.3939 | 207.1473 | 47.8654 | 8.938 | 663.364 | 288 | 454.9205 | 89.9331 | 117.2141 | 36607.7375 | 12.2222 | 0 | 0 | 89.9331 | 117.2141 | 0 | 36607.7375
1 | 25 | 15 | 0.25417 | 159.2669 | 159.5211 | 47.941 | 9.6075 | 0 | 0 | 484.4313 | 0 | 159.5211 | 0 | 16.6337 | 0 | 0 | 0 | 159.5211 | 0 | 0
1 | 25 | 16 | 0 | 0.16646 | 0.16646 | 48 | 10.9718 | 0 | 0 | 479.1693 | 0 | 0.16646 | 0 | 0.017357 | 0 | 0 | 0 | 0.16646 | 0 | 0
1 | 25 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 477.7997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 471.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 450.8624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 430.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 414.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 414.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 25 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 410.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 408.6649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 410.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 411.9944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 434.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 465.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 470.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 473.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 7 | 0 | 57.6332 | 57.6332 | 48 | 4.6502 | 24.3679 | 24.3679 | 475.3708 | 57.6332 | 0 | 24630.7312 | 0 | 0 | 0 | 57.6332 | 0 | 0 | 24630.7312
1 | 26 | 8 | 0 | 222.0516 | 222.0516 | 48 | 5.1417 | 104.2587 | 104.2587 | 475.0243 | 222.0516 | 0 | 94821.4378 | 0 | 0 | 0 | 222.0516 | 0 | 0 | 94821.4378
1 | 26 | 9 | 0 | 11.4963 | 11.4963 | 48 | 6.6161 | 8.0739 | 8.0739 | 471.5236 | 11.4963 | 0 | 4868.9573 | 0 | 0 | 0 | 11.4963 | 0 | 0 | 4868.9573
1 | 26 | 10 | 0 | 0.43 | 0.43 | 48 | 6.9721 | 0.34304 | 0.34304 | 471.4509 | 0.43 | 0 | 182.0839 | 0 | 0 | 0 | 0.43 | 0 | 0 | 182.0839
1 | 26 | 11 | 0 | 6.4042 | 6.4042 | 48 | 8.5652 | 13.0492 | 13.0492 | 468.0291 | 6.4042 | 0 | 2689.9648 | 0 | 0 | 0 | 6.4042 | 0 | 0 | 2689.9648
1 | 26 | 12 | 3.4767 | 96.5291 | 100.0057 | 46.7137 | 7.8957 | 123.2688 | 123.2688 | 467.6692 | 100.0057 | 0 | 42097.9635 | 0 | 0 | 0 | 100.0057 | 0 | 0 | 42097.9635
1 | 26 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 474.648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 14 | 0 | 0.46067 | 0.46067 | 48 | 7.2771 | 0.41597 | 0.41597 | 463.5468 | 0.46067 | 0 | 191.4286 | 0 | 0 | 0 | 0.46067 | 0 | 0 | 191.4286
1 | 26 | 15 | 1.0967 | 7.6585 | 8.7552 | 43.3654 | 7.3449 | 8.1445 | 8.1445 | 475.5333 | 8.7552 | 0 | 3783.7208 | 0 | 0 | 0 | 8.7552 | 0 | 0 | 3783.7208
1 | 26 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 482.3565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 17 | 0 | 0.053292 | 0.053292 | 48 | 7.167 | 0.045934 | 0.045934 | 494.4083 | 0.053292 | 0 | 23.7898 | 0 | 0 | 0 | 0.053292 | 0 | 0 | 23.7898
1 | 26 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 488.6817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 470.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 454.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 438.645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 432.2355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 26 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 432.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 431.3241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 428.4004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 441.1347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 460.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 480.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 492.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 491.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 497.4746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 8 | 46.6565 | 292.6447 | 339.3012 | 42.9122 | 6.8788 | 261.3779 | 261.3779 | 496.0526 | 339.3012 | 0 | 153751.0849 | 0 | 0 | 0 | 339.3012 | 0 | 0 | 153751.0849
1 | 27 | 9 | 45.0464 | 307.1547 | 352.2011 | 43.2677 | 7.3195 | 323.9645 | 288 | 499.3621 | 313.1019 | 39.0992 | 142804.0506 | 4.077 | 0 | 0 | 313.1019 | 39.0992 | 0 | 142804.0506
1 | 27 | 10 | 1.8085 | 6.2296 | 8.0381 | 39.6754 | 7.4805 | 7.9579 | 7.9579 | 497.2073 | 8.0381 | 0 | 3677.6879 | 0 | 0 | 0 | 8.0381 | 0 | 0 | 3677.6879
1 | 27 | 11 | 31.6867 | 65.2645 | 96.9511 | 35.9072 | 7.2263 | 85.662 | 85.662 | 493.2344 | 96.9511 | 0 | 44338.3782 | 0 | 0 | 0 | 96.9511 | 0 | 0 | 44338.3782
1 | 27 | 12 | 35.7635 | 32.5734 | 68.3369 | 28.6364 | 7.8703 | 82.9882 | 82.9882 | 487.8231 | 68.3369 | 0 | 31379.3894 | 0 | 0 | 0 | 68.3369 | 0 | 0 | 31379.3894
1 | 27 | 13 | 3.2092 | 0.93404 | 4.1432 | 19.3413 | 8.1754 | 6.1163 | 6.1163 | 487.2489 | 4.1432 | 0 | 1938.6389 | 0 | 0 | 0 | 4.1432 | 0 | 0 | 1938.6389
1 | 27 | 14 | 12.0849 | 2.4164 | 14.5013 | 17.1654 | 8.2431 | 22.4846 | 22.4846 | 481.4372 | 14.5013 | 0 | 6732.5532 | 0 | 0 | 0 | 14.5013 | 0 | 0 | 6732.5532
1 | 27 | 15 | 14.5758 | 54.1564 | 68.7323 | 40.1535 | 7.4212 | 66.1858 | 66.1858 | 489.0829 | 68.7323 | 0 | 30855.942 | 0 | 0 | 0 | 68.7323 | 0 | 0 | 30855.942
1 | 27 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 493.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 489.9916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 492.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 477.3779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 460.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 438.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 430.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 27 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 434.3788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 431.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 434.8122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 437.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 445.4913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 455.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 474.0097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 480.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 482.7054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 8 | 8.0817 | 110.0118 | 118.0935 | 45.4679 | 6.6246 | 83.1741 | 83.1741 | 480.1881 | 118.0935 | 0 | 51337.6263 | 0 | 0 | 0 | 118.0935 | 0 | 0 | 51337.6263
1 | 28 | 9 | 5.9558 | 31.7769 | 37.7328 | 42.1598 | 7.1924 | 32.8678 | 32.8678 | 473.4744 | 37.7328 | 0 | 16274.6879 | 0 | 0 | 0 | 37.7328 | 0 | 0 | 16274.6879
1 | 28 | 10 | 9.4442 | 94.3652 | 103.8094 | 44.6339 | 7.0398 | 85.0171 | 85.0171 | 468.5184 | 103.8094 | 0 | 44003.1967 | 0 | 0 | 0 | 103.8094 | 0 | 0 | 44003.1967
1 | 28 | 11 | 21.2783 | 443.8562 | 465.1345 | 46.3074 | 7.2093 | 408.0482 | 288 | 456.8908 | 328.2914 | 136.8431 | 134791.0275 | 14.269 | 0 | 0 | 328.2914 | 136.8431 | 0 | 134791.0275
1 | 28 | 12 | 20.0408 | 736.0733 | 756.1141 | 47.0193 | 7.9296 | 951.0226 | 288 | 449.0506 | 228.9755 | 527.1387 | 92055.3165 | 54.9661 | 0 | 0 | 228.9755 | 527.1387 | 0 | 92055.3165
1 | 28 | 13 | 17.5133 | 656.3177 | 673.831 | 47.0383 | 8.2601 | 1058.1022 | 288 | 456.7939 | 183.407 | 490.4241 | 75152.0277 | 51.1378 | 0 | 0 | 183.407 | 490.4241 | 0 | 75152.0277
1 | 28 | 14 | 18.79 | 623.1641 | 641.9541 | 46.917 | 8.5313 | 1266.169 | 288 | 460.3963 | 146.0175 | 495.9366 | 60375.1895 | 51.7126 | 0 | 0 | 146.0175 | 495.9366 | 0 | 60375.1895
1 | 28 | 15 | 13.9657 | 419.8823 | 433.8481 | 46.809 | 8.4041 | 764.0048 | 288 | 476.1944 | 163.5438 | 270.3043 | 70223.3272 | 28.1853 | 0 | 0 | 163.5438 | 270.3043 | 0 | 70223.3272
1 | 28 | 16 | 1.9408 | 0.25988 | 2.2007 | 15.3692 | 9.1753 | 11.0771 | 11.0771 | 476.8086 | 2.2007 | 0 | 1015.4934 | 0 | 0 | 0 | 2.2007 | 0 | 0 | 1015.4934
1 | 28 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 483.7412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 486.4798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 476.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 459.1482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 443.0887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 450.6573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 28 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 450.4564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 447.7731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 448.8985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 451.6205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 452.9894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 465.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 475.2701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 480.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 485.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 8 | 13.4508 | 366.3279 | 379.7787 | 46.6896 | 4.8451 | 167.1701 | 167.1701 | 475.0728 | 379.7787 | 0 | 162690.8519 | 0 | 0 | 0 | 379.7787 | 0 | 0 | 162690.8519
1 | 29 | 9 | 17.5117 | 511.4594 | 528.9711 | 46.7751 | 6.3789 | 344.0487 | 288 | 471.8765 | 442.7969 | 86.1742 | 188233.5597 | 8.9856 | 0 | 0 | 442.7969 | 86.1742 | 0 | 188233.5597
1 | 29 | 10 | 19.7292 | 362.0532 | 381.7824 | 46.088 | 8.4804 | 718.5177 | 288 | 468.5701 | 153.028 | 228.7544 | 64651.5837 | 23.8528 | 0 | 0 | 153.028 | 228.7544 | 0 | 64651.5837
1 | 29 | 11 | 22.535 | 619.5137 | 642.0487 | 46.7014 | 9.4549 | 9909.784 | 288 | 464.7998 | 18.6593 | 623.3894 | 7801.4402 | 65.0024 | 0 | 0 | 18.6593 | 623.3894 | 0 | 7801.4402
1 | 29 | 12 | 18.295 | 560.4685 | 578.7635 | 46.8304 | 9.8362 | 0 | 0 | 461.4929 | 0 | 578.7635 | 0 | 60.3492 | 0 | 0 | 0 | 578.7635 | 0 | 0
1 | 29 | 13 | 17.793 | 217.5683 | 235.3613 | 45.2029 | 9.6159 | 0 | 0 | 469.734 | 0 | 235.3613 | 0 | 24.5417 | 0 | 0 | 0 | 235.3613 | 0 | 0
1 | 29 | 14 | 14.9558 | 400.889 | 415.8449 | 46.6693 | 9.5227 | 12861.2438 | 288 | 475.4806 | 9.312 | 406.5329 | 3993.0715 | 42.3903 | 0 | 0 | 9.312 | 406.5329 | 0 | 3993.0715
1 | 29 | 15 | 8.2692 | 492.8703 | 501.1394 | 47.3895 | 10.7175 | 0 | 0 | 490.0078 | 0 | 501.1394 | 0 | 52.2551 | 0 | 0 | 0 | 501.1394 | 0 | 0
1 | 29 | 16 | 0 | 0.619 | 0.619 | 48 | 12.0564 | 0 | 0 | 498.8278 | 0 | 0.619 | 0 | 0.064545 | 0 | 0 | 0 | 0.619 | 0 | 0
1 | 29 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 500.5993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 508.3082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 506.5493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 485.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 475.9708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 475.5533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 29 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 469.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 469.7866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 473.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 490.6169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 500.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 514.5888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 527.0166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 533.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 526.4205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 8 | 0.17083 | 27.6289 | 27.7998 | 47.7726 | 5.4976 | 14.1878 | 14.1878 | 527.0663 | 27.7998 | 0 | 13324.253 | 0 | 0 | 0 | 27.7998 | 0 | 0 | 13324.253
1 | 30 | 9 | 0.66333 | 56.2863 | 56.9496 | 47.569 | 6.4043 | 37.3362 | 37.3362 | 516.7311 | 56.9496 | 0 | 26718.606 | 0 | 0 | 0 | 56.9496 | 0 | 0 | 26718.606
1 | 30 | 10 | 5.8233 | 144.3972 | 150.2206 | 46.5657 | 8.5991 | 316.5545 | 288 | 508.7592 | 136.6701 | 13.5505 | 63168.016 | 1.4129 | 0 | 0 | 136.6701 | 13.5505 | 0 | 63168.016
1 | 30 | 11 | 3.0407 | 74.7884 | 77.8291 | 46.5545 | 9.6413 | 0 | 0 | 500.5132 | 0 | 77.8291 | 0 | 8.1154 | 0 | 0 | 0 | 77.8291 | 0 | 0
1 | 30 | 12 | 3.5525 | 200.8599 | 204.4124 | 47.357 | 9.7176 | 0 | 0 | 501.3396 | 0 | 204.4124 | 0 | 21.3146 | 0 | 0 | 0 | 204.4124 | 0 | 0
1 | 30 | 13 | 0.69917 | 12.5781 | 13.2772 | 46.0516 | 9.7939 | 0 | 0 | 501.4902 | 0 | 13.2772 | 0 | 1.3845 | 0 | 0 | 0 | 13.2772 | 0 | 0
1 | 30 | 14 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 483.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 15 | 0 | 0.66575 | 0.66575 | 48 | 10.5311 | 0 | 0 | 500.6082 | 0 | 0.66575 | 0 | 0.069419 | 0 | 0 | 0 | 0.66575 | 0 | 0
1 | 30 | 16 | 0 | 0.99958 | 0.99958 | 48 | 11.0904 | 0 | 0 | 500.6671 | 0 | 0.99958 | 0 | 0.10423 | 0 | 0 | 0 | 0.99958 | 0 | 0
1 | 30 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 509.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 516.3906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 506.3611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 490.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 482.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 481.1539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 30 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 479.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 477.0214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 474.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 478.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 484.1522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 508.5011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 507.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 500.2959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 502.4353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 8 | 1.0408 | 294.8621 | 295.903 | 47.8699 | 6.2094 | 182.8108 | 182.8108 | 497.0154 | 295.903 | 0 | 132903.5115 | 0 | 0 | 0 | 295.903 | 0 | 0 | 132903.5115
1 | 31 | 9 | 0.45333 | 136.1852 | 136.6385 | 47.8772 | 7.328 | 126.1548 | 126.1548 | 493.7359 | 136.6385 | 0 | 60921.4726 | 0 | 0 | 0 | 136.6385 | 0 | 0 | 60921.4726
1 | 31 | 10 | 0.070833 | 21.6289 | 21.6997 | 47.8792 | 8.5482 | 43.496 | 43.496 | 494.6725 | 21.6997 | 0 | 9695.3005 | 0 | 0 | 0 | 21.6997 | 0 | 0 | 9695.3005
1 | 31 | 11 | 0.66417 | 135.3722 | 136.0363 | 47.8194 | 9.1838 | 699.0054 | 288 | 494.7137 | 56.0489 | 79.9875 | 25047.9274 | 8.3405 | 0 | 0 | 56.0489 | 79.9875 | 0 | 25047.9274
1 | 31 | 12 | 0.0625 | 5.1825 | 5.245 | 47.5591 | 9.8701 | 0 | 0 | 490.569 | 0 | 5.245 | 0 | 0.54691 | 0 | 0 | 0 | 5.245 | 0 | 0
1 | 31 | 13 | 0.24417 | 18.6947 | 18.9388 | 47.523 | 9.6668 | 0 | 0 | 494.0378 | 0 | 18.9388 | 0 | 1.9748 | 0 | 0 | 0 | 18.9388 | 0 | 0
1 | 31 | 14 | 0.43167 | 82.6977 | 83.1294 | 47.8079 | 10.2684 | 0 | 0 | 497.949 | 0 | 83.1294 | 0 | 8.6681 | 0 | 0 | 0 | 83.1294 | 0 | 0
1 | 31 | 15 | 0.096667 | 40.0339 | 40.1305 | 47.9109 | 11.226 | 0 | 0 | 512.0007 | 0 | 40.1305 | 0 | 4.1845 | 0 | 0 | 0 | 40.1305 | 0 | 0
1 | 31 | 16 | 0 | 0.49967 | 0.49967 | 48 | 11.853 | 0 | 0 | 514.9851 | 0 | 0.49967 | 0 | 0.052102 | 0 | 0 | 0 | 0.49967 | 0 | 0
1 | 31 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 513.2047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 503.2367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 496.3774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 477.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 458.1882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 454.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 31 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 446.7848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 443.3902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 443.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 460.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 480.0431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 509.5005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 511.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 511.8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 516.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 8 | 1.6492 | 7.7776 | 9.4267 | 41.527 | 6.2094 | 5.8239 | 5.8239 | 516.1396 | 9.4267 | 0 | 4474.043 | 0 | 0 | 0 | 9.4267 | 0 | 0 | 4474.043
2 | 1 | 9 | 0 | 5.0705 | 5.0705 | 48 | 7.311 | 4.6466 | 4.6466 | 511.7915 | 5.0705 | 0 | 2351.6529 | 0 | 0 | 0 | 5.0705 | 0 | 0 | 2351.6529
2 | 1 | 10 | 0.50083 | 287.7193 | 288.2201 | 47.9357 | 8.0567 | 392.5643 | 288 | 506.126 | 211.4491 | 76.7709 | 96883.9337 | 8.0051 | 0 | 0 | 211.4491 | 76.7709 | 0 | 96883.9337
2 | 1 | 11 | 0.70167 | 265.8357 | 266.5374 | 47.9026 | 9.3109 | 1992.6721 | 288 | 497.3757 | 38.5225 | 228.0149 | 17314.8424 | 23.7757 | 0 | 0 | 38.5225 | 228.0149 | 0 | 17314.8424
2 | 1 | 12 | 0.735 | 128.5777 | 129.3127 | 47.7897 | 9.0058 | 462.1419 | 288 | 488.7475 | 80.5858 | 48.7269 | 35534.9174 | 5.0809 | 0 | 0 | 80.5858 | 48.7269 | 0 | 35534.9174
2 | 1 | 13 | 0.20083 | 8.6193 | 8.8201 | 47.1575 | 8.4889 | 16.7272 | 16.7272 | 487.91 | 8.8201 | 0 | 3887.4767 | 0 | 0 | 0 | 8.8201 | 0 | 0 | 3887.4767
2 | 1 | 14 | 0 | 1.8881 | 1.8881 | 48 | 8.938 | 6.0465 | 6.0465 | 491.0042 | 1.8881 | 0 | 836.4474 | 0 | 0 | 0 | 1.8881 | 0 | 0 | 836.4474
2 | 1 | 15 | 1.6017 | 0.74704 | 2.3487 | 22.7684 | 9.6075 | 0 | 0 | 510.0279 | 0 | 2.3487 | 0 | 0.24491 | 0 | 0 | 0 | 2.3487 | 0 | 0
2 | 1 | 16 | 0 | 0.45433 | 0.45433 | 48 | 10.9718 | 0 | 0 | 508.3127 | 0 | 0.45433 | 0 | 0.047375 | 0 | 0 | 0 | 0.45433 | 0 | 0
2 | 1 | 17 | 0 | 0.032458 | 0.032458 | 48 | 10.3786 | 0 | 0 | 508.6427 | 0 | 0.032458 | 0 | 0.0033845 | 0 | 0 | 0 | 0.032458 | 0 | 0
2 | 1 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 497.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 479.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 457.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 444.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 435.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 1 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 433.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 433.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 437.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 458.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 466.2312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 503.2356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 512.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 498.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 7 | 8.9697 | 0 | 8.9697 | 11 | 4.6502 | 3.7925 | 3.7925 | 497.3156 | 8.9697 | 0 | 4362.1271 | 0 | 0 | 0 | 8.9697 | 0 | 0 | 4362.1271
2 | 2 | 8 | 44.135 | 0 | 44.135 | 11 | 5.1417 | 20.7224 | 20.7224 | 505.2653 | 44.135 | 0 | 21814.3875 | 0 | 0 | 0 | 44.135 | 0 | 0 | 21814.3875
2 | 2 | 9 | 107.1891 | 22.5206 | 129.7098 | 17.4241 | 6.6161 | 91.0952 | 91.0952 | 501.9652 | 129.7098 | 0 | 62849.7195 | 0 | 0 | 0 | 129.7098 | 0 | 0 | 62849.7195
2 | 2 | 10 | 52.0209 | 0 | 52.0209 | 11 | 6.9721 | 41.5006 | 41.5006 | 498.8083 | 52.0209 | 0 | 25376.2202 | 0 | 0 | 0 | 52.0209 | 0 | 0 | 25376.2202
2 | 2 | 11 | 11.9823 | 0 | 11.9823 | 11 | 8.5652 | 24.415 | 24.415 | 489.2583 | 11.9823 | 0 | 5730.645 | 0 | 0 | 0 | 11.9823 | 0 | 0 | 5730.645
2 | 2 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 477.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 13 | 0 | 0.17571 | 0.17571 | 48 | 7.4381 | 0.17053 | 0.17053 | 483.8683 | 0.17571 | 0 | 76.5857 | 0 | 0 | 0 | 0.17571 | 0 | 0 | 76.5857
2 | 2 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 484.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 15 | 0 | 1.1644 | 1.1644 | 48 | 7.3449 | 1.0832 | 1.0832 | 506.5486 | 1.1644 | 0 | 533.9226 | 0 | 0 | 0 | 1.1644 | 0 | 0 | 533.9226
2 | 2 | 16 | 0 | 0.219 | 0.219 | 48 | 6.9975 | 0.17642 | 0.17642 | 513.8903 | 0.219 | 0 | 102.03 | 0 | 0 | 0 | 0.219 | 0 | 0 | 102.03
2 | 2 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 514.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 516.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 511.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 506.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 498.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 490.6714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 487.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 483.793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 483.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 490.5366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 480.8492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 510.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 509.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 505.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 511.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 8 | 3.3789 | 11.7475 | 15.1264 | 39.735 | 6.8788 | 11.6525 | 11.6525 | 522.3748 | 15.1264 | 0 | 7300.599 | 0 | 0 | 0 | 15.1264 | 0 | 0 | 7300.599
2 | 3 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 519.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 515.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 509.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 508.4526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 505.1285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 14 | 2.2901 | 2.8916 | 5.1817 | 31.6475 | 8.2431 | 8.0343 | 8.0343 | 487.4583 | 5.1817 | 0 | 2361.8672 | 0 | 0 | 0 | 5.1817 | 0 | 0 | 2361.8672
2 | 3 | 15 | 35.0687 | 57.7804 | 92.8491 | 34.0253 | 7.4212 | 89.4091 | 89.4091 | 497.4028 | 92.8491 | 0 | 43024.1764 | 0 | 0 | 0 | 92.8491 | 0 | 0 | 43024.1764
2 | 3 | 16 | 0 | 0.014167 | 0.014167 | 48 | 7.3195 | 0.013031 | 0.013031 | 507.4406 | 0.014167 | 0 | 6.5087 | 0 | 0 | 0 | 0.014167 | 0 | 0 | 6.5087
2 | 3 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 513.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 522.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 525.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 523.2307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 515.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 510.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 504.0068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 504.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 514.3431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 518.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 519.3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 522.7541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 517.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 521.837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 7 | 39.4621 | 129.4229 | 168.885 | 39.3545 | 6.006 | 98.4179 | 98.4179 | 523.7847 | 168.885 | 0 | 81812.9915 | 0 | 0 | 0 | 168.885 | 0 | 0 | 81812.9915
2 | 4 | 8 | 89.3983 | 555.0266 | 644.425 | 42.8671 | 6.6246 | 453.873 | 288 | 503.6118 | 408.9126 | 235.5123 | 188404.294 | 24.5575 | 0 | 0 | 408.9126 | 235.5123 | 0 | 188404.294
2 | 4 | 9 | 81.7624 | 711.1577 | 792.9201 | 44.1847 | 7.1924 | 690.688 | 288 | 489.8084 | 330.6283 | 462.2918 | 147335.8086 | 48.2044 | 0 | 0 | 330.6283 | 462.2918 | 0 | 147335.8086
2 | 4 | 10 | 123.2775 | 828.6568 | 951.9344 | 43.2084 | 7.0398 | 779.6086 | 288 | 483.3395 | 351.6599 | 600.2745 | 154776.4605 | 62.5922 | 0 | 0 | 351.6599 | 600.2745 | 0 | 154776.4605
2 | 4 | 11 | 108.048 | 864.9425 | 972.9904 | 43.8912 | 7.2093 | 853.5746 | 288 | 467.7326 | 328.2914 | 644.699 | 139143.4836 | 67.2245 | 0 | 0 | 328.2914 | 644.699 | 0 | 139143.4836
2 | 4 | 12 | 63.8933 | 735.2418 | 799.1351 | 45.0417 | 7.9296 | 1005.1334 | 288 | 463.3782 | 228.9755 | 570.1596 | 95788.7903 | 59.452 | 0 | 0 | 228.9755 | 570.1596 | 0 | 95788.7903
2 | 4 | 13 | 56.2573 | 824.4397 | 880.6969 | 45.6365 | 8.2601 | 1382.9392 | 288 | 468.4908 | 183.407 | 697.2899 | 77554.4355 | 72.7082 | 0 | 0 | 183.407 | 697.2899 | 0 | 77554.4355
2 | 4 | 14 | 74.3179 | 733.1091 | 807.427 | 44.5944 | 8.5313 | 1592.5423 | 288 | 486.476 | 146.0175 | 661.4095 | 64522.425 | 68.9669 | 0 | 0 | 146.0175 | 661.4095 | 0 | 64522.425
2 | 4 | 15 | 39.995 | 373.2029 | 413.1979 | 44.4186 | 8.4041 | 727.6399 | 288 | 502.1668 | 163.5438 | 249.6541 | 74861.868 | 26.0321 | 0 | 0 | 163.5438 | 249.6541 | 0 | 74861.868
2 | 4 | 16 | 11.99 | 66.3481 | 78.3381 | 42.337 | 9.1753 | 394.3103 | 288 | 499.7838 | 57.2173 | 21.1208 | 26173.8691 | 2.2023 | 0 | 0 | 57.2173 | 21.1208 | 0 | 26173.8691
2 | 4 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 500.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 494.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 485.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 474.6865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 466.6247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 459.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 4 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 456.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 447.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 444.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 444.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 447.6958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 451.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 461.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 476.5577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 478.9377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 472.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 470.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 470.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 11 | 0 | 0.042333 | 0.042333 | 48 | 9.4549 | 0.6534 | 0.6534 | 464.2198 | 0.042333 | 0 | 17.62 | 0 | 0 | 0 | 0.042333 | 0 | 0 | 17.62
2 | 5 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 466.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 473.9627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 488.5629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 15 | 0 | 0.99787 | 0.99787 | 48 | 10.7175 | 0 | 0 | 497.348 | 0 | 0.99787 | 0 | 0.10405 | 0 | 0 | 0 | 0.99787 | 0 | 0
2 | 5 | 16 | 0 | 0.99883 | 0.99883 | 48 | 12.0564 | 0 | 0 | 497.1343 | 0 | 0.99883 | 0 | 0.10415 | 0 | 0 | 0 | 0.99883 | 0 | 0
2 | 5 | 17 | 0 | 0.073292 | 0.073292 | 48 | 11.8107 | 0 | 0 | 501.3831 | 0 | 0.073292 | 0 | 0.0076423 | 0 | 0 | 0 | 0.073292 | 0 | 0
2 | 5 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 497.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 493.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 492.7043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 474.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 469.9364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 5 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 465.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 470.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 473.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 484.1595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 488.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 503.6225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 507.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 510.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 507.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 504.5483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 495.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 492.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 482.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 12 | 0 | 0.035 | 0.035 | 48 | 9.7176 | 0 | 0 | 475.9147 | 0 | 0.035 | 0 | 0.0036495 | 0 | 0 | 0 | 0.035 | 0 | 0
2 | 6 | 13 | 0 | 0.079167 | 0.079167 | 48 | 9.7939 | 0 | 0 | 479.4954 | 0 | 0.079167 | 0 | 0.0082549 | 0 | 0 | 0 | 0.079167 | 0 | 0
2 | 6 | 14 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 481.1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 15 | 0 | 0.76663 | 0.76663 | 48 | 10.5311 | 0 | 0 | 502.592 | 0 | 0.76663 | 0 | 0.079938 | 0 | 0 | 0 | 0.76663 | 0 | 0
2 | 6 | 16 | 0 | 1.9185 | 1.9185 | 48 | 11.0904 | 0 | 0 | 495.6597 | 0 | 1.9185 | 0 | 0.20005 | 0 | 0 | 0 | 1.9185 | 0 | 0
2 | 6 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 494.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 491.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 475.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 454.3786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 445.2578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 447.3902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 6 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 443.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 442.3303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 439.3116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 452.5858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 469.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 497.1536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 5 | 0.53162 | 0 | 0.53162 | 11 | 3.8536 | 0.19357 | 0.19357 | 505.7701 | 0.53162 | 0 | 263.0322 | 0 | 0 | 0 | 0.53162 | 0 | 0 | 263.0322
2 | 7 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 498.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 7 | 0 | 1.9429 | 1.9429 | 48 | 5.2518 | 0.93542 | 0.93542 | 495.3686 | 1.9429 | 0 | 869.2126 | 0 | 0 | 0 | 1.9429 | 0 | 0 | 869.2126
2 | 7 | 8 | 0 | 65.1715 | 65.1715 | 48 | 6.2094 | 40.2634 | 40.2634 | 495.9327 | 65.1715 | 0 | 29192.4491 | 0 | 0 | 0 | 65.1715 | 0 | 0 | 29192.4491
2 | 7 | 9 | 0 | 32.3477 | 32.3477 | 48 | 7.328 | 29.8658 | 29.8658 | 485.5961 | 32.3477 | 0 | 14155.2178 | 0 | 0 | 0 | 32.3477 | 0 | 0 | 14155.2178
2 | 7 | 10 | 0.76838 | 64.1088 | 64.8772 | 47.5618 | 8.5482 | 130.0428 | 130.0428 | 482.2519 | 64.8772 | 0 | 28201.4663 | 0 | 0 | 0 | 64.8772 | 0 | 0 | 28201.4663
2 | 7 | 11 | 0 | 88.2613 | 88.2613 | 48 | 9.1838 | 453.5195 | 288 | 477.5196 | 56.0489 | 32.2124 | 24074.0888 | 3.3589 | 0 | 0 | 56.0489 | 32.2124 | 0 | 24074.0888
2 | 7 | 12 | 0 | 98.5762 | 98.5762 | 48 | 9.8701 | 0 | 0 | 467.7461 | 0 | 98.5762 | 0 | 10.2788 | 0 | 0 | 0 | 98.5762 | 0 | 0
2 | 7 | 13 | 0 | 49.9109 | 49.9109 | 48 | 9.6668 | 0 | 0 | 475.2059 | 0 | 49.9109 | 0 | 5.2043 | 0 | 0 | 0 | 49.9109 | 0 | 0
2 | 7 | 14 | 0 | 119.1662 | 119.1662 | 48 | 10.2684 | 0 | 0 | 479.5864 | 0 | 119.1662 | 0 | 12.4258 | 0 | 0 | 0 | 119.1662 | 0 | 0
2 | 7 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 489.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 497.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 485.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 480.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 461.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 432.9946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 421.9083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 421.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 417.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 420.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 428.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 444.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 471.1788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 506.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 513.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 514.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 7 | 4.1152 | 56.8397 | 60.9549 | 45.5021 | 5.0146 | 27.8248 | 27.8248 | 516.4177 | 60.9549 | 0 | 28704.6004 | 0 | 0 | 0 | 60.9549 | 0 | 0 | 28704.6004
2 | 8 | 8 | 16.24 | 121.1008 | 137.3407 | 43.6249 | 6.2094 | 84.85 | 84.85 | 515.2718 | 137.3407 | 0 | 64776.3338 | 0 | 0 | 0 | 137.3407 | 0 | 0 | 64776.3338
2 | 8 | 9 | 0 | 179.0089 | 179.0089 | 48 | 7.311 | 164.0453 | 164.0453 | 514.4577 | 179.0089 | 0 | 83500.0902 | 0 | 0 | 0 | 179.0089 | 0 | 0 | 83500.0902
2 | 8 | 10 | 0 | 196.3874 | 196.3874 | 48 | 8.0567 | 267.4854 | 267.4854 | 517.6528 | 196.3874 | 0 | 92233.8853 | 0 | 0 | 0 | 196.3874 | 0 | 0 | 92233.8853
2 | 8 | 11 | 77.14 | 352.4937 | 429.6337 | 41.3567 | 9.3109 | 3212.0033 | 288 | 507.8192 | 38.5225 | 391.1111 | 17969.3165 | 40.7822 | 0 | 0 | 38.5225 | 391.1111 | 0 | 17969.3165
2 | 8 | 12 | 0 | 188.7672 | 188.7672 | 48 | 9.0058 | 674.6222 | 288 | 506.7924 | 80.5858 | 108.1814 | 36972.1374 | 11.2804 | 0 | 0 | 80.5858 | 108.1814 | 0 | 36972.1374
2 | 8 | 13 | 0 | 175.5905 | 175.5905 | 48 | 8.4889 | 333.0054 | 288 | 496.7321 | 151.8596 | 23.7309 | 68144.2677 | 2.4745 | 0 | 0 | 151.8596 | 23.7309 | 0 | 68144.2677
2 | 8 | 14 | 0 | 172.6501 | 172.6501 | 48 | 8.938 | 552.891 | 288 | 490.9471 | 89.9331 | 82.717 | 39835.6263 | 8.6251 | 0 | 0 | 89.9331 | 82.717 | 0 | 39835.6263
2 | 8 | 15 | 0 | 22.745 | 22.745 | 48 | 9.6075 | 0 | 0 | 496.0181 | 0 | 22.745 | 0 | 2.3717 | 0 | 0 | 0 | 22.745 | 0 | 0
2 | 8 | 16 | 0.23746 | 0.18071 | 0.41817 | 26.9893 | 10.9718 | 0 | 0 | 503.2904 | 0 | 0.41817 | 0 | 0.043603 | 0 | 0 | 0 | 0.41817 | 0 | 0
2 | 8 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 515.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 512.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 496.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 471.4934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 447.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 444.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 8 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 435.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 433.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 434.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 446.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 470.5469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 503.9593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 513.5525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 520.9144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 523.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 8 | 31.6183 | 338.1395 | 369.7578 | 44.8361 | 5.1417 | 173.6103 | 173.6103 | 525.3124 | 369.7578 | 0 | 177659.8923 | 0 | 0 | 0 | 369.7578 | 0 | 0 | 177659.8923
2 | 9 | 9 | 34.4303 | 82.9635 | 117.3938 | 37.1483 | 6.6161 | 82.4457 | 82.4457 | 523.6585 | 117.3938 | 0 | 57113.2875 | 0 | 0 | 0 | 117.3938 | 0 | 0 | 57113.2875
2 | 9 | 10 | 1.4684 | 6.478 | 7.9463 | 41.163 | 6.9721 | 6.3393 | 6.3393 | 523.1914 | 7.9463 | 0 | 3830.3643 | 0 | 0 | 0 | 7.9463 | 0 | 0 | 3830.3643
2 | 9 | 11 | 0 | 8.624 | 8.624 | 48 | 8.5652 | 17.5722 | 17.5722 | 517.7262 | 8.624 | 0 | 4050.9374 | 0 | 0 | 0 | 8.624 | 0 | 0 | 4050.9374
2 | 9 | 12 | 0 | 0.14006 | 0.14006 | 48 | 7.8957 | 0.17264 | 0.17264 | 519.1876 | 0.14006 | 0 | 65.9946 | 0 | 0 | 0 | 0.14006 | 0 | 0 | 65.9946
2 | 9 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 521.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 14 | 0 | 0.32396 | 0.32396 | 48 | 7.2771 | 0.29253 | 0.29253 | 507.9308 | 0.32396 | 0 | 148.9984 | 0 | 0 | 0 | 0.32396 | 0 | 0 | 148.9984
2 | 9 | 15 | 0 | 0.499 | 0.499 | 48 | 7.3449 | 0.46419 | 0.46419 | 511.0701 | 0.499 | 0 | 231.072 | 0 | 0 | 0 | 0.499 | 0 | 0 | 231.072
2 | 9 | 16 | 0 | 0.71092 | 0.71092 | 48 | 6.9975 | 0.57271 | 0.57271 | 513.7372 | 0.71092 | 0 | 331.1003 | 0 | 0 | 0 | 0.71092 | 0 | 0 | 331.1003
2 | 9 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 514.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 520.8927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 533.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 530.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 528.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 523.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 9 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 519.3632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 523.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 525.3513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 2 | 143.313 | 0 | 143.313 | 11 | 3.0232 | 45.582 | 45.582 | 517.6167 | 143.313 | 0 | 72604.734 | 0 | 0 | 0 | 143.313 | 0 | 0 | 72604.734
2 | 10 | 3 | 17.0382 | 0 | 17.0382 | 11 | 2.9893 | 5.3913 | 5.3913 | 506.3655 | 17.0382 | 0 | 8440.1227 | 0 | 0 | 0 | 17.0382 | 0 | 0 | 8440.1227
2 | 10 | 4 | 3.6765 | 0 | 3.6765 | 11 | 2.9469 | 1.1559 | 1.1559 | 507.6973 | 3.6765 | 0 | 1826.0867 | 0 | 0 | 0 | 3.6765 | 0 | 0 | 1826.0867
2 | 10 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 510.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 504.3944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 522.2924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 529.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 527.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 10 | 0 | 11.6591 | 11.6591 | 48 | 7.4805 | 11.5428 | 11.5428 | 521.7119 | 11.6591 | 0 | 5523.074 | 0 | 0 | 0 | 11.6591 | 0 | 0 | 5523.074
2 | 10 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 520.3031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 518.8059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 521.3522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 517.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 15 | 0 | 0.18225 | 0.18225 | 48 | 7.4212 | 0.1755 | 0.1755 | 520.9134 | 0.18225 | 0 | 86.1885 | 0 | 0 | 0 | 0.18225 | 0 | 0 | 86.1885
2 | 10 | 16 | 0 | 0.019 | 0.019 | 48 | 7.3195 | 0.017477 | 0.017477 | 520.3527 | 0.019 | 0 | 8.9747 | 0 | 0 | 0 | 0.019 | 0 | 0 | 8.9747
2 | 10 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 511.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 503.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 490.6648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 475.6116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 460.7309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 463.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 10 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 456.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 455.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 459.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 461.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 3 | 136.1589 | 0 | 136.1589 | 11 | 3.3622 | 45.6635 | 45.6635 | 463.2962 | 136.1589 | 0 | 61584.1655 | 0 | 0 | 0 | 136.1589 | 0 | 0 | 61584.1655
2 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 480.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 484.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 494.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 494.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 8 | 0 | 0.16654 | 0.16654 | 48 | 6.6246 | 0.1173 | 0.1173 | 495.9231 | 0.16654 | 0 | 74.5979 | 0 | 0 | 0 | 0.16654 | 0 | 0 | 74.5979
2 | 11 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 491.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 10 | 8.5142 | 1.4435 | 9.9577 | 16.3637 | 7.0398 | 8.1551 | 8.1551 | 485.9036 | 9.9577 | 0 | 4675.5338 | 0 | 0 | 0 | 9.9577 | 0 | 0 | 4675.5338
2 | 11 | 11 | 0 | 3.7979 | 3.7979 | 48 | 7.2093 | 3.3318 | 3.3318 | 474.6869 | 3.7979 | 0 | 1620.5186 | 0 | 0 | 0 | 3.7979 | 0 | 0 | 1620.5186
2 | 11 | 12 | 0 | 2.8728 | 2.8728 | 48 | 7.9296 | 3.6134 | 3.6134 | 468.2085 | 2.8728 | 0 | 1207.1828 | 0 | 0 | 0 | 2.8728 | 0 | 0 | 1207.1828
2 | 11 | 13 | 0 | 0.057536 | 0.057536 | 48 | 8.2601 | 0.090348 | 0.090348 | 467.5853 | 0.057536 | 0 | 24.1413 | 0 | 0 | 0 | 0.057536 | 0 | 0 | 24.1413
2 | 11 | 14 | 0 | 0.333 | 0.333 | 48 | 8.5313 | 0.6568 | 0.6568 | 469.3627 | 0.333 | 0 | 140.3138 | 0 | 0 | 0 | 0.333 | 0 | 0 | 140.3138
2 | 11 | 15 | 0 | 0.45375 | 0.45375 | 48 | 8.4041 | 0.79905 | 0.79905 | 493.5176 | 0.45375 | 0 | 202.1536 | 0 | 0 | 0 | 0.45375 | 0 | 0 | 202.1536
2 | 11 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 479.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 476.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 475.9091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 478.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 459.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 449.075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 448.3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 11 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 429.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 422.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 417.8282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 416.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 424.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 432.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 437.5997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 450.3886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 457.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 8 | 41.1263 | 260.7497 | 301.876 | 42.9593 | 4.8451 | 132.879 | 132.879 | 455.9715 | 301.876 | 0 | 124678.479 | 0 | 0 | 0 | 301.876 | 0 | 0 | 124678.479
2 | 12 | 9 | 39.9896 | 604.6404 | 644.63 | 45.7047 | 6.3789 | 419.2745 | 288 | 441.2985 | 442.7969 | 201.8331 | 175167.7199 | 21.0457 | 0 | 0 | 442.7969 | 201.8331 | 0 | 175167.7199
2 | 12 | 10 | 28.2775 | 644.8812 | 673.1587 | 46.4457 | 8.4804 | 1266.8906 | 288 | 435.4314 | 153.028 | 520.1307 | 59525.6876 | 54.2354 | 0 | 0 | 153.028 | 520.1307 | 0 | 59525.6876
2 | 12 | 11 | 30.145 | 391.5796 | 421.7246 | 45.3552 | 9.4549 | 6509.1626 | 288 | 433.6765 | 18.6593 | 403.0652 | 7245.8179 | 42.0287 | 0 | 0 | 18.6593 | 403.0652 | 0 | 7245.8179
2 | 12 | 12 | 14.3449 | 37.9777 | 52.3227 | 37.856 | 9.8362 | 0 | 0 | 426.9324 | 0 | 52.3227 | 0 | 5.4558 | 0 | 0 | 0 | 52.3227 | 0 | 0
2 | 12 | 13 | 23.2817 | 344.0479 | 367.3296 | 45.6549 | 9.6159 | 0 | 0 | 433.8851 | 0 | 367.3296 | 0 | 38.3024 | 0 | 0 | 0 | 367.3296 | 0 | 0
2 | 12 | 14 | 25.0092 | 586.0386 | 611.0478 | 46.4857 | 9.5227 | 18898.4763 | 288 | 444.3071 | 9.312 | 601.7358 | 3704.4953 | 62.7446 | 0 | 0 | 9.312 | 601.7358 | 0 | 3704.4953
2 | 12 | 15 | 18.3225 | 292.4775 | 310.8 | 45.8188 | 10.7175 | 0 | 0 | 460.6773 | 0 | 310.8 | 0 | 32.4079 | 0 | 0 | 0 | 310.8 | 0 | 0
2 | 12 | 16 | 1.5367 | 7.2269 | 8.7636 | 41.5122 | 12.0564 | 0 | 0 | 473.5481 | 0 | 8.7636 | 0 | 0.9138 | 0 | 0 | 0 | 8.7636 | 0 | 0
2 | 12 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 478.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 469.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 462.4147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 446.3699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 419.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 424.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 12 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 430.6091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 441.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 454.8849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 465.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 485.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 493.3913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 499.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 511.1745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 513.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 8 | 3.09 | 342.7592 | 345.8492 | 47.6694 | 5.4976 | 176.5059 | 176.5059 | 515.3433 | 345.8492 | 0 | 161744.6485 | 0 | 0 | 0 | 345.8492 | 0 | 0 | 161744.6485
2 | 13 | 9 | 2.05 | 151.4656 | 153.5156 | 47.5059 | 6.4043 | 100.645 | 100.645 | 507.5372 | 153.5156 | 0 | 70621.9619 | 0 | 0 | 0 | 153.5156 | 0 | 0 | 70621.9619
2 | 13 | 10 | 6.3267 | 233.6456 | 239.9722 | 47.0245 | 8.5991 | 505.685 | 288 | 502.8864 | 136.6701 | 103.3022 | 62302.6691 | 10.7716 | 0 | 0 | 136.6701 | 103.3022 | 0 | 62302.6691
2 | 13 | 11 | 10.4125 | 170.9927 | 181.4052 | 45.8762 | 9.6413 | 0 | 0 | 494.5394 | 0 | 181.4052 | 0 | 18.9156 | 0 | 0 | 0 | 181.4052 | 0 | 0
2 | 13 | 12 | 0 | 6.1977 | 6.1977 | 48 | 9.7176 | 0 | 0 | 488.0783 | 0 | 6.1977 | 0 | 0.64625 | 0 | 0 | 0 | 6.1977 | 0 | 0
2 | 13 | 13 | 0.24417 | 2.2967 | 2.5409 | 44.4444 | 9.7939 | 0 | 0 | 491.2791 | 0 | 2.5409 | 0 | 0.26494 | 0 | 0 | 0 | 2.5409 | 0 | 0
2 | 13 | 14 | 1.3483 | 126.0279 | 127.3763 | 47.6083 | 9.4634 | 2097.3381 | 288 | 474.3195 | 17.4909 | 109.8853 | 7463.5692 | 11.458 | 0 | 0 | 17.4909 | 109.8853 | 0 | 7463.5692
2 | 13 | 15 | 0.665 | 96.536 | 97.201 | 47.7469 | 10.5311 | 0 | 0 | 479.6129 | 0 | 97.201 | 0 | 10.1354 | 0 | 0 | 0 | 97.201 | 0 | 0
2 | 13 | 16 | 0 | 0.39183 | 0.39183 | 48 | 11.0904 | 0 | 0 | 493.1291 | 0 | 0.39183 | 0 | 0.040857 | 0 | 0 | 0 | 0.39183 | 0 | 0
2 | 13 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 496.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 503.4506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 500.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 492.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 491.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 483.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 13 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 480.4288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 477.4255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 476.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 477.8376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 485.7089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 499.3497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 507.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 516.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 514.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 8 | 0.75037 | 118.3861 | 119.1364 | 47.767 | 6.2094 | 73.6033 | 73.6033 | 513.8549 | 119.1364 | 0 | 55528.0521 | 0 | 0 | 0 | 119.1364 | 0 | 0 | 55528.0521
2 | 14 | 9 | 1.6092 | 491.4359 | 493.0451 | 47.8792 | 7.328 | 455.2156 | 288 | 504.2466 | 311.9335 | 181.1116 | 142356.2889 | 18.885 | 0 | 0 | 311.9335 | 181.1116 | 0 | 142356.2889
2 | 14 | 10 | 1.1042 | 784.0727 | 785.1769 | 47.948 | 8.5482 | 1573.8447 | 288 | 505.5504 | 143.6806 | 641.4963 | 65748.5877 | 66.8905 | 0 | 0 | 143.6806 | 641.4963 | 0 | 65748.5877
2 | 14 | 11 | 0.82833 | 486.4028 | 487.2311 | 47.9371 | 9.1838 | 2503.5749 | 288 | 493.8489 | 56.0489 | 431.1822 | 24992.8576 | 44.9605 | 0 | 0 | 56.0489 | 431.1822 | 0 | 24992.8576
2 | 14 | 12 | 0.48667 | 86.9191 | 87.4057 | 47.794 | 9.8701 | 0 | 0 | 481.9625 | 0 | 87.4057 | 0 | 9.114 | 0 | 0 | 0 | 87.4057 | 0 | 0
2 | 14 | 13 | 0.64167 | 62.0282 | 62.6699 | 47.6212 | 9.6668 | 0 | 0 | 481.0939 | 0 | 62.6699 | 0 | 6.5348 | 0 | 0 | 0 | 62.6699 | 0 | 0
2 | 14 | 14 | 0.62 | 486.5372 | 487.1572 | 47.9529 | 10.2684 | 0 | 0 | 475.5273 | 0 | 487.1572 | 0 | 50.7972 | 0 | 0 | 0 | 487.1572 | 0 | 0
2 | 14 | 15 | 13.4448 | 852.5112 | 865.956 | 47.4255 | 11.226 | 0 | 0 | 493.014 | 0 | 865.956 | 0 | 90.2955 | 0 | 0 | 0 | 865.956 | 0 | 0
2 | 14 | 16 | 1.4642 | 145.6628 | 147.127 | 47.6318 | 11.853 | 0 | 0 | 502.6119 | 0 | 147.127 | 0 | 15.3413 | 0 | 0 | 0 | 147.127 | 0 | 0
2 | 14 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 500.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 492.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 480.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 475.5623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 464.9487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 456.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 448.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 445.9247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 455.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 463.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 474.5593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 493.5172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 495.1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 504.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 7 | 2.0425 | 110.3157 | 112.3582 | 47.3274 | 5.0146 | 51.2894 | 51.2894 | 507.7643 | 112.3582 | 0 | 51733.8527 | 0 | 0 | 0 | 112.3582 | 0 | 0 | 51733.8527
2 | 15 | 8 | 1.8092 | 63.623 | 65.4322 | 46.977 | 6.2094 | 40.4244 | 40.4244 | 502.046 | 65.4322 | 0 | 29776.1736 | 0 | 0 | 0 | 65.4322 | 0 | 0 | 29776.1736
2 | 15 | 9 | 1.3842 | 308.3947 | 309.7788 | 47.8347 | 7.311 | 283.8839 | 283.8839 | 497.0905 | 309.7788 | 0 | 139169.9453 | 0 | 0 | 0 | 309.7788 | 0 | 0 | 139169.9453
2 | 15 | 10 | 2.3292 | 170.2929 | 172.622 | 47.5008 | 8.0567 | 235.1163 | 235.1163 | 491.2701 | 172.622 | 0 | 76604.3634 | 0 | 0 | 0 | 172.622 | 0 | 0 | 76604.3634
2 | 15 | 11 | 1.1256 | 73.7527 | 74.8783 | 47.4438 | 9.3109 | 559.8011 | 288 | 486.5494 | 38.5225 | 36.3558 | 16915.4591 | 3.7909 | 0 | 0 | 38.5225 | 36.3558 | 0 | 16915.4591
2 | 15 | 12 | 1.2992 | 76.4078 | 77.707 | 47.3814 | 9.0058 | 277.7116 | 277.7116 | 481.8606 | 77.707 | 0 | 33762.0586 | 0 | 0 | 0 | 77.707 | 0 | 0 | 33762.0586
2 | 15 | 13 | 0.25 | 16.397 | 16.647 | 47.4443 | 8.4889 | 31.5708 | 31.5708 | 489.4763 | 16.647 | 0 | 7358.4964 | 0 | 0 | 0 | 16.647 | 0 | 0 | 7358.4964
2 | 15 | 14 | 1.3733 | 41.1728 | 42.5461 | 46.8057 | 8.938 | 136.2486 | 136.2486 | 495.2245 | 42.5461 | 0 | 19078.4588 | 0 | 0 | 0 | 42.5461 | 0 | 0 | 19078.4588
2 | 15 | 15 | 0 | 0.16575 | 0.16575 | 48 | 9.6075 | 0 | 0 | 503.8063 | 0 | 0.16575 | 0 | 0.017283 | 0 | 0 | 0 | 0.16575 | 0 | 0
2 | 15 | 16 | 0 | 0.29142 | 0.29142 | 48 | 10.9718 | 0 | 0 | 507.8127 | 0 | 0.29142 | 0 | 0.030387 | 0 | 0 | 0 | 0.29142 | 0 | 0
2 | 15 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 510.7349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 515.6941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 507.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 495.1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 488.0608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 489.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 15 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 495.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 496.9809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 503.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 507.6812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 500.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 510.7455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 520.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 522.9806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 7 | 0.15917 | 3.8342 | 3.9934 | 46.5253 | 4.6502 | 1.6884 | 1.6884 | 522.9485 | 3.9934 | 0 | 1902.5367 | 0 | 0 | 0 | 3.9934 | 0 | 0 | 1902.5367
2 | 16 | 8 | 25.0975 | 256.9444 | 282.0419 | 44.7075 | 5.1417 | 132.4255 | 132.4255 | 521.1018 | 282.0419 | 0 | 134363.1425 | 0 | 0 | 0 | 282.0419 | 0 | 0 | 134363.1425
2 | 16 | 9 | 10.005 | 332.4571 | 342.4621 | 46.9191 | 6.6161 | 240.5112 | 240.5112 | 515.1918 | 342.4621 | 0 | 160365.6763 | 0 | 0 | 0 | 342.4621 | 0 | 0 | 160365.6763
2 | 16 | 10 | 7.9045 | 403.7977 | 411.7022 | 47.2896 | 6.9721 | 328.4427 | 288 | 513.5917 | 361.0073 | 50.6949 | 168338.4474 | 5.2861 | 0 | 0 | 361.0073 | 50.6949 | 0 | 168338.4474
2 | 16 | 11 | 42.4525 | 659.1419 | 701.5944 | 45.7612 | 8.5652 | 1429.5585 | 288 | 504.2034 | 141.3438 | 560.2506 | 64797.947 | 58.4188 | 0 | 0 | 141.3438 | 560.2506 | 0 | 64797.947
2 | 16 | 12 | 24.9217 | 450.1214 | 475.0431 | 46.0589 | 7.8957 | 585.5463 | 288 | 494.8633 | 233.6492 | 241.3939 | 104862.7723 | 25.1708 | 0 | 0 | 233.6492 | 241.3939 | 0 | 104862.7723
2 | 16 | 13 | 19.1395 | 85.0532 | 104.1927 | 41.2033 | 7.4381 | 101.1225 | 101.1225 | 499.7632 | 104.1927 | 0 | 47778.5857 | 0 | 0 | 0 | 104.1927 | 0 | 0 | 47778.5857
2 | 16 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 499.7001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 502.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 16 | 0 | 1.4856 | 1.4856 | 48 | 6.9975 | 1.1968 | 1.1968 | 503.532 | 1.4856 | 0 | 676.7498 | 0 | 0 | 0 | 1.4856 | 0 | 0 | 676.7498
2 | 16 | 17 | 0 | 0.33304 | 0.33304 | 48 | 7.167 | 0.28706 | 0.28706 | 504.9256 | 0.33304 | 0 | 152.1753 | 0 | 0 | 0 | 0.33304 | 0 | 0 | 152.1753
2 | 16 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 515.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 514.6531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 501.6025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 490.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 476.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 16 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 470.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 0 | 7.1233 | 0 | 7.1233 | 11 | 3.5232 | 2.4523 | 2.4523 | 469.6905 | 7.1233 | 0 | 3267.4056 | 0 | 0 | 0 | 7.1233 | 0 | 0 | 3267.4056
2 | 17 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 473.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 479.0498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 483.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 4 | 20.3976 | 0 | 20.3976 | 11 | 2.9469 | 6.4131 | 6.4131 | 500.1852 | 20.3976 | 0 | 9978.1838 | 0 | 0 | 0 | 20.3976 | 0 | 0 | 9978.1838
2 | 17 | 5 | 3.325 | 0 | 3.325 | 11 | 3.091 | 1.0686 | 1.0686 | 505.4313 | 3.325 | 0 | 1643.9841 | 0 | 0 | 0 | 3.325 | 0 | 0 | 1643.9841
2 | 17 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 519.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 521.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 512.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 514.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 501.9984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 483.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 469.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 463.5783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 468.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 469.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 16 | 1.8725 | 0 | 1.8725 | 11 | 7.3195 | 1.7223 | 1.7223 | 483.0804 | 1.8725 | 0 | 883.9509 | 0 | 0 | 0 | 1.8725 | 0 | 0 | 883.9509
2 | 17 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 479.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 467.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 453.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 439.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 417.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 414.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 17 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 423.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 425.5283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 428.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 430.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 440.4051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 454.2876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 463.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 468.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 471.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 462.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 9 | 0 | 0.028333 | 0.028333 | 48 | 7.1924 | 0.02468 | 0.02468 | 462.5989 | 0.028333 | 0 | 11.747 | 0 | 0 | 0 | 0.028333 | 0 | 0 | 11.747
2 | 18 | 10 | 0 | 0.083963 | 0.083963 | 48 | 7.0398 | 0.068764 | 0.068764 | 456.3881 | 0.083963 | 0 | 34.2896 | 0 | 0 | 0 | 0.083963 | 0 | 0 | 34.2896
2 | 18 | 11 | 1.4609 | 0.44175 | 1.9027 | 19.5905 | 7.2093 | 1.6691 | 1.6691 | 441.5178 | 1.9027 | 0 | 802.7816 | 0 | 0 | 0 | 1.9027 | 0 | 0 | 802.7816
2 | 18 | 12 | 10.1685 | 7.9423 | 18.1108 | 27.226 | 7.9296 | 22.7793 | 22.7793 | 437.6436 | 18.1108 | 0 | 7432.9738 | 0 | 0 | 0 | 18.1108 | 0 | 0 | 7432.9738
2 | 18 | 13 | 0 | 0.006625 | 0.006625 | 48 | 8.2601 | 0.010403 | 0.010403 | 438.9388 | 0.006625 | 0 | 2.59 | 0 | 0 | 0 | 0.006625 | 0 | 0 | 2.59
2 | 18 | 14 | 27.9483 | 123.7779 | 151.7263 | 41.1845 | 8.5313 | 299.2599 | 288 | 444.2206 | 146.0175 | 5.7088 | 58850.3068 | 0.59527 | 0 | 0 | 146.0175 | 5.7088 | 0 | 58850.3068
2 | 18 | 15 | 109.5106 | 194.1966 | 303.7072 | 34.6586 | 8.4041 | 534.8273 | 288 | 463.863 | 163.5438 | 140.1635 | 70193.7319 | 14.6152 | 0 | 0 | 163.5438 | 140.1635 | 0 | 70193.7319
2 | 18 | 16 | 6.8133 | 16.7749 | 23.5882 | 37.3127 | 9.1753 | 118.73 | 118.73 | 469.7034 | 23.5882 | 0 | 10199.3308 | 0 | 0 | 0 | 23.5882 | 0 | 0 | 10199.3308
2 | 18 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 463.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 451.1721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 433.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 419.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 400.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 402.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 18 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 401.8365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 403.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 409.7064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 413.7548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 420.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 421.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 431.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 441.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 7 | 5.0608 | 1.9164 | 6.9773 | 21.1628 | 4.8705 | 3.0878 | 3.0878 | 444.3705 | 6.9773 | 0 | 2952.8372 | 0 | 0 | 0 | 6.9773 | 0 | 0 | 2952.8372
2 | 19 | 8 | 53.8472 | 495.7272 | 549.5743 | 44.3747 | 4.8451 | 241.9103 | 241.9103 | 443.7468 | 549.5743 | 0 | 219484.6298 | 0 | 0 | 0 | 549.5743 | 0 | 0 | 219484.6298
2 | 19 | 9 | 22.8392 | 477.938 | 500.7771 | 46.3125 | 6.3789 | 325.711 | 288 | 440.4967 | 442.7969 | 57.9802 | 174543.5494 | 6.0458 | 0 | 0 | 442.7969 | 57.9802 | 0 | 174543.5494
2 | 19 | 10 | 19.7025 | 127.0223 | 146.7248 | 43.0316 | 8.4804 | 276.1374 | 276.1374 | 429.5196 | 146.7248 | 0 | 56707.3859 | 0 | 0 | 0 | 146.7248 | 0 | 0 | 56707.3859
2 | 19 | 11 | 45.0008 | 388.7097 | 433.7106 | 44.161 | 9.4549 | 6694.162 | 288 | 426.3569 | 18.6593 | 415.0512 | 7131.5233 | 43.2785 | 0 | 0 | 18.6593 | 415.0512 | 0 | 7131.5233
2 | 19 | 12 | 69.57 | 261.2074 | 330.7774 | 40.2181 | 9.8362 | 0 | 0 | 425.3405 | 0 | 330.7774 | 0 | 34.491 | 0 | 0 | 0 | 330.7774 | 0 | 0
2 | 19 | 13 | 77.9817 | 124.0296 | 202.0113 | 33.717 | 9.6159 | 0 | 0 | 428.5291 | 0 | 202.0113 | 0 | 21.0642 | 0 | 0 | 0 | 202.0113 | 0 | 0
2 | 19 | 14 | 84.7846 | 464.9831 | 549.7676 | 42.2939 | 9.5227 | 17003.2038 | 288 | 434.6258 | 9.312 | 540.4556 | 3653.3767 | 56.3547 | 0 | 0 | 9.312 | 540.4556 | 0 | 3653.3767
2 | 19 | 15 | 220.5872 | 516.0738 | 736.661 | 36.9206 | 10.7175 | 0 | 0 | 452.918 | 0 | 736.661 | 0 | 76.8136 | 0 | 0 | 0 | 736.661 | 0 | 0
2 | 19 | 16 | 103.9825 | 93.5552 | 197.5377 | 28.5235 | 12.0564 | 0 | 0 | 462.3485 | 0 | 197.5377 | 0 | 20.5978 | 0 | 0 | 0 | 197.5377 | 0 | 0
2 | 19 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 447.8826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 444.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 427.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 414.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 406.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 19 | 22 | 6.2508 | 0 | 6.2508 | 11 | 5.04 | 2.8693 | 2.8693 | 405.3022 | 6.2508 | 0 | 2464.7176 | 0 | 0 | 0 | 6.2508 | 0 | 0 | 2464.7176
2 | 19 | 23 | 106.3638 | 0 | 106.3638 | 11 | 3.3504 | 35.6037 | 35.6037 | 405.3727 | 106.3638 | 0 | 41946.9862 | 0 | 0 | 0 | 106.3638 | 0 | 0 | 41946.9862
2 | 20 | 0 | 51.4709 | 0 | 51.4709 | 11 | 3.252 | 16.9617 | 16.9617 | 394.7153 | 51.4709 | 0 | 19750.1792 | 0 | 0 | 0 | 51.4709 | 0 | 0 | 19750.1792
2 | 20 | 1 | 22.5731 | 0 | 22.5731 | 11 | 3.1418 | 7.3117 | 7.3117 | 399.9161 | 22.5731 | 0 | 8779.0354 | 0 | 0 | 0 | 22.5731 | 0 | 0 | 8779.0354
2 | 20 | 2 | 40.4673 | 0 | 40.4673 | 11 | 3.0401 | 12.9043 | 12.9043 | 410.2187 | 40.4673 | 0 | 16155.3159 | 0 | 0 | 0 | 40.4673 | 0 | 0 | 16155.3159
2 | 20 | 3 | 9.0173 | 0 | 9.0173 | 11 | 3.1249 | 2.9132 | 2.9132 | 428.4295 | 9.0173 | 0 | 3764.1 | 0 | 0 | 0 | 9.0173 | 0 | 0 | 3764.1
2 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 431.5595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 5 | 8.1333 | 0 | 8.1333 | 11 | 3.6164 | 2.8437 | 2.8437 | 439.4606 | 8.1333 | 0 | 3484.8133 | 0 | 0 | 0 | 8.1333 | 0 | 0 | 3484.8133
2 | 20 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 441.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 448.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 8 | 6.8283 | 19.5995 | 26.4279 | 38.4401 | 5.4976 | 13.4876 | 13.4876 | 449.0291 | 26.4279 | 0 | 10850.9937 | 0 | 0 | 0 | 26.4279 | 0 | 0 | 10850.9937
2 | 20 | 9 | 3.71 | 44.8692 | 48.5792 | 45.1743 | 6.4043 | 31.8486 | 31.8486 | 440.4986 | 48.5792 | 0 | 19204.546 | 0 | 0 | 0 | 48.5792 | 0 | 0 | 19204.546
2 | 20 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 431.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 11 | 0 | 0.05075 | 0.05075 | 48 | 9.6413 | 0 | 0 | 433.9086 | 0 | 0.05075 | 0 | 0.0052918 | 0 | 0 | 0 | 0.05075 | 0 | 0
2 | 20 | 12 | 11.2216 | 101.7648 | 112.9864 | 44.3252 | 9.7176 | 0 | 0 | 425.831 | 0 | 112.9864 | 0 | 11.7814 | 0 | 0 | 0 | 112.9864 | 0 | 0
2 | 20 | 13 | 29.1217 | 558.9282 | 588.0499 | 46.1677 | 9.7939 | 0 | 0 | 431.504 | 0 | 588.0499 | 0 | 61.3175 | 0 | 0 | 0 | 588.0499 | 0 | 0
2 | 20 | 14 | 3.524 | 8.4461 | 11.9701 | 37.1071 | 9.4634 | 197.0955 | 197.0955 | 432.1564 | 11.9701 | 0 | 4728.767 | 0 | 0 | 0 | 11.9701 | 0 | 0 | 4728.767
2 | 20 | 15 | 3.225 | 7.7192 | 10.9442 | 37.0969 | 10.5311 | 0 | 0 | 420.4671 | 0 | 10.9442 | 0 | 1.1412 | 0 | 0 | 0 | 10.9442 | 0 | 0
2 | 20 | 16 | 4.9875 | 1.173 | 6.1604 | 18.0449 | 11.0904 | 0 | 0 | 425.3545 | 0 | 6.1604 | 0 | 0.64236 | 0 | 0 | 0 | 6.1604 | 0 | 0
2 | 20 | 17 | 0 | 0.20475 | 0.20475 | 48 | 11.1073 | 0 | 0 | 434.5015 | 0 | 0.20475 | 0 | 0.02135 | 0 | 0 | 0 | 0.20475 | 0 | 0
2 | 20 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 439.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 427.1657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 403.9062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 394.5765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 388.1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 20 | 23 | 0.73033 | 0 | 0.73033 | 11 | 4.3028 | 0.2885 | 0.2885 | 380.3224 | 0.73033 | 0 | 269.726 | 0 | 0 | 0 | 0.73033 | 0 | 0 | 269.726
2 | 21 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 383.4109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 392.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 397.0039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 411.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 430.6497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 447.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 457.6777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 462.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 8 | 0 | 0.16654 | 0.16654 | 48 | 6.2094 | 0.10289 | 0.10289 | 465.3977 | 0.16654 | 0 | 69.5141 | 0 | 0 | 0 | 0.16654 | 0 | 0 | 69.5141
2 | 21 | 9 | 0 | 6.3275 | 6.3275 | 48 | 7.328 | 5.842 | 5.842 | 465.0582 | 6.3275 | 0 | 2638.9183 | 0 | 0 | 0 | 6.3275 | 0 | 0 | 2638.9183
2 | 21 | 10 | 1.6308 | 3.6819 | 5.3127 | 36.6422 | 8.5482 | 10.6491 | 10.6491 | 466.2174 | 5.3127 | 0 | 2282.217 | 0 | 0 | 0 | 5.3127 | 0 | 0 | 2282.217
2 | 21 | 11 | 0 | 0 | 0 | 0 | 9.1838 | 0 | 0 | 466.8801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 460.5249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 467.809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 14 | 20.6142 | 59.2572 | 79.8714 | 38.4506 | 10.2684 | 0 | 0 | 464.9676 | 0 | 79.8714 | 0 | 8.3284 | 0 | 0 | 0 | 79.8714 | 0 | 0
2 | 21 | 15 | 9.7589 | 4.7035 | 14.4624 | 23.0332 | 11.226 | 0 | 0 | 452.5768 | 0 | 14.4624 | 0 | 1.508 | 0 | 0 | 0 | 14.4624 | 0 | 0
2 | 21 | 16 | 0 | 0.66542 | 0.66542 | 48 | 11.853 | 0 | 0 | 455.2448 | 0 | 0.66542 | 0 | 0.069385 | 0 | 0 | 0 | 0.66542 | 0 | 0
2 | 21 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 469.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 467.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 451.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 431.2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 414.5904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 399.6771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 21 | 23 | 12.2003 | 0 | 12.2003 | 11 | 4.2398 | 4.7628 | 4.7628 | 399.504 | 12.2003 | 0 | 4739.8492 | 0 | 0 | 0 | 12.2003 | 0 | 0 | 4739.8492
2 | 22 | 0 | 16.9219 | 0 | 16.9219 | 11 | 3.5147 | 5.8175 | 5.8175 | 397.0246 | 16.9219 | 0 | 6532.2539 | 0 | 0 | 0 | 16.9219 | 0 | 0 | 6532.2539
2 | 22 | 1 | 12.7054 | 0 | 12.7054 | 11 | 3.2859 | 4.2094 | 4.2094 | 404.4555 | 12.7054 | 0 | 4999.0045 | 0 | 0 | 0 | 12.7054 | 0 | 0 | 4999.0045
2 | 22 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 411.8183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 426.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 454.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 456.1678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 465.9963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 7 | 0 | 0.385 | 0.385 | 48 | 5.0146 | 0.17575 | 0.17575 | 471.5591 | 0.385 | 0 | 163.0703 | 0 | 0 | 0 | 0.385 | 0 | 0 | 163.0703
2 | 22 | 8 | 96.6927 | 422.4338 | 519.1265 | 41.1084 | 6.2094 | 320.7197 | 288 | 467.6544 | 466.1654 | 52.9612 | 198840.9654 | 5.5224 | 0 | 0 | 466.1654 | 52.9612 | 0 | 198840.9654
2 | 22 | 9 | 315.3435 | 913.4066 | 1228.7501 | 38.5044 | 7.311 | 1126.0369 | 288 | 464.4794 | 314.2704 | 914.4798 | 133871.3307 | 95.3552 | 0 | 0 | 314.2704 | 914.4798 | 0 | 133871.3307
2 | 22 | 10 | 93.179 | 895.5356 | 988.7145 | 44.513 | 8.0567 | 1346.6585 | 288 | 462.1611 | 211.4491 | 777.2654 | 88311.3167 | 81.0475 | 0 | 0 | 211.4491 | 777.2654 | 0 | 88311.3167
2 | 22 | 11 | 74.4667 | 360.7681 | 435.2347 | 41.6695 | 9.3109 | 3253.8778 | 288 | 456.5457 | 38.5225 | 396.7122 | 15982.0822 | 41.3662 | 0 | 0 | 38.5225 | 396.7122 | 0 | 15982.0822
2 | 22 | 12 | 39.8841 | 71.5284 | 111.4126 | 34.7545 | 9.0058 | 398.1698 | 288 | 449.2508 | 80.5858 | 30.8268 | 33402.4957 | 3.2144 | 0 | 0 | 80.5858 | 30.8268 | 0 | 33402.4957
2 | 22 | 13 | 10.3729 | 26.418 | 36.7909 | 37.5682 | 8.4889 | 69.7736 | 69.7736 | 442.6854 | 36.7909 | 0 | 14904.6423 | 0 | 0 | 0 | 36.7909 | 0 | 0 | 14904.6423
2 | 22 | 14 | 53.8543 | 52.4801 | 106.3344 | 29.2609 | 8.938 | 340.5229 | 288 | 439.522 | 89.9331 | 16.4012 | 36896.0675 | 1.7102 | 0 | 0 | 89.9331 | 16.4012 | 0 | 36896.0675
2 | 22 | 15 | 7.1008 | 14.5913 | 21.6921 | 35.8882 | 9.6075 | 0 | 0 | 428.5619 | 0 | 21.6921 | 0 | 2.2619 | 0 | 0 | 0 | 21.6921 | 0 | 0
2 | 22 | 16 | 37.3658 | 14.9979 | 52.3637 | 21.5975 | 10.9718 | 0 | 0 | 442.4838 | 0 | 52.3637 | 0 | 5.4601 | 0 | 0 | 0 | 52.3637 | 0 | 0
2 | 22 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 442.1634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 436.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 415.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 394.2534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 373.4743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 372.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 22 | 23 | 118.1536 | 0 | 118.1536 | 11 | 4.2265 | 46.0105 | 46.0105 | 366.0414 | 118.1536 | 0 | 41949.4312 | 0 | 0 | 0 | 118.1536 | 0 | 0 | 41949.4312
2 | 23 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 367.8416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 380.9853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 396.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 425.3772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 453.3702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 456.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 6 | 0 | 0.18167 | 0.18167 | 48 | 4.396 | 0.073051 | 0.073051 | 466.5361 | 0.18167 | 0 | 76.0341 | 0 | 0 | 0 | 0.18167 | 0 | 0 | 76.0341
2 | 23 | 7 | 35.6568 | 321.4079 | 357.0647 | 44.3051 | 4.6502 | 150.9709 | 150.9709 | 464.6443 | 357.0647 | 0 | 150088.2865 | 0 | 0 | 0 | 357.0647 | 0 | 0 | 150088.2865
2 | 23 | 8 | 219.8513 | 969.6229 | 1189.4742 | 41.1613 | 5.1417 | 558.4871 | 288 | 464.7047 | 613.3867 | 576.0875 | 259795.8884 | 60.0702 | 0 | 0 | 613.3867 | 576.0875 | 0 | 259795.8884
2 | 23 | 9 | 475.7855 | 1592.7866 | 2068.5721 | 39.4898 | 6.6161 | 1452.7585 | 288 | 460.0489 | 410.0811 | 1658.491 | 172463.3312 | 172.9352 | 0 | 0 | 410.0811 | 1658.491 | 0 | 172463.3312
2 | 23 | 10 | 265.6321 | 1222.5333 | 1488.1654 | 41.3956 | 6.9721 | 1187.2105 | 288 | 466.1619 | 361.0073 | 1127.1581 | 153343.7086 | 117.5317 | 0 | 0 | 361.0073 | 1127.1581 | 0 | 153343.7086
2 | 23 | 11 | 100.2305 | 1151.4032 | 1251.6337 | 45.037 | 8.5652 | 2550.3108 | 288 | 465.2649 | 141.3438 | 1110.29 | 59396.5831 | 115.7728 | 0 | 0 | 141.3438 | 1110.29 | 0 | 59396.5831
2 | 23 | 12 | 56.0384 | 1063.9259 | 1119.9643 | 46.1487 | 7.8957 | 1380.4873 | 288 | 454.51 | 233.6492 | 886.3151 | 95413.2873 | 92.4184 | 0 | 0 | 233.6492 | 886.3151 | 0 | 95413.2873
2 | 23 | 13 | 91.7751 | 1059.0927 | 1150.8678 | 45.0495 | 7.4381 | 1116.9556 | 288 | 452.8223 | 296.744 | 854.1237 | 121004.1612 | 89.0617 | 0 | 0 | 296.744 | 854.1237 | 0 | 121004.1612
2 | 23 | 14 | 225.7175 | 1138.4582 | 1364.1757 | 41.878 | 7.2771 | 1231.8229 | 288 | 451.9639 | 318.9441 | 1045.2316 | 130794.4613 | 108.989 | 0 | 0 | 318.9441 | 1045.2316 | 0 | 130794.4613
2 | 23 | 15 | 196.9591 | 967.1215 | 1164.0805 | 41.7397 | 7.3449 | 1082.8772 | 288 | 442.081 | 309.5967 | 854.4839 | 123944.3342 | 89.0993 | 0 | 0 | 309.5967 | 854.4839 | 0 | 123944.3342
2 | 23 | 16 | 16.5633 | 139.0379 | 155.6013 | 44.0615 | 6.9975 | 125.3508 | 125.3508 | 456.087 | 155.6013 | 0 | 64111.7016 | 0 | 0 | 0 | 155.6013 | 0 | 0 | 64111.7016
2 | 23 | 17 | 0 | 0.57263 | 0.57263 | 48 | 7.167 | 0.49356 | 0.49356 | 456.7749 | 0.57263 | 0 | 234.0747 | 0 | 0 | 0 | 0.57263 | 0 | 0 | 234.0747
2 | 23 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 458.3204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 437.8027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 403.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 379.6831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 359.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 23 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 354.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 353.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 350.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 361.9545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 393.5334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 421.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 423.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 435.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 7 | 0.23574 | 44.0255 | 44.2613 | 47.8029 | 6.1924 | 27.2085 | 27.2085 | 440.9345 | 44.2613 | 0 | 17400.5002 | 0 | 0 | 0 | 44.2613 | 0 | 0 | 17400.5002
2 | 24 | 8 | 1.5333 | 86.8795 | 88.4129 | 47.3583 | 6.8788 | 68.1081 | 68.1081 | 446.7591 | 88.4129 | 0 | 35312.1683 | 0 | 0 | 0 | 88.4129 | 0 | 0 | 35312.1683
2 | 24 | 9 | 1.275 | 73.8818 | 75.1568 | 47.3723 | 7.3195 | 69.1313 | 69.1313 | 446.6863 | 75.1568 | 0 | 30011.1468 | 0 | 0 | 0 | 75.1568 | 0 | 0 | 30011.1468
2 | 24 | 10 | 0.5975 | 82.7975 | 83.395 | 47.7349 | 7.4805 | 82.5631 | 82.5631 | 446.6097 | 83.395 | 0 | 33264.1661 | 0 | 0 | 0 | 83.395 | 0 | 0 | 33264.1661
2 | 24 | 11 | 1.8408 | 145.3451 | 147.1859 | 47.5372 | 7.2263 | 130.0474 | 130.0474 | 444.5167 | 147.1859 | 0 | 58429.783 | 0 | 0 | 0 | 147.1859 | 0 | 0 | 58429.783
2 | 24 | 12 | 2.6208 | 273.4734 | 276.0942 | 47.6488 | 7.8703 | 335.2884 | 288 | 437.2267 | 237.1544 | 38.9397 | 92390.1328 | 4.0603 | 0 | 0 | 237.1544 | 38.9397 | 0 | 92390.1328
2 | 24 | 13 | 1.77 | 266.6833 | 268.4533 | 47.756 | 8.1754 | 396.2995 | 288 | 436.6795 | 195.0912 | 73.3621 | 75875.5427 | 7.6497 | 0 | 0 | 195.0912 | 73.3621 | 0 | 75875.5427
2 | 24 | 14 | 3.6133 | 761.8198 | 765.4331 | 47.8253 | 8.2431 | 1186.8213 | 288 | 428.2451 | 185.7438 | 579.6893 | 70660.6197 | 60.4457 | 0 | 0 | 185.7438 | 579.6893 | 0 | 70660.6197
2 | 24 | 15 | 3.4492 | 639.1491 | 642.5983 | 47.8014 | 7.4212 | 618.7902 | 288 | 417.2225 | 299.0809 | 343.5174 | 110486.769 | 35.8195 | 0 | 0 | 299.0809 | 343.5174 | 0 | 110486.769
2 | 24 | 16 | 21.3641 | 291.3095 | 312.6737 | 45.4719 | 7.3195 | 287.6061 | 287.6061 | 431.4862 | 312.6737 | 0 | 120696.5051 | 0 | 0 | 0 | 312.6737 | 0 | 0 | 120696.5051
2 | 24 | 17 | 0 | 0.85663 | 0.85663 | 48 | 7.2686 | 0.77069 | 0.77069 | 421.8585 | 0.85663 | 0 | 320.2565 | 0 | 0 | 0 | 0.85663 | 0 | 0 | 320.2565
2 | 24 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 425.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 413.1488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 402.6502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 383.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 381.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 24 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 372.7326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 368.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 363.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 363.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 362.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 370.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 388.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 408.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 7 | 0.54167 | 54.1155 | 54.6571 | 47.6333 | 6.006 | 31.8515 | 31.8515 | 425.8144 | 54.6571 | 0 | 20670.2939 | 0 | 0 | 0 | 54.6571 | 0 | 0 | 20670.2939
2 | 25 | 8 | 0.3425 | 73.9548 | 74.2973 | 47.8294 | 6.6246 | 52.3281 | 52.3281 | 430.7176 | 74.2973 | 0 | 28447.5737 | 0 | 0 | 0 | 74.2973 | 0 | 0 | 28447.5737
2 | 25 | 9 | 0.74417 | 38.491 | 39.2352 | 47.2982 | 7.1924 | 34.1766 | 34.1766 | 424.1287 | 39.2352 | 0 | 14785.0231 | 0 | 0 | 0 | 39.2352 | 0 | 0 | 14785.0231
2 | 25 | 10 | 3.115 | 141.7919 | 144.9069 | 47.2046 | 7.0398 | 118.6749 | 118.6749 | 419.5655 | 144.9069 | 0 | 53957.6735 | 0 | 0 | 0 | 144.9069 | 0 | 0 | 53957.6735
2 | 25 | 11 | 2.5833 | 83.1527 | 85.7361 | 46.8851 | 7.2093 | 75.2136 | 75.2136 | 415.033 | 85.7361 | 0 | 31563.5438 | 0 | 0 | 0 | 85.7361 | 0 | 0 | 31563.5438
2 | 25 | 12 | 0 | 12.5382 | 12.5382 | 48 | 7.9296 | 15.7702 | 15.7702 | 411.7014 | 12.5382 | 0 | 4560.1487 | 0 | 0 | 0 | 12.5382 | 0 | 0 | 4560.1487
2 | 25 | 13 | 0 | 4.9208 | 4.9208 | 48 | 8.2601 | 7.727 | 7.727 | 406.7399 | 4.9208 | 0 | 1765.2845 | 0 | 0 | 0 | 4.9208 | 0 | 0 | 1765.2845
2 | 25 | 14 | 0 | 3.7578 | 3.7578 | 48 | 8.5313 | 7.4117 | 7.4117 | 414.6614 | 3.7578 | 0 | 1377.8217 | 0 | 0 | 0 | 3.7578 | 0 | 0 | 1377.8217
2 | 25 | 15 | 3.8992 | 7.2705 | 11.1696 | 35.0838 | 8.4041 | 19.6697 | 19.6697 | 426.1397 | 11.1696 | 0 | 4367.9557 | 0 | 0 | 0 | 11.1696 | 0 | 0 | 4367.9557
2 | 25 | 16 | 0 | 4.1689 | 4.1689 | 48 | 9.1753 | 20.984 | 20.984 | 447.8173 | 4.1689 | 0 | 1666.8049 | 0 | 0 | 0 | 4.1689 | 0 | 0 | 1666.8049
2 | 25 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 455.4795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 452.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 444.4847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 428.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 415.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 410.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 25 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 412.5441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 418.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 419.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 418.5626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 420.8131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 424.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 428.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 6 | 0 | 0.027042 | 0.027042 | 48 | 4.1926 | 0.010464 | 0.010464 | 419.4311 | 0.027042 | 0 | 10.0441 | 0 | 0 | 0 | 0.027042 | 0 | 0 | 10.0441
2 | 26 | 7 | 0 | 0.44833 | 0.44833 | 48 | 4.8705 | 0.19841 | 0.19841 | 406.0341 | 0.44833 | 0 | 160.5186 | 0 | 0 | 0 | 0.44833 | 0 | 0 | 160.5186
2 | 26 | 8 | 23.21 | 126.1318 | 149.3418 | 42.2496 | 4.8451 | 65.7369 | 65.7369 | 404.7002 | 149.3418 | 0 | 54129.014 | 0 | 0 | 0 | 149.3418 | 0 | 0 | 54129.014
2 | 26 | 9 | 28.5767 | 265.642 | 294.2186 | 44.4063 | 6.3789 | 191.363 | 191.363 | 401.2964 | 294.2186 | 0 | 105003.7204 | 0 | 0 | 0 | 294.2186 | 0 | 0 | 105003.7204
2 | 26 | 10 | 23.65 | 495.46 | 519.11 | 46.3143 | 8.4804 | 976.9695 | 288 | 392.819 | 153.028 | 366.082 | 53024.9107 | 38.1723 | 0 | 0 | 153.028 | 366.082 | 0 | 53024.9107
2 | 26 | 11 | 31.54 | 409.499 | 441.039 | 45.354 | 9.4549 | 6807.2743 | 288 | 385.8709 | 18.6593 | 422.3797 | 6353.8203 | 44.0426 | 0 | 0 | 18.6593 | 422.3797 | 0 | 6353.8203
2 | 26 | 12 | 26.5832 | 200.8081 | 227.3914 | 43.6745 | 9.8362 | 0 | 0 | 384.5652 | 0 | 227.3914 | 0 | 23.7107 | 0 | 0 | 0 | 227.3914 | 0 | 0
2 | 26 | 13 | 5.9692 | 59.8644 | 65.8336 | 44.6452 | 9.6159 | 0 | 0 | 386.582 | 0 | 65.8336 | 0 | 6.8646 | 0 | 0 | 0 | 65.8336 | 0 | 0
2 | 26 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 398.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 15 | 14.9065 | 6.8393 | 21.7458 | 22.6369 | 10.7175 | 0 | 0 | 406.2851 | 0 | 21.7458 | 0 | 2.2675 | 0 | 0 | 0 | 21.7458 | 0 | 0
2 | 26 | 16 | 27.67 | 35.1392 | 62.8092 | 31.7 | 12.0564 | 0 | 0 | 434.2102 | 0 | 62.8092 | 0 | 6.5493 | 0 | 0 | 0 | 62.8092 | 0 | 0
2 | 26 | 17 | 0 | 0.19375 | 0.19375 | 48 | 11.8107 | 0 | 0 | 452.2876 | 0 | 0.19375 | 0 | 0.020203 | 0 | 0 | 0 | 0.19375 | 0 | 0
2 | 26 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 459.2433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 445.8406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 433.3611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 424.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 420.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 26 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 418.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 424.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 1 | 35.2525 | 0 | 35.2525 | 11 | 3.1418 | 11.4187 | 11.4187 | 442.1531 | 35.2525 | 0 | 15199.2245 | 0 | 0 | 0 | 35.2525 | 0 | 0 | 15199.2245
2 | 27 | 2 | 24.2262 | 0 | 24.2262 | 11 | 3.0401 | 7.7253 | 7.7253 | 455.1242 | 24.2262 | 0 | 10759.4471 | 0 | 0 | 0 | 24.2262 | 0 | 0 | 10759.4471
2 | 27 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 463.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 473.663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 475.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 486.5563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 491.2218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 488.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 483.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 490.3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 485.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 483.1412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 488.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 14 | 0 | 0.18654 | 0.18654 | 48 | 9.4634 | 3.0715 | 3.0715 | 485.5798 | 0.18654 | 0 | 81.6269 | 0 | 0 | 0 | 0.18654 | 0 | 0 | 81.6269
2 | 27 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 482.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 16 | 0 | 1.497 | 1.497 | 48 | 11.0904 | 0 | 0 | 481.1205 | 0 | 1.497 | 0 | 0.1561 | 0 | 0 | 0 | 1.497 | 0 | 0
2 | 27 | 17 | 0 | 0.39475 | 0.39475 | 48 | 11.1073 | 0 | 0 | 483.3039 | 0 | 0.39475 | 0 | 0.041162 | 0 | 0 | 0 | 0.39475 | 0 | 0
2 | 27 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 473.7363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 450.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 427.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 416.4574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 409.7456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 27 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 411.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 417.7337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 416.6581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 436.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 460.9195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 481.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 474.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 469.7816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 7 | 12.4242 | 18.5151 | 30.9393 | 33.1421 | 5.2518 | 14.8956 | 14.8956 | 468.9322 | 30.9393 | 0 | 13483.038 | 0 | 0 | 0 | 30.9393 | 0 | 0 | 13483.038
2 | 28 | 8 | 144.6323 | 724.9173 | 869.5496 | 41.8458 | 6.2094 | 537.2134 | 288 | 470.8932 | 466.1654 | 403.3843 | 200007.028 | 42.0619 | 0 | 0 | 466.1654 | 403.3843 | 0 | 200007.028
2 | 28 | 9 | 171.3322 | 1021.361 | 1192.6932 | 42.6849 | 7.328 | 1101.1822 | 288 | 471.0493 | 311.9335 | 880.7597 | 133621.2142 | 91.8391 | 0 | 0 | 311.9335 | 880.7597 | 0 | 133621.2142
2 | 28 | 10 | 153.7596 | 1093.2138 | 1246.9734 | 43.4377 | 8.5482 | 2499.4908 | 288 | 471.8803 | 143.6806 | 1103.2928 | 61558.8908 | 115.0432 | 0 | 0 | 143.6806 | 1103.2928 | 0 | 61558.8908
2 | 28 | 11 | 76.6872 | 848.1625 | 924.8497 | 44.932 | 9.1838 | 4752.2223 | 288 | 475.0029 | 56.0489 | 868.8008 | 24104.987 | 90.5921 | 0 | 0 | 56.0489 | 868.8008 | 0 | 24104.987
2 | 28 | 12 | 27.8925 | 393.2512 | 421.1437 | 45.5495 | 9.8701 | 0 | 0 | 477.0582 | 0 | 421.1437 | 0 | 43.9138 | 0 | 0 | 0 | 421.1437 | 0 | 0
2 | 28 | 13 | 23.0375 | 489.6501 | 512.6876 | 46.3374 | 9.6668 | 0 | 0 | 473.2222 | 0 | 512.6876 | 0 | 53.4593 | 0 | 0 | 0 | 512.6876 | 0 | 0
2 | 28 | 14 | 76.6346 | 1244.4283 | 1321.063 | 45.8536 | 10.2684 | 0 | 0 | 470.067 | 0 | 1321.063 | 0 | 137.7507 | 0 | 0 | 0 | 1321.063 | 0 | 0
2 | 28 | 15 | 58.844 | 1064.0873 | 1122.9313 | 46.0611 | 11.226 | 0 | 0 | 475.4632 | 0 | 1122.9313 | 0 | 117.091 | 0 | 0 | 0 | 1122.9313 | 0 | 0
2 | 28 | 16 | 54.6352 | 437.8578 | 492.493 | 43.8954 | 11.853 | 0 | 0 | 476.8956 | 0 | 492.493 | 0 | 51.3535 | 0 | 0 | 0 | 492.493 | 0 | 0
2 | 28 | 17 | 0 | 0.69771 | 0.69771 | 48 | 11.7514 | 0 | 0 | 475.7551 | 0 | 0.69771 | 0 | 0.072752 | 0 | 0 | 0 | 0.69771 | 0 | 0
2 | 28 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 469.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 444.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 417.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 403.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 399.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 28 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 395.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 0 | 0.6175 | 0 | 0.6175 | 11 | 3.5147 | 0.21229 | 0.21229 | 394.0661 | 0.6175 | 0 | 236.5433 | 0 | 0 | 0 | 0.6175 | 0 | 0 | 236.5433
3 | 1 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 402.803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 417.9677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 433.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 457.6563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 459.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 459.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 7 | 7.48 | 286.5596 | 294.0396 | 47.0588 | 5.0146 | 134.2236 | 134.2236 | 462.1589 | 294.0396 | 0 | 122055.8603 | 0 | 0 | 0 | 294.0396 | 0 | 0 | 122055.8603
3 | 1 | 8 | 10.7117 | 647.7372 | 658.4488 | 47.3981 | 6.2094 | 406.794 | 288 | 459.7313 | 466.1654 | 192.2835 | 192215.4838 | 20.0499 | 0 | 0 | 466.1654 | 192.2835 | 0 | 192215.4838
3 | 1 | 9 | 11.0366 | 538.685 | 549.7216 | 47.2572 | 7.311 | 503.7695 | 288 | 456.8355 | 314.2704 | 235.4512 | 128718.331 | 24.5511 | 0 | 0 | 314.2704 | 235.4512 | 0 | 128718.331
3 | 1 | 10 | 15.7258 | 488.2838 | 504.0097 | 46.8455 | 8.0567 | 686.4761 | 288 | 460.6821 | 211.4491 | 292.5605 | 87505.3823 | 30.5061 | 0 | 0 | 211.4491 | 292.5605 | 0 | 87505.3823
3 | 1 | 11 | 22.8042 | 346.1343 | 368.9385 | 45.713 | 9.3109 | 2758.2375 | 288 | 449.7964 | 38.5225 | 330.416 | 15566.3146 | 34.4533 | 0 | 0 | 38.5225 | 330.416 | 0 | 15566.3146
3 | 1 | 12 | 17.36 | 395.4994 | 412.8594 | 46.4442 | 9.0058 | 1475.4901 | 288 | 450.9075 | 80.5858 | 332.2736 | 32593.9822 | 34.647 | 0 | 0 | 80.5858 | 332.2736 | 0 | 32593.9822
3 | 1 | 13 | 11.5933 | 176.6864 | 188.2797 | 45.7217 | 8.4889 | 357.0704 | 288 | 452.9109 | 151.8596 | 36.4202 | 61835.5689 | 3.7976 | 0 | 0 | 151.8596 | 36.4202 | 0 | 61835.5689
3 | 1 | 14 | 8.735 | 114.5818 | 123.3168 | 45.3791 | 8.938 | 394.9071 | 288 | 458.065 | 89.9331 | 33.3837 | 37114.1387 | 3.481 | 0 | 0 | 89.9331 | 33.3837 | 0 | 37114.1387
3 | 1 | 15 | 9.8667 | 320.0006 | 329.8673 | 46.8933 | 9.6075 | 0 | 0 | 461.4231 | 0 | 329.8673 | 0 | 34.3961 | 0 | 0 | 0 | 329.8673 | 0 | 0
3 | 1 | 16 | 11.9258 | 373.6601 | 385.586 | 46.8556 | 10.9718 | 0 | 0 | 464.0975 | 0 | 385.586 | 0 | 40.2061 | 0 | 0 | 0 | 385.586 | 0 | 0
3 | 1 | 17 | 0 | 0.74683 | 0.74683 | 48 | 10.3786 | 0 | 0 | 464.6319 | 0 | 0.74683 | 0 | 0.077874 | 0 | 0 | 0 | 0.74683 | 0 | 0
3 | 1 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 462.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 443.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 422.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 416.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 413.3401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 421.4814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 422.211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 418.2588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 431.0532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 463.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 483.1652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 474.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 478.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 7 | 10.6008 | 152.6818 | 163.2826 | 45.5978 | 4.6502 | 69.0377 | 69.0377 | 485.3153 | 163.2826 | 0 | 71798.2139 | 0 | 0 | 0 | 163.2826 | 0 | 0 | 71798.2139
3 | 2 | 8 | 27.8733 | 706.6232 | 734.4966 | 46.5959 | 5.1417 | 344.8641 | 288 | 485.8031 | 613.3867 | 121.1099 | 269403.842 | 12.6284 | 0 | 0 | 613.3867 | 121.1099 | 0 | 269403.842
3 | 2 | 9 | 21.3225 | 277.4789 | 298.8014 | 45.3597 | 6.6161 | 209.8483 | 209.8483 | 483.5502 | 298.8014 | 0 | 130931.9489 | 0 | 0 | 0 | 298.8014 | 0 | 0 | 130931.9489
3 | 2 | 10 | 17.4667 | 189.9562 | 207.4228 | 44.8843 | 6.9721 | 165.4753 | 165.4753 | 484.1799 | 207.4228 | 0 | 91119.9455 | 0 | 0 | 0 | 207.4228 | 0 | 0 | 91119.9455
3 | 2 | 11 | 16.4383 | 269.3157 | 285.7541 | 45.8715 | 8.5652 | 582.2483 | 288 | 472.732 | 141.3438 | 144.4103 | 60334.0681 | 15.058 | 0 | 0 | 141.3438 | 144.4103 | 0 | 60334.0681
3 | 2 | 12 | 0 | 14.4976 | 14.4976 | 48 | 7.8957 | 17.87 | 17.87 | 463.3814 | 14.4976 | 0 | 6022.0437 | 0 | 0 | 0 | 14.4976 | 0 | 0 | 6022.0437
3 | 2 | 13 | 0 | 3.1759 | 3.1759 | 48 | 7.4381 | 3.0823 | 3.0823 | 465.9533 | 3.1759 | 0 | 1327.3827 | 0 | 0 | 0 | 3.1759 | 0 | 0 | 1327.3827
3 | 2 | 14 | 0 | 5.6708 | 5.6708 | 48 | 7.2771 | 5.1206 | 5.1206 | 475.7999 | 5.6708 | 0 | 2425.9821 | 0 | 0 | 0 | 5.6708 | 0 | 0 | 2425.9821
3 | 2 | 15 | 0 | 5.4732 | 5.4732 | 48 | 7.3449 | 5.0914 | 5.0914 | 456.9444 | 5.4732 | 0 | 2238.2378 | 0 | 0 | 0 | 5.4732 | 0 | 0 | 2238.2378
3 | 2 | 16 | 1.015 | 5.2164 | 6.2314 | 41.9733 | 6.9975 | 5.02 | 5.02 | 474.6064 | 6.2314 | 0 | 2695.917 | 0 | 0 | 0 | 6.2314 | 0 | 0 | 2695.917
3 | 2 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 489.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 502.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 495.1955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 477.3454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 462.3927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 457.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 456.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 456.6902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 458.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 473.6315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 471.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 478.5961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 485.4794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 491.3626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 7 | 0.67 | 5.905 | 6.575 | 44.2297 | 6.1924 | 4.0418 | 4.0418 | 497.54 | 6.575 | 0 | 2980.5272 | 0 | 0 | 0 | 6.575 | 0 | 0 | 2980.5272
3 | 3 | 8 | 4.5467 | 114.9382 | 119.4849 | 46.5921 | 6.8788 | 92.0442 | 92.0442 | 500.8339 | 119.4849 | 0 | 54275.0261 | 0 | 0 | 0 | 119.4849 | 0 | 0 | 54275.0261
3 | 3 | 9 | 0 | 3.6553 | 3.6553 | 48 | 7.3195 | 3.3622 | 3.3622 | 503.7168 | 3.6553 | 0 | 1665.7587 | 0 | 0 | 0 | 3.6553 | 0 | 0 | 1665.7587
3 | 3 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 498.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 11 | 0 | 1.235 | 1.235 | 48 | 7.2263 | 1.0912 | 1.0912 | 497.9218 | 1.235 | 0 | 555.6351 | 0 | 0 | 0 | 1.235 | 0 | 0 | 555.6351
3 | 3 | 12 | 0 | 2.77 | 2.77 | 48 | 7.8703 | 3.3638 | 3.3638 | 495.111 | 2.77 | 0 | 1238.4788 | 0 | 0 | 0 | 2.77 | 0 | 0 | 1238.4788
3 | 3 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 496.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 486.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 15 | 0 | 7.4672 | 7.4672 | 48 | 7.4212 | 7.1906 | 7.1906 | 487.133 | 7.4672 | 0 | 3279.0976 | 0 | 0 | 0 | 7.4672 | 0 | 0 | 3279.0976
3 | 3 | 16 | 0 | 1.5897 | 1.5897 | 48 | 7.3195 | 1.4622 | 1.4622 | 492.0592 | 1.5897 | 0 | 705.9061 | 0 | 0 | 0 | 1.5897 | 0 | 0 | 705.9061
3 | 3 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 502.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 512.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 512.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 507.2553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 504.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 503.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 494.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 492.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 488.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 492.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 3 | 5.3467 | 0 | 5.3467 | 11 | 3.3622 | 1.7931 | 1.7931 | 491.8157 | 5.3467 | 0 | 2570.7614 | 0 | 0 | 0 | 5.3467 | 0 | 0 | 2570.7614
3 | 4 | 4 | 1.1308 | 0 | 1.1308 | 11 | 3.3622 | 0.37925 | 0.37925 | 478.2167 | 1.1308 | 0 | 528.3442 | 0 | 0 | 0 | 1.1308 | 0 | 0 | 528.3442
3 | 4 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 473.2556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 481.4891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 7 | 0 | 0.62833 | 0.62833 | 48 | 6.006 | 0.36616 | 0.36616 | 485.8157 | 0.62833 | 0 | 275.0942 | 0 | 0 | 0 | 0.62833 | 0 | 0 | 275.0942
3 | 4 | 8 | 9.1667 | 122.3638 | 131.5304 | 45.4214 | 6.6246 | 92.6378 | 92.6378 | 485.6597 | 131.5304 | 0 | 57904.7423 | 0 | 0 | 0 | 131.5304 | 0 | 0 | 57904.7423
3 | 4 | 9 | 5.0792 | 437.2431 | 442.3222 | 47.5751 | 7.1924 | 385.2931 | 288 | 485.0143 | 330.6283 | 111.6939 | 144629.7506 | 11.6466 | 0 | 0 | 330.6283 | 111.6939 | 0 | 144629.7506
3 | 4 | 10 | 14.0367 | 377.1443 | 391.181 | 46.6723 | 7.0398 | 320.3667 | 288 | 479.3036 | 351.6599 | 39.5211 | 152139.054 | 4.121 | 0 | 0 | 351.6599 | 39.5211 | 0 | 152139.054
3 | 4 | 11 | 21.0483 | 386.0617 | 407.1101 | 46.087 | 7.2093 | 357.1452 | 288 | 480.2529 | 328.2914 | 78.8186 | 142532.9398 | 8.2186 | 0 | 0 | 328.2914 | 78.8186 | 0 | 142532.9398
3 | 4 | 12 | 22.8743 | 284.3151 | 307.1894 | 45.2449 | 7.9296 | 386.3757 | 288 | 477.9552 | 228.9755 | 78.2139 | 99080.0588 | 8.1556 | 0 | 0 | 228.9755 | 78.2139 | 0 | 99080.0588
3 | 4 | 13 | 6.6742 | 26.0517 | 32.7259 | 40.4542 | 8.2601 | 51.3888 | 51.3888 | 479.7329 | 32.7259 | 0 | 14375.791 | 0 | 0 | 0 | 32.7259 | 0 | 0 | 14375.791
3 | 4 | 14 | 0 | 1.3833 | 1.3833 | 48 | 8.5313 | 2.7284 | 2.7284 | 482.6726 | 1.3833 | 0 | 601.2789 | 0 | 0 | 0 | 1.3833 | 0 | 0 | 601.2789
3 | 4 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 483.6284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 16 | 0 | 1.7481 | 1.7481 | 48 | 9.1753 | 8.7989 | 8.7989 | 493.1472 | 1.7481 | 0 | 778.1544 | 0 | 0 | 0 | 1.7481 | 0 | 0 | 778.1544
3 | 4 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 501.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 503.7921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 504.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 502.9683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 499.2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 496.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 493.5193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 494.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 498.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 502.6951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 496.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 496.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 500.5572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 503.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 505.3302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 495.4737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 9 | 55.9 | 87.3007 | 143.2007 | 33.5566 | 6.3789 | 93.1393 | 93.1393 | 488.3556 | 143.2007 | 0 | 65127.5121 | 0 | 0 | 0 | 143.2007 | 0 | 0 | 65127.5121
3 | 5 | 10 | 81.6673 | 127.5666 | 209.2339 | 33.5583 | 8.4804 | 393.78 | 288 | 487.2765 | 153.028 | 56.2059 | 69431.5883 | 5.8607 | 0 | 0 | 153.028 | 56.2059 | 0 | 69431.5883
3 | 5 | 11 | 101.9263 | 112.5733 | 214.4996 | 30.4183 | 9.4549 | 3310.7226 | 288 | 477.5585 | 18.6593 | 195.8403 | 8343.342 | 20.4208 | 0 | 0 | 18.6593 | 195.8403 | 0 | 8343.342
3 | 5 | 12 | 116.648 | 159.6014 | 276.2493 | 32.3765 | 9.8362 | 0 | 0 | 468.8009 | 0 | 276.2493 | 0 | 28.8052 | 0 | 0 | 0 | 276.2493 | 0 | 0
3 | 5 | 13 | 322.8771 | 793.1055 | 1115.9826 | 37.2951 | 9.6159 | 0 | 0 | 468.2917 | 0 | 1115.9826 | 0 | 116.3664 | 0 | 0 | 0 | 1115.9826 | 0 | 0
3 | 5 | 14 | 85.8075 | 487.6136 | 573.4211 | 42.4633 | 9.5227 | 17734.7587 | 288 | 480.5959 | 9.312 | 564.1091 | 4079.8717 | 58.8211 | 0 | 0 | 9.312 | 564.1091 | 0 | 4079.8717
3 | 5 | 15 | 108.7841 | 697.8953 | 806.6794 | 43.0104 | 10.7175 | 0 | 0 | 481.1913 | 0 | 806.6794 | 0 | 84.1146 | 0 | 0 | 0 | 806.6794 | 0 | 0
3 | 5 | 16 | 138.2065 | 311.2693 | 449.4758 | 36.6231 | 12.0564 | 0 | 0 | 485.9988 | 0 | 449.4758 | 0 | 46.868 | 0 | 0 | 0 | 449.4758 | 0 | 0
3 | 5 | 17 | 0 | 0.83263 | 0.83263 | 48 | 11.8107 | 0 | 0 | 496.9557 | 0 | 0.83263 | 0 | 0.08682 | 0 | 0 | 0 | 0.83263 | 0 | 0
3 | 5 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 500.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 489.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 476.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 470.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 465.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 5 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 459.6693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 463.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 466.8054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 473.7639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 474.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 488.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 493.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 490.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 7 | 8.7875 | 87.6218 | 96.4093 | 44.6275 | 4.8281 | 42.2862 | 42.2862 | 506.2127 | 96.4093 | 0 | 44501.1055 | 0 | 0 | 0 | 96.4093 | 0 | 0 | 44501.1055
3 | 6 | 8 | 50.5884 | 903.7769 | 954.3652 | 46.0387 | 5.4976 | 487.0652 | 288 | 507.9924 | 564.3129 | 390.0523 | 260686.4078 | 40.6718 | 0 | 0 | 564.3129 | 390.0523 | 0 | 260686.4078
3 | 6 | 9 | 19.6083 | 885.5196 | 905.1279 | 47.1984 | 6.4043 | 593.4027 | 288 | 496.308 | 439.2916 | 465.8363 | 197290.061 | 48.574 | 0 | 0 | 439.2916 | 465.8363 | 0 | 197290.061
3 | 6 | 10 | 16.4925 | 387.0546 | 403.5471 | 46.4879 | 8.5991 | 850.3806 | 288 | 498.8969 | 136.6701 | 266.8771 | 61830.7777 | 27.828 | 0 | 0 | 136.6701 | 266.8771 | 0 | 61830.7777
3 | 6 | 11 | 9.5325 | 105.4261 | 114.9586 | 44.9319 | 9.6413 | 0 | 0 | 492.3376 | 0 | 114.9586 | 0 | 11.987 | 0 | 0 | 0 | 114.9586 | 0 | 0
3 | 6 | 12 | 11.4667 | 316.723 | 328.1896 | 46.7073 | 9.7176 | 0 | 0 | 487.5595 | 0 | 328.1896 | 0 | 34.2212 | 0 | 0 | 0 | 328.1896 | 0 | 0
3 | 6 | 13 | 10.2292 | 446.3044 | 456.5336 | 47.171 | 9.7939 | 0 | 0 | 487.9784 | 0 | 456.5336 | 0 | 47.604 | 0 | 0 | 0 | 456.5336 | 0 | 0
3 | 6 | 14 | 1.6483 | 432.3861 | 434.0345 | 47.8595 | 9.4634 | 7146.677 | 288 | 486.8848 | 17.4909 | 416.5435 | 7678.9543 | 43.4341 | 0 | 0 | 17.4909 | 416.5435 | 0 | 7678.9543
3 | 6 | 15 | 1.1417 | 158.8939 | 160.0356 | 47.736 | 10.5311 | 0 | 0 | 491.7836 | 0 | 160.0356 | 0 | 16.6873 | 0 | 0 | 0 | 160.0356 | 0 | 0
3 | 6 | 16 | 0.89333 | 172.3724 | 173.2657 | 47.8092 | 11.0904 | 0 | 0 | 497.6627 | 0 | 173.2657 | 0 | 18.0669 | 0 | 0 | 0 | 173.2657 | 0 | 0
3 | 6 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 496.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 488.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 468.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 447.259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 426.9398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 425.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 6 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 424.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 416.4731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 419.7359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 427.5284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 450.3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 468.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 474.3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 479.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 7 | 0 | 3.8908 | 3.8908 | 48 | 5.2518 | 1.8732 | 1.8732 | 484.1373 | 3.8908 | 0 | 1696.9376 | 0 | 0 | 0 | 3.8908 | 0 | 0 | 1696.9376
3 | 7 | 8 | 2.7633 | 39.3943 | 42.1576 | 45.5747 | 6.2094 | 26.0452 | 26.0452 | 482.5422 | 42.1576 | 0 | 18421.4998 | 0 | 0 | 0 | 42.1576 | 0 | 0 | 18421.4998
3 | 7 | 9 | 0.14359 | 6.037 | 6.1806 | 47.1404 | 7.328 | 5.7064 | 5.7064 | 485.2644 | 6.1806 | 0 | 2707.8627 | 0 | 0 | 0 | 6.1806 | 0 | 0 | 2707.8627
3 | 7 | 10 | 2.7617 | 36.0795 | 38.8412 | 45.3692 | 8.5482 | 77.855 | 77.855 | 480.5379 | 38.8412 | 0 | 16902.4507 | 0 | 0 | 0 | 38.8412 | 0 | 0 | 16902.4507
3 | 7 | 11 | 0 | 0 | 0 | 0 | 9.1838 | 0 | 0 | 474.5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 472.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 471.4057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 473.3087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 15 | 0 | 0.98629 | 0.98629 | 48 | 11.226 | 0 | 0 | 487.5002 | 0 | 0.98629 | 0 | 0.10284 | 0 | 0 | 0 | 0.98629 | 0 | 0
3 | 7 | 16 | 0 | 1.0741 | 1.0741 | 48 | 11.853 | 0 | 0 | 490.6302 | 0 | 1.0741 | 0 | 0.112 | 0 | 0 | 0 | 1.0741 | 0 | 0
3 | 7 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 489.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 496.4774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 468.2356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 435.7183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 411.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 405.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 409.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 414.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 422.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 432.8688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 452.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 477.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 482.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 477.5679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 7 | 0.1025 | 54.1828 | 54.2853 | 47.9301 | 5.0146 | 24.7802 | 24.7802 | 470.9366 | 54.2853 | 0 | 22963.0245 | 0 | 0 | 0 | 54.2853 | 0 | 0 | 22963.0245
3 | 8 | 8 | 0.6425 | 220.5416 | 221.1841 | 47.8925 | 6.2094 | 136.649 | 136.649 | 461.5426 | 221.1841 | 0 | 91492.8464 | 0 | 0 | 0 | 221.1841 | 0 | 0 | 91492.8464
3 | 8 | 9 | 1.4983 | 412.2158 | 413.7141 | 47.866 | 7.311 | 379.1311 | 288 | 466.1674 | 314.2704 | 99.4437 | 131459.7203 | 10.3693 | 0 | 0 | 314.2704 | 99.4437 | 0 | 131459.7203
3 | 8 | 10 | 2.7308 | 307.5578 | 310.2886 | 47.6744 | 8.0567 | 422.6223 | 288 | 465.0364 | 211.4491 | 98.8395 | 88250.8455 | 10.3063 | 0 | 0 | 211.4491 | 98.8395 | 0 | 88250.8455
3 | 8 | 11 | 1.6167 | 172.4986 | 174.1153 | 47.6565 | 9.3109 | 1301.7108 | 288 | 464.8979 | 38.5225 | 135.5927 | 16073.1976 | 14.1386 | 0 | 0 | 38.5225 | 135.5927 | 0 | 16073.1976
3 | 8 | 12 | 0.32723 | 269.1725 | 269.4997 | 47.9551 | 9.0058 | 963.1469 | 288 | 458.5385 | 80.5858 | 188.914 | 33087.179 | 19.6986 | 0 | 0 | 80.5858 | 188.914 | 0 | 33087.179
3 | 8 | 13 | 5.1675 | 314.3725 | 319.54 | 47.4016 | 8.4889 | 606.0042 | 288 | 455.1094 | 151.8596 | 167.6805 | 61914.3281 | 17.4845 | 0 | 0 | 151.8596 | 167.6805 | 0 | 61914.3281
3 | 8 | 14 | 1.2875 | 194.4863 | 195.7738 | 47.7567 | 8.938 | 626.942 | 288 | 458.4205 | 89.9331 | 105.8407 | 36932.2911 | 11.0363 | 0 | 0 | 89.9331 | 105.8407 | 0 | 36932.2911
3 | 8 | 15 | 0.74417 | 133.3286 | 134.0727 | 47.7946 | 9.6075 | 0 | 0 | 469.6001 | 0 | 134.0727 | 0 | 13.9801 | 0 | 0 | 0 | 134.0727 | 0 | 0
3 | 8 | 16 | 0.59167 | 88.4296 | 89.0213 | 47.7541 | 10.9718 | 0 | 0 | 480.8961 | 0 | 89.0213 | 0 | 9.2825 | 0 | 0 | 0 | 89.0213 | 0 | 0
3 | 8 | 17 | 0.23583 | 0 | 0.23583 | 11 | 10.3786 | 0 | 0 | 488.6073 | 0 | 0.23583 | 0 | 0.024591 | 0 | 0 | 0 | 0.23583 | 0 | 0
3 | 8 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 492.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 491.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 464.5402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 441.3767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 440.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 8 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 443.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 440.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 450.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 467.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 477.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 486.8754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 495.7242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 502.4579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 7 | 0.28583 | 264.9789 | 265.2647 | 47.9601 | 4.6502 | 112.1569 | 112.1569 | 495.3755 | 265.2647 | 0 | 118683.5058 | 0 | 0 | 0 | 265.2647 | 0 | 0 | 118683.5058
3 | 9 | 8 | 0.80167 | 259.7832 | 260.5849 | 47.8862 | 5.1417 | 122.351 | 122.351 | 497.8965 | 260.5849 | 0 | 117265.9086 | 0 | 0 | 0 | 260.5849 | 0 | 0 | 117265.9086
3 | 9 | 9 | 0.51833 | 276.0538 | 276.5721 | 47.9307 | 6.6161 | 194.2367 | 194.2367 | 498.1005 | 276.5721 | 0 | 124504.4197 | 0 | 0 | 0 | 276.5721 | 0 | 0 | 124504.4197
3 | 9 | 10 | 0 | 168.3749 | 168.3749 | 48 | 6.9721 | 134.3241 | 134.3241 | 493.4084 | 168.3749 | 0 | 74995.586 | 0 | 0 | 0 | 168.3749 | 0 | 0 | 74995.586
3 | 9 | 11 | 0 | 155.5755 | 155.5755 | 48 | 8.5652 | 316.9985 | 288 | 493.1138 | 141.3438 | 14.2318 | 62914.0576 | 1.484 | 0 | 0 | 141.3438 | 14.2318 | 0 | 62914.0576
3 | 9 | 12 | 0 | 55.7015 | 55.7015 | 48 | 7.8957 | 68.6587 | 68.6587 | 488.7069 | 55.7015 | 0 | 24548.0439 | 0 | 0 | 0 | 55.7015 | 0 | 0 | 24548.0439
3 | 9 | 13 | 0 | 33.7862 | 33.7862 | 48 | 7.4381 | 32.7906 | 32.7906 | 485.4267 | 33.7862 | 0 | 14778.9899 | 0 | 0 | 0 | 33.7862 | 0 | 0 | 14778.9899
3 | 9 | 14 | 0 | 15.0565 | 15.0565 | 48 | 7.2771 | 13.5957 | 13.5957 | 485.5738 | 15.0565 | 0 | 6588.3447 | 0 | 0 | 0 | 15.0565 | 0 | 0 | 6588.3447
3 | 9 | 15 | 0 | 0.43279 | 0.43279 | 48 | 7.3449 | 0.4026 | 0.4026 | 481.2273 | 0.43279 | 0 | 187.4972 | 0 | 0 | 0 | 0.43279 | 0 | 0 | 187.4972
3 | 9 | 16 | 0 | 3.7108 | 3.7108 | 48 | 6.9975 | 2.9894 | 2.9894 | 486.6515 | 3.7108 | 0 | 1627.7444 | 0 | 0 | 0 | 3.7108 | 0 | 0 | 1627.7444
3 | 9 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 486.9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 494.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 480.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 462.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 451.4807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 433.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 9 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 427.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 417.9717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 422.4873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 430.8396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 451.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 473.3103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 488.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 6 | 0 | 0.205 | 0.205 | 48 | 4.6163 | 0.086086 | 0.086086 | 483.852 | 0.205 | 0 | 89.3497 | 0 | 0 | 0 | 0.205 | 0 | 0 | 89.3497
3 | 10 | 7 | 1.0392 | 18.9792 | 20.0184 | 46.0793 | 6.1924 | 12.3058 | 12.3058 | 490.1882 | 20.0184 | 0 | 8890.3516 | 0 | 0 | 0 | 20.0184 | 0 | 0 | 8890.3516
3 | 10 | 8 | 0.425 | 36.587 | 37.012 | 47.5751 | 6.8788 | 28.5119 | 28.5119 | 491.6332 | 37.012 | 0 | 16435.4705 | 0 | 0 | 0 | 37.012 | 0 | 0 | 16435.4705
3 | 10 | 9 | 0 | 47.4517 | 47.4517 | 48 | 7.3195 | 43.6475 | 43.6475 | 499.3886 | 47.4517 | 0 | 21419.1776 | 0 | 0 | 0 | 47.4517 | 0 | 0 | 21419.1776
3 | 10 | 10 | 0 | 90.9551 | 90.9551 | 48 | 7.4805 | 90.0478 | 90.0478 | 496.7613 | 90.9551 | 0 | 40817.1166 | 0 | 0 | 0 | 90.9551 | 0 | 0 | 40817.1166
3 | 10 | 11 | 0 | 63.0194 | 63.0194 | 48 | 7.2263 | 55.6814 | 55.6814 | 494.8115 | 63.0194 | 0 | 28157.8018 | 0 | 0 | 0 | 63.0194 | 0 | 0 | 28157.8018
3 | 10 | 12 | 0 | 36.9894 | 36.9894 | 48 | 7.8703 | 44.9199 | 44.9199 | 488.774 | 36.9894 | 0 | 16303.9859 | 0 | 0 | 0 | 36.9894 | 0 | 0 | 16303.9859
3 | 10 | 13 | 1.2983 | 52.4422 | 53.7406 | 47.1061 | 8.1754 | 79.3336 | 79.3336 | 489.6828 | 53.7406 | 0 | 23784.3204 | 0 | 0 | 0 | 53.7406 | 0 | 0 | 23784.3204
3 | 10 | 14 | 1.3325 | 7.2415 | 8.574 | 42.2498 | 8.2431 | 13.2941 | 13.2941 | 494.9796 | 8.574 | 0 | 3881.6954 | 0 | 0 | 0 | 8.574 | 0 | 0 | 3881.6954
3 | 10 | 15 | 2.8492 | 31.6318 | 34.481 | 44.9427 | 7.4212 | 33.2034 | 33.2034 | 495.6231 | 34.481 | 0 | 15539.8931 | 0 | 0 | 0 | 34.481 | 0 | 0 | 15539.8931
3 | 10 | 16 | 6.725 | 12.7815 | 19.5065 | 35.244 | 7.3195 | 17.9427 | 17.9427 | 493.725 | 19.5065 | 0 | 8943.3727 | 0 | 0 | 0 | 19.5065 | 0 | 0 | 8943.3727
3 | 10 | 17 | 0 | 0.16646 | 0.16646 | 48 | 7.2686 | 0.14976 | 0.14976 | 499.5813 | 0.16646 | 0 | 75.1695 | 0 | 0 | 0 | 0.16646 | 0 | 0 | 75.1695
3 | 10 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 501.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 513.8717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 512.4411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 507.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 506.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 10 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 506.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 508.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 509.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 514.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 513.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 505.6031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 503.4769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 6 | 0 | 0.28583 | 0.28583 | 48 | 4.4638 | 0.11646 | 0.11646 | 507.2616 | 0.28583 | 0 | 131.2723 | 0 | 0 | 0 | 0.28583 | 0 | 0 | 131.2723
3 | 11 | 7 | 2.045 | 134.0523 | 136.0973 | 47.444 | 6.006 | 79.3109 | 79.3109 | 513.8117 | 136.0973 | 0 | 63471.3978 | 0 | 0 | 0 | 136.0973 | 0 | 0 | 63471.3978
3 | 11 | 8 | 2.9933 | 477.9153 | 480.9086 | 47.7697 | 6.6246 | 338.7073 | 288 | 522.8254 | 408.9126 | 71.996 | 194256.2795 | 7.5072 | 0 | 0 | 408.9126 | 71.996 | 0 | 194256.2795
3 | 11 | 9 | 0.83 | 702.6952 | 703.5252 | 47.9563 | 7.1924 | 612.8189 | 288 | 520.6324 | 330.6283 | 372.897 | 156280.0831 | 38.8829 | 0 | 0 | 330.6283 | 372.897 | 0 | 156280.0831
3 | 11 | 10 | 1.88 | 242.2047 | 244.0847 | 47.715 | 7.0398 | 199.8988 | 199.8988 | 523.1887 | 244.0847 | 0 | 116055.8666 | 0 | 0 | 0 | 244.0847 | 0 | 0 | 116055.8666
3 | 11 | 11 | 4.5375 | 216.5243 | 221.0618 | 47.2405 | 7.2093 | 193.9307 | 193.9307 | 520.8188 | 221.0618 | 0 | 104690.0739 | 0 | 0 | 0 | 221.0618 | 0 | 0 | 104690.0739
3 | 11 | 12 | 2.8967 | 169.2427 | 172.1393 | 47.3774 | 7.9296 | 216.5128 | 216.5128 | 514.7602 | 172.1393 | 0 | 80454.9635 | 0 | 0 | 0 | 172.1393 | 0 | 0 | 80454.9635
3 | 11 | 13 | 1.6242 | 282.5569 | 284.1811 | 47.7885 | 8.2601 | 446.2434 | 288 | 513.7986 | 183.407 | 100.7741 | 85469.499 | 10.508 | 0 | 0 | 183.407 | 100.7741 | 0 | 85469.499
3 | 11 | 14 | 0.435 | 161.4252 | 161.8602 | 47.9006 | 8.5313 | 319.2477 | 288 | 517.35 | 146.0175 | 15.8428 | 68547.8154 | 1.652 | 0 | 0 | 146.0175 | 15.8428 | 0 | 68547.8154
3 | 11 | 15 | 95.6717 | 746.3012 | 841.9729 | 43.7958 | 8.4041 | 1482.7111 | 288 | 514.1885 | 163.5438 | 678.4291 | 76929.806 | 70.7416 | 0 | 0 | 163.5438 | 678.4291 | 0 | 76929.806
3 | 11 | 16 | 6.81 | 88.7981 | 95.6081 | 45.3646 | 9.1753 | 481.2377 | 288 | 513.7021 | 57.2173 | 38.3908 | 26797.0084 | 4.0031 | 0 | 0 | 57.2173 | 38.3908 | 0 | 26797.0084
3 | 11 | 17 | 0 | 0.31833 | 0.31833 | 48 | 8.6753 | 0.72673 | 0.72673 | 520.0037 | 0.31833 | 0 | 150.2545 | 0 | 0 | 0 | 0.31833 | 0 | 0 | 150.2545
3 | 11 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 530.1845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 530.9638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 531.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 529.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 529.2634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 11 | 23 | 0.084167 | 0 | 0.084167 | 11 | 4.4722 | 0.034349 | 0.034349 | 528.3611 | 0.084167 | 0 | 43.5446 | 0 | 0 | 0 | 0.084167 | 0 | 0 | 43.5446
3 | 12 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 527.4518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 529.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 529.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 530.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 4 | 0.9225 | 0 | 0.9225 | 11 | 3.0317 | 0.29379 | 0.29379 | 532.2849 | 0.9225 | 0 | 480.8853 | 0 | 0 | 0 | 0.9225 | 0 | 0 | 480.8853
3 | 12 | 5 | 19.0861 | 0 | 19.0861 | 11 | 3.4638 | 6.5071 | 6.5071 | 535.2522 | 19.0861 | 0 | 10005.9425 | 0 | 0 | 0 | 19.0861 | 0 | 0 | 10005.9425
3 | 12 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 539.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 7 | 0.073333 | 1.5808 | 1.6541 | 46.3597 | 4.8705 | 0.73204 | 0.73204 | 537.0311 | 1.6541 | 0 | 811.64 | 0 | 0 | 0 | 1.6541 | 0 | 0 | 811.64
3 | 12 | 8 | 11.4758 | 489.5653 | 501.0411 | 47.1526 | 4.8451 | 220.547 | 220.547 | 533.0697 | 501.0411 | 0 | 243464.4396 | 0 | 0 | 0 | 501.0411 | 0 | 0 | 243464.4396
3 | 12 | 9 | 14.7339 | 1222.5554 | 1237.2893 | 47.5594 | 6.3789 | 804.7467 | 288 | 536.6553 | 442.7969 | 794.4924 | 216570.1578 | 82.8438 | 0 | 0 | 442.7969 | 794.4924 | 0 | 216570.1578
3 | 12 | 10 | 7.4092 | 1325.7334 | 1333.1425 | 47.7944 | 8.4804 | 2508.9858 | 288 | 532.0473 | 153.028 | 1180.1146 | 74104.2479 | 123.0536 | 0 | 0 | 153.028 | 1180.1146 | 0 | 74104.2479
3 | 12 | 11 | 1.5567 | 677.2958 | 678.8524 | 47.9152 | 9.4549 | 10477.8359 | 288 | 523.8129 | 18.6593 | 660.1931 | 8879.9379 | 68.8401 | 0 | 0 | 18.6593 | 660.1931 | 0 | 8879.9379
3 | 12 | 12 | 3.0125 | 886.8604 | 889.8729 | 47.8747 | 9.8362 | 0 | 0 | 519.49 | 0 | 889.8729 | 0 | 92.7894 | 0 | 0 | 0 | 889.8729 | 0 | 0
3 | 12 | 13 | 3.3592 | 1107.0786 | 1110.4378 | 47.8881 | 9.6159 | 0 | 0 | 512.2837 | 0 | 1110.4378 | 0 | 115.7883 | 0 | 0 | 0 | 1110.4378 | 0 | 0
3 | 12 | 14 | 1.2625 | 852.0928 | 853.3553 | 47.9453 | 9.5227 | 26392.5585 | 288 | 515.245 | 9.312 | 844.0433 | 4351.4745 | 88.0106 | 0 | 0 | 9.312 | 844.0433 | 0 | 4351.4745
3 | 12 | 15 | 0.98417 | 211.7652 | 212.7494 | 47.8288 | 10.7175 | 0 | 0 | 522.3544 | 0 | 212.7494 | 0 | 22.1839 | 0 | 0 | 0 | 212.7494 | 0 | 0
3 | 12 | 16 | 0.71917 | 421.6205 | 422.3396 | 47.937 | 12.0564 | 0 | 0 | 518.3726 | 0 | 422.3396 | 0 | 44.0385 | 0 | 0 | 0 | 422.3396 | 0 | 0
3 | 12 | 17 | 0.25583 | 183.0793 | 183.3351 | 47.9484 | 11.8107 | 0 | 0 | 523.7058 | 0 | 183.3351 | 0 | 19.1168 | 0 | 0 | 0 | 183.3351 | 0 | 0
3 | 12 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 541.1848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 540.7737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 538.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 532.392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 531.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 12 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 533.6579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 537.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 537.9322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 537.0773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 527.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 530.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 532.6229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 533.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 534.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 8 | 0.20333 | 43.2743 | 43.4777 | 47.827 | 5.4976 | 22.189 | 22.189 | 540.1987 | 43.4777 | 0 | 21407.1662 | 0 | 0 | 0 | 43.4777 | 0 | 0 | 21407.1662
3 | 13 | 9 | 0.4325 | 14.2555 | 14.688 | 46.9105 | 6.4043 | 9.6295 | 9.6295 | 540.4205 | 14.688 | 0 | 7248.6755 | 0 | 0 | 0 | 14.688 | 0 | 0 | 7248.6755
3 | 13 | 10 | 0 | 4.4794 | 4.4794 | 48 | 8.5991 | 9.4393 | 9.4393 | 542.9542 | 4.4794 | 0 | 2217.0978 | 0 | 0 | 0 | 4.4794 | 0 | 0 | 2217.0978
3 | 13 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 543.9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 543.0805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 543.8552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 14 | 0 | 2.4885 | 2.4885 | 48 | 9.4634 | 40.9742 | 40.9742 | 541.9887 | 2.4885 | 0 | 1229.2704 | 0 | 0 | 0 | 2.4885 | 0 | 0 | 1229.2704
3 | 13 | 15 | 0 | 15.0133 | 15.0133 | 48 | 10.5311 | 0 | 0 | 531.8224 | 0 | 15.0133 | 0 | 1.5655 | 0 | 0 | 0 | 15.0133 | 0 | 0
3 | 13 | 16 | 0.033333 | 16.636 | 16.6694 | 47.926 | 11.0904 | 0 | 0 | 523.2508 | 0 | 16.6694 | 0 | 1.7382 | 0 | 0 | 0 | 16.6694 | 0 | 0
3 | 13 | 17 | 0 | 1.0142 | 1.0142 | 48 | 11.1073 | 0 | 0 | 527.027 | 0 | 1.0142 | 0 | 0.10575 | 0 | 0 | 0 | 1.0142 | 0 | 0
3 | 13 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 539.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 539.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 540.5722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 536.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 530.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 13 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 533.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 530.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 536.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 541.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 539.3963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 535.3888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 535.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 535.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 535.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 8 | 0.15583 | 96.5046 | 96.6604 | 47.9403 | 6.2094 | 59.7174 | 59.7174 | 539.1332 | 96.6604 | 0 | 47478.9146 | 0 | 0 | 0 | 96.6604 | 0 | 0 | 47478.9146
3 | 14 | 9 | 0.64417 | 45.8408 | 46.485 | 47.4873 | 7.328 | 42.9183 | 42.9183 | 541.347 | 46.485 | 0 | 22957.056 | 0 | 0 | 0 | 46.485 | 0 | 0 | 22957.056
3 | 14 | 10 | 0.059167 | 52.1125 | 52.1716 | 47.958 | 8.5482 | 104.5752 | 104.5752 | 545.9233 | 52.1716 | 0 | 25979.6639 | 0 | 0 | 0 | 52.1716 | 0 | 0 | 25979.6639
3 | 14 | 11 | 0 | 6.2517 | 6.2517 | 48 | 9.1838 | 32.1236 | 32.1236 | 546.0262 | 6.2517 | 0 | 3113.5156 | 0 | 0 | 0 | 6.2517 | 0 | 0 | 3113.5156
3 | 14 | 12 | 0 | 3.5951 | 3.5951 | 48 | 9.8701 | 0 | 0 | 546.6272 | 0 | 3.5951 | 0 | 0.37487 | 0 | 0 | 0 | 3.5951 | 0 | 0
3 | 14 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 543.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 14 | 0.10083 | 24.9328 | 25.0337 | 47.851 | 10.2684 | 0 | 0 | 541.7316 | 0 | 25.0337 | 0 | 2.6103 | 0 | 0 | 0 | 25.0337 | 0 | 0
3 | 14 | 15 | 0 | 6.8352 | 6.8352 | 48 | 11.226 | 0 | 0 | 537.7173 | 0 | 6.8352 | 0 | 0.71272 | 0 | 0 | 0 | 6.8352 | 0 | 0
3 | 14 | 16 | 0 | 8.1622 | 8.1622 | 48 | 11.853 | 0 | 0 | 523.0588 | 0 | 8.1622 | 0 | 0.85109 | 0 | 0 | 0 | 8.1622 | 0 | 0
3 | 14 | 17 | 0 | 0.001625 | 0.001625 | 48 | 11.7514 | 0 | 0 | 525.536 | 0 | 0.001625 | 0 | 0.00016944 | 0 | 0 | 0 | 0.001625 | 0 | 0
3 | 14 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 538.1532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 544.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 549.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 547.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 540.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 540.2254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 542.0763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 543.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 544.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 531.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 4 | 5.6014 | 0 | 5.6014 | 11 | 3.3028 | 1.8608 | 1.8608 | 532.8588 | 5.6014 | 0 | 2923.1528 | 0 | 0 | 0 | 5.6014 | 0 | 0 | 2923.1528
3 | 15 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 536.1149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 544.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 547.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 8 | 0 | 10.6185 | 10.6185 | 48 | 6.2094 | 6.5602 | 6.5602 | 550.6988 | 10.6185 | 0 | 5337.8947 | 0 | 0 | 0 | 10.6185 | 0 | 0 | 5337.8947
3 | 15 | 9 | 0.6575 | 5.39 | 6.0475 | 43.9772 | 7.311 | 5.5419 | 5.5419 | 554.1462 | 6.0475 | 0 | 3085.2254 | 0 | 0 | 0 | 6.0475 | 0 | 0 | 3085.2254
3 | 15 | 10 | 0.46583 | 5.1349 | 5.6007 | 44.9226 | 8.0567 | 7.6284 | 7.6284 | 558.4747 | 5.6007 | 0 | 2876.2771 | 0 | 0 | 0 | 5.6007 | 0 | 0 | 2876.2771
3 | 15 | 11 | 1.3092 | 2.1558 | 3.465 | 34.0203 | 9.3109 | 25.9045 | 25.9045 | 556.5004 | 3.465 | 0 | 1810.3718 | 0 | 0 | 0 | 3.465 | 0 | 0 | 1810.3718
3 | 15 | 12 | 5.8183 | 174.9305 | 180.7488 | 46.809 | 9.0058 | 645.9661 | 288 | 558.9154 | 80.5858 | 100.1631 | 41268.4884 | 10.4443 | 0 | 0 | 80.5858 | 100.1631 | 0 | 41268.4884
3 | 15 | 13 | 8.9267 | 46.8058 | 55.7324 | 42.0737 | 8.4889 | 105.6959 | 105.6959 | 558.5964 | 55.7324 | 0 | 28787.0606 | 0 | 0 | 0 | 55.7324 | 0 | 0 | 28787.0606
3 | 15 | 14 | 6.3977 | 14.7595 | 21.1572 | 36.8117 | 8.938 | 67.7532 | 67.7532 | 554.9487 | 21.1572 | 0 | 10962.3049 | 0 | 0 | 0 | 21.1572 | 0 | 0 | 10962.3049
3 | 15 | 15 | 7.3093 | 33.0696 | 40.3789 | 41.3024 | 9.6075 | 0 | 0 | 545.6821 | 0 | 40.3789 | 0 | 4.2104 | 0 | 0 | 0 | 40.3789 | 0 | 0
3 | 15 | 16 | 3.6075 | 3.4751 | 7.0826 | 29.1541 | 10.9718 | 0 | 0 | 536.6692 | 0 | 7.0826 | 0 | 0.73852 | 0 | 0 | 0 | 7.0826 | 0 | 0
3 | 15 | 17 | 0 | 3.94 | 3.94 | 48 | 10.3786 | 0 | 0 | 542.8887 | 0 | 3.94 | 0 | 0.41083 | 0 | 0 | 0 | 3.94 | 0 | 0
3 | 15 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 548.0632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 558.2317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 556.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 557.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 558.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 15 | 23 | 50.1082 | 0 | 50.1082 | 11 | 4.2265 | 19.5127 | 19.5127 | 557.1725 | 50.1082 | 0 | 27367.7272 | 0 | 0 | 0 | 50.1082 | 0 | 0 | 27367.7272
3 | 16 | 0 | 28.3309 | 0 | 28.3309 | 11 | 4.1757 | 10.9288 | 10.9288 | 558.3421 | 28.3309 | 0 | 15506.682 | 0 | 0 | 0 | 28.3309 | 0 | 0 | 15506.682
3 | 16 | 1 | 45.6333 | 0 | 45.6333 | 11 | 3.8791 | 16.6891 | 16.6891 | 558.3657 | 45.6333 | 0 | 24978.0987 | 0 | 0 | 0 | 45.6333 | 0 | 0 | 24978.0987
3 | 16 | 2 | 25.8321 | 0 | 25.8321 | 11 | 3.8197 | 9.3503 | 9.3503 | 555.4456 | 25.8321 | 0 | 14064.168 | 0 | 0 | 0 | 25.8321 | 0 | 0 | 14064.168
3 | 16 | 3 | 25.5142 | 0 | 25.5142 | 11 | 3.4638 | 8.6987 | 8.6987 | 542.2536 | 25.5142 | 0 | 13554.4922 | 0 | 0 | 0 | 25.5142 | 0 | 0 | 13554.4922
3 | 16 | 4 | 2.9192 | 0 | 2.9192 | 11 | 3.4045 | 0.9857 | 0.9857 | 544.5854 | 2.9192 | 0 | 1557.6246 | 0 | 0 | 0 | 2.9192 | 0 | 0 | 1557.6246
3 | 16 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 546.3381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 550.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 553.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 8 | 77.9375 | 180.5448 | 258.4824 | 36.8438 | 5.1417 | 121.3638 | 121.3638 | 553.557 | 258.4824 | 0 | 133561.251 | 0 | 0 | 0 | 258.4824 | 0 | 0 | 133561.251
3 | 16 | 9 | 23.0917 | 41.4591 | 64.5507 | 34.764 | 6.6161 | 45.334 | 45.334 | 556.1237 | 64.5507 | 0 | 33654.1547 | 0 | 0 | 0 | 64.5507 | 0 | 0 | 33654.1547
3 | 16 | 10 | 17.185 | 97.804 | 114.989 | 42.4704 | 6.9721 | 91.7345 | 91.7345 | 559.5065 | 114.989 | 0 | 59453.4785 | 0 | 0 | 0 | 114.989 | 0 | 0 | 59453.4785
3 | 16 | 11 | 22.4892 | 55.6762 | 78.1654 | 37.3546 | 8.5652 | 159.2686 | 159.2686 | 557.0591 | 78.1654 | 0 | 40622.8824 | 0 | 0 | 0 | 78.1654 | 0 | 0 | 40622.8824
3 | 16 | 12 | 0 | 15.0433 | 15.0433 | 48 | 7.8957 | 18.5426 | 18.5426 | 553.3907 | 15.0433 | 0 | 7602.7392 | 0 | 0 | 0 | 15.0433 | 0 | 0 | 7602.7392
3 | 16 | 13 | 0 | 1.25 | 1.25 | 48 | 7.4381 | 1.2132 | 1.2132 | 548.481 | 1.25 | 0 | 625.6013 | 0 | 0 | 0 | 1.25 | 0 | 0 | 625.6013
3 | 16 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 544.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 15 | 6.4583 | 9.3233 | 15.7817 | 32.8585 | 7.3449 | 14.6808 | 14.6808 | 532.5358 | 15.7817 | 0 | 7885.7412 | 0 | 0 | 0 | 15.7817 | 0 | 0 | 7885.7412
3 | 16 | 16 | 27.3375 | 290.6765 | 318.014 | 44.8194 | 6.9975 | 256.1889 | 256.1889 | 530.6458 | 318.014 | 0 | 154499.6222 | 0 | 0 | 0 | 318.014 | 0 | 0 | 154499.6222
3 | 16 | 17 | 0 | 1.035 | 1.035 | 48 | 7.167 | 0.8921 | 0.8921 | 544.0185 | 1.035 | 0 | 513.3791 | 0 | 0 | 0 | 1.035 | 0 | 0 | 513.3791
3 | 16 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 547.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 548.3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 538.4334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 521.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 516.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 16 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 520.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 523.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 527.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 526.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 517.7864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 522.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 528.216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 535.3466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 540.7847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 8 | 0.375 | 3.3967 | 3.7717 | 44.3213 | 6.8788 | 2.9055 | 2.9055 | 543.0833 | 3.7717 | 0 | 1881.164 | 0 | 0 | 0 | 3.7717 | 0 | 0 | 1881.164
3 | 17 | 9 | 0.0325 | 10.9163 | 10.9488 | 47.8902 | 7.3195 | 10.071 | 10.071 | 542.0391 | 10.9488 | 0 | 5410.3568 | 0 | 0 | 0 | 10.9488 | 0 | 0 | 5410.3568
3 | 17 | 10 | 0.34 | 13.9573 | 14.2973 | 47.1201 | 7.4805 | 14.1547 | 14.1547 | 539.3912 | 14.2973 | 0 | 7038.1436 | 0 | 0 | 0 | 14.2973 | 0 | 0 | 7038.1436
3 | 17 | 11 | 0.070833 | 18.9655 | 19.0363 | 47.8623 | 7.2263 | 16.8197 | 16.8197 | 537.6648 | 19.0363 | 0 | 9324.046 | 0 | 0 | 0 | 19.0363 | 0 | 0 | 9324.046
3 | 17 | 12 | 0.076667 | 2.5135 | 2.5901 | 46.9048 | 7.8703 | 3.1454 | 3.1454 | 533.6448 | 2.5901 | 0 | 1260.7174 | 0 | 0 | 0 | 2.5901 | 0 | 0 | 1260.7174
3 | 17 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 539.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 14 | 0 | 4.789 | 4.789 | 48 | 8.2431 | 7.4255 | 7.4255 | 538.2786 | 4.789 | 0 | 2347.949 | 0 | 0 | 0 | 4.789 | 0 | 0 | 2347.949
3 | 17 | 15 | 0.14333 | 4.231 | 4.3743 | 46.7876 | 7.4212 | 4.2122 | 4.2122 | 528.7641 | 4.3743 | 0 | 2108.3057 | 0 | 0 | 0 | 4.3743 | 0 | 0 | 2108.3057
3 | 17 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 528.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 17 | 0 | 0.10071 | 0.10071 | 48 | 7.2686 | 0.090606 | 0.090606 | 529.5525 | 0.10071 | 0 | 48.4963 | 0 | 0 | 0 | 0.10071 | 0 | 0 | 48.4963
3 | 17 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 528.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 517.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 509.7621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 479.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 466.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 17 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 461.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 454.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 450.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 455.9947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 459.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 469.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 478.6294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 481.1418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 7 | 0 | 0.73417 | 0.73417 | 48 | 6.006 | 0.42784 | 0.42784 | 483.5836 | 0.73417 | 0 | 319.7909 | 0 | 0 | 0 | 0.73417 | 0 | 0 | 319.7909
3 | 18 | 8 | 28.7125 | 211.5217 | 240.2342 | 43.5778 | 6.6246 | 169.1986 | 169.1986 | 483.5057 | 240.2342 | 0 | 105685.7372 | 0 | 0 | 0 | 240.2342 | 0 | 0 | 105685.7372
3 | 18 | 9 | 3.2342 | 18.3576 | 21.5917 | 42.4579 | 7.1924 | 18.8079 | 18.8079 | 483.6593 | 21.5917 | 0 | 9526.3097 | 0 | 0 | 0 | 21.5917 | 0 | 0 | 9526.3097
3 | 18 | 10 | 1.4725 | 5.942 | 7.4145 | 40.6519 | 7.0398 | 6.0723 | 6.0723 | 481.3247 | 7.4145 | 0 | 3267.3682 | 0 | 0 | 0 | 7.4145 | 0 | 0 | 3267.3682
3 | 18 | 11 | 0 | 3.6402 | 3.6402 | 48 | 7.2093 | 3.1934 | 3.1934 | 478.8764 | 3.6402 | 0 | 1568.4619 | 0 | 0 | 0 | 3.6402 | 0 | 0 | 1568.4619
3 | 18 | 12 | 3.4124 | 37.4739 | 40.8863 | 44.912 | 7.9296 | 51.4259 | 51.4259 | 478.1097 | 40.8863 | 0 | 17711.8644 | 0 | 0 | 0 | 40.8863 | 0 | 0 | 17711.8644
3 | 18 | 13 | 2.1008 | 74.9089 | 77.0097 | 46.9906 | 8.2601 | 120.9267 | 120.9267 | 479.3065 | 77.0097 | 0 | 33292.5203 | 0 | 0 | 0 | 77.0097 | 0 | 0 | 33292.5203
3 | 18 | 14 | 15.5519 | 154.1727 | 169.7247 | 44.6097 | 8.5313 | 334.7593 | 288 | 483.4913 | 146.0175 | 23.7072 | 64084.3763 | 2.472 | 0 | 0 | 146.0175 | 23.7072 | 0 | 64084.3763
3 | 18 | 15 | 35.3283 | 217.0711 | 252.3994 | 42.8211 | 8.4041 | 444.4744 | 288 | 491.0001 | 163.5438 | 88.8556 | 73296.8989 | 9.2652 | 0 | 0 | 163.5438 | 88.8556 | 0 | 73296.8989
3 | 18 | 16 | 19.0553 | 109.2262 | 128.2815 | 42.5039 | 9.1753 | 645.6976 | 288 | 493.2939 | 57.2173 | 71.0642 | 25792.9871 | 7.41 | 0 | 0 | 57.2173 | 71.0642 | 0 | 25792.9871
3 | 18 | 17 | 0 | 4.8675 | 4.8675 | 48 | 8.6753 | 11.112 | 11.112 | 497.5049 | 4.8675 | 0 | 2187.9462 | 0 | 0 | 0 | 4.8675 | 0 | 0 | 2187.9462
3 | 18 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 496.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 495.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 495.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 483.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 478.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 18 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 479.9609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 474.8897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 476.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 481.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 484.0961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 490.9536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 493.9984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 495.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 7 | 1.03 | 47.1251 | 48.1551 | 47.2086 | 4.8705 | 21.311 | 21.311 | 495.2342 | 48.1551 | 0 | 21574.727 | 0 | 0 | 0 | 48.1551 | 0 | 0 | 21574.727
3 | 19 | 8 | 0 | 3.8067 | 3.8067 | 48 | 4.8451 | 1.6756 | 1.6756 | 495.0429 | 3.8067 | 0 | 1701.7435 | 0 | 0 | 0 | 3.8067 | 0 | 0 | 1701.7435
3 | 19 | 9 | 0.074167 | 14.4133 | 14.4875 | 47.8106 | 6.3789 | 9.4228 | 9.4228 | 496.2741 | 14.4875 | 0 | 6497.1116 | 0 | 0 | 0 | 14.4875 | 0 | 0 | 6497.1116
3 | 19 | 10 | 0.85167 | 584.3004 | 585.1521 | 47.9461 | 8.4804 | 1101.2613 | 288 | 491.8819 | 153.028 | 432.1241 | 67934.5948 | 45.0587 | 0 | 0 | 153.028 | 432.1241 | 0 | 67934.5948
3 | 19 | 11 | 0.60917 | 528.0724 | 528.6816 | 47.9574 | 9.4549 | 8160.0042 | 288 | 483.1601 | 18.6593 | 510.0222 | 8120.5947 | 53.1814 | 0 | 0 | 18.6593 | 510.0222 | 0 | 8120.5947
3 | 19 | 12 | 0.58 | 223.4568 | 224.0368 | 47.9042 | 9.8362 | 0 | 0 | 486.1346 | 0 | 224.0368 | 0 | 23.3609 | 0 | 0 | 0 | 224.0368 | 0 | 0
3 | 19 | 13 | 0.1725 | 80.8004 | 80.9729 | 47.9212 | 9.6159 | 0 | 0 | 480.8095 | 0 | 80.9729 | 0 | 8.4433 | 0 | 0 | 0 | 80.9729 | 0 | 0
3 | 19 | 14 | 0 | 3.639 | 3.639 | 48 | 9.5227 | 112.5468 | 112.5468 | 478.9154 | 3.639 | 0 | 1568.0995 | 0 | 0 | 0 | 3.639 | 0 | 0 | 1568.0995
3 | 19 | 15 | 4.5825 | 124.9867 | 129.5692 | 46.6914 | 10.7175 | 0 | 0 | 473.6035 | 0 | 129.5692 | 0 | 13.5105 | 0 | 0 | 0 | 129.5692 | 0 | 0
3 | 19 | 16 | 3.2308 | 3.2558 | 6.4867 | 29.5713 | 12.0564 | 0 | 0 | 463.0854 | 0 | 6.4867 | 0 | 0.67638 | 0 | 0 | 0 | 6.4867 | 0 | 0
3 | 19 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 474.5793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 483.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 483.5332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 479.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 467.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 449.3856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 19 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 450.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 449.8994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 459.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 482.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 478.7444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 483.3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 488.3107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 482.3979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 487.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 8 | 22.4975 | 18.1044 | 40.6019 | 27.4983 | 5.4976 | 20.7214 | 20.7214 | 498.1353 | 40.6019 | 0 | 19108.7473 | 0 | 0 | 0 | 40.6019 | 0 | 0 | 19108.7473
3 | 20 | 9 | 0 | 2.8109 | 2.8109 | 48 | 6.4043 | 1.8428 | 1.8428 | 499.9031 | 2.8109 | 0 | 1270.2431 | 0 | 0 | 0 | 2.8109 | 0 | 0 | 1270.2431
3 | 20 | 10 | 0 | 0.92975 | 0.92975 | 48 | 8.5991 | 1.9592 | 1.9592 | 506.0765 | 0.92975 | 0 | 425.8966 | 0 | 0 | 0 | 0.92975 | 0 | 0 | 425.8966
3 | 20 | 11 | 0 | 4.8145 | 4.8145 | 48 | 9.6413 | 0 | 0 | 502.4995 | 0 | 4.8145 | 0 | 0.50202 | 0 | 0 | 0 | 4.8145 | 0 | 0
3 | 20 | 12 | 0 | 6.2883 | 6.2883 | 48 | 9.7176 | 0 | 0 | 503.7872 | 0 | 6.2883 | 0 | 0.6557 | 0 | 0 | 0 | 6.2883 | 0 | 0
3 | 20 | 13 | 0 | 5.5074 | 5.5074 | 48 | 9.7939 | 0 | 0 | 501.0121 | 0 | 5.5074 | 0 | 0.57427 | 0 | 0 | 0 | 5.5074 | 0 | 0
3 | 20 | 14 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 505.7939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 504.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 16 | 0 | 0.23413 | 0.23413 | 48 | 11.0904 | 0 | 0 | 495.9899 | 0 | 0.23413 | 0 | 0.024413 | 0 | 0 | 0 | 0.23413 | 0 | 0
3 | 20 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 499.617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 510.0875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 511.9283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 497.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 481.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 464.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 20 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 471.2597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 469.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 1 | 50.8492 | 0 | 50.8492 | 11 | 3.3198 | 16.938 | 16.938 | 471.3466 | 50.8492 | 0 | 23408.2401 | 0 | 0 | 0 | 50.8492 | 0 | 0 | 23408.2401
3 | 21 | 2 | 8.4606 | 0 | 8.4606 | 11 | 3.2096 | 2.7696 | 2.7696 | 480.7025 | 8.4606 | 0 | 3973.9449 | 0 | 0 | 0 | 8.4606 | 0 | 0 | 3973.9449
3 | 21 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 478.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 486.0752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 491.2938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 500.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 501.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 8 | 18.6283 | 35.544 | 54.1724 | 35.2768 | 6.2094 | 33.468 | 33.468 | 498.2981 | 54.1724 | 0 | 25082.9582 | 0 | 0 | 0 | 54.1724 | 0 | 0 | 25082.9582
3 | 21 | 9 | 0 | 2.586 | 2.586 | 48 | 7.328 | 2.3876 | 2.3876 | 493.1108 | 2.586 | 0 | 1151.0566 | 0 | 0 | 0 | 2.586 | 0 | 0 | 1151.0566
3 | 21 | 10 | 48.281 | 141.1923 | 189.4733 | 38.5718 | 8.5482 | 379.7891 | 288 | 494.8454 | 143.6806 | 45.7927 | 65557.6709 | 4.7749 | 0 | 0 | 143.6806 | 45.7927 | 0 | 65557.6709
3 | 21 | 11 | 79.525 | 72.4419 | 151.9669 | 28.6377 | 9.1838 | 780.8624 | 288 | 486.3459 | 56.0489 | 95.918 | 25654.0279 | 10.0016 | 0 | 0 | 56.0489 | 95.918 | 0 | 25654.0279
3 | 21 | 12 | 28.8525 | 48.5799 | 77.4324 | 34.2132 | 9.8701 | 0 | 0 | 479.5287 | 0 | 77.4324 | 0 | 8.0741 | 0 | 0 | 0 | 77.4324 | 0 | 0
3 | 21 | 13 | 103.0308 | 491.2318 | 594.2626 | 41.5851 | 9.6668 | 0 | 0 | 477.2428 | 0 | 594.2626 | 0 | 61.9653 | 0 | 0 | 0 | 594.2626 | 0 | 0
3 | 21 | 14 | 21.1416 | 76.4062 | 97.5479 | 39.981 | 10.2684 | 0 | 0 | 480.9821 | 0 | 97.5479 | 0 | 10.1716 | 0 | 0 | 0 | 97.5479 | 0 | 0
3 | 21 | 15 | 0 | 3.4075 | 3.4075 | 48 | 11.226 | 0 | 0 | 480.8343 | 0 | 3.4075 | 0 | 0.35531 | 0 | 0 | 0 | 3.4075 | 0 | 0
3 | 21 | 16 | 43.7392 | 48.6119 | 92.351 | 30.4761 | 11.853 | 0 | 0 | 474.992 | 0 | 92.351 | 0 | 9.6297 | 0 | 0 | 0 | 92.351 | 0 | 0
3 | 21 | 17 | 9.6617 | 48.8782 | 58.5399 | 41.8934 | 11.7514 | 0 | 0 | 483.3405 | 0 | 58.5399 | 0 | 6.1041 | 0 | 0 | 0 | 58.5399 | 0 | 0
3 | 21 | 18 | 0 | 0.49 | 0.49 | 48 | 12.4971 | 0 | 0 | 485.2587 | 0 | 0.49 | 0 | 0.051094 | 0 | 0 | 0 | 0.49 | 0 | 0
3 | 21 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 476.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 457.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 431.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 415.7989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 21 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 413.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 412.3376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 417.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 438.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 447.3844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 474.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 482.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 482.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 482.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 8 | 12.975 | 30.9456 | 43.9206 | 37.0695 | 6.2094 | 27.1344 | 27.1344 | 485.0819 | 43.9206 | 0 | 19676.975 | 0 | 0 | 0 | 43.9206 | 0 | 0 | 19676.975
3 | 22 | 9 | 8.0187 | 44.4211 | 52.4399 | 42.3422 | 7.311 | 48.0563 | 48.0563 | 489.221 | 52.4399 | 0 | 23434.2669 | 0 | 0 | 0 | 52.4399 | 0 | 0 | 23434.2669
3 | 22 | 10 | 44.4758 | 139.4187 | 183.8945 | 39.0514 | 8.0567 | 250.4698 | 250.4698 | 495.7326 | 183.8945 | 0 | 83981.1648 | 0 | 0 | 0 | 183.8945 | 0 | 0 | 83981.1648
3 | 22 | 11 | 24.7575 | 191.4969 | 216.2544 | 43.7641 | 9.3109 | 1616.7487 | 288 | 497.54 | 38.5225 | 177.7318 | 17480.5963 | 18.5326 | 0 | 0 | 38.5225 | 177.7318 | 0 | 17480.5963
3 | 22 | 12 | 36.0044 | 75.7842 | 111.7886 | 36.0832 | 9.0058 | 399.5135 | 288 | 490.7482 | 80.5858 | 31.2028 | 36639.5277 | 3.2536 | 0 | 0 | 80.5858 | 31.2028 | 0 | 36639.5277
3 | 22 | 13 | 0 | 15.5846 | 15.5846 | 48 | 8.4889 | 29.5561 | 29.5561 | 490.1601 | 15.5846 | 0 | 6890.8978 | 0 | 0 | 0 | 15.5846 | 0 | 0 | 6890.8978
3 | 22 | 14 | 3.9869 | 6.4832 | 10.4701 | 33.9108 | 8.938 | 33.5293 | 33.5293 | 492.3419 | 10.4701 | 0 | 4799.8282 | 0 | 0 | 0 | 10.4701 | 0 | 0 | 4799.8282
3 | 22 | 15 | 0 | 2.6658 | 2.6658 | 48 | 9.6075 | 0 | 0 | 496.3227 | 0 | 2.6658 | 0 | 0.27796 | 0 | 0 | 0 | 2.6658 | 0 | 0
3 | 22 | 16 | 16.68 | 37.4788 | 54.1588 | 36.6046 | 10.9718 | 0 | 0 | 484.8438 | 0 | 54.1588 | 0 | 5.6473 | 0 | 0 | 0 | 54.1588 | 0 | 0
3 | 22 | 17 | 5.2696 | 1.0775 | 6.3471 | 17.2812 | 10.3786 | 0 | 0 | 496.5937 | 0 | 6.3471 | 0 | 0.66183 | 0 | 0 | 0 | 6.3471 | 0 | 0
3 | 22 | 18 | 19.7867 | 30.1165 | 49.9032 | 33.3295 | 11.0734 | 0 | 0 | 501.3803 | 0 | 49.9032 | 0 | 5.2035 | 0 | 0 | 0 | 49.9032 | 0 | 0
3 | 22 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 509.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 502.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 493.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 22 | 22 | 11.7407 | 0 | 11.7407 | 11 | 5.2264 | 5.6196 | 5.6196 | 493.5672 | 11.7407 | 0 | 5665.6743 | 0 | 0 | 0 | 11.7407 | 0 | 0 | 5665.6743
3 | 22 | 23 | 12.2317 | 0 | 12.2317 | 11 | 4.2265 | 4.7632 | 4.7632 | 490.5656 | 12.2317 | 0 | 5865.8867 | 0 | 0 | 0 | 12.2317 | 0 | 0 | 5865.8867
3 | 23 | 0 | 6.4558 | 0 | 6.4558 | 11 | 4.1757 | 2.4904 | 2.4904 | 493.3418 | 6.4558 | 0 | 3113.9181 | 0 | 0 | 0 | 6.4558 | 0 | 0 | 3113.9181
3 | 23 | 1 | 8.3658 | 0 | 8.3658 | 11 | 3.8791 | 3.0596 | 3.0596 | 494.4128 | 8.3658 | 0 | 4044.1511 | 0 | 0 | 0 | 8.3658 | 0 | 0 | 4044.1511
3 | 23 | 2 | 36.196 | 0 | 36.196 | 11 | 3.8197 | 13.1016 | 13.1016 | 495.9156 | 36.196 | 0 | 17551.9955 | 0 | 0 | 0 | 36.196 | 0 | 0 | 17551.9955
3 | 23 | 3 | 53.8561 | 0 | 53.8561 | 11 | 3.4638 | 18.3615 | 18.3615 | 496.8586 | 53.8561 | 0 | 26166.4607 | 0 | 0 | 0 | 53.8561 | 0 | 0 | 26166.4607
3 | 23 | 4 | 92.0383 | 0 | 92.0383 | 11 | 3.4045 | 31.0782 | 31.0782 | 504.4007 | 92.0383 | 0 | 45411.7729 | 0 | 0 | 0 | 92.0383 | 0 | 0 | 45411.7729
3 | 23 | 5 | 54.6608 | 0 | 54.6608 | 11 | 3.6418 | 19.1933 | 19.1933 | 501.3183 | 54.6608 | 0 | 26801.1982 | 0 | 0 | 0 | 54.6608 | 0 | 0 | 26801.1982
3 | 23 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 500.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 7 | 0 | 0.69788 | 0.69788 | 48 | 4.6502 | 0.29507 | 0.29507 | 503.7591 | 0.69788 | 0 | 318.0653 | 0 | 0 | 0 | 0.69788 | 0 | 0 | 318.0653
3 | 23 | 8 | 52.7888 | 481.7438 | 534.5325 | 44.346 | 5.1417 | 250.9761 | 250.9761 | 502.6672 | 534.5325 | 0 | 244987.6227 | 0 | 0 | 0 | 534.5325 | 0 | 0 | 244987.6227
3 | 23 | 9 | 210.6919 | 1028.5556 | 1239.2475 | 41.7094 | 6.6161 | 870.3237 | 288 | 507.4112 | 410.0811 | 829.1664 | 190975.4686 | 86.4594 | 0 | 0 | 410.0811 | 829.1664 | 0 | 190975.4686
3 | 23 | 10 | 76.7875 | 760.5474 | 837.3349 | 44.6069 | 6.9721 | 667.9988 | 288 | 506.7719 | 361.0073 | 476.3276 | 166844.9073 | 49.6679 | 0 | 0 | 361.0073 | 476.3276 | 0 | 166844.9073
3 | 23 | 11 | 79.3183 | 608.0967 | 687.415 | 43.7307 | 8.5652 | 1400.6669 | 288 | 492.4005 | 141.3438 | 546.0713 | 63416.6774 | 56.9403 | 0 | 0 | 141.3438 | 546.0713 | 0 | 63416.6774
3 | 23 | 12 | 72.2942 | 769.1662 | 841.4604 | 44.8211 | 7.8957 | 1037.1986 | 288 | 486.9743 | 233.6492 | 607.8112 | 103308.7145 | 63.3781 | 0 | 0 | 233.6492 | 607.8112 | 0 | 103308.7145
3 | 23 | 13 | 74.5925 | 601.5917 | 676.1842 | 43.9184 | 7.4381 | 656.2593 | 288 | 478.7308 | 296.744 | 379.4401 | 129027.9829 | 39.5652 | 0 | 0 | 296.744 | 379.4401 | 0 | 129027.9829
3 | 23 | 14 | 72.5942 | 701.9529 | 774.547 | 44.5322 | 7.2771 | 699.4002 | 288 | 480.1736 | 318.9441 | 455.603 | 138945.2263 | 47.5069 | 0 | 0 | 318.9441 | 455.603 | 0 | 138945.2263
3 | 23 | 15 | 62.805 | 927.4474 | 990.2524 | 45.6533 | 7.3449 | 921.175 | 288 | 488.2292 | 309.5967 | 680.6558 | 137020.0298 | 70.9738 | 0 | 0 | 309.5967 | 680.6558 | 0 | 137020.0298
3 | 23 | 16 | 66.8042 | 900.1943 | 966.9985 | 45.4439 | 6.9975 | 779.0042 | 288 | 481.6864 | 357.502 | 609.4965 | 155957.5836 | 63.5538 | 0 | 0 | 357.502 | 609.4965 | 0 | 155957.5836
3 | 23 | 17 | 234.2108 | 630.7783 | 864.9892 | 37.9816 | 7.167 | 745.5608 | 288 | 488.8101 | 334.1336 | 530.8556 | 150636.9375 | 55.3537 | 0 | 0 | 334.1336 | 530.8556 | 0 | 150636.9375
3 | 23 | 18 | 19.5517 | 2.7786 | 22.3303 | 15.604 | 6.7094 | 16.19 | 16.19 | 484.2549 | 22.3303 | 0 | 10465.1154 | 0 | 0 | 0 | 22.3303 | 0 | 0 | 10465.1154
3 | 23 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 480.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 467.8655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 440.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 430.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 23 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 441.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 445.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 454.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 465.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 470.5185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 477.6413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 481.0196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 489.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 7 | 0 | 0.265 | 0.265 | 48 | 6.1924 | 0.1629 | 0.1629 | 488.7205 | 0.265 | 0 | 116.7909 | 0 | 0 | 0 | 0.265 | 0 | 0 | 116.7909
3 | 24 | 8 | 11.7425 | 168.0951 | 179.8376 | 45.5841 | 6.8788 | 138.5364 | 138.5364 | 487.4097 | 179.8376 | 0 | 79456.8599 | 0 | 0 | 0 | 179.8376 | 0 | 0 | 79456.8599
3 | 24 | 9 | 2.05 | 58.1309 | 60.1809 | 46.7396 | 7.3195 | 55.3561 | 55.3561 | 482.3892 | 60.1809 | 0 | 26217.7826 | 0 | 0 | 0 | 60.1809 | 0 | 0 | 26217.7826
3 | 24 | 10 | 0 | 19.9256 | 19.9256 | 48 | 7.4805 | 19.7269 | 19.7269 | 473.3145 | 19.9256 | 0 | 8474.6649 | 0 | 0 | 0 | 19.9256 | 0 | 0 | 8474.6649
3 | 24 | 11 | 0 | 16.8169 | 16.8169 | 48 | 7.2263 | 14.8587 | 14.8587 | 466.9053 | 16.8169 | 0 | 7044.6863 | 0 | 0 | 0 | 16.8169 | 0 | 0 | 7044.6863
3 | 24 | 12 | 2.645 | 170.3975 | 173.0425 | 47.4344 | 7.8703 | 210.1426 | 210.1426 | 459.8605 | 173.0425 | 0 | 71367.2496 | 0 | 0 | 0 | 173.0425 | 0 | 0 | 71367.2496
3 | 24 | 13 | 7.06 | 483.0193 | 490.0793 | 47.467 | 8.1754 | 723.471 | 288 | 453.2451 | 195.0912 | 294.9881 | 79163.7387 | 30.7592 | 0 | 0 | 195.0912 | 294.9881 | 0 | 79163.7387
3 | 24 | 14 | 6.1133 | 450.4649 | 456.5782 | 47.5046 | 8.2431 | 707.9349 | 288 | 453.55 | 185.7438 | 270.8344 | 75420.4354 | 28.2406 | 0 | 0 | 185.7438 | 270.8344 | 0 | 75420.4354
3 | 24 | 15 | 10.5017 | 466.9068 | 477.4085 | 47.1861 | 7.4212 | 459.7206 | 288 | 454.1106 | 299.0809 | 178.3276 | 121703.3337 | 18.5947 | 0 | 0 | 299.0809 | 178.3276 | 0 | 121703.3337
3 | 24 | 16 | 15.7675 | 236.6755 | 252.443 | 45.689 | 7.3195 | 232.2042 | 232.2042 | 453.3062 | 252.443 | 0 | 102900.0926 | 0 | 0 | 0 | 252.443 | 0 | 0 | 102900.0926
3 | 24 | 17 | 67.0235 | 363.784 | 430.8074 | 42.2437 | 7.2686 | 387.5905 | 288 | 470.7099 | 320.1125 | 110.695 | 137157.3963 | 11.5425 | 0 | 0 | 320.1125 | 110.695 | 0 | 137157.3963
3 | 24 | 18 | 0 | 0.060833 | 0.060833 | 48 | 6.9297 | 0.047758 | 0.047758 | 465.6071 | 0.060833 | 0 | 25.4044 | 0 | 0 | 0 | 0.060833 | 0 | 0 | 25.4044
3 | 24 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 455.9507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 433.3706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 418.7729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 413.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 24 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 422.3955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 412.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 409.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 420.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 424.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 433.6649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 446.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 455.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 7 | 0 | 0.79 | 0.79 | 48 | 6.006 | 0.46037 | 0.46037 | 458.8969 | 0.79 | 0 | 324.6086 | 0 | 0 | 0 | 0.79 | 0 | 0 | 324.6086
3 | 25 | 8 | 40.6692 | 40.6926 | 81.3617 | 29.5053 | 6.6246 | 57.3036 | 57.3036 | 458.7325 | 81.3617 | 0 | 34922.6744 | 0 | 0 | 0 | 81.3617 | 0 | 0 | 34922.6744
3 | 25 | 9 | 12.4483 | 4.1608 | 16.6092 | 20.269 | 7.1924 | 14.4677 | 14.4677 | 459.6104 | 16.6092 | 0 | 7297.0933 | 0 | 0 | 0 | 16.6092 | 0 | 0 | 7297.0933
3 | 25 | 10 | 45.6718 | 153.2896 | 198.9614 | 39.5066 | 7.0398 | 162.944 | 162.944 | 465.271 | 198.9614 | 0 | 84710.6677 | 0 | 0 | 0 | 198.9614 | 0 | 0 | 84710.6677
3 | 25 | 11 | 70.9183 | 671.6062 | 742.5245 | 44.4661 | 7.2093 | 651.394 | 288 | 456.2637 | 328.2914 | 414.2331 | 135189.6301 | 43.1932 | 0 | 0 | 328.2914 | 414.2331 | 0 | 135189.6301
3 | 25 | 12 | 78.525 | 543.8233 | 622.3483 | 43.3315 | 7.9296 | 782.7751 | 288 | 455.0528 | 228.9755 | 393.3728 | 94274.0878 | 41.018 | 0 | 0 | 228.9755 | 393.3728 | 0 | 94274.0878
3 | 25 | 13 | 81.0825 | 764.1316 | 845.2141 | 44.4505 | 8.2601 | 1327.2213 | 288 | 465.2634 | 183.407 | 661.8071 | 77180.0198 | 69.0084 | 0 | 0 | 183.407 | 661.8071 | 0 | 77180.0198
3 | 25 | 14 | 138.9058 | 1171.3187 | 1310.2245 | 44.0774 | 8.5313 | 2584.2435 | 288 | 475.0936 | 146.0175 | 1164.207 | 62935.8832 | 121.3949 | 0 | 0 | 146.0175 | 1164.207 | 0 | 62935.8832
3 | 25 | 15 | 78.65 | 867.4842 | 946.1342 | 44.9243 | 8.4041 | 1666.1387 | 288 | 476.141 | 163.5438 | 782.5904 | 70522.8191 | 81.6027 | 0 | 0 | 163.5438 | 782.5904 | 0 | 70522.8191
3 | 25 | 16 | 220.2611 | 1245.4327 | 1465.6938 | 42.4397 | 9.1753 | 7377.4858 | 288 | 475.2307 | 57.2173 | 1408.4765 | 24763.1311 | 146.8655 | 0 | 0 | 57.2173 | 1408.4765 | 0 | 24763.1311
3 | 25 | 17 | 244.0534 | 777.2033 | 1021.2568 | 39.158 | 8.6753 | 2331.4468 | 288 | 471.4183 | 126.1543 | 895.1025 | 54531.4803 | 93.3347 | 0 | 0 | 126.1543 | 895.1025 | 0 | 54531.4803
3 | 25 | 18 | 28.5496 | 91.8181 | 120.3677 | 39.2241 | 9.0397 | 456.6585 | 288 | 475.3187 | 75.9121 | 44.4556 | 33104.8465 | 4.6355 | 0 | 0 | 75.9121 | 44.4556 | 0 | 33104.8465
3 | 25 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 466.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 441.9033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 421.8201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 404.7999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 25 | 23 | 10.5525 | 0 | 10.5525 | 11 | 4.4722 | 4.3066 | 4.3066 | 399.6202 | 10.5525 | 0 | 4100.9145 | 0 | 0 | 0 | 10.5525 | 0 | 0 | 4100.9145
3 | 26 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 398.1386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 399.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 403.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 408.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 4 | 0.2828 | 0 | 0.2828 | 11 | 3.0317 | 0.090063 | 0.090063 | 413.1245 | 0.2828 | 0 | 113.721 | 0 | 0 | 0 | 0.2828 | 0 | 0 | 113.721
3 | 26 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 429.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 451.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 7 | 19.4683 | 115.8092 | 135.2775 | 42.6752 | 4.8705 | 59.8668 | 59.8668 | 464.5992 | 135.2775 | 0 | 57076.8194 | 0 | 0 | 0 | 135.2775 | 0 | 0 | 57076.8194
3 | 26 | 8 | 30.3961 | 203.2388 | 233.6349 | 43.1863 | 4.8451 | 102.8408 | 102.8408 | 461.3968 | 233.6349 | 0 | 97708.5902 | 0 | 0 | 0 | 233.6349 | 0 | 0 | 97708.5902
3 | 26 | 9 | 44.7442 | 329.044 | 373.7881 | 43.5709 | 6.3789 | 243.1159 | 243.1159 | 460.6524 | 373.7881 | 0 | 155900.0876 | 0 | 0 | 0 | 373.7881 | 0 | 0 | 155900.0876
3 | 26 | 10 | 32.4175 | 521.0654 | 553.4829 | 45.8329 | 8.4804 | 1041.6596 | 288 | 459.9032 | 153.028 | 400.4549 | 63364.3508 | 41.7565 | 0 | 0 | 153.028 | 400.4549 | 0 | 63364.3508
3 | 26 | 11 | 47.6758 | 804.4935 | 852.1693 | 45.93 | 9.4549 | 13152.918 | 288 | 450.0636 | 18.6593 | 833.51 | 7540.8673 | 86.9123 | 0 | 0 | 18.6593 | 833.51 | 0 | 7540.8673
3 | 26 | 12 | 63.0925 | 610.3496 | 673.4421 | 44.5336 | 9.8362 | 0 | 0 | 454.2168 | 0 | 673.4421 | 0 | 70.2216 | 0 | 0 | 0 | 673.4421 | 0 | 0
3 | 26 | 13 | 85.4317 | 1204.1005 | 1289.5323 | 45.5487 | 9.6159 | 0 | 0 | 460.2493 | 0 | 1289.5323 | 0 | 134.4629 | 0 | 0 | 0 | 1289.5323 | 0 | 0
3 | 26 | 14 | 216.8663 | 1293.2329 | 1510.0993 | 42.6864 | 9.5227 | 46704.3263 | 288 | 464.5208 | 9.312 | 1500.7873 | 3928.1031 | 156.491 | 0 | 0 | 9.312 | 1500.7873 | 0 | 3928.1031
3 | 26 | 15 | 136.9352 | 1066.6026 | 1203.5378 | 43.7902 | 10.7175 | 0 | 0 | 469.7038 | 0 | 1203.5378 | 0 | 125.496 | 0 | 0 | 0 | 1203.5378 | 0 | 0
3 | 26 | 16 | 52.55 | 315.2398 | 367.7898 | 42.7134 | 12.0564 | 0 | 0 | 462.6442 | 0 | 367.7898 | 0 | 38.3504 | 0 | 0 | 0 | 367.7898 | 0 | 0
3 | 26 | 17 | 12.0663 | 1.7283 | 13.7946 | 15.6358 | 11.8107 | 0 | 0 | 469.0901 | 0 | 13.7946 | 0 | 1.4384 | 0 | 0 | 0 | 13.7946 | 0 | 0
3 | 26 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 474.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 466.2462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 439.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 432.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 26 | 22 | 1.9098 | 0 | 1.9098 | 11 | 5.04 | 0.87664 | 0.87664 | 418.1345 | 1.9098 | 0 | 777.5328 | 0 | 0 | 0 | 1.9098 | 0 | 0 | 777.5328
3 | 26 | 23 | 128.263 | 0 | 128.263 | 11 | 3.3504 | 42.9341 | 42.9341 | 412.7686 | 128.263 | 0 | 51532.046 | 0 | 0 | 0 | 128.263 | 0 | 0 | 51532.046
3 | 27 | 0 | 1.3548 | 0 | 1.3548 | 11 | 3.252 | 0.44647 | 0.44647 | 427.1679 | 1.3548 | 0 | 563.8316 | 0 | 0 | 0 | 1.3548 | 0 | 0 | 563.8316
3 | 27 | 1 | 4.6653 | 0 | 4.6653 | 11 | 3.1418 | 1.5112 | 1.5112 | 431.3058 | 4.6653 | 0 | 1960.8672 | 0 | 0 | 0 | 4.6653 | 0 | 0 | 1960.8672
3 | 27 | 2 | 20.3463 | 0 | 20.3463 | 11 | 3.0401 | 6.4881 | 6.4881 | 446.737 | 20.3463 | 0 | 8865.6537 | 0 | 0 | 0 | 20.3463 | 0 | 0 | 8865.6537
3 | 27 | 3 | 33.396 | 0 | 33.396 | 11 | 3.1249 | 10.7889 | 10.7889 | 466.8969 | 33.396 | 0 | 15225.1103 | 0 | 0 | 0 | 33.396 | 0 | 0 | 15225.1103
3 | 27 | 4 | 44.9178 | 0 | 44.9178 | 11 | 3.3706 | 15.0846 | 15.0846 | 486.3429 | 44.9178 | 0 | 21351.3658 | 0 | 0 | 0 | 44.9178 | 0 | 0 | 21351.3658
3 | 27 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 491.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 488.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 483.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 8 | 0 | 3.595 | 3.595 | 48 | 5.4976 | 1.8347 | 1.8347 | 484.6743 | 3.595 | 0 | 1569.8442 | 0 | 0 | 0 | 3.595 | 0 | 0 | 1569.8442
3 | 27 | 9 | 29.2575 | 36.0287 | 65.2862 | 31.4187 | 6.4043 | 42.8017 | 42.8017 | 491.9084 | 65.2862 | 0 | 30063.6217 | 0 | 0 | 0 | 65.2862 | 0 | 0 | 30063.6217
3 | 27 | 10 | 26.238 | 63.4181 | 89.6562 | 37.1719 | 8.5991 | 188.9293 | 188.9293 | 493.1499 | 89.6562 | 0 | 40881.2502 | 0 | 0 | 0 | 89.6562 | 0 | 0 | 40881.2502
3 | 27 | 11 | 54.1805 | 178.8091 | 232.9896 | 39.3958 | 9.6413 | 0 | 0 | 498.2852 | 0 | 232.9896 | 0 | 24.2944 | 0 | 0 | 0 | 232.9896 | 0 | 0
3 | 27 | 12 | 27.7414 | 88.634 | 116.3753 | 39.18 | 9.7176 | 0 | 0 | 485.7159 | 0 | 116.3753 | 0 | 12.1348 | 0 | 0 | 0 | 116.3753 | 0 | 0
3 | 27 | 13 | 78.75 | 533.7326 | 612.4826 | 43.2427 | 9.7939 | 0 | 0 | 487.5135 | 0 | 612.4826 | 0 | 63.8652 | 0 | 0 | 0 | 612.4826 | 0 | 0
3 | 27 | 14 | 80.5283 | 450.1948 | 530.7232 | 42.3859 | 9.4634 | 8738.7235 | 288 | 490.1507 | 17.4909 | 513.2323 | 7831.8163 | 53.5161 | 0 | 0 | 17.4909 | 513.2323 | 0 | 7831.8163
3 | 27 | 15 | 40.3073 | 195.5739 | 235.8812 | 41.6774 | 10.5311 | 0 | 0 | 483.1845 | 0 | 235.8812 | 0 | 24.596 | 0 | 0 | 0 | 235.8812 | 0 | 0
3 | 27 | 16 | 26.3963 | 67.6904 | 94.0867 | 37.6195 | 11.0904 | 0 | 0 | 462.5023 | 0 | 94.0867 | 0 | 9.8107 | 0 | 0 | 0 | 94.0867 | 0 | 0
3 | 27 | 17 | 37.5452 | 283.6119 | 321.1571 | 43.6745 | 11.1073 | 0 | 0 | 472.3845 | 0 | 321.1571 | 0 | 33.4879 | 0 | 0 | 0 | 321.1571 | 0 | 0
3 | 27 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 482.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 480.5778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 464.4205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 433.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 419.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 27 | 23 | 122.4684 | 0 | 122.4684 | 11 | 4.3028 | 48.3786 | 48.3786 | 419.1462 | 122.4684 | 0 | 49985.0249 | 0 | 0 | 0 | 122.4684 | 0 | 0 | 49985.0249
3 | 28 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 408.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 407.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 428.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 451.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 473.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 477.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 483.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 485.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 8 | 8.1558 | 499.3252 | 507.481 | 47.4054 | 6.2094 | 313.5251 | 288 | 481.8598 | 466.1654 | 41.3156 | 202527.591 | 4.3081 | 0 | 0 | 466.1654 | 41.3156 | 0 | 202527.591
3 | 28 | 9 | 5.8783 | 581.7478 | 587.6261 | 47.6299 | 7.328 | 542.5397 | 288 | 486.1147 | 311.9335 | 275.6926 | 136778.1323 | 28.7472 | 0 | 0 | 311.9335 | 275.6926 | 0 | 136778.1323
3 | 28 | 10 | 12.6992 | 574.9578 | 587.657 | 47.2004 | 8.5482 | 1177.9267 | 288 | 485.362 | 143.6806 | 443.9764 | 62955.3227 | 46.2946 | 0 | 0 | 143.6806 | 443.9764 | 0 | 62955.3227
3 | 28 | 11 | 34.0908 | 318.919 | 353.0098 | 44.4268 | 9.1838 | 1813.8959 | 288 | 487.3646 | 56.0489 | 296.9609 | 24826.1641 | 30.9649 | 0 | 0 | 56.0489 | 296.9609 | 0 | 24826.1641
3 | 28 | 12 | 44.9117 | 709.4807 | 754.3924 | 45.7973 | 9.8701 | 0 | 0 | 485.4496 | 0 | 754.3924 | 0 | 78.6625 | 0 | 0 | 0 | 754.3924 | 0 | 0
3 | 28 | 13 | 41.6733 | 591.5974 | 633.2707 | 45.5652 | 9.6668 | 0 | 0 | 487.1811 | 0 | 633.2707 | 0 | 66.0328 | 0 | 0 | 0 | 633.2707 | 0 | 0
3 | 28 | 14 | 22.2784 | 374.5113 | 396.7897 | 45.9226 | 10.2684 | 0 | 0 | 487.0272 | 0 | 396.7897 | 0 | 41.3743 | 0 | 0 | 0 | 396.7897 | 0 | 0
3 | 28 | 15 | 5.7756 | 201.5448 | 207.3204 | 46.9692 | 11.226 | 0 | 0 | 486.0412 | 0 | 207.3204 | 0 | 21.6178 | 0 | 0 | 0 | 207.3204 | 0 | 0
3 | 28 | 16 | 49.7108 | 485.6787 | 535.3895 | 44.5646 | 11.853 | 0 | 0 | 463.5631 | 0 | 535.3895 | 0 | 55.8265 | 0 | 0 | 0 | 535.3895 | 0 | 0
3 | 28 | 17 | 32.59 | 605.0952 | 637.6852 | 46.1091 | 11.7514 | 0 | 0 | 475.8074 | 0 | 637.6852 | 0 | 66.4931 | 0 | 0 | 0 | 637.6852 | 0 | 0
3 | 28 | 18 | 0 | 0.26079 | 0.26079 | 48 | 12.4971 | 0 | 0 | 481.0262 | 0 | 0.26079 | 0 | 0.027193 | 0 | 0 | 0 | 0.26079 | 0 | 0
3 | 28 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 485.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 462.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 433.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 419.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 28 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 419.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 408.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 407.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 428.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 473.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 477.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 483.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 7 | 0 | 1.26 | 1.26 | 48 | 5.0146 | 0.57517 | 0.57517 | 485.6016 | 1.26 | 0 | 551.378 | 0 | 0 | 0 | 1.26 | 0 | 0 | 551.378
3 | 29 | 8 | 4.5792 | 493.3426 | 497.9217 | 47.6597 | 6.2094 | 307.6193 | 288 | 481.8598 | 466.1654 | 31.7564 | 202409.0163 | 3.3113 | 0 | 0 | 466.1654 | 31.7564 | 0 | 202409.0163
3 | 29 | 9 | 0.0625 | 271.4749 | 271.5374 | 47.9915 | 7.311 | 248.8392 | 248.8392 | 486.1147 | 271.5374 | 0 | 118966.8656 | 0 | 0 | 0 | 271.5374 | 0 | 0 | 118966.8656
3 | 29 | 10 | 0 | 244.7909 | 244.7909 | 48 | 8.0567 | 333.4124 | 288 | 485.362 | 211.4491 | 33.3417 | 92479.8256 | 3.4766 | 0 | 0 | 211.4491 | 33.3417 | 0 | 92479.8256
3 | 29 | 11 | 0 | 72.8579 | 72.8579 | 48 | 9.3109 | 544.6959 | 288 | 487.3646 | 38.5225 | 34.3353 | 16925.4367 | 3.5802 | 0 | 0 | 38.5225 | 34.3353 | 0 | 16925.4367
3 | 29 | 12 | 2.1442 | 113.0683 | 115.2125 | 47.3114 | 9.0058 | 411.7501 | 288 | 485.4496 | 80.5858 | 34.6267 | 35307.6955 | 3.6106 | 0 | 0 | 80.5858 | 34.6267 | 0 | 35307.6955
3 | 29 | 13 | 1.2567 | 153.6434 | 154.9 | 47.6998 | 8.4889 | 293.7662 | 288 | 487.1811 | 151.8596 | 3.0405 | 66739.4402 | 0.31704 | 0 | 0 | 151.8596 | 3.0405 | 0 | 66739.4402
3 | 29 | 14 | 0 | 49.7096 | 49.7096 | 48 | 8.938 | 159.189 | 159.189 | 487.0272 | 49.7096 | 0 | 21823.871 | 0 | 0 | 0 | 49.7096 | 0 | 0 | 21823.871
3 | 29 | 15 | 9.3347 | 159.9715 | 169.3062 | 45.96 | 9.6075 | 0 | 0 | 486.0412 | 0 | 169.3062 | 0 | 17.654 | 0 | 0 | 0 | 169.3062 | 0 | 0
3 | 29 | 16 | 0 | 15.9668 | 15.9668 | 48 | 10.9718 | 0 | 0 | 463.5631 | 0 | 15.9668 | 0 | 1.6649 | 0 | 0 | 0 | 15.9668 | 0 | 0
3 | 29 | 17 | 5.1108 | 152.1243 | 157.2351 | 46.7973 | 10.3786 | 0 | 0 | 475.8074 | 0 | 157.2351 | 0 | 16.3953 | 0 | 0 | 0 | 157.2351 | 0 | 0
3 | 29 | 18 | 0 | 0.29821 | 0.29821 | 48 | 11.0734 | 0 | 0 | 481.0262 | 0 | 0.29821 | 0 | 0.031095 | 0 | 0 | 0 | 0.29821 | 0 | 0
3 | 29 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 485.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 462.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 433.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 419.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 29 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 419.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 408.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 407.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 2 | 3.3529 | 0 | 3.3529 | 11 | 3.8197 | 1.2136 | 1.2136 | 428.0435 | 3.3529 | 0 | 1398.2988 | 0 | 0 | 0 | 3.3529 | 0 | 0 | 1398.2988
3 | 30 | 3 | 0.9718 | 0 | 0.9718 | 11 | 3.4638 | 0.33132 | 0.33132 | 451.936 | 0.9718 | 0 | 428.5019 | 0 | 0 | 0 | 0.9718 | 0 | 0 | 428.5019
3 | 30 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 473.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 477.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 483.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 7 | 0 | 0.76917 | 0.76917 | 48 | 4.6502 | 0.32521 | 0.32521 | 485.6016 | 0.76917 | 0 | 336.5885 | 0 | 0 | 0 | 0.76917 | 0 | 0 | 336.5885
3 | 30 | 8 | 85.7285 | 223.2489 | 308.9774 | 37.734 | 5.1417 | 145.0724 | 145.0724 | 481.8598 | 308.9774 | 0 | 137224.8158 | 0 | 0 | 0 | 308.9774 | 0 | 0 | 137224.8158
3 | 30 | 9 | 77.7918 | 568.5742 | 646.366 | 43.547 | 6.6161 | 453.9429 | 288 | 486.1147 | 410.0811 | 236.2849 | 181488.6682 | 24.638 | 0 | 0 | 410.0811 | 236.2849 | 0 | 181488.6682
3 | 30 | 10 | 72.1125 | 489.4162 | 561.5286 | 43.2484 | 6.9721 | 447.9695 | 288 | 485.362 | 361.0073 | 200.5213 | 159606.2447 | 20.9089 | 0 | 0 | 361.0073 | 200.5213 | 0 | 159606.2447
3 | 30 | 11 | 90.2244 | 490.0875 | 580.3119 | 42.2474 | 8.5652 | 1182.4351 | 288 | 487.3646 | 141.3438 | 438.9681 | 62914.5398 | 45.7724 | 0 | 0 | 141.3438 | 438.9681 | 0 | 62914.5398
3 | 30 | 12 | 94.4892 | 781.608 | 876.0971 | 44.0095 | 7.8957 | 1079.8924 | 288 | 485.4496 | 233.6492 | 642.448 | 103142.1163 | 66.9897 | 0 | 0 | 233.6492 | 642.448 | 0 | 103142.1163
3 | 30 | 13 | 84.3658 | 913.622 | 997.9879 | 44.8722 | 7.4381 | 968.5806 | 288 | 487.1811 | 296.744 | 701.2438 | 131252.5414 | 73.1205 | 0 | 0 | 296.744 | 701.2438 | 0 | 131252.5414
3 | 30 | 14 | 32.8842 | 516.5438 | 549.4279 | 45.7855 | 7.2771 | 496.1222 | 288 | 487.0272 | 318.9441 | 230.4839 | 140731.4344 | 24.0332 | 0 | 0 | 318.9441 | 230.4839 | 0 | 140731.4344
3 | 30 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 486.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 463.5631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 475.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 481.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 485.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 462.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 433.7276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 419.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 30 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 419.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 0 | 16.0952 | 0 | 16.0952 | 11 | 3.5232 | 5.5411 | 5.5411 | 408.2216 | 16.0952 | 0 | 6393.3781 | 0 | 0 | 0 | 16.0952 | 0 | 0 | 6393.3781
3 | 31 | 1 | 8.7692 | 0 | 8.7692 | 11 | 3.1079 | 2.8256 | 2.8256 | 407.5202 | 8.7692 | 0 | 3477.1513 | 0 | 0 | 0 | 8.7692 | 0 | 0 | 3477.1513
3 | 31 | 2 | 1.9265 | 0 | 1.9265 | 11 | 3.0232 | 0.61274 | 0.61274 | 428.0435 | 1.9265 | 0 | 803.4334 | 0 | 0 | 0 | 1.9265 | 0 | 0 | 803.4334
3 | 31 | 3 | 112.6024 | 0 | 112.6024 | 11 | 2.9893 | 35.6303 | 35.6303 | 451.936 | 112.6024 | 0 | 49650.4713 | 0 | 0 | 0 | 112.6024 | 0 | 0 | 49650.4713
3 | 31 | 4 | 216.3088 | 0 | 216.3088 | 11 | 2.9469 | 68.0091 | 68.0091 | 473.6796 | 216.3088 | 0 | 100081.6717 | 0 | 0 | 0 | 216.3088 | 0 | 0 | 100081.6717
3 | 31 | 5 | 22.7781 | 0 | 22.7781 | 11 | 3.091 | 7.3204 | 7.3204 | 477.6788 | 22.7781 | 0 | 10630.0614 | 0 | 0 | 0 | 22.7781 | 0 | 0 | 10630.0614
3 | 31 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 483.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 7 | 45.4558 | 34.4871 | 79.9428 | 26.9617 | 6.1924 | 49.1429 | 49.1429 | 485.6016 | 79.9428 | 0 | 36664.9784 | 0 | 0 | 0 | 79.9428 | 0 | 0 | 36664.9784
3 | 31 | 8 | 52.2176 | 391.4185 | 443.6361 | 43.645 | 6.8788 | 341.7515 | 288 | 481.8598 | 373.8599 | 69.7762 | 163830.9598 | 7.2757 | 0 | 0 | 373.8599 | 69.7762 | 0 | 163830.9598
3 | 31 | 9 | 71.9107 | 715.6163 | 787.5271 | 44.6215 | 7.3195 | 724.3896 | 288 | 486.1147 | 313.1019 | 474.4251 | 138232.4093 | 49.4696 | 0 | 0 | 313.1019 | 474.4251 | 0 | 138232.4093
3 | 31 | 10 | 69.7087 | 606.7674 | 676.4761 | 44.1873 | 7.4805 | 669.7279 | 288 | 485.362 | 290.9019 | 385.5742 | 128338.5792 | 40.2048 | 0 | 0 | 290.9019 | 385.5742 | 0 | 128338.5792
3 | 31 | 11 | 91.268 | 883.0156 | 974.2836 | 44.5339 | 7.2263 | 860.8367 | 288 | 487.3646 | 325.9546 | 648.329 | 144342.6909 | 67.603 | 0 | 0 | 325.9546 | 648.329 | 0 | 144342.6909
3 | 31 | 12 | 88.7478 | 410.4696 | 499.2174 | 41.4224 | 7.8703 | 606.2489 | 288 | 485.4496 | 237.1544 | 262.063 | 105303.0227 | 27.326 | 0 | 0 | 237.1544 | 262.063 | 0 | 105303.0227
3 | 31 | 13 | 109.6786 | 498.7019 | 608.3805 | 41.3297 | 8.1754 | 898.111 | 288 | 487.1811 | 195.0912 | 413.2893 | 86981.7077 | 43.0948 | 0 | 0 | 195.0912 | 413.2893 | 0 | 86981.7077
3 | 31 | 14 | 79.207 | 478.6386 | 557.8456 | 42.7465 | 8.2431 | 864.9522 | 288 | 487.0272 | 185.7438 | 372.1018 | 82522.4132 | 38.8 | 0 | 0 | 185.7438 | 372.1018 | 0 | 82522.4132
3 | 31 | 15 | 45.5498 | 501.2606 | 546.8103 | 44.9179 | 7.4212 | 526.5512 | 288 | 486.0412 | 299.0809 | 247.7295 | 131931.5615 | 25.8314 | 0 | 0 | 299.0809 | 247.7295 | 0 | 131931.5615
3 | 31 | 16 | 4.915 | 88.3769 | 93.2919 | 46.0507 | 7.3195 | 85.8126 | 85.8126 | 463.5631 | 93.2919 | 0 | 38950.5389 | 0 | 0 | 0 | 93.2919 | 0 | 0 | 38950.5389
3 | 31 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 476.2475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 482.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 478.9815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 465.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 459.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 419.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 31 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 419.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 408.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 407.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 428.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 451.936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 473.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 477.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 483.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 7 | 9.7732 | 270.4067 | 280.1798 | 46.7094 | 6.006 | 163.2751 | 163.2751 | 485.6016 | 280.1798 | 0 | 122968.7386 | 0 | 0 | 0 | 280.1798 | 0 | 0 | 122968.7386
4 | 1 | 8 | 5.895 | 713.3135 | 719.2085 | 47.6967 | 6.6246 | 506.5436 | 288 | 481.8598 | 408.9126 | 310.2959 | 177534.7486 | 32.3554 | 0 | 0 | 408.9126 | 310.2959 | 0 | 177534.7486
4 | 1 | 9 | 1.1525 | 1267.6882 | 1268.8407 | 47.9664 | 7.1924 | 1105.2476 | 288 | 486.1147 | 330.6283 | 938.2124 | 144864.2412 | 97.8299 | 0 | 0 | 330.6283 | 938.2124 | 0 | 144864.2412
4 | 1 | 10 | 2.55 | 1499.3779 | 1501.9279 | 47.9372 | 7.0398 | 1230.0385 | 288 | 485.362 | 351.6599 | 1150.268 | 153824.7813 | 119.9415 | 0 | 0 | 351.6599 | 1150.268 | 0 | 153824.7813
4 | 1 | 11 | 1.6991 | 1483.1057 | 1484.8048 | 47.9577 | 7.2093 | 1302.5737 | 288 | 487.3646 | 328.2914 | 1156.5134 | 144253.5433 | 120.5927 | 0 | 0 | 328.2914 | 1156.5134 | 0 | 144253.5433
4 | 1 | 12 | 0.89079 | 1293.4328 | 1294.3236 | 47.9745 | 7.9296 | 1627.9699 | 288 | 485.4496 | 228.9755 | 1065.3482 | 100171.0561 | 111.0866 | 0 | 0 | 228.9755 | 1065.3482 | 0 | 100171.0561
4 | 1 | 13 | 0.054167 | 612.5373 | 612.5914 | 47.9967 | 8.2601 | 961.939 | 288 | 487.1811 | 183.407 | 429.1844 | 80549.4892 | 44.7522 | 0 | 0 | 183.407 | 429.1844 | 0 | 80549.4892
4 | 1 | 14 | 0.11083 | 720.4703 | 720.5811 | 47.9943 | 8.5313 | 1421.2503 | 288 | 487.0272 | 146.0175 | 574.5636 | 64106.469 | 59.9113 | 0 | 0 | 146.0175 | 574.5636 | 0 | 64106.469
4 | 1 | 15 | 0.058333 | 552.3563 | 552.4146 | 47.9961 | 8.4041 | 972.8 | 288 | 486.0412 | 163.5438 | 388.8708 | 71639.5661 | 40.5486 | 0 | 0 | 163.5438 | 388.8708 | 0 | 71639.5661
4 | 1 | 16 | 0.085833 | 520.947 | 521.0328 | 47.9939 | 9.1753 | 2622.5889 | 288 | 471.9537 | 57.2173 | 463.8155 | 24257.8324 | 48.3633 | 0 | 0 | 57.2173 | 463.8155 | 0 | 24257.8324
4 | 1 | 17 | 0.023333 | 161.2858 | 161.3091 | 47.9946 | 8.6753 | 368.2557 | 288 | 469.4524 | 126.1543 | 35.1549 | 53168.6884 | 3.6657 | 0 | 0 | 126.1543 | 35.1549 | 0 | 53168.6884
4 | 1 | 18 | 0 | 0.52833 | 0.52833 | 48 | 9.0397 | 2.0044 | 2.0044 | 470.8499 | 0.52833 | 0 | 223.4057 | 0 | 0 | 0 | 0.52833 | 0 | 0 | 223.4057
4 | 1 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 470.9724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 464.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 422.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 409.8149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 413.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 419.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 427.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 437.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 453.8087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 462.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 456.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 458.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 7 | 55.9471 | 319.6873 | 375.6345 | 42.4892 | 4.8705 | 166.2364 | 166.2364 | 460.8988 | 375.6345 | 0 | 157169.0564 | 0 | 0 | 0 | 375.6345 | 0 | 0 | 157169.0564
4 | 2 | 8 | 10.245 | 995.8906 | 1006.1356 | 47.6232 | 4.8451 | 442.8783 | 288 | 470.8508 | 654.2815 | 351.8542 | 276909.9778 | 36.6888 | 0 | 0 | 654.2815 | 351.8542 | 0 | 276909.9778
4 | 2 | 9 | 1.1975 | 903.6121 | 904.8096 | 47.951 | 6.3789 | 588.4982 | 288 | 465.5402 | 442.7969 | 462.0127 | 184907.1697 | 48.1753 | 0 | 0 | 442.7969 | 462.0127 | 0 | 184907.1697
4 | 2 | 10 | 0.094167 | 1096.8927 | 1096.9869 | 47.9968 | 8.4804 | 2064.5388 | 288 | 470.6801 | 153.028 | 943.9589 | 64682.3732 | 98.4291 | 0 | 0 | 153.028 | 943.9589 | 0 | 64682.3732
4 | 2 | 11 | 0.1075 | 1280.9243 | 1281.0318 | 47.9969 | 9.4549 | 19772.2522 | 288 | 473.9993 | 18.6593 | 1262.3725 | 7948.9236 | 131.6309 | 0 | 0 | 18.6593 | 1262.3725 | 0 | 7948.9236
4 | 2 | 12 | 0.20833 | 1384.6479 | 1384.8563 | 47.9944 | 9.8362 | 0 | 0 | 472.2466 | 0 | 1384.8563 | 0 | 144.4026 | 0 | 0 | 0 | 1384.8563 | 0 | 0
4 | 2 | 13 | 8.92 | 1521.6788 | 1530.5988 | 47.7844 | 9.6159 | 0 | 0 | 472.1534 | 0 | 1530.5988 | 0 | 159.5995 | 0 | 0 | 0 | 1530.5988 | 0 | 0
4 | 2 | 14 | 10.2092 | 1448.4365 | 1458.6457 | 47.741 | 9.5227 | 45112.9719 | 288 | 471.8427 | 9.312 | 1449.3338 | 3949.2157 | 151.1258 | 0 | 0 | 9.312 | 1449.3338 | 0 | 3949.2157
4 | 2 | 15 | 7.8267 | 1524.4973 | 1532.3239 | 47.811 | 10.7175 | 0 | 0 | 464.7636 | 0 | 1532.3239 | 0 | 159.7794 | 0 | 0 | 0 | 1532.3239 | 0 | 0
4 | 2 | 16 | 23.0833 | 1295.5776 | 1318.6609 | 47.3523 | 12.0564 | 0 | 0 | 458.6222 | 0 | 1318.6609 | 0 | 137.5002 | 0 | 0 | 0 | 1318.6609 | 0 | 0
4 | 2 | 17 | 0.14833 | 215.1516 | 215.2999 | 47.9745 | 11.8107 | 0 | 0 | 455.3808 | 0 | 215.2999 | 0 | 22.4499 | 0 | 0 | 0 | 215.2999 | 0 | 0
4 | 2 | 18 | 0 | 0.97667 | 0.97667 | 48 | 12.3445 | 0 | 0 | 451.6234 | 0 | 0.97667 | 0 | 0.10184 | 0 | 0 | 0 | 0.97667 | 0 | 0
4 | 2 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 456.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 446.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 422.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 409.8149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 413.0252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 419.3751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 427.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 437.475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 453.8087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 462.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 456.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 458.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 460.8988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 8 | 0 | 46.1342 | 46.1342 | 48 | 5.4976 | 23.5448 | 23.5448 | 470.8508 | 46.1342 | 0 | 19507.8905 | 0 | 0 | 0 | 46.1342 | 0 | 0 | 19507.8905
4 | 3 | 9 | 3.1467 | 537.7361 | 540.8828 | 47.7847 | 6.4043 | 354.6033 | 288 | 465.5402 | 439.2916 | 101.5912 | 183516.4549 | 10.5932 | 0 | 0 | 439.2916 | 101.5912 | 0 | 183516.4549
4 | 3 | 10 | 6.5158 | 535.7995 | 542.3153 | 47.5555 | 8.5991 | 1142.802 | 288 | 470.6801 | 136.6701 | 405.6453 | 57828.4754 | 42.2977 | 0 | 0 | 136.6701 | 405.6453 | 0 | 57828.4754
4 | 3 | 11 | 1.9652 | 466.1795 | 468.1447 | 47.8447 | 9.6413 | 0 | 0 | 473.9993 | 0 | 468.1447 | 0 | 48.8147 | 0 | 0 | 0 | 468.1447 | 0 | 0
4 | 3 | 12 | 1.785 | 608.7479 | 610.5329 | 47.8918 | 9.7176 | 0 | 0 | 472.2466 | 0 | 610.5329 | 0 | 63.6619 | 0 | 0 | 0 | 610.5329 | 0 | 0
4 | 3 | 13 | 0 | 216.1306 | 216.1306 | 48 | 9.7939 | 0 | 0 | 472.1534 | 0 | 216.1306 | 0 | 22.5365 | 0 | 0 | 0 | 216.1306 | 0 | 0
4 | 3 | 14 | 0 | 160.026 | 160.026 | 48 | 9.4634 | 2634.9378 | 288 | 471.8427 | 17.4909 | 142.535 | 7413.3969 | 14.8625 | 0 | 0 | 17.4909 | 142.535 | 0 | 7413.3969
4 | 3 | 15 | 0 | 190.7602 | 190.7602 | 48 | 10.5311 | 0 | 0 | 464.7636 | 0 | 190.7602 | 0 | 19.8911 | 0 | 0 | 0 | 190.7602 | 0 | 0
4 | 3 | 16 | 0 | 177.5327 | 177.5327 | 48 | 11.0904 | 0 | 0 | 458.6222 | 0 | 177.5327 | 0 | 18.5118 | 0 | 0 | 0 | 177.5327 | 0 | 0
4 | 3 | 17 | 0 | 11.7038 | 11.7038 | 48 | 11.1073 | 0 | 0 | 455.3808 | 0 | 11.7038 | 0 | 1.2204 | 0 | 0 | 0 | 11.7038 | 0 | 0
4 | 3 | 18 | 0 | 0.38333 | 0.38333 | 48 | 11.4802 | 0 | 0 | 451.6234 | 0 | 0.38333 | 0 | 0.039971 | 0 | 0 | 0 | 0.38333 | 0 | 0
4 | 3 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 456.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 446.2131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 410.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 396.2398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 3 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 383.3322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 0 | 6.0633 | 0 | 6.0633 | 11 | 3.6333 | 2.126 | 2.126 | 380.931 | 6.0633 | 0 | 2243.0152 | 0 | 0 | 0 | 6.0633 | 0 | 0 | 2243.0152
4 | 4 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 386.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 2 | 3.225 | 0 | 3.225 | 11 | 3.2096 | 1.0557 | 1.0557 | 403.0889 | 3.225 | 0 | 1264.4868 | 0 | 0 | 0 | 3.225 | 0 | 0 | 1264.4868
4 | 4 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 422.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 4 | 4.2225 | 0 | 4.2225 | 11 | 3.2689 | 1.3952 | 1.3952 | 449.0328 | 4.2225 | 0 | 1849.5936 | 0 | 0 | 0 | 4.2225 | 0 | 0 | 1849.5936
4 | 4 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 449.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 451.209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 446.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 8 | 1.19 | 92.8587 | 94.0487 | 47.5318 | 6.2094 | 58.1039 | 58.1039 | 444.496 | 94.0487 | 0 | 37333.9628 | 0 | 0 | 0 | 94.0487 | 0 | 0 | 37333.9628
4 | 4 | 9 | 0 | 3.0854 | 3.0854 | 48 | 7.328 | 2.8487 | 2.8487 | 451.765 | 3.0854 | 0 | 1245.7911 | 0 | 0 | 0 | 3.0854 | 0 | 0 | 1245.7911
4 | 4 | 10 | 0 | 7.4828 | 7.4828 | 48 | 8.5482 | 14.9989 | 14.9989 | 455.1417 | 7.4828 | 0 | 3046.5763 | 0 | 0 | 0 | 7.4828 | 0 | 0 | 3046.5763
4 | 4 | 11 | 0 | 21.4902 | 21.4902 | 48 | 9.1838 | 110.4245 | 110.4245 | 461.0346 | 21.4902 | 0 | 8876.1882 | 0 | 0 | 0 | 21.4902 | 0 | 0 | 8876.1882
4 | 4 | 12 | 0 | 44.3321 | 44.3321 | 48 | 9.8701 | 0 | 0 | 463.416 | 0 | 44.3321 | 0 | 4.6226 | 0 | 0 | 0 | 44.3321 | 0 | 0
4 | 4 | 13 | 0 | 29.6996 | 29.6996 | 48 | 9.6668 | 0 | 0 | 465.5488 | 0 | 29.6996 | 0 | 3.0969 | 0 | 0 | 0 | 29.6996 | 0 | 0
4 | 4 | 14 | 0 | 9.4218 | 9.4218 | 48 | 10.2684 | 0 | 0 | 463.2046 | 0 | 9.4218 | 0 | 0.98244 | 0 | 0 | 0 | 9.4218 | 0 | 0
4 | 4 | 15 | 0 | 3.0484 | 3.0484 | 48 | 11.226 | 0 | 0 | 465.2267 | 0 | 3.0484 | 0 | 0.31786 | 0 | 0 | 0 | 3.0484 | 0 | 0
4 | 4 | 16 | 0 | 0.64487 | 0.64487 | 48 | 11.853 | 0 | 0 | 462.835 | 0 | 0.64487 | 0 | 0.067243 | 0 | 0 | 0 | 0.64487 | 0 | 0
4 | 4 | 17 | 0 | 1.74 | 1.74 | 48 | 11.7514 | 0 | 0 | 457.1958 | 0 | 1.74 | 0 | 0.18143 | 0 | 0 | 0 | 1.74 | 0 | 0
4 | 4 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 453.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 461.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 461.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 419.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 402.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 394.6811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 394.4724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 395.6534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 404.133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 421.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 443.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 452.5952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 453.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 7 | 0 | 60.9061 | 60.9061 | 48 | 5.0146 | 27.8025 | 27.8025 | 454.1381 | 60.9061 | 0 | 24736.2964 | 0 | 0 | 0 | 60.9061 | 0 | 0 | 24736.2964
4 | 5 | 8 | 0 | 69.2166 | 69.2166 | 48 | 6.2094 | 42.7625 | 42.7625 | 455.3524 | 69.2166 | 0 | 28195.5434 | 0 | 0 | 0 | 69.2166 | 0 | 0 | 28195.5434
4 | 5 | 9 | 0 | 37.9157 | 37.9157 | 48 | 7.311 | 34.7463 | 34.7463 | 462.1014 | 37.9157 | 0 | 15700.9399 | 0 | 0 | 0 | 37.9157 | 0 | 0 | 15700.9399
4 | 5 | 10 | 0 | 28.7237 | 28.7237 | 48 | 8.0567 | 39.1226 | 39.1226 | 464.2413 | 28.7237 | 0 | 11956.0007 | 0 | 0 | 0 | 28.7237 | 0 | 0 | 11956.0007
4 | 5 | 11 | 0 | 20.109 | 20.109 | 48 | 9.3109 | 150.3379 | 150.3379 | 465.9209 | 20.109 | 0 | 8403.9786 | 0 | 0 | 0 | 20.109 | 0 | 0 | 8403.9786
4 | 5 | 12 | 0 | 23.7927 | 23.7927 | 48 | 9.0058 | 85.0311 | 85.0311 | 462.0183 | 23.7927 | 0 | 9850.6115 | 0 | 0 | 0 | 23.7927 | 0 | 0 | 9850.6115
4 | 5 | 13 | 0 | 19.8418 | 19.8418 | 48 | 8.4889 | 37.6297 | 37.6297 | 464.7357 | 19.8418 | 0 | 8268.7793 | 0 | 0 | 0 | 19.8418 | 0 | 0 | 8268.7793
4 | 5 | 14 | 0 | 19.4942 | 19.4942 | 48 | 8.938 | 62.4277 | 62.4277 | 459.8411 | 19.4942 | 0 | 8028.4983 | 0 | 0 | 0 | 19.4942 | 0 | 0 | 8028.4983
4 | 5 | 15 | 0 | 12.5151 | 12.5151 | 48 | 9.6075 | 0 | 0 | 454.1738 | 0 | 12.5151 | 0 | 1.305 | 0 | 0 | 0 | 12.5151 | 0 | 0
4 | 5 | 16 | 0 | 3.199 | 3.199 | 48 | 10.9718 | 0 | 0 | 439.0557 | 0 | 3.199 | 0 | 0.33357 | 0 | 0 | 0 | 3.199 | 0 | 0
4 | 5 | 17 | 0 | 0.61141 | 0.61141 | 48 | 10.3786 | 0 | 0 | 446.0028 | 0 | 0.61141 | 0 | 0.063754 | 0 | 0 | 0 | 0.61141 | 0 | 0
4 | 5 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 436.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 443.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 429.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 396.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 384.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 389.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 388.7876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 390.0388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 401.5513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 417.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 450.1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 451.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 6 | 3.1979 | 0.04 | 3.2379 | 11.4571 | 4.396 | 1.302 | 1.302 | 449.0343 | 3.2379 | 0 | 1416.8204 | 0 | 0 | 0 | 3.2379 | 0 | 0 | 1416.8204
4 | 6 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 451.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 450.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 454.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 10 | 0 | 1.0067 | 1.0067 | 48 | 6.9721 | 0.80313 | 0.80313 | 452.8499 | 1.0067 | 0 | 407.5716 | 0 | 0 | 0 | 1.0067 | 0 | 0 | 407.5716
4 | 6 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 458.9057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 464.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 13 | 0 | 51.9022 | 51.9022 | 48 | 7.4381 | 50.3728 | 50.3728 | 465.1097 | 51.9022 | 0 | 21648.9217 | 0 | 0 | 0 | 51.9022 | 0 | 0 | 21648.9217
4 | 6 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 463.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 15 | 0 | 0.13246 | 0.13246 | 48 | 7.3449 | 0.12322 | 0.12322 | 462.8179 | 0.13246 | 0 | 54.9461 | 0 | 0 | 0 | 0.13246 | 0 | 0 | 54.9461
4 | 6 | 16 | 0 | 0.38488 | 0.38488 | 48 | 6.9975 | 0.31005 | 0.31005 | 447.9342 | 0.38488 | 0 | 153.9247 | 0 | 0 | 0 | 0.38488 | 0 | 0 | 153.9247
4 | 6 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 452.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 463.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 472.359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 464.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 6 | 21 | 200.7298 | 0 | 200.7298 | 11 | 6.1924 | 123.3936 | 123.3936 | 453.7505 | 200.7298 | 0 | 88873.2166 | 0 | 0 | 0 | 200.7298 | 0 | 0 | 88873.2166
4 | 6 | 22 | 90.6623 | 0 | 90.6623 | 11 | 4.5824 | 37.8141 | 37.8141 | 430.447 | 90.6623 | 0 | 38028.0182 | 0 | 0 | 0 | 90.6623 | 0 | 0 | 38028.0182
4 | 6 | 23 | 43.4921 | 0 | 43.4921 | 11 | 4.2615 | 17.0477 | 17.0477 | 434.7205 | 43.4921 | 0 | 18428.4857 | 0 | 0 | 0 | 43.4921 | 0 | 0 | 18428.4857
4 | 7 | 0 | 0.82135 | 0 | 0.82135 | 11 | 3.5232 | 0.28276 | 0.28276 | 430.2238 | 0.82135 | 0 | 344.329 | 0 | 0 | 0 | 0.82135 | 0 | 0 | 344.329
4 | 7 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 437.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 443.9751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 438.6806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 442.8231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 443.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 450.1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 452.0598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 452.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 455.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 460.2108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 11 | 0 | 2.4257 | 2.4257 | 48 | 7.2263 | 2.1433 | 2.1433 | 458.5992 | 2.4257 | 0 | 995.9949 | 0 | 0 | 0 | 2.4257 | 0 | 0 | 995.9949
4 | 7 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 461.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 463.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 14 | 0 | 29.0252 | 29.0252 | 48 | 8.2431 | 45.0042 | 45.0042 | 463.0278 | 29.0252 | 0 | 12046.2605 | 0 | 0 | 0 | 29.0252 | 0 | 0 | 12046.2605
4 | 7 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 464.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 459.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 452.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 463.6836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 19 | 5.3872 | 0 | 5.3872 | 11 | 6.9382 | 4.2428 | 4.2428 | 472.359 | 5.3872 | 0 | 2485.4432 | 0 | 0 | 0 | 5.3872 | 0 | 0 | 2485.4432
4 | 7 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 464.6461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 457.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 445.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 7 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 442.9783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 442.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 441.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 446.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 445.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 444.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 431.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 436.1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 443.6338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 8 | 0 | 0.36561 | 0.36561 | 48 | 6.6246 | 0.2575 | 0.2575 | 429.1291 | 0.36561 | 0 | 139.3449 | 0 | 0 | 0 | 0.36561 | 0 | 0 | 139.3449
4 | 8 | 9 | 1.9451 | 49.6937 | 51.6388 | 46.6063 | 7.1924 | 44.981 | 44.981 | 423.4834 | 51.6388 | 0 | 19461.4886 | 0 | 0 | 0 | 51.6388 | 0 | 0 | 19461.4886
4 | 8 | 10 | 4.5233 | 492.6819 | 497.2053 | 47.6634 | 7.0398 | 407.1977 | 288 | 416.6034 | 351.6599 | 145.5454 | 129741.4027 | 15.1764 | 0 | 0 | 351.6599 | 145.5454 | 0 | 129741.4027
4 | 8 | 11 | 55.0403 | 1634.3274 | 1689.3678 | 46.7945 | 7.2093 | 1482.0304 | 288 | 413.4073 | 328.2914 | 1361.0763 | 120355.8339 | 141.923 | 0 | 0 | 328.2914 | 1361.0763 | 0 | 120355.8339
4 | 8 | 12 | 217.6739 | 1693.2873 | 1910.9612 | 43.7854 | 7.9296 | 2403.5622 | 288 | 406.7748 | 228.9755 | 1681.9857 | 83115.6757 | 175.3851 | 0 | 0 | 228.9755 | 1681.9857 | 0 | 83115.6757
4 | 8 | 13 | 115.5008 | 1519.5768 | 1635.0776 | 45.3863 | 8.2601 | 2567.5268 | 288 | 404.8114 | 183.407 | 1451.6706 | 65921.0584 | 151.3695 | 0 | 0 | 183.407 | 1451.6706 | 0 | 65921.0584
4 | 8 | 14 | 50.6931 | 1463.3872 | 1514.0804 | 46.7612 | 8.5313 | 2986.3222 | 288 | 405.1235 | 146.0175 | 1368.0629 | 52327.1437 | 142.6515 | 0 | 0 | 146.0175 | 1368.0629 | 0 | 52327.1437
4 | 8 | 15 | 96.8152 | 1443.8761 | 1540.6913 | 45.675 | 8.4041 | 2713.1514 | 288 | 402.3312 | 163.5438 | 1377.1475 | 58328.9102 | 143.5988 | 0 | 0 | 163.5438 | 1377.1475 | 0 | 58328.9102
4 | 8 | 16 | 39.8312 | 1035.3146 | 1075.1457 | 46.6293 | 9.1753 | 5411.6843 | 288 | 397.6968 | 57.2173 | 1017.9284 | 20087.1363 | 106.1421 | 0 | 0 | 57.2173 | 1017.9284 | 0 | 20087.1363
4 | 8 | 17 | 14.7646 | 400.7785 | 415.5432 | 46.6854 | 8.6753 | 948.6516 | 288 | 417.0486 | 126.1543 | 289.3889 | 46722.8943 | 30.1753 | 0 | 0 | 126.1543 | 289.3889 | 0 | 46722.8943
4 | 8 | 18 | 0 | 0.70329 | 0.70329 | 48 | 9.0397 | 2.6682 | 2.6682 | 427.7503 | 0.70329 | 0 | 267.0752 | 0 | 0 | 0 | 0.70329 | 0 | 0 | 267.0752
4 | 8 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 427.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 415.8623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 387.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 382.6811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 8 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 386.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 386.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 391.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 401.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 410.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 414.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 413.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 405.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 405.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 8 | 0 | 1.9425 | 1.9425 | 48 | 4.8451 | 0.85504 | 0.85504 | 407.1684 | 1.9425 | 0 | 697.6846 | 0 | 0 | 0 | 1.9425 | 0 | 0 | 697.6846
4 | 9 | 9 | 0 | 4.6718 | 4.6718 | 48 | 6.3789 | 3.0386 | 3.0386 | 404.4798 | 4.6718 | 0 | 1665.3995 | 0 | 0 | 0 | 4.6718 | 0 | 0 | 1665.3995
4 | 9 | 10 | 0 | 138.0049 | 138.0049 | 48 | 8.4804 | 259.7264 | 259.7264 | 396.417 | 138.0049 | 0 | 48083.2539 | 0 | 0 | 0 | 138.0049 | 0 | 0 | 48083.2539
4 | 9 | 11 | 0.010833 | 378.9109 | 378.9217 | 47.9989 | 9.4549 | 5848.5162 | 288 | 394.6911 | 18.6593 | 360.2624 | 6469.046 | 37.5655 | 0 | 0 | 18.6593 | 360.2624 | 0 | 6469.046
4 | 9 | 12 | 0 | 280.1969 | 280.1969 | 48 | 9.8362 | 0 | 0 | 398.7398 | 0 | 280.1969 | 0 | 29.2169 | 0 | 0 | 0 | 280.1969 | 0 | 0
4 | 9 | 13 | 0 | 422.6137 | 422.6137 | 48 | 9.6159 | 0 | 0 | 398.1892 | 0 | 422.6137 | 0 | 44.067 | 0 | 0 | 0 | 422.6137 | 0 | 0
4 | 9 | 14 | 0.0125 | 505.3762 | 505.3887 | 47.9991 | 9.5227 | 15630.6526 | 288 | 412.6402 | 9.312 | 496.0767 | 3395.5215 | 51.7272 | 0 | 0 | 9.312 | 496.0767 | 0 | 3395.5215
4 | 9 | 15 | 0.0275 | 385.3411 | 385.3686 | 47.9974 | 10.7175 | 0 | 0 | 418.7554 | 0 | 385.3686 | 0 | 40.1834 | 0 | 0 | 0 | 385.3686 | 0 | 0
4 | 9 | 16 | 0 | 112.3828 | 112.3828 | 48 | 12.0564 | 0 | 0 | 403.0725 | 0 | 112.3828 | 0 | 11.7184 | 0 | 0 | 0 | 112.3828 | 0 | 0
4 | 9 | 17 | 0 | 2.0449 | 2.0449 | 48 | 11.8107 | 0 | 0 | 415.8375 | 0 | 2.0449 | 0 | 0.21323 | 0 | 0 | 0 | 2.0449 | 0 | 0
4 | 9 | 18 | 0 | 0.61408 | 0.61408 | 48 | 12.3445 | 0 | 0 | 431.8595 | 0 | 0.61408 | 0 | 0.064032 | 0 | 0 | 0 | 0.61408 | 0 | 0
4 | 9 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 422.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 406.0853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 374.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 359.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 9 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 360.5534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 355.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 361.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 370.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 407.6472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 424.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 433.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 442.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 7 | 0 | 1.2633 | 1.2633 | 48 | 4.8281 | 0.55411 | 0.55411 | 451.3638 | 1.2633 | 0 | 509.583 | 0 | 0 | 0 | 1.2633 | 0 | 0 | 509.583
4 | 10 | 8 | 0 | 9.5968 | 9.5968 | 48 | 5.4976 | 4.8978 | 4.8978 | 443.8486 | 9.5968 | 0 | 3798.8964 | 0 | 0 | 0 | 9.5968 | 0 | 0 | 3798.8964
4 | 10 | 9 | 0 | 15.3882 | 15.3882 | 48 | 6.4043 | 10.0885 | 10.0885 | 445.1079 | 15.3882 | 0 | 6110.7616 | 0 | 0 | 0 | 15.3882 | 0 | 0 | 6110.7616
4 | 10 | 10 | 0 | 4.8244 | 4.8244 | 48 | 8.5991 | 10.1663 | 10.1663 | 443.8307 | 4.8244 | 0 | 1909.6547 | 0 | 0 | 0 | 4.8244 | 0 | 0 | 1909.6547
4 | 10 | 11 | 0 | 15.4486 | 15.4486 | 48 | 9.6413 | 0 | 0 | 448.5418 | 0 | 15.4486 | 0 | 1.6109 | 0 | 0 | 0 | 15.4486 | 0 | 0
4 | 10 | 12 | 0 | 13.5201 | 13.5201 | 48 | 9.7176 | 0 | 0 | 452.4101 | 0 | 13.5201 | 0 | 1.4098 | 0 | 0 | 0 | 13.5201 | 0 | 0
4 | 10 | 13 | 0 | 26.8495 | 26.8495 | 48 | 9.7939 | 0 | 0 | 446.1751 | 0 | 26.8495 | 0 | 2.7997 | 0 | 0 | 0 | 26.8495 | 0 | 0
4 | 10 | 14 | 0 | 30.0632 | 30.0632 | 48 | 9.4634 | 495.0109 | 288 | 450.2931 | 17.4909 | 12.5723 | 7036.4741 | 1.3109 | 0 | 0 | 17.4909 | 12.5723 | 0 | 7036.4741
4 | 10 | 15 | 0 | 15.3278 | 15.3278 | 48 | 10.5311 | 0 | 0 | 454.2311 | 0 | 15.3278 | 0 | 1.5983 | 0 | 0 | 0 | 15.3278 | 0 | 0
4 | 10 | 16 | 0.1875 | 17.687 | 17.8745 | 47.6119 | 11.0904 | 0 | 0 | 443.4192 | 0 | 17.8745 | 0 | 1.8638 | 0 | 0 | 0 | 17.8745 | 0 | 0
4 | 10 | 17 | 0.023333 | 30.1073 | 30.1306 | 47.9713 | 11.1073 | 0 | 0 | 455.0864 | 0 | 30.1306 | 0 | 3.1418 | 0 | 0 | 0 | 30.1306 | 0 | 0
4 | 10 | 18 | 0 | 0.6275 | 0.6275 | 48 | 11.4802 | 0 | 0 | 459.3585 | 0 | 0.6275 | 0 | 0.065431 | 0 | 0 | 0 | 0.6275 | 0 | 0
4 | 10 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 458.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 448.5412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 405.5821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 376.4538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 10 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 366.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 363.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 358.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 364.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 398.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 433.3056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 449.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 451.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 452.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 459.3458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 458.5656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 10 | 0 | 0 | 0 | 0 | 8.5482 | 0 | 0 | 460.6521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 11 | 0 | 5.8141 | 5.8141 | 48 | 9.1838 | 29.8752 | 29.8752 | 461.6034 | 5.8141 | 0 | 2404.7449 | 0 | 0 | 0 | 5.8141 | 0 | 0 | 2404.7449
4 | 11 | 12 | 0.2025 | 121.0967 | 121.2992 | 47.9382 | 9.8701 | 0 | 0 | 461.1987 | 0 | 121.2992 | 0 | 12.6482 | 0 | 0 | 0 | 121.2992 | 0 | 0
4 | 11 | 13 | 0 | 15.6466 | 15.6466 | 48 | 9.6668 | 0 | 0 | 464.7425 | 0 | 15.6466 | 0 | 1.6315 | 0 | 0 | 0 | 15.6466 | 0 | 0
4 | 11 | 14 | 0 | 32.3157 | 32.3157 | 48 | 10.2684 | 0 | 0 | 464.7373 | 0 | 32.3157 | 0 | 3.3696 | 0 | 0 | 0 | 32.3157 | 0 | 0
4 | 11 | 15 | 9.4375 | 79.8805 | 89.318 | 44.0905 | 11.226 | 0 | 0 | 464.2337 | 0 | 89.318 | 0 | 9.3134 | 0 | 0 | 0 | 89.318 | 0 | 0
4 | 11 | 16 | 0 | 4.3862 | 4.3862 | 48 | 11.853 | 0 | 0 | 457.2858 | 0 | 4.3862 | 0 | 0.45736 | 0 | 0 | 0 | 4.3862 | 0 | 0
4 | 11 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 464.1661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 18 | 0 | 0.085417 | 0.085417 | 48 | 12.4971 | 0 | 0 | 469.0357 | 0 | 0.085417 | 0 | 0.0089066 | 0 | 0 | 0 | 0.085417 | 0 | 0
4 | 11 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 468.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 462.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 425.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 407.4258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 11 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 405.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 404.8842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 400.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 424.6849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.9097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 4 | 0.020833 | 0 | 0.020833 | 11 | 3.3028 | 0.0069209 | 0.0069209 | 463.4773 | 0.020833 | 0 | 9.4266 | 0 | 0 | 0 | 0.020833 | 0 | 0 | 9.4266
4 | 12 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 467.9098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 467.7781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 7 | 0 | 3.6244 | 3.6244 | 48 | 5.0146 | 1.6545 | 1.6545 | 469.4951 | 3.6244 | 0 | 1527.6867 | 0 | 0 | 0 | 3.6244 | 0 | 0 | 1527.6867
4 | 12 | 8 | 0 | 213.5445 | 213.5445 | 48 | 6.2094 | 131.9292 | 131.9292 | 472.6922 | 213.5445 | 0 | 90690.7012 | 0 | 0 | 0 | 213.5445 | 0 | 0 | 90690.7012
4 | 12 | 9 | 0 | 12.226 | 12.226 | 48 | 7.311 | 11.204 | 11.204 | 474.3159 | 12.226 | 0 | 5212.1395 | 0 | 0 | 0 | 12.226 | 0 | 0 | 5212.1395
4 | 12 | 10 | 0 | 7.7194 | 7.7194 | 48 | 8.0567 | 10.5141 | 10.5141 | 471.2421 | 7.7194 | 0 | 3267.1827 | 0 | 0 | 0 | 7.7194 | 0 | 0 | 3267.1827
4 | 12 | 11 | 0 | 15.4254 | 15.4254 | 48 | 9.3109 | 115.3225 | 115.3225 | 471.6107 | 15.4254 | 0 | 6534.3634 | 0 | 0 | 0 | 15.4254 | 0 | 0 | 6534.3634
4 | 12 | 12 | 3.9892 | 14.2292 | 18.2184 | 39.8983 | 9.0058 | 65.1094 | 65.1094 | 473.1286 | 18.2184 | 0 | 7892.7487 | 0 | 0 | 0 | 18.2184 | 0 | 0 | 7892.7487
4 | 12 | 13 | 0 | 5.657 | 5.657 | 48 | 8.4889 | 10.7285 | 10.7285 | 476.6574 | 5.657 | 0 | 2424.9318 | 0 | 0 | 0 | 5.657 | 0 | 0 | 2424.9318
4 | 12 | 14 | 0 | 2.0828 | 2.0828 | 48 | 8.938 | 6.6699 | 6.6699 | 478.2158 | 2.0828 | 0 | 896.0521 | 0 | 0 | 0 | 2.0828 | 0 | 0 | 896.0521
4 | 12 | 15 | 0 | 1.8 | 1.8 | 48 | 9.6075 | 0 | 0 | 476.6952 | 0 | 1.8 | 0 | 0.18769 | 0 | 0 | 0 | 1.8 | 0 | 0
4 | 12 | 16 | 0 | 4.4604 | 4.4604 | 48 | 10.9718 | 0 | 0 | 467.9738 | 0 | 4.4604 | 0 | 0.46509 | 0 | 0 | 0 | 4.4604 | 0 | 0
4 | 12 | 17 | 0 | 22.8939 | 22.8939 | 48 | 10.3786 | 0 | 0 | 463.4778 | 0 | 22.8939 | 0 | 2.3872 | 0 | 0 | 0 | 22.8939 | 0 | 0
4 | 12 | 18 | 0 | 7.8595 | 7.8595 | 48 | 11.0734 | 0 | 0 | 473.4597 | 0 | 7.8595 | 0 | 0.81953 | 0 | 0 | 0 | 7.8595 | 0 | 0
4 | 12 | 19 | 0 | 2.6427 | 2.6427 | 48 | 10.4633 | 0 | 0 | 468.6715 | 0 | 2.6427 | 0 | 0.27556 | 0 | 0 | 0 | 2.6427 | 0 | 0
4 | 12 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 441.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 417.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 389.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 378.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 0 | 115.1107 | 0 | 115.1107 | 11 | 4.1757 | 44.4046 | 44.4046 | 375.9065 | 115.1107 | 0 | 42004.628 | 0 | 0 | 0 | 115.1107 | 0 | 0 | 42004.628
4 | 13 | 1 | 20.4041 | 0 | 20.4041 | 11 | 3.8791 | 7.4623 | 7.4623 | 376.3563 | 20.4041 | 0 | 7454.7774 | 0 | 0 | 0 | 20.4041 | 0 | 0 | 7454.7774
4 | 13 | 2 | 31.0056 | 0 | 31.0056 | 11 | 3.8197 | 11.2229 | 11.2229 | 381.2019 | 31.0056 | 0 | 11478.3394 | 0 | 0 | 0 | 31.0056 | 0 | 0 | 11478.3394
4 | 13 | 3 | 25.1627 | 0 | 25.1627 | 11 | 3.4638 | 8.5788 | 8.5788 | 402.8912 | 25.1627 | 0 | 9861.0257 | 0 | 0 | 0 | 25.1627 | 0 | 0 | 9861.0257
4 | 13 | 4 | 3.8978 | 0 | 3.8978 | 11 | 3.4045 | 1.3161 | 1.3161 | 436.4486 | 3.8978 | 0 | 1658.3007 | 0 | 0 | 0 | 3.8978 | 0 | 0 | 1658.3007
4 | 13 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 440.6257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 440.1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 7 | 0 | 0.42333 | 0.42333 | 48 | 4.6502 | 0.17899 | 0.17899 | 451.3436 | 0.42333 | 0 | 170.7488 | 0 | 0 | 0 | 0.42333 | 0 | 0 | 170.7488
4 | 13 | 8 | 0 | 6.4516 | 6.4516 | 48 | 5.1417 | 3.0292 | 3.0292 | 461.4355 | 6.4516 | 0 | 2667.3308 | 0 | 0 | 0 | 6.4516 | 0 | 0 | 2667.3308
4 | 13 | 9 | 2.7575 | 1.5668 | 4.3243 | 24.4057 | 6.6161 | 3.0369 | 3.0369 | 466.3282 | 4.3243 | 0 | 1910.9842 | 0 | 0 | 0 | 4.3243 | 0 | 0 | 1910.9842
4 | 13 | 10 | 5.3367 | 420.2451 | 425.5818 | 47.536 | 6.9721 | 339.5155 | 288 | 473.3179 | 361.0073 | 64.5745 | 153710.3615 | 6.7334 | 0 | 0 | 361.0073 | 64.5745 | 0 | 153710.3615
4 | 13 | 11 | 4.4925 | 536.6732 | 541.1657 | 47.6928 | 8.5652 | 1102.6714 | 288 | 476.1632 | 141.3438 | 399.8219 | 60561.6118 | 41.6905 | 0 | 0 | 141.3438 | 399.8219 | 0 | 60561.6118
4 | 13 | 12 | 0 | 171.3979 | 171.3979 | 48 | 7.8957 | 211.268 | 211.268 | 477.4156 | 171.3979 | 0 | 73600.92 | 0 | 0 | 0 | 171.3979 | 0 | 0 | 73600.92
4 | 13 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 478.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 14 | 0 | 83.8491 | 83.8491 | 48 | 7.2771 | 75.7141 | 75.7141 | 484.9793 | 83.8491 | 0 | 36640.3329 | 0 | 0 | 0 | 83.8491 | 0 | 0 | 36640.3329
4 | 13 | 15 | 0 | 140.08 | 140.08 | 48 | 7.3449 | 130.3084 | 130.3084 | 480.668 | 140.08 | 0 | 60608.1255 | 0 | 0 | 0 | 140.08 | 0 | 0 | 60608.1255
4 | 13 | 16 | 0 | 146.0254 | 146.0254 | 48 | 6.9975 | 117.6366 | 117.6366 | 463.8309 | 146.0254 | 0 | 60721.8713 | 0 | 0 | 0 | 146.0254 | 0 | 0 | 60721.8713
4 | 13 | 17 | 6.126 | 57.4289 | 63.5549 | 44.4336 | 7.167 | 54.7799 | 54.7799 | 463.4778 | 63.5549 | 0 | 26632.3099 | 0 | 0 | 0 | 63.5549 | 0 | 0 | 26632.3099
4 | 13 | 18 | 76.0438 | 119.8923 | 195.9361 | 33.6401 | 6.7094 | 142.0583 | 142.0583 | 473.4597 | 195.9361 | 0 | 86176.5544 | 0 | 0 | 0 | 195.9361 | 0 | 0 | 86176.5544
4 | 13 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 468.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 441.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 395.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 13 | 22 | 3.2108 | 0 | 3.2108 | 11 | 4.5824 | 1.3392 | 1.3392 | 372.5878 | 3.2108 | 0 | 1160.9982 | 0 | 0 | 0 | 3.2108 | 0 | 0 | 1160.9982
4 | 13 | 23 | 29.7475 | 0 | 29.7475 | 11 | 4.2615 | 11.6602 | 11.6602 | 359.5725 | 29.7475 | 0 | 10369.1534 | 0 | 0 | 0 | 29.7475 | 0 | 0 | 10369.1534
4 | 14 | 0 | 37.381 | 0 | 37.381 | 11 | 3.5232 | 12.8691 | 12.8691 | 358.2431 | 37.381 | 0 | 12980.2939 | 0 | 0 | 0 | 37.381 | 0 | 0 | 12980.2939
4 | 14 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 362.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 378.7914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 394.4913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 411.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 416.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 435.5214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 7 | 3.4075 | 175.8404 | 179.2479 | 47.2966 | 6.1924 | 110.1882 | 110.1882 | 433 | 179.2479 | 0 | 69136.5256 | 0 | 0 | 0 | 179.2479 | 0 | 0 | 69136.5256
4 | 14 | 8 | 1.9233 | 761.287 | 763.2103 | 47.9068 | 6.8788 | 587.9329 | 288 | 436.8518 | 373.8599 | 389.3504 | 145410.9549 | 40.5986 | 0 | 0 | 373.8599 | 389.3504 | 0 | 145410.9549
4 | 14 | 9 | 0.23417 | 271.528 | 271.7622 | 47.9681 | 7.3195 | 249.9745 | 249.9745 | 439.4918 | 271.7622 | 0 | 106401.3249 | 0 | 0 | 0 | 271.7622 | 0 | 0 | 106401.3249
4 | 14 | 10 | 0.99833 | 416.4497 | 417.448 | 47.9115 | 7.4805 | 413.2838 | 288 | 450.0685 | 290.9019 | 126.5461 | 116988.2391 | 13.1953 | 0 | 0 | 290.9019 | 126.5461 | 0 | 116988.2391
4 | 14 | 11 | 0.29667 | 540.9252 | 541.2218 | 47.9797 | 7.2263 | 478.2012 | 288 | 455.6913 | 325.9546 | 215.2672 | 132895.4535 | 22.4465 | 0 | 0 | 325.9546 | 215.2672 | 0 | 132895.4535
4 | 14 | 12 | 0.45917 | 1100.8176 | 1101.2767 | 47.9846 | 7.8703 | 1337.3888 | 288 | 455.453 | 237.1544 | 864.1223 | 96632.9582 | 90.1043 | 0 | 0 | 237.1544 | 864.1223 | 0 | 96632.9582
4 | 14 | 13 | 0.41333 | 1065.1902 | 1065.6036 | 47.9856 | 8.1754 | 1573.0787 | 288 | 463.4407 | 195.0912 | 870.5124 | 81051.6299 | 90.7706 | 0 | 0 | 195.0912 | 870.5124 | 0 | 81051.6299
4 | 14 | 14 | 0.40917 | 1270.6167 | 1271.0258 | 47.9881 | 8.2431 | 1970.7542 | 288 | 462.4279 | 185.7438 | 1085.282 | 76979.6476 | 113.1652 | 0 | 0 | 185.7438 | 1085.282 | 0 | 76979.6476
4 | 14 | 15 | 0.39917 | 1279.7043 | 1280.1035 | 47.9885 | 7.4212 | 1232.676 | 288 | 469.5098 | 299.0809 | 981.0226 | 126068.9571 | 102.2938 | 0 | 0 | 299.0809 | 981.0226 | 0 | 126068.9571
4 | 14 | 16 | 0.41917 | 1115.5519 | 1115.9711 | 47.9861 | 7.3195 | 1026.5017 | 288 | 448.3081 | 313.1019 | 802.8691 | 125341.6074 | 83.7173 | 0 | 0 | 313.1019 | 802.8691 | 0 | 125341.6074
4 | 14 | 17 | 0.44833 | 529.7895 | 530.2379 | 47.9687 | 7.2686 | 477.0464 | 288 | 461.0736 | 320.1125 | 210.1254 | 132240.0164 | 21.9103 | 0 | 0 | 320.1125 | 210.1254 | 0 | 132240.0164
4 | 14 | 18 | 0.025833 | 86.2363 | 86.2621 | 47.9889 | 6.9297 | 67.7212 | 67.7212 | 454.3577 | 86.2621 | 0 | 35054.2394 | 0 | 0 | 0 | 86.2621 | 0 | 0 | 35054.2394
4 | 14 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 454.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 454.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 397.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 376.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 14 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 364.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 355.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 354.9925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 365.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 3 | 2.7208 | 0 | 2.7208 | 11 | 3.3622 | 0.91247 | 0.91247 | 369.8487 | 2.7208 | 0 | 976.3525 | 0 | 0 | 0 | 2.7208 | 0 | 0 | 976.3525
4 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 370.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 375.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 402.3119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 7 | 0 | 2.1567 | 2.1567 | 48 | 6.006 | 1.2568 | 1.2568 | 422.1386 | 2.1567 | 0 | 806.8922 | 0 | 0 | 0 | 2.1567 | 0 | 0 | 806.8922
4 | 15 | 8 | 0.10083 | 417.8028 | 417.9036 | 47.9911 | 6.6246 | 294.3324 | 288 | 422.0717 | 408.9126 | 8.991 | 152966.3126 | 0.93751 | 0 | 0 | 408.9126 | 8.991 | 0 | 152966.3126
4 | 15 | 9 | 0.044167 | 256.5729 | 256.617 | 47.9936 | 7.1924 | 223.5311 | 223.5311 | 406.2409 | 256.617 | 0 | 91932.3514 | 0 | 0 | 0 | 256.617 | 0 | 0 | 91932.3514
4 | 15 | 10 | 0.115 | 315.9452 | 316.0602 | 47.9865 | 7.0398 | 258.8448 | 258.8448 | 406.1015 | 316.0602 | 0 | 113185.8938 | 0 | 0 | 0 | 316.0602 | 0 | 0 | 113185.8938
4 | 15 | 11 | 0.87917 | 643.2757 | 644.1549 | 47.9495 | 7.2093 | 565.0973 | 288 | 412.6647 | 328.2914 | 315.8634 | 119732.894 | 32.9359 | 0 | 0 | 328.2914 | 315.8634 | 0 | 119732.894
4 | 15 | 12 | 0.18333 | 891.8813 | 892.0646 | 47.9924 | 7.9296 | 1122.018 | 288 | 421.929 | 228.9755 | 663.0891 | 85622.3052 | 69.142 | 0 | 0 | 228.9755 | 663.0891 | 0 | 85622.3052
4 | 15 | 13 | 0.7975 | 314.0464 | 314.8439 | 47.9063 | 8.2601 | 494.3926 | 288 | 420.7869 | 183.407 | 131.437 | 68388.911 | 13.7053 | 0 | 0 | 183.407 | 131.437 | 0 | 68388.911
4 | 15 | 14 | 0 | 285.6636 | 285.6636 | 48 | 8.5313 | 563.4335 | 288 | 437.3456 | 146.0175 | 139.6461 | 56851.2533 | 14.5613 | 0 | 0 | 146.0175 | 139.6461 | 0 | 56851.2533
4 | 15 | 15 | 0 | 200.9056 | 200.9056 | 48 | 8.4041 | 353.794 | 288 | 431.7736 | 163.5438 | 37.3618 | 62763.7873 | 3.8958 | 0 | 0 | 163.5438 | 37.3618 | 0 | 62763.7873
4 | 15 | 16 | 0 | 13.1838 | 13.1838 | 48 | 9.1753 | 66.36 | 66.36 | 432.5837 | 13.1838 | 0 | 5070.2798 | 0 | 0 | 0 | 13.1838 | 0 | 0 | 5070.2798
4 | 15 | 17 | 0 | 22.3246 | 22.3246 | 48 | 8.6753 | 50.9653 | 50.9653 | 431.4559 | 22.3246 | 0 | 8560.5107 | 0 | 0 | 0 | 22.3246 | 0 | 0 | 8560.5107
4 | 15 | 18 | 0 | 5.6851 | 5.6851 | 48 | 9.0397 | 21.5684 | 21.5684 | 435.6493 | 5.6851 | 0 | 2203.8187 | 0 | 0 | 0 | 5.6851 | 0 | 0 | 2203.8187
4 | 15 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 431.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 408.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 373.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 354.9691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 15 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 340.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 343.5251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 344.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 343.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 355.6631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 360.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 365.6929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 385.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 7 | 0.375 | 27.1907 | 27.5657 | 47.4967 | 4.8705 | 12.1991 | 12.1991 | 401.4304 | 27.5657 | 0 | 9756.4198 | 0 | 0 | 0 | 27.5657 | 0 | 0 | 9756.4198
4 | 16 | 8 | 0 | 4.8728 | 4.8728 | 48 | 4.8451 | 2.1449 | 2.1449 | 409.9911 | 4.8728 | 0 | 1763.8932 | 0 | 0 | 0 | 4.8728 | 0 | 0 | 1763.8932
4 | 16 | 9 | 0 | 86.2711 | 86.2711 | 48 | 6.3789 | 56.1117 | 56.1117 | 423.9767 | 86.2711 | 0 | 32435.918 | 0 | 0 | 0 | 86.2711 | 0 | 0 | 32435.918
4 | 16 | 10 | 0 | 144.7963 | 144.7963 | 48 | 8.4804 | 272.5078 | 272.5078 | 426.1458 | 144.7963 | 0 | 54754.0943 | 0 | 0 | 0 | 144.7963 | 0 | 0 | 54754.0943
4 | 16 | 11 | 0 | 9.3608 | 9.3608 | 48 | 9.4549 | 144.4804 | 144.4804 | 428.9719 | 9.3608 | 0 | 3566.1985 | 0 | 0 | 0 | 9.3608 | 0 | 0 | 3566.1985
4 | 16 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 428.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 13 | 0 | 19.3944 | 19.3944 | 48 | 9.6159 | 0 | 0 | 424.4451 | 0 | 19.3944 | 0 | 2.0223 | 0 | 0 | 0 | 19.3944 | 0 | 0
4 | 16 | 14 | 0.16583 | 306.6791 | 306.8449 | 47.98 | 9.5227 | 9490.0957 | 288 | 424.4144 | 9.312 | 297.533 | 3505.3399 | 31.0245 | 0 | 0 | 9.312 | 297.533 | 0 | 3505.3399
4 | 16 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 422.4178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 436.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 448.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 18 | 0 | 2.8725 | 2.8725 | 48 | 12.3445 | 0 | 0 | 467.9334 | 0 | 2.8725 | 0 | 0.29952 | 0 | 0 | 0 | 2.8725 | 0 | 0
4 | 16 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 461.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 446.276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 422.7657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 407.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 16 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 396.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 396.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 404.0904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 419.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 436.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 461.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 467.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 481.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 7 | 0 | 0.22833 | 0.22833 | 48 | 4.8281 | 0.10015 | 0.10015 | 487.1795 | 0.22833 | 0 | 100.2793 | 0 | 0 | 0 | 0.22833 | 0 | 0 | 100.2793
4 | 17 | 8 | 0 | 0.21417 | 0.21417 | 48 | 5.4976 | 0.1093 | 0.1093 | 489.0743 | 0.21417 | 0 | 94.4634 | 0 | 0 | 0 | 0.21417 | 0 | 0 | 94.4634
4 | 17 | 9 | 1.7254 | 1.0452 | 2.7706 | 24.9582 | 6.4043 | 1.8164 | 1.8164 | 495.0784 | 2.7706 | 0 | 1302.5224 | 0 | 0 | 0 | 2.7706 | 0 | 0 | 1302.5224
4 | 17 | 10 | 2.7551 | 3.0053 | 5.7605 | 30.3036 | 8.5991 | 12.1388 | 12.1388 | 499.6258 | 5.7605 | 0 | 2703.508 | 0 | 0 | 0 | 5.7605 | 0 | 0 | 2703.508
4 | 17 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 500.3107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 498.0481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 13 | 0 | 0.06427 | 0.06427 | 48 | 9.7939 | 0 | 0 | 498.6943 | 0 | 0.06427 | 0 | 0.0067016 | 0 | 0 | 0 | 0.06427 | 0 | 0
4 | 17 | 14 | 0 | 0.040792 | 0.040792 | 48 | 9.4634 | 0.67166 | 0.67166 | 499.5956 | 0.040792 | 0 | 18.4213 | 0 | 0 | 0 | 0.040792 | 0 | 0 | 18.4213
4 | 17 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 501.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 490.8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 17 | 0 | 13.5126 | 13.5126 | 48 | 11.1073 | 0 | 0 | 493.2854 | 0 | 13.5126 | 0 | 1.409 | 0 | 0 | 0 | 13.5126 | 0 | 0
4 | 17 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 496.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 481.2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 454.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 429.3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 416.5747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 17 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 423.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 421.7427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 420.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 435.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 443.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 462.5523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 473.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 480.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 472.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 8 | 0 | 0.22083 | 0.22083 | 48 | 6.2094 | 0.13643 | 0.13643 | 465.9843 | 0.22083 | 0 | 92.3049 | 0 | 0 | 0 | 0.22083 | 0 | 0 | 92.3049
4 | 18 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 469.5884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 10 | 0 | 1.1741 | 1.1741 | 48 | 8.5482 | 2.3534 | 2.3534 | 468.3826 | 1.1741 | 0 | 493.5641 | 0 | 0 | 0 | 1.1741 | 0 | 0 | 493.5641
4 | 18 | 11 | 0 | 3.6974 | 3.6974 | 48 | 9.1838 | 18.9987 | 18.9987 | 480.9122 | 3.6974 | 0 | 1600.6567 | 0 | 0 | 0 | 3.6974 | 0 | 0 | 1600.6567
4 | 18 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 479.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 479.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 474.9241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 472.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 471.3026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 480.8042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 18 | 0 | 5.8516 | 5.8516 | 48 | 12.4971 | 0 | 0 | 487.5565 | 0 | 5.8516 | 0 | 0.61016 | 0 | 0 | 0 | 5.8516 | 0 | 0
4 | 18 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 475.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 452.2863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 417.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 396.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 18 | 23 | 14.0867 | 0 | 14.0867 | 11 | 4.2398 | 5.4992 | 5.4992 | 391.0251 | 14.0867 | 0 | 5353.2871 | 0 | 0 | 0 | 14.0867 | 0 | 0 | 5353.2871
4 | 19 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 387.2241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 391.7931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 406.3131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 436.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 465.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 475.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 487.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 7 | 0.041667 | 48.8287 | 48.8703 | 47.9685 | 5.0146 | 22.3084 | 22.3084 | 491.4046 | 48.8703 | 0 | 21670.8771 | 0 | 0 | 0 | 48.8703 | 0 | 0 | 21670.8771
4 | 19 | 8 | 0.13083 | 338.6356 | 338.7665 | 47.9857 | 6.2094 | 209.2921 | 209.2921 | 490.4804 | 338.7665 | 0 | 149902.3466 | 0 | 0 | 0 | 338.7665 | 0 | 0 | 149902.3466
4 | 19 | 9 | 0 | 31.7523 | 31.7523 | 48 | 7.311 | 29.098 | 29.098 | 488.7458 | 31.7523 | 0 | 13994.6768 | 0 | 0 | 0 | 31.7523 | 0 | 0 | 13994.6768
4 | 19 | 10 | 0.2475 | 50.449 | 50.6965 | 47.8194 | 8.0567 | 69.0502 | 69.0502 | 488.5829 | 50.6965 | 0 | 22345.1785 | 0 | 0 | 0 | 50.6965 | 0 | 0 | 22345.1785
4 | 19 | 11 | 0.935 | 58.4787 | 59.4137 | 47.4177 | 9.3109 | 444.1851 | 288 | 493.1431 | 38.5225 | 20.8911 | 17170.4689 | 2.1784 | 0 | 0 | 38.5225 | 20.8911 | 0 | 17170.4689
4 | 19 | 12 | 0 | 65.3112 | 65.3112 | 48 | 9.0058 | 233.4113 | 233.4113 | 497.594 | 65.3112 | 0 | 29363.5281 | 0 | 0 | 0 | 65.3112 | 0 | 0 | 29363.5281
4 | 19 | 13 | 0 | 85.1962 | 85.1962 | 48 | 8.4889 | 161.5736 | 161.5736 | 491.8016 | 85.1962 | 0 | 37810.1948 | 0 | 0 | 0 | 85.1962 | 0 | 0 | 37810.1948
4 | 19 | 14 | 0.93167 | 246.186 | 247.1177 | 47.8605 | 8.938 | 791.3645 | 288 | 491.8905 | 89.9331 | 157.1846 | 39933.0161 | 16.39 | 0 | 0 | 89.9331 | 157.1846 | 0 | 39933.0161
4 | 19 | 15 | 10.3675 | 463.2444 | 473.6119 | 47.1901 | 9.6075 | 0 | 0 | 492.4993 | 0 | 473.6119 | 0 | 49.3848 | 0 | 0 | 0 | 473.6119 | 0 | 0
4 | 19 | 16 | 6.8858 | 557.2919 | 564.1777 | 47.5484 | 10.9718 | 0 | 0 | 488.5324 | 0 | 564.1777 | 0 | 58.8283 | 0 | 0 | 0 | 564.1777 | 0 | 0
4 | 19 | 17 | 3.2192 | 180.8307 | 184.0498 | 47.3528 | 10.3786 | 0 | 0 | 485.7729 | 0 | 184.0498 | 0 | 19.1914 | 0 | 0 | 0 | 184.0498 | 0 | 0
4 | 19 | 18 | 3.0492 | 19.9719 | 23.0211 | 43.0993 | 11.0734 | 0 | 0 | 486.0415 | 0 | 23.0211 | 0 | 2.4005 | 0 | 0 | 0 | 23.0211 | 0 | 0
4 | 19 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 475.3559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 461.6948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 434.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 411.6472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 409.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 398.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 395.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 405.6727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 435.5759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 453.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 460.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 460.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 7 | 0.1025 | 105.0559 | 105.1584 | 47.9639 | 4.6502 | 44.4621 | 44.4621 | 464.1767 | 105.1584 | 0 | 43768.2607 | 0 | 0 | 0 | 105.1584 | 0 | 0 | 43768.2607
4 | 20 | 8 | 0.695 | 597.8344 | 598.5294 | 47.957 | 5.1417 | 281.0241 | 281.0241 | 468.2692 | 598.5294 | 0 | 251569.1605 | 0 | 0 | 0 | 598.5294 | 0 | 0 | 251569.1605
4 | 20 | 9 | 0.84583 | 340.7866 | 341.6324 | 47.9084 | 6.6161 | 239.9285 | 239.9285 | 472.0536 | 341.6324 | 0 | 144901.7517 | 0 | 0 | 0 | 341.6324 | 0 | 0 | 144901.7517
4 | 20 | 10 | 0.061667 | 93.897 | 93.9587 | 47.9757 | 6.9721 | 74.9572 | 74.9572 | 476.1146 | 93.9587 | 0 | 40227.3505 | 0 | 0 | 0 | 93.9587 | 0 | 0 | 40227.3505
4 | 20 | 11 | 0.16083 | 582.8388 | 582.9996 | 47.9898 | 8.5652 | 1187.9117 | 288 | 476.0873 | 141.3438 | 441.6559 | 60508.9097 | 46.0526 | 0 | 0 | 141.3438 | 441.6559 | 0 | 60508.9097
4 | 20 | 12 | 0.285 | 914.3001 | 914.5851 | 47.9885 | 7.8957 | 1127.3334 | 288 | 475.4562 | 233.6492 | 680.936 | 99877.4849 | 71.003 | 0 | 0 | 233.6492 | 680.936 | 0 | 99877.4849
4 | 20 | 13 | 0.28917 | 759.5619 | 759.8511 | 47.9859 | 7.4381 | 737.4609 | 288 | 468.3857 | 296.744 | 463.107 | 124751.1197 | 48.2894 | 0 | 0 | 296.744 | 463.107 | 0 | 124751.1197
4 | 20 | 14 | 0.24917 | 530.9798 | 531.229 | 47.9826 | 7.2771 | 479.689 | 288 | 473.2014 | 318.9441 | 212.2849 | 135620.993 | 22.1355 | 0 | 0 | 318.9441 | 212.2849 | 0 | 135620.993
4 | 20 | 15 | 0.044167 | 661.6478 | 661.6919 | 47.9975 | 7.3449 | 615.534 | 288 | 467.8383 | 309.5967 | 352.0953 | 129981.3093 | 36.7139 | 0 | 0 | 309.5967 | 352.0953 | 0 | 129981.3093
4 | 20 | 16 | 0 | 277.0639 | 277.0639 | 48 | 6.9975 | 223.1999 | 223.1999 | 473.9053 | 277.0639 | 0 | 118003.0004 | 0 | 0 | 0 | 277.0639 | 0 | 0 | 118003.0004
4 | 20 | 17 | 0.55917 | 265.0433 | 265.6025 | 47.9221 | 7.167 | 228.9309 | 228.9309 | 469.1268 | 265.6025 | 0 | 111873.0089 | 0 | 0 | 0 | 265.6025 | 0 | 0 | 111873.0089
4 | 20 | 18 | 0 | 6.0427 | 6.0427 | 48 | 6.7094 | 4.3811 | 4.3811 | 475.3708 | 6.0427 | 0 | 2582.459 | 0 | 0 | 0 | 6.0427 | 0 | 0 | 2582.459
4 | 20 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 471.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 448.727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 420.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 404.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 20 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 395.4695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 386.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 390.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 418.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 444.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 476.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 474.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 474.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 7 | 0 | 1.7017 | 1.7017 | 48 | 6.1924 | 1.0461 | 1.0461 | 488.7116 | 1.7017 | 0 | 749.9443 | 0 | 0 | 0 | 1.7017 | 0 | 0 | 749.9443
4 | 21 | 8 | 0.1875 | 78.348 | 78.5355 | 47.9117 | 6.8788 | 60.4992 | 60.4992 | 490.6492 | 78.5355 | 0 | 34770.6146 | 0 | 0 | 0 | 78.5355 | 0 | 0 | 34770.6146
4 | 21 | 9 | 0.255 | 62.369 | 62.624 | 47.8493 | 7.3195 | 57.6033 | 57.6033 | 494.566 | 62.624 | 0 | 27975.1818 | 0 | 0 | 0 | 62.624 | 0 | 0 | 27975.1818
4 | 21 | 10 | 0.65734 | 49.3086 | 49.9659 | 47.5132 | 7.4805 | 49.4675 | 49.4675 | 495.7754 | 49.9659 | 0 | 22397.8349 | 0 | 0 | 0 | 49.9659 | 0 | 0 | 22397.8349
4 | 21 | 11 | 0 | 50.1805 | 50.1805 | 48 | 7.2263 | 44.3374 | 44.3374 | 492.8915 | 50.1805 | 0 | 22324.8794 | 0 | 0 | 0 | 50.1805 | 0 | 0 | 22324.8794
4 | 21 | 12 | 0 | 29.0956 | 29.0956 | 48 | 7.8703 | 35.3337 | 35.3337 | 485.2991 | 29.0956 | 0 | 12723.4962 | 0 | 0 | 0 | 29.0956 | 0 | 0 | 12723.4962
4 | 21 | 13 | 0 | 31.0981 | 31.0981 | 48 | 8.1754 | 45.9081 | 45.9081 | 482.1331 | 31.0981 | 0 | 13500.7249 | 0 | 0 | 0 | 31.0981 | 0 | 0 | 13500.7249
4 | 21 | 14 | 0 | 16.0425 | 16.0425 | 48 | 8.2431 | 24.8743 | 24.8743 | 477.0353 | 16.0425 | 0 | 6882.8106 | 0 | 0 | 0 | 16.0425 | 0 | 0 | 6882.8106
4 | 21 | 15 | 0 | 14.7121 | 14.7121 | 48 | 7.4212 | 14.167 | 14.167 | 479.069 | 14.7121 | 0 | 6341.9143 | 0 | 0 | 0 | 14.7121 | 0 | 0 | 6341.9143
4 | 21 | 16 | 0 | 125.3141 | 125.3141 | 48 | 7.3195 | 115.2675 | 115.2675 | 472.8649 | 125.3141 | 0 | 53241.5681 | 0 | 0 | 0 | 125.3141 | 0 | 0 | 53241.5681
4 | 21 | 17 | 0 | 111.1928 | 111.1928 | 48 | 7.2686 | 100.0384 | 100.0384 | 483.7472 | 111.1928 | 0 | 48451.9651 | 0 | 0 | 0 | 111.1928 | 0 | 0 | 48451.9651
4 | 21 | 18 | 0 | 6.407 | 6.407 | 48 | 6.9297 | 5.0299 | 5.0299 | 488.009 | 6.407 | 0 | 2819.1191 | 0 | 0 | 0 | 6.407 | 0 | 0 | 2819.1191
4 | 21 | 19 | 0 | 0.05 | 0.05 | 48 | 6.9382 | 0.039379 | 0.039379 | 478.6007 | 0.05 | 0 | 21.53 | 0 | 0 | 0 | 0.05 | 0 | 0 | 21.53
4 | 21 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 462.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 435.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 424.3375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 21 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 422.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 414.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 410.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 414.5274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 419.2394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 432.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 449.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 453.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 7 | 7.0175 | 162.9397 | 169.9572 | 46.4723 | 6.006 | 99.0428 | 99.0428 | 459.6285 | 169.9572 | 0 | 70218.8755 | 0 | 0 | 0 | 169.9572 | 0 | 0 | 70218.8755
4 | 22 | 8 | 15.7176 | 301.165 | 316.8826 | 46.1648 | 6.6246 | 223.1826 | 223.1826 | 467.9283 | 316.8826 | 0 | 133649.5136 | 0 | 0 | 0 | 316.8826 | 0 | 0 | 133649.5136
4 | 22 | 9 | 0 | 48.2627 | 48.2627 | 48 | 7.1924 | 42.0401 | 42.0401 | 466.7272 | 48.2627 | 0 | 20208.9048 | 0 | 0 | 0 | 48.2627 | 0 | 0 | 20208.9048
4 | 22 | 10 | 0 | 34.3893 | 34.3893 | 48 | 7.0398 | 28.1639 | 28.1639 | 467.471 | 34.3893 | 0 | 14425.2993 | 0 | 0 | 0 | 34.3893 | 0 | 0 | 14425.2993
4 | 22 | 11 | 0 | 41.8515 | 41.8515 | 48 | 7.2093 | 36.715 | 36.715 | 459.9886 | 41.8515 | 0 | 17242.3316 | 0 | 0 | 0 | 41.8515 | 0 | 0 | 17242.3316
4 | 22 | 12 | 0 | 60.1837 | 60.1837 | 48 | 7.9296 | 75.6976 | 75.6976 | 457.0436 | 60.1837 | 0 | 24617.7538 | 0 | 0 | 0 | 60.1837 | 0 | 0 | 24617.7538
4 | 22 | 13 | 0 | 29.4848 | 29.4848 | 48 | 8.2601 | 46.2994 | 46.2994 | 454.9831 | 29.4848 | 0 | 11999.8316 | 0 | 0 | 0 | 29.4848 | 0 | 0 | 11999.8316
4 | 22 | 14 | 5.2458 | 35.1612 | 40.407 | 43.1965 | 8.5313 | 79.6975 | 79.6975 | 457.2899 | 40.407 | 0 | 16732.2827 | 0 | 0 | 0 | 40.407 | 0 | 0 | 16732.2827
4 | 22 | 15 | 0 | 26.9834 | 26.9834 | 48 | 8.4041 | 47.5178 | 47.5178 | 459.2129 | 26.9834 | 0 | 11095.9419 | 0 | 0 | 0 | 26.9834 | 0 | 0 | 11095.9419
4 | 22 | 16 | 0 | 9.2662 | 9.2662 | 48 | 9.1753 | 46.6407 | 46.6407 | 461.5765 | 9.2662 | 0 | 3832.2638 | 0 | 0 | 0 | 9.2662 | 0 | 0 | 3832.2638
4 | 22 | 17 | 0 | 1.6875 | 1.6875 | 48 | 8.6753 | 3.8524 | 3.8524 | 472.6027 | 1.6875 | 0 | 716.5171 | 0 | 0 | 0 | 1.6875 | 0 | 0 | 716.5171
4 | 22 | 18 | 6.771 | 36.5504 | 43.3214 | 42.217 | 9.0397 | 164.3553 | 164.3553 | 472.1724 | 43.3214 | 0 | 18626.2546 | 0 | 0 | 0 | 43.3214 | 0 | 0 | 18626.2546
4 | 22 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 464.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 457.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 429.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 407.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 22 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 407.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 404.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 405.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 407.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 416.7128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 416.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 5 | 2.0333 | 0 | 2.0333 | 11 | 3.4638 | 0.69323 | 0.69323 | 426.9414 | 2.0333 | 0 | 845.735 | 0 | 0 | 0 | 2.0333 | 0 | 0 | 845.735
4 | 23 | 6 | 15.9101 | 25.7936 | 41.7037 | 33.8844 | 4.1926 | 16.138 | 16.138 | 439.0015 | 41.7037 | 0 | 16894.8959 | 0 | 0 | 0 | 41.7037 | 0 | 0 | 16894.8959
4 | 23 | 7 | 73.3284 | 442.9623 | 516.2907 | 42.7449 | 4.8705 | 228.4837 | 228.4837 | 449.869 | 516.2907 | 0 | 210194.4021 | 0 | 0 | 0 | 516.2907 | 0 | 0 | 210194.4021
4 | 23 | 8 | 20.7382 | 846.7656 | 867.5038 | 47.1155 | 4.8451 | 381.8557 | 288 | 448.3302 | 654.2815 | 213.2223 | 262507.3503 | 22.2332 | 0 | 0 | 654.2815 | 213.2223 | 0 | 262507.3503
4 | 23 | 9 | 14.3442 | 1069.1617 | 1083.5059 | 47.5102 | 6.3789 | 704.7242 | 288 | 449.7494 | 442.7969 | 640.709 | 178110.2824 | 66.8084 | 0 | 0 | 442.7969 | 640.709 | 0 | 178110.2824
4 | 23 | 10 | 7.9 | 927.5937 | 935.4937 | 47.6875 | 8.4804 | 1760.6072 | 288 | 444.5889 | 153.028 | 782.4657 | 60737.0137 | 81.5897 | 0 | 0 | 153.028 | 782.4657 | 0 | 60737.0137
4 | 23 | 11 | 12.9208 | 1019.7165 | 1032.6373 | 47.537 | 9.4549 | 15938.3749 | 288 | 442.7934 | 18.6593 | 1013.978 | 7375.2225 | 105.7301 | 0 | 0 | 18.6593 | 1013.978 | 0 | 7375.2225
4 | 23 | 12 | 13.8508 | 1309.0928 | 1322.9436 | 47.6126 | 9.8362 | 0 | 0 | 439.7744 | 0 | 1322.9436 | 0 | 137.9468 | 0 | 0 | 0 | 1322.9436 | 0 | 0
4 | 23 | 13 | 35.47 | 1102.1162 | 1137.5862 | 46.8463 | 9.6159 | 0 | 0 | 446.0214 | 0 | 1137.5862 | 0 | 118.6191 | 0 | 0 | 0 | 1137.5862 | 0 | 0
4 | 23 | 14 | 36.7717 | 782.6863 | 819.4579 | 46.3397 | 9.5227 | 25344.1821 | 288 | 454.0359 | 9.312 | 810.146 | 3796.4492 | 84.476 | 0 | 0 | 9.312 | 810.146 | 0 | 3796.4492
4 | 23 | 15 | 34.125 | 701.899 | 736.024 | 46.2845 | 10.7175 | 0 | 0 | 462.8641 | 0 | 736.024 | 0 | 76.7471 | 0 | 0 | 0 | 736.024 | 0 | 0
4 | 23 | 16 | 3.5767 | 255.922 | 259.4987 | 47.49 | 12.0564 | 0 | 0 | 463.1205 | 0 | 259.4987 | 0 | 27.0586 | 0 | 0 | 0 | 259.4987 | 0 | 0
4 | 23 | 17 | 0 | 29.8584 | 29.8584 | 48 | 11.8107 | 0 | 0 | 460.8907 | 0 | 29.8584 | 0 | 3.1134 | 0 | 0 | 0 | 29.8584 | 0 | 0
4 | 23 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 473.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 453.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 427.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 399.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 392.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 23 | 23 | 3.1604 | 0 | 3.1604 | 11 | 3.3504 | 1.0579 | 1.0579 | 389.2706 | 3.1604 | 0 | 1195.4944 | 0 | 0 | 0 | 3.1604 | 0 | 0 | 1195.4944
4 | 24 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 389.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 394.6308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 412.206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 441.9964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 475.6382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 484.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 494.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 493.8361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 8 | 2.3834 | 112.6458 | 115.0292 | 47.2334 | 5.4976 | 58.7057 | 58.7057 | 487.6652 | 115.0292 | 0 | 50662.5065 | 0 | 0 | 0 | 115.0292 | 0 | 0 | 50662.5065
4 | 24 | 9 | 0 | 20.4523 | 20.4523 | 48 | 6.4043 | 13.4086 | 13.4086 | 489.0146 | 20.4523 | 0 | 9019.7822 | 0 | 0 | 0 | 20.4523 | 0 | 0 | 9019.7822
4 | 24 | 10 | 0 | 16.5242 | 16.5242 | 48 | 8.5991 | 34.8208 | 34.8208 | 489.8653 | 16.5242 | 0 | 7301.4667 | 0 | 0 | 0 | 16.5242 | 0 | 0 | 7301.4667
4 | 24 | 11 | 0 | 22.1522 | 22.1522 | 48 | 9.6413 | 0 | 0 | 488.2195 | 0 | 22.1522 | 0 | 2.3099 | 0 | 0 | 0 | 22.1522 | 0 | 0
4 | 24 | 12 | 0 | 29.364 | 29.364 | 48 | 9.7176 | 0 | 0 | 486.5429 | 0 | 29.364 | 0 | 3.0619 | 0 | 0 | 0 | 29.364 | 0 | 0
4 | 24 | 13 | 0 | 24.5033 | 24.5033 | 48 | 9.7939 | 0 | 0 | 483.6695 | 0 | 24.5033 | 0 | 2.555 | 0 | 0 | 0 | 24.5033 | 0 | 0
4 | 24 | 14 | 0.94667 | 40.3706 | 41.3173 | 47.1523 | 9.4634 | 680.3173 | 288 | 481.7095 | 17.4909 | 23.8263 | 7600.8047 | 2.4844 | 0 | 0 | 17.4909 | 23.8263 | 0 | 7600.8047
4 | 24 | 15 | 0 | 11.6772 | 11.6772 | 48 | 10.5311 | 0 | 0 | 481.6787 | 0 | 11.6772 | 0 | 1.2176 | 0 | 0 | 0 | 11.6772 | 0 | 0
4 | 24 | 16 | 0 | 6.5759 | 6.5759 | 48 | 11.0904 | 0 | 0 | 472.5101 | 0 | 6.5759 | 0 | 0.68569 | 0 | 0 | 0 | 6.5759 | 0 | 0
4 | 24 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 464.8201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 476.2982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 462.1852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 434.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 396.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 378.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 24 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 375.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 376.7447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 375.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 390.3108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 427.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 459.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 474.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 484.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 7 | 0 | 1.5692 | 1.5692 | 48 | 5.2518 | 0.75547 | 0.75547 | 487.0009 | 1.5692 | 0 | 688.8699 | 0 | 0 | 0 | 1.5692 | 0 | 0 | 688.8699
4 | 25 | 8 | 3.3425 | 183.359 | 186.7015 | 47.3376 | 6.2094 | 115.3454 | 115.3454 | 479.7168 | 186.7015 | 0 | 80725.8585 | 0 | 0 | 0 | 186.7015 | 0 | 0 | 80725.8585
4 | 25 | 9 | 2.4568 | 67.6587 | 70.1155 | 46.7035 | 7.328 | 64.7358 | 64.7358 | 477.345 | 70.1155 | 0 | 30194.6261 | 0 | 0 | 0 | 70.1155 | 0 | 0 | 30194.6261
4 | 25 | 10 | 23.7751 | 25.939 | 49.7141 | 30.3052 | 8.5482 | 99.6493 | 99.6493 | 480.1027 | 49.7141 | 0 | 22361.2872 | 0 | 0 | 0 | 49.7141 | 0 | 0 | 22361.2872
4 | 25 | 11 | 9.3467 | 276.4338 | 285.7805 | 46.7899 | 9.1838 | 1468.4467 | 288 | 474.5103 | 56.0489 | 229.7316 | 23973.2465 | 23.9547 | 0 | 0 | 56.0489 | 229.7316 | 0 | 23973.2465
4 | 25 | 12 | 4.6618 | 81.0102 | 85.6719 | 45.9867 | 9.8701 | 0 | 0 | 473.3426 | 0 | 85.6719 | 0 | 8.9332 | 0 | 0 | 0 | 85.6719 | 0 | 0
4 | 25 | 13 | 4.0717 | 204.961 | 209.0327 | 47.2793 | 9.6668 | 0 | 0 | 469.6523 | 0 | 209.0327 | 0 | 21.7964 | 0 | 0 | 0 | 209.0327 | 0 | 0
4 | 25 | 14 | 14.0192 | 443.8137 | 457.8328 | 46.867 | 10.2684 | 0 | 0 | 469.6523 | 0 | 457.8328 | 0 | 47.7394 | 0 | 0 | 0 | 457.8328 | 0 | 0
4 | 25 | 15 | 13.525 | 266.9553 | 280.4803 | 46.2158 | 11.226 | 0 | 0 | 476.8407 | 0 | 280.4803 | 0 | 29.2464 | 0 | 0 | 0 | 280.4803 | 0 | 0
4 | 25 | 16 | 12.1592 | 153.7152 | 165.8744 | 45.2878 | 11.853 | 0 | 0 | 475.7075 | 0 | 165.8744 | 0 | 17.2962 | 0 | 0 | 0 | 165.8744 | 0 | 0
4 | 25 | 17 | 11.37 | 112.3744 | 123.7444 | 44.6003 | 11.7514 | 0 | 0 | 474.8767 | 0 | 123.7444 | 0 | 12.9032 | 0 | 0 | 0 | 123.7444 | 0 | 0
4 | 25 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 477.2217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 464.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 440.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 412.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 395.2455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 25 | 23 | 0.31996 | 0 | 0.31996 | 11 | 4.2398 | 0.12491 | 0.12491 | 389.6088 | 0.31996 | 0 | 121.139 | 0 | 0 | 0 | 0.31996 | 0 | 0 | 121.139
4 | 26 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 384.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 386.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 405.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 442.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 4 | 10.3892 | 0 | 10.3892 | 11 | 3.3028 | 3.4513 | 3.4513 | 469.0364 | 10.3892 | 0 | 4758.6169 | 0 | 0 | 0 | 10.3892 | 0 | 0 | 4758.6169
4 | 26 | 5 | 7.8942 | 0 | 7.8942 | 11 | 3.7096 | 2.8039 | 2.8039 | 478.7494 | 7.8942 | 0 | 3692.5115 | 0 | 0 | 0 | 7.8942 | 0 | 0 | 3692.5115
4 | 26 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 487.5857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 7 | 0 | 0.23516 | 0.23516 | 48 | 5.0146 | 0.10734 | 0.10734 | 479.4721 | 0.23516 | 0 | 101.4631 | 0 | 0 | 0 | 0.23516 | 0 | 0 | 101.4631
4 | 26 | 8 | 0 | 6.6928 | 6.6928 | 48 | 6.2094 | 4.1348 | 4.1348 | 482.93 | 6.6928 | 0 | 2910.8879 | 0 | 0 | 0 | 6.6928 | 0 | 0 | 2910.8879
4 | 26 | 9 | 0 | 11.9159 | 11.9159 | 48 | 7.311 | 10.9198 | 10.9198 | 489.5539 | 11.9159 | 0 | 5261.5213 | 0 | 0 | 0 | 11.9159 | 0 | 0 | 5261.5213
4 | 26 | 10 | 0 | 61.8611 | 61.8611 | 48 | 8.0567 | 84.2567 | 84.2567 | 481.1754 | 61.8611 | 0 | 26796.7243 | 0 | 0 | 0 | 61.8611 | 0 | 0 | 26796.7243
4 | 26 | 11 | 0 | 25.4489 | 25.4489 | 48 | 9.3109 | 190.2595 | 190.2595 | 472.9973 | 25.4489 | 0 | 10815.7076 | 0 | 0 | 0 | 25.4489 | 0 | 0 | 10815.7076
4 | 26 | 12 | 64.5817 | 196.991 | 261.5727 | 38.8648 | 9.0058 | 934.817 | 288 | 474.6477 | 80.5858 | 180.9869 | 35117.901 | 18.872 | 0 | 0 | 80.5858 | 180.9869 | 0 | 35117.901
4 | 26 | 13 | 11.6239 | 119.6314 | 131.2554 | 44.7233 | 8.4889 | 248.9244 | 248.9244 | 475.4621 | 131.2554 | 0 | 56536.7714 | 0 | 0 | 0 | 131.2554 | 0 | 0 | 56536.7714
4 | 26 | 14 | 0 | 4.8096 | 4.8096 | 48 | 8.938 | 15.4022 | 15.4022 | 472.8172 | 4.8096 | 0 | 2043.2 | 0 | 0 | 0 | 4.8096 | 0 | 0 | 2043.2
4 | 26 | 15 | 0 | 9.553 | 9.553 | 48 | 9.6075 | 0 | 0 | 480.1171 | 0 | 9.553 | 0 | 0.99611 | 0 | 0 | 0 | 9.553 | 0 | 0
4 | 26 | 16 | 0 | 11.0838 | 11.0838 | 48 | 10.9718 | 0 | 0 | 490.5434 | 0 | 11.0838 | 0 | 1.1557 | 0 | 0 | 0 | 11.0838 | 0 | 0
4 | 26 | 17 | 0 | 3.3748 | 3.3748 | 48 | 10.3786 | 0 | 0 | 484.124 | 0 | 3.3748 | 0 | 0.3519 | 0 | 0 | 0 | 3.3748 | 0 | 0
4 | 26 | 18 | 0 | 0.018292 | 0.018292 | 48 | 11.0734 | 0 | 0 | 489.0289 | 0 | 0.018292 | 0 | 0.0019073 | 0 | 0 | 0 | 0.018292 | 0 | 0
4 | 26 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 487.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 475.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 445.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 413.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 26 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 391.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 380.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 379.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 393.1081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 419.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 444.6053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 452.1366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 461.7892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 7 | 0 | 1.3958 | 1.3958 | 48 | 4.6502 | 0.59017 | 0.59017 | 456.9272 | 1.3958 | 0 | 570.7942 | 0 | 0 | 0 | 1.3958 | 0 | 0 | 570.7942
4 | 27 | 8 | 1.4242 | 168.4107 | 169.8349 | 47.6897 | 5.1417 | 79.7416 | 79.7416 | 457.8566 | 169.8349 | 0 | 69660.6467 | 0 | 0 | 0 | 169.8349 | 0 | 0 | 69660.6467
4 | 27 | 9 | 0 | 59.0745 | 59.0745 | 48 | 6.6161 | 41.488 | 41.488 | 461.1084 | 59.0745 | 0 | 24404.1584 | 0 | 0 | 0 | 59.0745 | 0 | 0 | 24404.1584
4 | 27 | 10 | 0 | 66.8552 | 66.8552 | 48 | 6.9721 | 53.335 | 53.335 | 466.5615 | 66.8552 | 0 | 27983.0284 | 0 | 0 | 0 | 66.8552 | 0 | 0 | 27983.0284
4 | 27 | 11 | 0 | 72.701 | 72.701 | 48 | 8.5652 | 148.1344 | 148.1344 | 468.0744 | 72.701 | 0 | 30539.8091 | 0 | 0 | 0 | 72.701 | 0 | 0 | 30539.8091
4 | 27 | 12 | 0 | 45.3513 | 45.3513 | 48 | 7.8957 | 55.9009 | 55.9009 | 465.8894 | 45.3513 | 0 | 18951.8485 | 0 | 0 | 0 | 45.3513 | 0 | 0 | 18951.8485
4 | 27 | 13 | 0.57025 | 38.6187 | 39.189 | 47.4616 | 7.4381 | 38.0342 | 38.0342 | 466.2772 | 39.189 | 0 | 16412.95 | 0 | 0 | 0 | 39.189 | 0 | 0 | 16412.95
4 | 27 | 14 | 0 | 24.4799 | 24.4799 | 48 | 7.2771 | 22.1049 | 22.1049 | 470.151 | 24.4799 | 0 | 10334.2293 | 0 | 0 | 0 | 24.4799 | 0 | 0 | 10334.2293
4 | 27 | 15 | 0 | 35.1008 | 35.1008 | 48 | 7.3449 | 32.6522 | 32.6522 | 479.0091 | 35.1008 | 0 | 15128.7431 | 0 | 0 | 0 | 35.1008 | 0 | 0 | 15128.7431
4 | 27 | 16 | 0 | 33.5799 | 33.5799 | 48 | 6.9975 | 27.0516 | 27.0516 | 485.7314 | 33.5799 | 0 | 14698.9563 | 0 | 0 | 0 | 33.5799 | 0 | 0 | 14698.9563
4 | 27 | 17 | 0 | 4.621 | 4.621 | 48 | 7.167 | 3.9829 | 3.9829 | 487.923 | 4.621 | 0 | 2032.8627 | 0 | 0 | 0 | 4.621 | 0 | 0 | 2032.8627
4 | 27 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 497.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 484.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 460.7701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 443.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 421.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 27 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 412.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 405.1961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 414.7823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 433.1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 454.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 474.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 493.4927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 498.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 7 | 0 | 1.0017 | 1.0017 | 48 | 6.1924 | 0.61575 | 0.61575 | 491.9761 | 1.0017 | 0 | 444.7161 | 0 | 0 | 0 | 1.0017 | 0 | 0 | 444.7161
4 | 28 | 8 | 5.5383 | 48.2381 | 53.7764 | 44.1894 | 6.8788 | 41.4262 | 41.4262 | 495.264 | 53.7764 | 0 | 24257.1733 | 0 | 0 | 0 | 53.7764 | 0 | 0 | 24257.1733
4 | 28 | 9 | 0 | 43.3245 | 43.3245 | 48 | 7.3195 | 39.8511 | 39.8511 | 491.7922 | 43.3245 | 0 | 19227.0946 | 0 | 0 | 0 | 43.3245 | 0 | 0 | 19227.0946
4 | 28 | 10 | 31.8967 | 353.8247 | 385.7214 | 44.9403 | 7.4805 | 381.8736 | 288 | 499.3186 | 290.9019 | 94.8195 | 132179.5154 | 9.8871 | 0 | 0 | 290.9019 | 94.8195 | 0 | 132179.5154
4 | 28 | 11 | 42.8081 | 692.9745 | 735.7826 | 45.8473 | 7.2263 | 650.1071 | 288 | 498.1983 | 325.9546 | 409.828 | 147445.8755 | 42.7338 | 0 | 0 | 325.9546 | 409.828 | 0 | 147445.8755
4 | 28 | 12 | 25.595 | 799.2444 | 824.8394 | 46.8519 | 7.8703 | 1001.6837 | 288 | 499.4687 | 237.1544 | 587.6849 | 107340.0881 | 61.2794 | 0 | 0 | 237.1544 | 587.6849 | 0 | 107340.0881
4 | 28 | 13 | 17.4559 | 918.3375 | 935.7933 | 47.3098 | 8.1754 | 1381.4486 | 288 | 490.2411 | 195.0912 | 740.7021 | 86412.0077 | 77.235 | 0 | 0 | 195.0912 | 740.7021 | 0 | 86412.0077
4 | 28 | 14 | 190.1005 | 761.4698 | 951.5703 | 40.6083 | 8.2431 | 1475.4312 | 288 | 498.8687 | 185.7438 | 765.8265 | 85119.0362 | 79.8547 | 0 | 0 | 185.7438 | 765.8265 | 0 | 85119.0362
4 | 28 | 15 | 90.1164 | 593.989 | 684.1054 | 43.126 | 7.4212 | 658.7595 | 288 | 504.7792 | 299.0809 | 385.0245 | 138071.6363 | 40.1475 | 0 | 0 | 299.0809 | 385.0245 | 0 | 138071.6363
4 | 28 | 16 | 30.8876 | 72.7631 | 103.6507 | 36.9741 | 7.3195 | 95.3409 | 95.3409 | 498.4488 | 103.6507 | 0 | 47832.1969 | 0 | 0 | 0 | 103.6507 | 0 | 0 | 47832.1969
4 | 28 | 17 | 4.3473 | 257.5278 | 261.8751 | 47.3858 | 7.2686 | 235.6048 | 235.6048 | 497.7837 | 261.8751 | 0 | 117948.0107 | 0 | 0 | 0 | 261.8751 | 0 | 0 | 117948.0107
4 | 28 | 18 | 0 | 1.785 | 1.785 | 48 | 6.9297 | 1.4013 | 1.4013 | 499.8072 | 1.785 | 0 | 806.4759 | 0 | 0 | 0 | 1.785 | 0 | 0 | 806.4759
4 | 28 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 490.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 486.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 462.2945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 434.3626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 28 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 425.6374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 406.8391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 395.8809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 400.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 409.7321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 414.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 434.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 447.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 7 | 1.9817 | 243.1884 | 245.1701 | 47.7009 | 6.006 | 142.8731 | 142.8731 | 456.0384 | 245.1701 | 0 | 100112.1336 | 0 | 0 | 0 | 245.1701 | 0 | 0 | 100112.1336
4 | 29 | 8 | 1.995 | 472.6854 | 474.6804 | 47.8445 | 6.6246 | 334.3207 | 288 | 461.7557 | 408.9126 | 65.7678 | 169253.5407 | 6.8578 | 0 | 0 | 408.9126 | 65.7678 | 0 | 169253.5407
4 | 29 | 9 | 0 | 254.2783 | 254.2783 | 48 | 7.1924 | 221.4939 | 221.4939 | 471.5517 | 254.2783 | 0 | 107700.0111 | 0 | 0 | 0 | 254.2783 | 0 | 0 | 107700.0111
4 | 29 | 10 | 0 | 227.1978 | 227.1978 | 48 | 7.0398 | 186.0689 | 186.0689 | 471.1618 | 227.1978 | 0 | 96141.4184 | 0 | 0 | 0 | 227.1978 | 0 | 0 | 96141.4184
4 | 29 | 11 | 0 | 314.7836 | 314.7836 | 48 | 7.2093 | 276.15 | 276.15 | 464.7304 | 314.7836 | 0 | 131179.8752 | 0 | 0 | 0 | 314.7836 | 0 | 0 | 131179.8752
4 | 29 | 12 | 0 | 185.8153 | 185.8153 | 48 | 7.9296 | 233.7141 | 233.7141 | 465.9424 | 185.8153 | 0 | 77660.0811 | 0 | 0 | 0 | 185.8153 | 0 | 0 | 77660.0811
4 | 29 | 13 | 0 | 43.5046 | 43.5046 | 48 | 8.2601 | 68.3143 | 68.3143 | 464.3342 | 43.5046 | 0 | 18112.4527 | 0 | 0 | 0 | 43.5046 | 0 | 0 | 18112.4527
4 | 29 | 14 | 0 | 33.5603 | 33.5603 | 48 | 8.5313 | 66.1933 | 66.1933 | 467.3316 | 33.5603 | 0 | 14072.9073 | 0 | 0 | 0 | 33.5603 | 0 | 0 | 14072.9073
4 | 29 | 15 | 0 | 21.347 | 21.347 | 48 | 8.4041 | 37.592 | 37.592 | 473.0199 | 21.347 | 0 | 9072.8921 | 0 | 0 | 0 | 21.347 | 0 | 0 | 9072.8921
4 | 29 | 16 | 0 | 11.718 | 11.718 | 48 | 9.1753 | 58.9818 | 58.9818 | 475.1475 | 11.718 | 0 | 5005.3039 | 0 | 0 | 0 | 11.718 | 0 | 0 | 5005.3039
4 | 29 | 17 | 0 | 3.6082 | 3.6082 | 48 | 8.6753 | 8.2373 | 8.2373 | 464.8148 | 3.6082 | 0 | 1503.967 | 0 | 0 | 0 | 3.6082 | 0 | 0 | 1503.967
4 | 29 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 473.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 472.9215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 465.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 448.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 426.4958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 29 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 420.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 401.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 394.272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 394.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 402.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 401.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 422.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 6 | 0 | 0.34083 | 0.34083 | 48 | 4.1926 | 0.13189 | 0.13189 | 432.6714 | 0.34083 | 0 | 131.1088 | 0 | 0 | 0 | 0.34083 | 0 | 0 | 131.1088
4 | 30 | 7 | 65.1954 | 566.5623 | 631.7577 | 44.1817 | 4.8705 | 279.5834 | 279.5834 | 458.6658 | 631.7577 | 0 | 261853.5018 | 0 | 0 | 0 | 631.7577 | 0 | 0 | 261853.5018
4 | 30 | 8 | 3.1309 | 891.1815 | 894.3123 | 47.8705 | 4.8451 | 393.6562 | 288 | 478.9815 | 654.2815 | 240.0309 | 282067.9459 | 25.0286 | 0 | 0 | 654.2815 | 240.0309 | 0 | 282067.9459
4 | 30 | 9 | 0.22583 | 1270.263 | 1270.4888 | 47.9934 | 6.3789 | 826.34 | 288 | 485.6468 | 442.7969 | 827.6919 | 193791.5441 | 86.3056 | 0 | 0 | 442.7969 | 827.6919 | 0 | 193791.5441
4 | 30 | 10 | 0.20083 | 820.6269 | 820.8277 | 47.9909 | 8.4804 | 1544.8048 | 288 | 482.8513 | 153.028 | 667.7997 | 66545.8007 | 69.6332 | 0 | 0 | 153.028 | 667.7997 | 0 | 66545.8007
4 | 30 | 11 | 0.029167 | 459.6591 | 459.6883 | 47.9977 | 9.4549 | 7095.1188 | 288 | 485.9713 | 18.6593 | 441.029 | 8172.2991 | 45.9872 | 0 | 0 | 18.6593 | 441.029 | 0 | 8172.2991
4 | 30 | 12 | 0 | 110.2638 | 110.2638 | 48 | 9.8362 | 0 | 0 | 480.295 | 0 | 110.2638 | 0 | 11.4975 | 0 | 0 | 0 | 110.2638 | 0 | 0
4 | 30 | 13 | 0 | 48.0626 | 48.0626 | 48 | 9.6159 | 0 | 0 | 477.3343 | 0 | 48.0626 | 0 | 5.0116 | 0 | 0 | 0 | 48.0626 | 0 | 0
4 | 30 | 14 | 0 | 139.6692 | 139.6692 | 48 | 9.5227 | 4319.6882 | 288 | 482.3444 | 9.312 | 130.3573 | 4044.5953 | 13.5927 | 0 | 0 | 9.312 | 130.3573 | 0 | 4044.5953
4 | 30 | 15 | 0.023333 | 396.4954 | 396.5187 | 47.9978 | 10.7175 | 0 | 0 | 484.0159 | 0 | 396.5187 | 0 | 41.346 | 0 | 0 | 0 | 396.5187 | 0 | 0
4 | 30 | 16 | 0 | 216.2992 | 216.2992 | 48 | 12.0564 | 0 | 0 | 485.0758 | 0 | 216.2992 | 0 | 22.5541 | 0 | 0 | 0 | 216.2992 | 0 | 0
4 | 30 | 17 | 0 | 7.0087 | 7.0087 | 48 | 11.8107 | 0 | 0 | 478.8796 | 0 | 7.0087 | 0 | 0.73082 | 0 | 0 | 0 | 7.0087 | 0 | 0
4 | 30 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 481.6106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 19 | 0 | 0.014772 | 0.014772 | 48 | 12.2767 | 0 | 0 | 480.1887 | 0 | 0.014772 | 0 | 0.0015403 | 0 | 0 | 0 | 0.014772 | 0 | 0
4 | 30 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 459.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 434.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 410.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 30 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 403.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 399.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 401.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 424.1818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 472.3914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 481.9108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 478.2597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 7 | 0 | 7.7542 | 7.7542 | 48 | 4.8281 | 3.4011 | 3.4011 | 464.526 | 7.7542 | 0 | 3229.8291 | 0 | 0 | 0 | 7.7542 | 0 | 0 | 3229.8291
5 | 1 | 8 | 0 | 20.6226 | 20.6226 | 48 | 5.4976 | 10.5249 | 10.5249 | 467.0585 | 20.6226 | 0 | 8642.0805 | 0 | 0 | 0 | 20.6226 | 0 | 0 | 8642.0805
5 | 1 | 9 | 0 | 20.5885 | 20.5885 | 48 | 6.4043 | 13.4979 | 13.4979 | 465.9719 | 20.5885 | 0 | 8605.4315 | 0 | 0 | 0 | 20.5885 | 0 | 0 | 8605.4315
5 | 1 | 10 | 0 | 18.5657 | 18.5657 | 48 | 8.5991 | 39.1227 | 39.1227 | 467.7435 | 18.5657 | 0 | 7792.8136 | 0 | 0 | 0 | 18.5657 | 0 | 0 | 7792.8136
5 | 1 | 11 | 0 | 27.9318 | 27.9318 | 48 | 9.6413 | 0 | 0 | 462.6473 | 0 | 27.9318 | 0 | 2.9125 | 0 | 0 | 0 | 27.9318 | 0 | 0
5 | 1 | 12 | 0 | 32.8862 | 32.8862 | 48 | 9.7176 | 0 | 0 | 461.3792 | 0 | 32.8862 | 0 | 3.4291 | 0 | 0 | 0 | 32.8862 | 0 | 0
5 | 1 | 13 | 0 | 25.582 | 25.582 | 48 | 9.7939 | 0 | 0 | 464.3309 | 0 | 25.582 | 0 | 2.6675 | 0 | 0 | 0 | 25.582 | 0 | 0
5 | 1 | 14 | 0 | 29.3817 | 29.3817 | 48 | 9.4634 | 483.7901 | 288 | 464.2312 | 17.4909 | 11.8908 | 7280.2652 | 1.2399 | 0 | 0 | 17.4909 | 11.8908 | 0 | 7280.2652
5 | 1 | 15 | 0 | 23.2949 | 23.2949 | 48 | 10.5311 | 0 | 0 | 474.2626 | 0 | 23.2949 | 0 | 2.429 | 0 | 0 | 0 | 23.2949 | 0 | 0
5 | 1 | 16 | 0 | 19.2389 | 19.2389 | 48 | 11.0904 | 0 | 0 | 469.7648 | 0 | 19.2389 | 0 | 2.0061 | 0 | 0 | 0 | 19.2389 | 0 | 0
5 | 1 | 17 | 0 | 0.84066 | 0.84066 | 48 | 11.1073 | 0 | 0 | 467.3806 | 0 | 0.84066 | 0 | 0.087657 | 0 | 0 | 0 | 0.84066 | 0 | 0
5 | 1 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 475.6626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 469.504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 451.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 428.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 423.6603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 423.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 415.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 419.3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 430.8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 461.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 475.6985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 477.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 476.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 7 | 0 | 3.7584 | 3.7584 | 48 | 5.2518 | 1.8095 | 1.8095 | 468.1924 | 3.7584 | 0 | 1579.2408 | 0 | 0 | 0 | 3.7584 | 0 | 0 | 1579.2408
5 | 2 | 8 | 0 | 9.8973 | 9.8973 | 48 | 6.2094 | 6.1146 | 6.1146 | 467.5669 | 9.8973 | 0 | 4152.5859 | 0 | 0 | 0 | 9.8973 | 0 | 0 | 4152.5859
5 | 2 | 9 | 0 | 19.6723 | 19.6723 | 48 | 7.328 | 18.1629 | 18.1629 | 473.4485 | 19.6723 | 0 | 8369.5386 | 0 | 0 | 0 | 19.6723 | 0 | 0 | 8369.5386
5 | 2 | 10 | 0 | 15.0176 | 15.0176 | 48 | 8.5482 | 30.102 | 30.102 | 469.8526 | 15.0176 | 0 | 6335.2213 | 0 | 0 | 0 | 15.0176 | 0 | 0 | 6335.2213
5 | 2 | 11 | 0 | 30.5062 | 30.5062 | 48 | 9.1838 | 156.752 | 156.752 | 467.6858 | 30.5062 | 0 | 12803 | 0 | 0 | 0 | 30.5062 | 0 | 0 | 12803
5 | 2 | 12 | 0 | 19.0815 | 19.0815 | 48 | 9.8701 | 0 | 0 | 467.6862 | 0 | 19.0815 | 0 | 1.9897 | 0 | 0 | 0 | 19.0815 | 0 | 0
5 | 2 | 13 | 0 | 17.3374 | 17.3374 | 48 | 9.6668 | 0 | 0 | 465.9247 | 0 | 17.3374 | 0 | 1.8078 | 0 | 0 | 0 | 17.3374 | 0 | 0
5 | 2 | 14 | 0 | 12.7452 | 12.7452 | 48 | 10.2684 | 0 | 0 | 469.4144 | 0 | 12.7452 | 0 | 1.329 | 0 | 0 | 0 | 12.7452 | 0 | 0
5 | 2 | 15 | 0 | 5.2545 | 5.2545 | 48 | 11.226 | 0 | 0 | 471.2507 | 0 | 5.2545 | 0 | 0.5479 | 0 | 0 | 0 | 5.2545 | 0 | 0
5 | 2 | 16 | 0 | 0.02825 | 0.02825 | 48 | 11.853 | 0 | 0 | 484.4137 | 0 | 0.02825 | 0 | 0.0029457 | 0 | 0 | 0 | 0.02825 | 0 | 0
5 | 2 | 17 | 0 | 0.041667 | 0.041667 | 48 | 11.7514 | 0 | 0 | 487.0578 | 0 | 0.041667 | 0 | 0.0043447 | 0 | 0 | 0 | 0.041667 | 0 | 0
5 | 2 | 18 | 0 | 4.6986 | 4.6986 | 48 | 12.4971 | 0 | 0 | 489.3201 | 0 | 4.6986 | 0 | 0.48994 | 0 | 0 | 0 | 4.6986 | 0 | 0
5 | 2 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 495.5541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 480.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 459.1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 444.4098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 448.7343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 446.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 452.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 465.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 481.2089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 488.9161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 497.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 493.4977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 494.3758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 8 | 0 | 0.10074 | 0.10074 | 48 | 6.2094 | 0.062237 | 0.062237 | 497.9903 | 0.10074 | 0 | 45.3317 | 0 | 0 | 0 | 0.10074 | 0 | 0 | 45.3317
5 | 3 | 9 | 0 | 4.4032 | 4.4032 | 48 | 7.311 | 4.0351 | 4.0351 | 492.2615 | 4.4032 | 0 | 1956.1561 | 0 | 0 | 0 | 4.4032 | 0 | 0 | 1956.1561
5 | 3 | 10 | 0 | 6.4284 | 6.4284 | 48 | 8.0567 | 8.7557 | 8.7557 | 497.8633 | 6.4284 | 0 | 2891.9052 | 0 | 0 | 0 | 6.4284 | 0 | 0 | 2891.9052
5 | 3 | 11 | 0 | 23.0915 | 23.0915 | 48 | 9.3109 | 172.6355 | 172.6355 | 492.2647 | 23.0915 | 0 | 10258.7471 | 0 | 0 | 0 | 23.0915 | 0 | 0 | 10258.7471
5 | 3 | 12 | 0 | 13.0018 | 13.0018 | 48 | 9.0058 | 46.4662 | 46.4662 | 499.8245 | 13.0018 | 0 | 5874.5222 | 0 | 0 | 0 | 13.0018 | 0 | 0 | 5874.5222
5 | 3 | 13 | 0 | 14.6999 | 14.6999 | 48 | 8.4889 | 27.8783 | 27.8783 | 499.7016 | 14.6999 | 0 | 6639.9816 | 0 | 0 | 0 | 14.6999 | 0 | 0 | 6639.9816
5 | 3 | 14 | 0 | 69.0806 | 69.0806 | 48 | 8.938 | 221.2222 | 221.2222 | 500.7902 | 69.0806 | 0 | 31279.0103 | 0 | 0 | 0 | 69.0806 | 0 | 0 | 31279.0103
5 | 3 | 15 | 0 | 55.0546 | 55.0546 | 48 | 9.6075 | 0 | 0 | 503.9439 | 0 | 55.0546 | 0 | 5.7407 | 0 | 0 | 0 | 55.0546 | 0 | 0
5 | 3 | 16 | 0 | 76.0945 | 76.0945 | 48 | 10.9718 | 0 | 0 | 505.7956 | 0 | 76.0945 | 0 | 7.9346 | 0 | 0 | 0 | 76.0945 | 0 | 0
5 | 3 | 17 | 0 | 8.4073 | 8.4073 | 48 | 10.3786 | 0 | 0 | 498.1847 | 0 | 8.4073 | 0 | 0.87665 | 0 | 0 | 0 | 8.4073 | 0 | 0
5 | 3 | 18 | 0 | 0.63612 | 0.63612 | 48 | 11.0734 | 0 | 0 | 502.9995 | 0 | 0.63612 | 0 | 0.06633 | 0 | 0 | 0 | 0.63612 | 0 | 0
5 | 3 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 499.9282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 487.6716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 466.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 434.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 427.3157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 419.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 425.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 440.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 452.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 468.9324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 461.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 455.7353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 7 | 0 | 5.4917 | 5.4917 | 48 | 4.6502 | 2.322 | 2.322 | 464.6129 | 5.4917 | 0 | 2287.9166 | 0 | 0 | 0 | 5.4917 | 0 | 0 | 2287.9166
5 | 4 | 8 | 0 | 2.8796 | 2.8796 | 48 | 5.1417 | 1.352 | 1.352 | 466.683 | 2.8796 | 0 | 1205.6461 | 0 | 0 | 0 | 2.8796 | 0 | 0 | 1205.6461
5 | 4 | 9 | 0 | 15.5112 | 15.5112 | 48 | 6.6161 | 10.8935 | 10.8935 | 462.1169 | 15.5112 | 0 | 6423.4648 | 0 | 0 | 0 | 15.5112 | 0 | 0 | 6423.4648
5 | 4 | 10 | 0 | 23.0147 | 23.0147 | 48 | 6.9721 | 18.3604 | 18.3604 | 462.3071 | 23.0147 | 0 | 9535.1668 | 0 | 0 | 0 | 23.0147 | 0 | 0 | 9535.1668
5 | 4 | 11 | 0 | 34.4145 | 34.4145 | 48 | 8.5652 | 70.1226 | 70.1226 | 463.0438 | 34.4145 | 0 | 14283.5431 | 0 | 0 | 0 | 34.4145 | 0 | 0 | 14283.5431
5 | 4 | 12 | 0 | 28.8746 | 28.8746 | 48 | 7.8957 | 35.5913 | 35.5913 | 454.4198 | 28.8746 | 0 | 11735.214 | 0 | 0 | 0 | 28.8746 | 0 | 0 | 11735.214
5 | 4 | 13 | 0 | 48.4646 | 48.4646 | 48 | 7.4381 | 47.0365 | 47.0365 | 459.1504 | 48.4646 | 0 | 19926.2397 | 0 | 0 | 0 | 48.4646 | 0 | 0 | 19926.2397
5 | 4 | 14 | 0 | 21.7499 | 21.7499 | 48 | 7.2771 | 19.6398 | 19.6398 | 458.5238 | 21.7499 | 0 | 8928.871 | 0 | 0 | 0 | 21.7499 | 0 | 0 | 8928.871
5 | 4 | 15 | 55.4674 | 12.8089 | 68.2763 | 17.9413 | 7.3449 | 63.5135 | 63.5135 | 465.2399 | 68.2763 | 0 | 30539.8949 | 0 | 0 | 0 | 68.2763 | 0 | 0 | 30539.8949
5 | 4 | 16 | 48.4992 | 9.7093 | 58.2085 | 17.1717 | 6.9975 | 46.8922 | 46.8922 | 460.8569 | 58.2085 | 0 | 25826.2466 | 0 | 0 | 0 | 58.2085 | 0 | 0 | 25826.2466
5 | 4 | 17 | 0 | 1.205 | 1.205 | 48 | 7.167 | 1.0386 | 1.0386 | 459.7066 | 1.205 | 0 | 496.1127 | 0 | 0 | 0 | 1.205 | 0 | 0 | 496.1127
5 | 4 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 466.5904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 467.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 455.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 429.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 400.7154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 4 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 395.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 392.4589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 387.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 399.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 424.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 453.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 466.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 6 | 0 | 1.2545 | 1.2545 | 48 | 4.6163 | 0.5268 | 0.5268 | 468.3476 | 1.2545 | 0 | 527.326 | 0 | 0 | 0 | 1.2545 | 0 | 0 | 527.326
5 | 5 | 7 | 0.52505 | 3.6175 | 4.1426 | 43.3104 | 6.1924 | 2.5466 | 2.5466 | 462.1018 | 4.1426 | 0 | 1734.8826 | 0 | 0 | 0 | 4.1426 | 0 | 0 | 1734.8826
5 | 5 | 8 | 3.1253 | 6.56 | 9.6853 | 36.0606 | 6.8788 | 7.461 | 7.461 | 458.3395 | 9.6853 | 0 | 4089.9115 | 0 | 0 | 0 | 9.6853 | 0 | 0 | 4089.9115
5 | 5 | 9 | 66.3704 | 1.7804 | 68.1508 | 11.9666 | 7.3195 | 62.687 | 62.687 | 453.7899 | 68.1508 | 0 | 30110.5943 | 0 | 0 | 0 | 68.1508 | 0 | 0 | 30110.5943
5 | 5 | 10 | 122.7519 | 0.87833 | 123.6302 | 11.2629 | 7.4805 | 122.3969 | 122.3969 | 459.2929 | 123.6302 | 0 | 55390.0434 | 0 | 0 | 0 | 123.6302 | 0 | 0 | 55390.0434
5 | 5 | 11 | 103.3235 | 14.809 | 118.1325 | 15.6383 | 7.2263 | 104.377 | 104.377 | 464.1472 | 118.1325 | 0 | 52983.4873 | 0 | 0 | 0 | 118.1325 | 0 | 0 | 52983.4873
5 | 5 | 12 | 0 | 34.1131 | 34.1131 | 48 | 7.8703 | 41.4269 | 41.4269 | 461.5053 | 34.1131 | 0 | 14105.9441 | 0 | 0 | 0 | 34.1131 | 0 | 0 | 14105.9441
5 | 5 | 13 | 0 | 11.2639 | 11.2639 | 48 | 8.1754 | 16.6281 | 16.6281 | 466.8951 | 11.2639 | 0 | 4718.3783 | 0 | 0 | 0 | 11.2639 | 0 | 0 | 4718.3783
5 | 5 | 14 | 0 | 7.0865 | 7.0865 | 48 | 8.2431 | 10.9877 | 10.9877 | 460.2776 | 7.0865 | 0 | 2921.5963 | 0 | 0 | 0 | 7.0865 | 0 | 0 | 2921.5963
5 | 5 | 15 | 0 | 0.45894 | 0.45894 | 48 | 7.4212 | 0.44194 | 0.44194 | 467.0923 | 0.45894 | 0 | 192.339 | 0 | 0 | 0 | 0.45894 | 0 | 0 | 192.339
5 | 5 | 16 | 0 | 0.32798 | 0.32798 | 48 | 7.3195 | 0.30169 | 0.30169 | 471.3469 | 0.32798 | 0 | 138.85 | 0 | 0 | 0 | 0.32798 | 0 | 0 | 138.85
5 | 5 | 17 | 0 | 2.9135 | 2.9135 | 48 | 7.2686 | 2.6212 | 2.6212 | 469.7616 | 2.9135 | 0 | 1228.8042 | 0 | 0 | 0 | 2.9135 | 0 | 0 | 1228.8042
5 | 5 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 478.6957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 477.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 472.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 450.4164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 431.6412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 5 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 428.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 431.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 425.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 432.3394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 3 | 1.495 | 0 | 1.495 | 11 | 3.3622 | 0.50139 | 0.50139 | 448.9586 | 1.495 | 0 | 654.7664 | 0 | 0 | 0 | 1.495 | 0 | 0 | 654.7664
5 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 450.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 465.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 6 | 0 | 0.012042 | 0.012042 | 48 | 4.4638 | 0.0049062 | 0.0049062 | 470.8486 | 0.012042 | 0 | 5.0918 | 0 | 0 | 0 | 0.012042 | 0 | 0 | 5.0918
5 | 6 | 7 | 4.6634 | 141.0207 | 145.6841 | 46.8156 | 6.006 | 84.8976 | 84.8976 | 469.0614 | 145.6841 | 0 | 61514.501 | 0 | 0 | 0 | 145.6841 | 0 | 0 | 61514.501
5 | 6 | 8 | 0.74004 | 17.6496 | 18.3896 | 46.511 | 6.6246 | 12.9519 | 12.9519 | 469.259 | 18.3896 | 0 | 7774.164 | 0 | 0 | 0 | 18.3896 | 0 | 0 | 7774.164
5 | 6 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 454.3899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 10 | 0 | 12.5856 | 12.5856 | 48 | 7.0398 | 10.3073 | 10.3073 | 447.5382 | 12.5856 | 0 | 5028.4455 | 0 | 0 | 0 | 12.5856 | 0 | 0 | 5028.4455
5 | 6 | 11 | 0 | 6.8104 | 6.8104 | 48 | 7.2093 | 5.9746 | 5.9746 | 447.5211 | 6.8104 | 0 | 2720.9001 | 0 | 0 | 0 | 6.8104 | 0 | 0 | 2720.9001
5 | 6 | 12 | 0 | 16.1609 | 16.1609 | 48 | 7.9296 | 20.3268 | 20.3268 | 441.4837 | 16.1609 | 0 | 6359.0352 | 0 | 0 | 0 | 16.1609 | 0 | 0 | 6359.0352
5 | 6 | 13 | 0 | 13.9595 | 13.9595 | 48 | 8.2601 | 21.9203 | 21.9203 | 444.4661 | 13.9595 | 0 | 5534.4748 | 0 | 0 | 0 | 13.9595 | 0 | 0 | 5534.4748
5 | 6 | 14 | 0 | 17.1692 | 17.1692 | 48 | 8.5313 | 33.864 | 33.864 | 436.9578 | 17.1692 | 0 | 6678.0994 | 0 | 0 | 0 | 17.1692 | 0 | 0 | 6678.0994
5 | 6 | 15 | 0 | 116.4701 | 116.4701 | 48 | 8.4041 | 205.1035 | 205.1035 | 450.6864 | 116.4701 | 0 | 46900.942 | 0 | 0 | 0 | 116.4701 | 0 | 0 | 46900.942
5 | 6 | 16 | 0 | 11.7453 | 11.7453 | 48 | 9.1753 | 59.1191 | 59.1191 | 452.2254 | 11.7453 | 0 | 4747.7291 | 0 | 0 | 0 | 11.7453 | 0 | 0 | 4747.7291
5 | 6 | 17 | 0 | 2.0125 | 2.0125 | 48 | 8.6753 | 4.5944 | 4.5944 | 461.5855 | 2.0125 | 0 | 832.3409 | 0 | 0 | 0 | 2.0125 | 0 | 0 | 832.3409
5 | 6 | 18 | 0 | 0.060583 | 0.060583 | 48 | 9.0397 | 0.22984 | 0.22984 | 470.0546 | 0.060583 | 0 | 25.5695 | 0 | 0 | 0 | 0.060583 | 0 | 0 | 25.5695
5 | 6 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 472.6486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 451.1531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 414.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 403.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 401.4618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 405.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 406.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 406.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 413.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 415.9012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 433.1185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 6 | 0 | 0.78917 | 0.78917 | 48 | 4.1926 | 0.30538 | 0.30538 | 447.3249 | 0.78917 | 0 | 315.1339 | 0 | 0 | 0 | 0.78917 | 0 | 0 | 315.1339
5 | 7 | 7 | 9.8414 | 27.8743 | 37.7156 | 38.3454 | 4.8705 | 16.691 | 16.691 | 449.5521 | 37.7156 | 0 | 15508.9171 | 0 | 0 | 0 | 37.7156 | 0 | 0 | 15508.9171
5 | 7 | 8 | 10.3046 | 94.348 | 104.6526 | 44.3568 | 4.8451 | 46.0657 | 46.0657 | 448.1941 | 104.6526 | 0 | 42262.6153 | 0 | 0 | 0 | 104.6526 | 0 | 0 | 42262.6153
5 | 7 | 9 | 8.6828 | 413.0542 | 421.737 | 47.2382 | 6.3789 | 274.3024 | 274.3024 | 443.0686 | 421.737 | 0 | 166936.297 | 0 | 0 | 0 | 421.737 | 0 | 0 | 166936.297
5 | 7 | 10 | 0.019327 | 37.4485 | 37.4679 | 47.9809 | 8.4804 | 70.5148 | 70.5148 | 431.2776 | 37.4679 | 0 | 14361.3065 | 0 | 0 | 0 | 37.4679 | 0 | 0 | 14361.3065
5 | 7 | 11 | 0.3254 | 139.3928 | 139.7182 | 47.9138 | 9.4549 | 2156.4984 | 288 | 427.5101 | 18.6593 | 121.0588 | 7083.0155 | 12.6231 | 0 | 0 | 18.6593 | 121.0588 | 0 | 7083.0155
5 | 7 | 12 | 0 | 79.1577 | 79.1577 | 48 | 9.8362 | 0 | 0 | 430.703 | 0 | 79.1577 | 0 | 8.254 | 0 | 0 | 0 | 79.1577 | 0 | 0
5 | 7 | 13 | 0 | 99.3494 | 99.3494 | 48 | 9.6159 | 0 | 0 | 432.9051 | 0 | 99.3494 | 0 | 10.3594 | 0 | 0 | 0 | 99.3494 | 0 | 0
5 | 7 | 14 | 0 | 30.8769 | 30.8769 | 48 | 9.5227 | 954.9602 | 288 | 446.2051 | 9.312 | 21.5649 | 3708.0678 | 2.2486 | 0 | 0 | 9.312 | 21.5649 | 0 | 3708.0678
5 | 7 | 15 | 0 | 8.2546 | 8.2546 | 48 | 10.7175 | 0 | 0 | 454.11 | 0 | 8.2546 | 0 | 0.86073 | 0 | 0 | 0 | 8.2546 | 0 | 0
5 | 7 | 16 | 0 | 4.4637 | 4.4637 | 48 | 12.0564 | 0 | 0 | 469.9179 | 0 | 4.4637 | 0 | 0.46544 | 0 | 0 | 0 | 4.4637 | 0 | 0
5 | 7 | 17 | 0.56 | 172.8462 | 173.4062 | 47.8805 | 11.8107 | 0 | 0 | 464.0211 | 0 | 173.4062 | 0 | 18.0815 | 0 | 0 | 0 | 173.4062 | 0 | 0
5 | 7 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 474.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 19 | 0 | 0.0023925 | 0.0023925 | 48 | 12.2767 | 0 | 0 | 473.6636 | 0 | 0.0023925 | 0 | 0.00024948 | 0 | 0 | 0 | 0.0023925 | 0 | 0
5 | 7 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 451.5124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 425.4787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 418.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 7 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 426.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 428.4813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 435.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 454.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 471.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 471.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 477.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 482.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 7 | 0 | 0.47333 | 0.47333 | 48 | 4.8281 | 0.20761 | 0.20761 | 483.3221 | 0.47333 | 0 | 206.0524 | 0 | 0 | 0 | 0.47333 | 0 | 0 | 206.0524
5 | 8 | 8 | 0 | 2.9695 | 2.9695 | 48 | 5.4976 | 1.5155 | 1.5155 | 482.2869 | 2.9695 | 0 | 1289.6132 | 0 | 0 | 0 | 2.9695 | 0 | 0 | 1289.6132
5 | 8 | 9 | 0 | 10.0921 | 10.0921 | 48 | 6.4043 | 6.6164 | 6.6164 | 484.6943 | 10.0921 | 0 | 4407.1549 | 0 | 0 | 0 | 10.0921 | 0 | 0 | 4407.1549
5 | 8 | 10 | 9.0767 | 225.2165 | 234.2932 | 46.5666 | 8.5991 | 493.7178 | 288 | 482.4435 | 136.6701 | 97.6231 | 59571.3232 | 10.1794 | 0 | 0 | 136.6701 | 97.6231 | 0 | 59571.3232
5 | 8 | 11 | 0 | 28.6857 | 28.6857 | 48 | 9.6413 | 0 | 0 | 486.1409 | 0 | 28.6857 | 0 | 2.9911 | 0 | 0 | 0 | 28.6857 | 0 | 0
5 | 8 | 12 | 0 | 15.722 | 15.722 | 48 | 9.7176 | 0 | 0 | 484.9388 | 0 | 15.722 | 0 | 1.6394 | 0 | 0 | 0 | 15.722 | 0 | 0
5 | 8 | 13 | 0 | 12.5465 | 12.5465 | 48 | 9.7939 | 0 | 0 | 485.2257 | 0 | 12.5465 | 0 | 1.3083 | 0 | 0 | 0 | 12.5465 | 0 | 0
5 | 8 | 14 | 0 | 5.4064 | 5.4064 | 48 | 9.4634 | 89.0207 | 89.0207 | 479.0942 | 5.4064 | 0 | 2330.6841 | 0 | 0 | 0 | 5.4064 | 0 | 0 | 2330.6841
5 | 8 | 15 | 0 | 14.8504 | 14.8504 | 48 | 10.5311 | 0 | 0 | 484.3087 | 0 | 14.8504 | 0 | 1.5485 | 0 | 0 | 0 | 14.8504 | 0 | 0
5 | 8 | 16 | 0 | 6.7586 | 6.7586 | 48 | 11.0904 | 0 | 0 | 486.5017 | 0 | 6.7586 | 0 | 0.70474 | 0 | 0 | 0 | 6.7586 | 0 | 0
5 | 8 | 17 | 0 | 0.47569 | 0.47569 | 48 | 11.1073 | 0 | 0 | 474.7398 | 0 | 0.47569 | 0 | 0.049601 | 0 | 0 | 0 | 0.47569 | 0 | 0
5 | 8 | 18 | 0 | 0.12146 | 0.12146 | 48 | 11.4802 | 0 | 0 | 483.5454 | 0 | 0.12146 | 0 | 0.012665 | 0 | 0 | 0 | 0.12146 | 0 | 0
5 | 8 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 481.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 474.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 449.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 429.873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 8 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 428.8267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 427.7649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 440.0286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 451.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 460.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 466.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 470.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 475.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 7 | 0 | 0.27167 | 0.27167 | 48 | 5.2518 | 0.13079 | 0.13079 | 484.1212 | 0.27167 | 0 | 118.4796 | 0 | 0 | 0 | 0.27167 | 0 | 0 | 118.4796
5 | 9 | 8 | 0 | 2.275 | 2.275 | 48 | 6.2094 | 1.4055 | 1.4055 | 484.9863 | 2.275 | 0 | 994.133 | 0 | 0 | 0 | 2.275 | 0 | 0 | 994.133
5 | 9 | 9 | 0 | 2.3729 | 2.3729 | 48 | 7.328 | 2.1909 | 2.1909 | 484.7145 | 2.3729 | 0 | 1036.301 | 0 | 0 | 0 | 2.3729 | 0 | 0 | 1036.301
5 | 9 | 10 | 0 | 7.5277 | 7.5277 | 48 | 8.5482 | 15.0889 | 15.0889 | 488.286 | 7.5277 | 0 | 3314.3388 | 0 | 0 | 0 | 7.5277 | 0 | 0 | 3314.3388
5 | 9 | 11 | 0 | 27.5475 | 27.5475 | 48 | 9.1838 | 141.5491 | 141.5491 | 491.0896 | 27.5475 | 0 | 12205.9922 | 0 | 0 | 0 | 27.5475 | 0 | 0 | 12205.9922
5 | 9 | 12 | 0 | 19.723 | 19.723 | 48 | 9.8701 | 0 | 0 | 493.6735 | 0 | 19.723 | 0 | 2.0566 | 0 | 0 | 0 | 19.723 | 0 | 0
5 | 9 | 13 | 0 | 27.9785 | 27.9785 | 48 | 9.6668 | 0 | 0 | 495.4456 | 0 | 27.9785 | 0 | 2.9174 | 0 | 0 | 0 | 27.9785 | 0 | 0
5 | 9 | 14 | 0 | 12.0037 | 12.0037 | 48 | 10.2684 | 0 | 0 | 498.1194 | 0 | 12.0037 | 0 | 1.2517 | 0 | 0 | 0 | 12.0037 | 0 | 0
5 | 9 | 15 | 0 | 6.1066 | 6.1066 | 48 | 11.226 | 0 | 0 | 498.6519 | 0 | 6.1066 | 0 | 0.63676 | 0 | 0 | 0 | 6.1066 | 0 | 0
5 | 9 | 16 | 0 | 0.53917 | 0.53917 | 48 | 11.853 | 0 | 0 | 499.0783 | 0 | 0.53917 | 0 | 0.05622 | 0 | 0 | 0 | 0.53917 | 0 | 0
5 | 9 | 17 | 0 | 0.5175 | 0.5175 | 48 | 11.7514 | 0 | 0 | 483.7256 | 0 | 0.5175 | 0 | 0.053961 | 0 | 0 | 0 | 0.5175 | 0 | 0
5 | 9 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 487.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 500.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 491.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 468.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 455.3641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 9 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 458.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 456.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 461.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 476.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 494.2198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 494.7387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 500.9032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 6 | 0 | 0.077875 | 0.077875 | 48 | 4.8366 | 0.034218 | 0.034218 | 502.4902 | 0.077875 | 0 | 35.3934 | 0 | 0 | 0 | 0.077875 | 0 | 0 | 35.3934
5 | 10 | 7 | 0 | 3.2125 | 3.2125 | 48 | 5.0146 | 1.4664 | 1.4664 | 502.7808 | 3.2125 | 0 | 1460.9834 | 0 | 0 | 0 | 3.2125 | 0 | 0 | 1460.9834
5 | 10 | 8 | 0 | 21.5772 | 21.5772 | 48 | 6.2094 | 13.3306 | 13.3306 | 500.1728 | 21.5772 | 0 | 9756.6336 | 0 | 0 | 0 | 21.5772 | 0 | 0 | 9756.6336
5 | 10 | 9 | 0 | 32.389 | 32.389 | 48 | 7.311 | 29.6816 | 29.6816 | 498.2552 | 32.389 | 0 | 14583.3324 | 0 | 0 | 0 | 32.389 | 0 | 0 | 14583.3324
5 | 10 | 10 | 0 | 33.9294 | 33.9294 | 48 | 8.0567 | 46.2129 | 46.2129 | 498.7581 | 33.9294 | 0 | 15293.9584 | 0 | 0 | 0 | 33.9294 | 0 | 0 | 15293.9584
5 | 10 | 11 | 0 | 22.4663 | 22.4663 | 48 | 9.3109 | 167.9612 | 167.9612 | 496.0443 | 22.4663 | 0 | 10065.8877 | 0 | 0 | 0 | 22.4663 | 0 | 0 | 10065.8877
5 | 10 | 12 | 0 | 26.4024 | 26.4024 | 48 | 9.0058 | 94.3576 | 94.3576 | 493.7273 | 26.4024 | 0 | 11768.2562 | 0 | 0 | 0 | 26.4024 | 0 | 0 | 11768.2562
5 | 10 | 13 | 0 | 19.6256 | 19.6256 | 48 | 8.4889 | 37.2196 | 37.2196 | 491.091 | 19.6256 | 0 | 8695.9055 | 0 | 0 | 0 | 19.6256 | 0 | 0 | 8695.9055
5 | 10 | 14 | 7.2382 | 37.9285 | 45.1668 | 42.0705 | 8.938 | 144.6411 | 144.6411 | 490.9596 | 45.1668 | 0 | 20274.8719 | 0 | 0 | 0 | 45.1668 | 0 | 0 | 20274.8719
5 | 10 | 15 | 0 | 22.5981 | 22.5981 | 48 | 9.6075 | 0 | 0 | 494.6668 | 0 | 22.5981 | 0 | 2.3564 | 0 | 0 | 0 | 22.5981 | 0 | 0
5 | 10 | 16 | 0 | 19.8166 | 19.8166 | 48 | 10.9718 | 0 | 0 | 492.2714 | 0 | 19.8166 | 0 | 2.0663 | 0 | 0 | 0 | 19.8166 | 0 | 0
5 | 10 | 17 | 0 | 19.8793 | 19.8793 | 48 | 10.3786 | 0 | 0 | 480.0849 | 0 | 19.8793 | 0 | 2.0729 | 0 | 0 | 0 | 19.8793 | 0 | 0
5 | 10 | 18 | 0 | 0.11487 | 0.11487 | 48 | 11.0734 | 0 | 0 | 490.5542 | 0 | 0.11487 | 0 | 0.011978 | 0 | 0 | 0 | 0.11487 | 0 | 0
5 | 10 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 491.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 20 | 6.4388 | 0 | 6.4388 | 11 | 8.0228 | 8.5801 | 8.5801 | 486.2407 | 6.4388 | 0 | 3059.9593 | 0 | 0 | 0 | 6.4388 | 0 | 0 | 3059.9593
5 | 10 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 471.7294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 463.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 10 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 454.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 434.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 435.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 458.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 476.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 491.4229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 500.8298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 491.2289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 7 | 0 | 171.698 | 171.698 | 48 | 4.6502 | 72.5958 | 72.5958 | 490.7786 | 171.698 | 0 | 76024.1891 | 0 | 0 | 0 | 171.698 | 0 | 0 | 76024.1891
5 | 11 | 8 | 0 | 209.8998 | 209.8998 | 48 | 5.1417 | 98.5531 | 98.5531 | 491.6886 | 209.8998 | 0 | 93130.1708 | 0 | 0 | 0 | 209.8998 | 0 | 0 | 93130.1708
5 | 11 | 9 | 0 | 43.9955 | 43.9955 | 48 | 6.6161 | 30.8981 | 30.8981 | 493.2631 | 43.9955 | 0 | 19589.5895 | 0 | 0 | 0 | 43.9955 | 0 | 0 | 19589.5895
5 | 11 | 10 | 0 | 8.4184 | 8.4184 | 48 | 6.9721 | 6.7159 | 6.7159 | 498.2292 | 8.4184 | 0 | 3790.2071 | 0 | 0 | 0 | 8.4184 | 0 | 0 | 3790.2071
5 | 11 | 11 | 0 | 17.567 | 17.567 | 48 | 8.5652 | 35.7943 | 35.7943 | 494.4919 | 17.567 | 0 | 7843.5408 | 0 | 0 | 0 | 17.567 | 0 | 0 | 7843.5408
5 | 11 | 12 | 0 | 34.4846 | 34.4846 | 48 | 7.8957 | 42.5063 | 42.5063 | 496.958 | 34.4846 | 0 | 15482.1343 | 0 | 0 | 0 | 34.4846 | 0 | 0 | 15482.1343
5 | 11 | 13 | 0 | 40.4272 | 40.4272 | 48 | 7.4381 | 39.2359 | 39.2359 | 497.8371 | 40.4272 | 0 | 18185.646 | 0 | 0 | 0 | 40.4272 | 0 | 0 | 18185.646
5 | 11 | 14 | 0 | 20.2367 | 20.2367 | 48 | 7.2771 | 18.2733 | 18.2733 | 499.8689 | 20.2367 | 0 | 9144.3362 | 0 | 0 | 0 | 20.2367 | 0 | 0 | 9144.3362
5 | 11 | 15 | 0 | 12.2502 | 12.2502 | 48 | 7.3449 | 11.3957 | 11.3957 | 499.2285 | 12.2502 | 0 | 5527.6443 | 0 | 0 | 0 | 12.2502 | 0 | 0 | 5527.6443
5 | 11 | 16 | 0 | 11.5983 | 11.5983 | 48 | 6.9975 | 9.3435 | 9.3435 | 490.4077 | 11.5983 | 0 | 5131.1741 | 0 | 0 | 0 | 11.5983 | 0 | 0 | 5131.1741
5 | 11 | 17 | 0 | 4.5405 | 4.5405 | 48 | 7.167 | 3.9136 | 3.9136 | 486.2226 | 4.5405 | 0 | 1989.7537 | 0 | 0 | 0 | 4.5405 | 0 | 0 | 1989.7537
5 | 11 | 18 | 0 | 0.18804 | 0.18804 | 48 | 6.7094 | 0.13633 | 0.13633 | 502.81 | 0.18804 | 0 | 85.5232 | 0 | 0 | 0 | 0.18804 | 0 | 0 | 85.5232
5 | 11 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 497.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 487.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 476.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 462.8082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 11 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 461.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 449.129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 455.1396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 467.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 482.269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 494.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 489.8043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 481.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 7 | 0 | 3.785 | 3.785 | 48 | 6.1924 | 2.3267 | 2.3267 | 479.6859 | 3.785 | 0 | 1633.9313 | 0 | 0 | 0 | 3.785 | 0 | 0 | 1633.9313
5 | 12 | 8 | 0 | 13.2872 | 13.2872 | 48 | 6.8788 | 10.2357 | 10.2357 | 476.4728 | 13.2872 | 0 | 5693.2029 | 0 | 0 | 0 | 13.2872 | 0 | 0 | 5693.2029
5 | 12 | 9 | 0 | 0.19917 | 0.19917 | 48 | 7.3195 | 0.1832 | 0.1832 | 471.7461 | 0.19917 | 0 | 84.3961 | 0 | 0 | 0 | 0.19917 | 0 | 0 | 84.3961
5 | 12 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 482.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 488.2863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 494.8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 13 | 0 | 3.9386 | 3.9386 | 48 | 8.1754 | 5.8142 | 5.8142 | 494.5355 | 3.9386 | 0 | 1758.7092 | 0 | 0 | 0 | 3.9386 | 0 | 0 | 1758.7092
5 | 12 | 14 | 0 | 14.3605 | 14.3605 | 48 | 8.2431 | 22.2663 | 22.2663 | 492.1419 | 14.3605 | 0 | 6378.1081 | 0 | 0 | 0 | 14.3605 | 0 | 0 | 6378.1081
5 | 12 | 15 | 0 | 6.8836 | 6.8836 | 48 | 7.4212 | 6.6286 | 6.6286 | 485.4752 | 6.8836 | 0 | 3011.4156 | 0 | 0 | 0 | 6.8836 | 0 | 0 | 3011.4156
5 | 12 | 16 | 51.1553 | 9.7035 | 60.8588 | 16.8994 | 7.3195 | 55.9796 | 55.9796 | 481.5013 | 60.8588 | 0 | 28275.1114 | 0 | 0 | 0 | 60.8588 | 0 | 0 | 28275.1114
5 | 12 | 17 | 49.3681 | 8.3735 | 57.7416 | 16.3656 | 7.2686 | 51.9492 | 51.9492 | 489.2251 | 57.7416 | 0 | 27303.6625 | 0 | 0 | 0 | 57.7416 | 0 | 0 | 27303.6625
5 | 12 | 18 | 48.5757 | 0 | 48.5757 | 11 | 6.9297 | 38.135 | 38.135 | 494.1199 | 48.5757 | 0 | 23467.8959 | 0 | 0 | 0 | 48.5757 | 0 | 0 | 23467.8959
5 | 12 | 19 | 14.9549 | 0 | 14.9549 | 11 | 6.9382 | 11.7781 | 11.7781 | 490.1969 | 14.9549 | 0 | 7166.3382 | 0 | 0 | 0 | 14.9549 | 0 | 0 | 7166.3382
5 | 12 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 484.2262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 463.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 454.3313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 12 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 450.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 453.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 452.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 457.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 458.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 463.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 473.7822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 6 | 0 | 7.821 | 7.821 | 48 | 4.4638 | 3.1865 | 3.1865 | 473.6492 | 7.821 | 0 | 3328.9876 | 0 | 0 | 0 | 7.821 | 0 | 0 | 3328.9876
5 | 13 | 7 | 4.0392 | 329.6408 | 333.6799 | 47.5521 | 6.006 | 194.4524 | 194.4524 | 476.5661 | 333.6799 | 0 | 143153.3748 | 0 | 0 | 0 | 333.6799 | 0 | 0 | 143153.3748
5 | 13 | 8 | 0.19 | 683.0398 | 683.2298 | 47.9897 | 6.6246 | 481.2035 | 288 | 478.2754 | 408.9126 | 274.3171 | 175949.2339 | 28.6038 | 0 | 0 | 408.9126 | 274.3171 | 0 | 175949.2339
5 | 13 | 9 | 0.2525 | 703.8046 | 704.0571 | 47.9867 | 7.1924 | 613.2822 | 288 | 475.19 | 330.6283 | 373.4288 | 141245.4963 | 38.9384 | 0 | 0 | 330.6283 | 373.4288 | 0 | 141245.4963
5 | 13 | 10 | 1.0633 | 1080.1365 | 1081.1998 | 47.9636 | 7.0398 | 885.4736 | 288 | 471.4084 | 351.6599 | 729.5399 | 148908.5436 | 76.071 | 0 | 0 | 351.6599 | 729.5399 | 0 | 148908.5436
5 | 13 | 11 | 0.23583 | 661.1612 | 661.3971 | 47.9868 | 7.2093 | 580.2233 | 288 | 465.9767 | 328.2914 | 333.1056 | 137222.4977 | 34.7338 | 0 | 0 | 328.2914 | 333.1056 | 0 | 137222.4977
5 | 13 | 12 | 0.27833 | 772.9108 | 773.1891 | 47.9867 | 7.9296 | 972.4992 | 288 | 457.1496 | 228.9755 | 544.2136 | 93688.2776 | 56.7466 | 0 | 0 | 228.9755 | 544.2136 | 0 | 93688.2776
5 | 13 | 13 | 0.25167 | 631.1039 | 631.3556 | 47.9853 | 8.2601 | 991.4039 | 288 | 458.3391 | 183.407 | 447.9486 | 75261.759 | 46.7088 | 0 | 0 | 183.407 | 447.9486 | 0 | 75261.759
5 | 13 | 14 | 0 | 417.1358 | 417.1358 | 48 | 8.5313 | 822.7448 | 288 | 463.1612 | 146.0175 | 271.1183 | 60620.779 | 28.2702 | 0 | 0 | 146.0175 | 271.1183 | 0 | 60620.779
5 | 13 | 15 | 0.18333 | 456.8377 | 457.0211 | 47.9852 | 8.4041 | 804.8123 | 288 | 468.8331 | 163.5438 | 293.4773 | 68827.074 | 30.6016 | 0 | 0 | 163.5438 | 293.4773 | 0 | 68827.074
5 | 13 | 16 | 3.2417 | 514.1748 | 517.4165 | 47.7682 | 9.1753 | 2604.3861 | 288 | 471.6897 | 57.2173 | 460.1992 | 24255.6456 | 47.9862 | 0 | 0 | 57.2173 | 460.1992 | 0 | 24255.6456
5 | 13 | 17 | 2.8775 | 447.7378 | 450.6153 | 47.7637 | 8.6753 | 1028.7185 | 288 | 476.1085 | 126.1543 | 324.4611 | 54037.5165 | 33.8324 | 0 | 0 | 126.1543 | 324.4611 | 0 | 54037.5165
5 | 13 | 18 | 1.4609 | 136.6792 | 138.1401 | 47.6087 | 9.0397 | 524.0845 | 288 | 472.0835 | 75.9121 | 62.228 | 32222.7618 | 6.4887 | 0 | 0 | 75.9121 | 62.228 | 0 | 32222.7618
5 | 13 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 475.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 457.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 434.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 423.4936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 13 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 415.9946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 416.7089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 1 | 1.4846 | 0 | 1.4846 | 11 | 2.8876 | 0.46264 | 0.46264 | 418.2818 | 1.4846 | 0 | 604.655 | 0 | 0 | 0 | 1.4846 | 0 | 0 | 604.655
5 | 14 | 2 | 19.0962 | 0 | 19.0962 | 11 | 2.8791 | 5.9433 | 5.9433 | 418.5687 | 19.0962 | 0 | 7783 | 0 | 0 | 0 | 19.0962 | 0 | 0 | 7783
5 | 14 | 3 | 5.0002 | 0 | 5.0002 | 11 | 3.0147 | 1.5883 | 1.5883 | 412.7504 | 5.0002 | 0 | 2008.8485 | 0 | 0 | 0 | 5.0002 | 0 | 0 | 2008.8485
5 | 14 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 416.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 431.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 6 | 1.505 | 85.384 | 86.889 | 47.3591 | 4.1926 | 33.6232 | 33.6232 | 442.0079 | 86.889 | 0 | 34290.6483 | 0 | 0 | 0 | 86.889 | 0 | 0 | 34290.6483
5 | 14 | 7 | 104.477 | 569.4138 | 673.8908 | 42.2637 | 4.8705 | 298.2293 | 288 | 447.0812 | 650.7762 | 23.1145 | 263445.5735 | 2.4102 | 0 | 0 | 650.7762 | 23.1145 | 0 | 263445.5735
5 | 14 | 8 | 2.9983 | 633.7453 | 636.7436 | 47.8258 | 4.8451 | 280.2802 | 280.2802 | 437.5429 | 636.7436 | 0 | 248149.8824 | 0 | 0 | 0 | 636.7436 | 0 | 0 | 248149.8824
5 | 14 | 9 | 0.016667 | 359.5979 | 359.6145 | 47.9983 | 6.3789 | 233.8973 | 233.8973 | 440.0124 | 359.6145 | 0 | 140973.9568 | 0 | 0 | 0 | 359.6145 | 0 | 0 | 140973.9568
5 | 14 | 10 | 0.4875 | 447.0625 | 447.55 | 47.9597 | 8.4804 | 842.293 | 288 | 443.506 | 153.028 | 294.522 | 60529.6509 | 30.7106 | 0 | 0 | 153.028 | 294.522 | 0 | 60529.6509
5 | 14 | 11 | 0.54333 | 781.7146 | 782.2579 | 47.9743 | 9.4549 | 12073.8615 | 288 | 453.3225 | 18.6593 | 763.5986 | 7563.5288 | 79.6224 | 0 | 0 | 18.6593 | 763.5986 | 0 | 7563.5288
5 | 14 | 12 | 0.19083 | 745.3045 | 745.4954 | 47.9905 | 9.8362 | 0 | 0 | 455.7959 | 0 | 745.4954 | 0 | 77.7348 | 0 | 0 | 0 | 745.4954 | 0 | 0
5 | 14 | 13 | 0.16667 | 672.5949 | 672.7616 | 47.9908 | 9.6159 | 0 | 0 | 461.4595 | 0 | 672.7616 | 0 | 70.1506 | 0 | 0 | 0 | 672.7616 | 0 | 0
5 | 14 | 14 | 0.42167 | 738.2365 | 738.6581 | 47.9789 | 9.5227 | 22845.207 | 288 | 472.5407 | 9.312 | 729.3462 | 3953.5004 | 76.0508 | 0 | 0 | 9.312 | 729.3462 | 0 | 3953.5004
5 | 14 | 15 | 0.48083 | 635.527 | 636.0079 | 47.972 | 10.7175 | 0 | 0 | 477.9287 | 0 | 636.0079 | 0 | 66.3182 | 0 | 0 | 0 | 636.0079 | 0 | 0
5 | 14 | 16 | 1.3667 | 314.267 | 315.6337 | 47.8398 | 12.0564 | 0 | 0 | 467.4339 | 0 | 315.6337 | 0 | 32.912 | 0 | 0 | 0 | 315.6337 | 0 | 0
5 | 14 | 17 | 0 | 83.2242 | 83.2242 | 48 | 11.8107 | 0 | 0 | 457.2459 | 0 | 83.2242 | 0 | 8.678 | 0 | 0 | 0 | 83.2242 | 0 | 0
5 | 14 | 18 | 0 | 0.54038 | 0.54038 | 48 | 12.3445 | 0 | 0 | 466.2276 | 0 | 0.54038 | 0 | 0.056346 | 0 | 0 | 0 | 0.54038 | 0 | 0
5 | 14 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 470.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 464.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 441.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 430.4022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 14 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 429.6135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 421.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 430.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 434.6525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 460.2215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 485.1136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 496.3705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 507.3239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 7 | 0 | 54.6689 | 54.6689 | 48 | 4.8281 | 23.9784 | 23.9784 | 512.4669 | 54.6689 | 0 | 25391.8995 | 0 | 0 | 0 | 54.6689 | 0 | 0 | 25391.8995
5 | 15 | 8 | 2.2992 | 439.6663 | 441.9655 | 47.8075 | 5.4976 | 225.5594 | 225.5594 | 512.4608 | 441.9655 | 0 | 205360.7184 | 0 | 0 | 0 | 441.9655 | 0 | 0 | 205360.7184
5 | 15 | 9 | 0 | 321.1888 | 321.1888 | 48 | 6.4043 | 210.5717 | 210.5717 | 502.6451 | 321.1888 | 0 | 146026.9141 | 0 | 0 | 0 | 321.1888 | 0 | 0 | 146026.9141
5 | 15 | 10 | 0 | 511.1604 | 511.1604 | 48 | 8.5991 | 1077.1503 | 288 | 499.5453 | 136.6701 | 374.4903 | 61712.7204 | 39.0491 | 0 | 0 | 136.6701 | 374.4903 | 0 | 61712.7204
5 | 15 | 11 | 16.7665 | 638.994 | 655.7605 | 47.054 | 9.6413 | 0 | 0 | 499.4734 | 0 | 655.7605 | 0 | 68.3779 | 0 | 0 | 0 | 655.7605 | 0 | 0
5 | 15 | 12 | 26.0871 | 600.4172 | 626.5043 | 46.4594 | 9.7176 | 0 | 0 | 496.9889 | 0 | 626.5043 | 0 | 65.3272 | 0 | 0 | 0 | 626.5043 | 0 | 0
5 | 15 | 13 | 19.6245 | 667.7399 | 687.3645 | 46.9436 | 9.7939 | 0 | 0 | 490.5 | 0 | 687.3645 | 0 | 71.6733 | 0 | 0 | 0 | 687.3645 | 0 | 0
5 | 15 | 14 | 8.1972 | 410.7611 | 418.9583 | 47.2761 | 9.4634 | 6898.4386 | 288 | 491.9841 | 17.4909 | 401.4674 | 7778.3502 | 41.8621 | 0 | 0 | 17.4909 | 401.4674 | 0 | 7778.3502
5 | 15 | 15 | 0 | 248.8586 | 248.8586 | 48 | 10.5311 | 0 | 0 | 495.1676 | 0 | 248.8586 | 0 | 25.9491 | 0 | 0 | 0 | 248.8586 | 0 | 0
5 | 15 | 16 | 0 | 210.0136 | 210.0136 | 48 | 11.0904 | 0 | 0 | 502.3168 | 0 | 210.0136 | 0 | 21.8987 | 0 | 0 | 0 | 210.0136 | 0 | 0
5 | 15 | 17 | 0 | 19.7172 | 19.7172 | 48 | 11.1073 | 0 | 0 | 496.9672 | 0 | 19.7172 | 0 | 2.056 | 0 | 0 | 0 | 19.7172 | 0 | 0
5 | 15 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 504.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 503.8057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 495.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 468.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 446.4396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 15 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 428.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 416.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 412.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 428.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 3 | 245.0035 | 0 | 245.0035 | 11 | 3.2435 | 80.6307 | 80.6307 | 459.9882 | 245.0035 | 0 | 110003.6904 | 0 | 0 | 0 | 245.0035 | 0 | 0 | 110003.6904
5 | 16 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 483.2054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 498.2254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 502.4792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 7 | 0 | 98.5654 | 98.5654 | 48 | 5.2518 | 47.454 | 47.454 | 508.4784 | 98.5654 | 0 | 45387.2348 | 0 | 0 | 0 | 98.5654 | 0 | 0 | 45387.2348
5 | 16 | 8 | 8.3871 | 291.6881 | 300.0752 | 46.9659 | 6.2094 | 185.3884 | 185.3884 | 507.1784 | 300.0752 | 0 | 138098.3661 | 0 | 0 | 0 | 300.0752 | 0 | 0 | 138098.3661
5 | 16 | 9 | 0 | 41.8881 | 41.8881 | 48 | 7.328 | 38.6741 | 38.6741 | 509.4534 | 41.8881 | 0 | 19329.3855 | 0 | 0 | 0 | 41.8881 | 0 | 0 | 19329.3855
5 | 16 | 10 | 0 | 133.5552 | 133.5552 | 48 | 8.5482 | 267.7041 | 267.7041 | 507.0575 | 133.5552 | 0 | 61309.4934 | 0 | 0 | 0 | 133.5552 | 0 | 0 | 61309.4934
5 | 16 | 11 | 0 | 248.7126 | 248.7126 | 48 | 9.1838 | 1277.978 | 288 | 502.3382 | 56.0489 | 192.6637 | 25465.1456 | 20.0896 | 0 | 0 | 56.0489 | 192.6637 | 0 | 25465.1456
5 | 16 | 12 | 5.23 | 362.9056 | 368.1356 | 47.4744 | 9.8701 | 0 | 0 | 498.1781 | 0 | 368.1356 | 0 | 38.3865 | 0 | 0 | 0 | 368.1356 | 0 | 0
5 | 16 | 13 | 2.5705 | 292.5994 | 295.1699 | 47.6778 | 9.6668 | 0 | 0 | 497.8438 | 0 | 295.1699 | 0 | 30.7781 | 0 | 0 | 0 | 295.1699 | 0 | 0
5 | 16 | 14 | 8.5626 | 445.957 | 454.5196 | 47.303 | 10.2684 | 0 | 0 | 495.9717 | 0 | 454.5196 | 0 | 47.394 | 0 | 0 | 0 | 454.5196 | 0 | 0
5 | 16 | 15 | 0 | 60.0864 | 60.0864 | 48 | 11.226 | 0 | 0 | 505.4443 | 0 | 60.0864 | 0 | 6.2654 | 0 | 0 | 0 | 60.0864 | 0 | 0
5 | 16 | 16 | 9.7051 | 1.7955 | 11.5006 | 16.7765 | 11.853 | 0 | 0 | 507.99 | 0 | 11.5006 | 0 | 1.1992 | 0 | 0 | 0 | 11.5006 | 0 | 0
5 | 16 | 17 | 0 | 11.0968 | 11.0968 | 48 | 11.7514 | 0 | 0 | 509.7788 | 0 | 11.0968 | 0 | 1.1571 | 0 | 0 | 0 | 11.0968 | 0 | 0
5 | 16 | 18 | 0 | 23.5718 | 23.5718 | 48 | 12.4971 | 0 | 0 | 510.5757 | 0 | 23.5718 | 0 | 2.4579 | 0 | 0 | 0 | 23.5718 | 0 | 0
5 | 16 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 510.8027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 495.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 477.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 452.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 16 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 436.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 427.0827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 424.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 439.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 468.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 474.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 486.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 6 | 0 | 0.20871 | 0.20871 | 48 | 4.8366 | 0.091705 | 0.091705 | 501.549 | 0.20871 | 0 | 94.6595 | 0 | 0 | 0 | 0.20871 | 0 | 0 | 94.6595
5 | 17 | 7 | 0 | 34.1722 | 34.1722 | 48 | 5.0146 | 15.599 | 15.599 | 507.6725 | 34.1722 | 0 | 15708.0201 | 0 | 0 | 0 | 34.1722 | 0 | 0 | 15708.0201
5 | 17 | 8 | 0 | 133.6658 | 133.6658 | 48 | 6.2094 | 82.5796 | 82.5796 | 509.8193 | 133.6658 | 0 | 61729.4618 | 0 | 0 | 0 | 133.6658 | 0 | 0 | 61729.4618
5 | 17 | 9 | 0 | 299.8443 | 299.8443 | 48 | 7.311 | 274.7799 | 274.7799 | 510.1882 | 299.8443 | 0 | 138584.5106 | 0 | 0 | 0 | 299.8443 | 0 | 0 | 138584.5106
5 | 17 | 10 | 15.4715 | 117.9081 | 133.3796 | 43.7081 | 8.0567 | 181.6669 | 181.6669 | 505.4814 | 133.3796 | 0 | 61591.1206 | 0 | 0 | 0 | 133.3796 | 0 | 0 | 61591.1206
5 | 17 | 11 | 0 | 191.2923 | 191.2923 | 48 | 9.3109 | 1430.129 | 288 | 506.0249 | 38.5225 | 152.7698 | 17644.2773 | 15.9297 | 0 | 0 | 38.5225 | 152.7698 | 0 | 17644.2773
5 | 17 | 12 | 0 | 278.8105 | 278.8105 | 48 | 9.0058 | 996.4221 | 288 | 508.6421 | 80.5858 | 198.2248 | 37121.1905 | 20.6694 | 0 | 0 | 80.5858 | 198.2248 | 0 | 37121.1905
5 | 17 | 13 | 0 | 124.0178 | 124.0178 | 48 | 8.4889 | 235.1984 | 235.1984 | 511.7001 | 124.0178 | 0 | 57507.0577 | 0 | 0 | 0 | 124.0178 | 0 | 0 | 57507.0577
5 | 17 | 14 | 0 | 60.7258 | 60.7258 | 48 | 8.938 | 194.467 | 194.467 | 518.4071 | 60.7258 | 0 | 28565.8386 | 0 | 0 | 0 | 60.7258 | 0 | 0 | 28565.8386
5 | 17 | 15 | 0 | 18.5555 | 18.5555 | 48 | 9.6075 | 0 | 0 | 519.7065 | 0 | 18.5555 | 0 | 1.9348 | 0 | 0 | 0 | 18.5555 | 0 | 0
5 | 17 | 16 | 0 | 12.9457 | 12.9457 | 48 | 10.9718 | 0 | 0 | 525.1668 | 0 | 12.9457 | 0 | 1.3499 | 0 | 0 | 0 | 12.9457 | 0 | 0
5 | 17 | 17 | 0 | 13.8976 | 13.8976 | 48 | 10.3786 | 0 | 0 | 528.1794 | 0 | 13.8976 | 0 | 1.4491 | 0 | 0 | 0 | 13.8976 | 0 | 0
5 | 17 | 18 | 0 | 0.014167 | 0.014167 | 48 | 11.0734 | 0 | 0 | 530.7483 | 0 | 0.014167 | 0 | 0.0014772 | 0 | 0 | 0 | 0.014167 | 0 | 0
5 | 17 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 533.752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 533.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 526.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 510.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 17 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 492.1533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 0 | 19.2953 | 0 | 19.2953 | 11 | 4.1757 | 7.4433 | 7.4433 | 477.2486 | 19.2953 | 0 | 8996.3947 | 0 | 0 | 0 | 19.2953 | 0 | 0 | 8996.3947
5 | 18 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 469.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 485.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 501.0346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 511.4578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 513.0434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 6 | 0 | 0.32704 | 0.32704 | 48 | 4.396 | 0.13151 | 0.13151 | 512.5181 | 0.32704 | 0 | 151.9168 | 0 | 0 | 0 | 0.32704 | 0 | 0 | 151.9168
5 | 18 | 7 | 0 | 35.7121 | 35.7121 | 48 | 4.6502 | 15.0995 | 15.0995 | 509.9203 | 35.7121 | 0 | 16496.1401 | 0 | 0 | 0 | 35.7121 | 0 | 0 | 16496.1401
5 | 18 | 8 | 0 | 48.6887 | 48.6887 | 48 | 5.1417 | 22.8605 | 22.8605 | 504.559 | 48.6887 | 0 | 22229.267 | 0 | 0 | 0 | 48.6887 | 0 | 0 | 22229.267
5 | 18 | 9 | 0 | 40.4589 | 40.4589 | 48 | 6.6161 | 28.4143 | 28.4143 | 505.5992 | 40.4589 | 0 | 18513.9614 | 0 | 0 | 0 | 40.4589 | 0 | 0 | 18513.9614
5 | 18 | 10 | 0.083424 | 22.2758 | 22.3593 | 47.862 | 6.9721 | 17.8375 | 17.8375 | 508.0297 | 22.3593 | 0 | 10289.0131 | 0 | 0 | 0 | 22.3593 | 0 | 0 | 10289.0131
5 | 18 | 11 | 0 | 34.3198 | 34.3198 | 48 | 8.5652 | 69.9295 | 69.9295 | 508.8439 | 34.3198 | 0 | 15816.0548 | 0 | 0 | 0 | 34.3198 | 0 | 0 | 15816.0548
5 | 18 | 12 | 1.3145 | 33.3221 | 34.6366 | 46.5958 | 7.8957 | 42.6937 | 42.6937 | 509.82 | 34.6366 | 0 | 16044.5119 | 0 | 0 | 0 | 34.6366 | 0 | 0 | 16044.5119
5 | 18 | 13 | 0 | 30.8763 | 30.8763 | 48 | 7.4381 | 29.9665 | 29.9665 | 509.4873 | 30.8763 | 0 | 14249.0173 | 0 | 0 | 0 | 30.8763 | 0 | 0 | 14249.0173
5 | 18 | 14 | 0 | 22.4514 | 22.4514 | 48 | 7.2771 | 20.2731 | 20.2731 | 513.0117 | 22.4514 | 0 | 10440.1514 | 0 | 0 | 0 | 22.4514 | 0 | 0 | 10440.1514
5 | 18 | 15 | 0 | 20.8078 | 20.8078 | 48 | 7.3449 | 19.3563 | 19.3563 | 516.7144 | 20.8078 | 0 | 9752.9345 | 0 | 0 | 0 | 20.8078 | 0 | 0 | 9752.9345
5 | 18 | 16 | 0 | 3.5746 | 3.5746 | 48 | 6.9975 | 2.8796 | 2.8796 | 518.6085 | 3.5746 | 0 | 1682.2222 | 0 | 0 | 0 | 3.5746 | 0 | 0 | 1682.2222
5 | 18 | 17 | 0 | 1.7783 | 1.7783 | 48 | 7.167 | 1.5328 | 1.5328 | 528.0937 | 1.7783 | 0 | 853.7668 | 0 | 0 | 0 | 1.7783 | 0 | 0 | 853.7668
5 | 18 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 533.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 534.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 527.9366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 510.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 502.3851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 18 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 485.8399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 476.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 469.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 478.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 510.3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 524.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 528.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 6 | 0 | 0.46454 | 0.46454 | 48 | 4.6163 | 0.19507 | 0.19507 | 535.6939 | 0.46454 | 0 | 226.5541 | 0 | 0 | 0 | 0.46454 | 0 | 0 | 226.5541
5 | 19 | 7 | 0 | 17.05 | 17.05 | 48 | 6.1924 | 10.481 | 10.481 | 530.9061 | 17.05 | 0 | 8233.5338 | 0 | 0 | 0 | 17.05 | 0 | 0 | 8233.5338
5 | 19 | 8 | 0.31346 | 20.6566 | 20.9701 | 47.4469 | 6.8788 | 16.1541 | 16.1541 | 519.5102 | 20.9701 | 0 | 9899.1902 | 0 | 0 | 0 | 20.9701 | 0 | 0 | 9899.1902
5 | 19 | 9 | 0 | 1.8196 | 1.8196 | 48 | 7.3195 | 1.6738 | 1.6738 | 521.4413 | 1.8196 | 0 | 861.4964 | 0 | 0 | 0 | 1.8196 | 0 | 0 | 861.4964
5 | 19 | 10 | 3.6012 | 6.1106 | 9.7118 | 34.2802 | 7.4805 | 9.6149 | 9.6149 | 512.744 | 9.7118 | 0 | 4646.7588 | 0 | 0 | 0 | 9.7118 | 0 | 0 | 4646.7588
5 | 19 | 11 | 0 | 16.2735 | 16.2735 | 48 | 7.2263 | 14.3786 | 14.3786 | 514.8408 | 16.2735 | 0 | 7597.1334 | 0 | 0 | 0 | 16.2735 | 0 | 0 | 7597.1334
5 | 19 | 12 | 0 | 15.8853 | 15.8853 | 48 | 7.8703 | 19.2911 | 19.2911 | 516.9278 | 15.8853 | 0 | 7449.0792 | 0 | 0 | 0 | 15.8853 | 0 | 0 | 7449.0792
5 | 19 | 13 | 0 | 12.6469 | 12.6469 | 48 | 8.1754 | 18.6697 | 18.6697 | 518.0551 | 12.6469 | 0 | 5944.7208 | 0 | 0 | 0 | 12.6469 | 0 | 0 | 5944.7208
5 | 19 | 14 | 0 | 1.6642 | 1.6642 | 48 | 8.2431 | 2.5803 | 2.5803 | 517.5021 | 1.6642 | 0 | 781.3298 | 0 | 0 | 0 | 1.6642 | 0 | 0 | 781.3298
5 | 19 | 15 | 0 | 0.054167 | 0.054167 | 48 | 7.4212 | 0.05216 | 0.05216 | 519.4493 | 0.054167 | 0 | 25.5369 | 0 | 0 | 0 | 0.054167 | 0 | 0 | 25.5369
5 | 19 | 16 | 0 | 0.0775 | 0.0775 | 48 | 7.3195 | 0.071287 | 0.071287 | 530.8433 | 0.0775 | 0 | 37.4205 | 0 | 0 | 0 | 0.0775 | 0 | 0 | 37.4205
5 | 19 | 17 | 0 | 0.10133 | 0.10133 | 48 | 7.2686 | 0.091168 | 0.091168 | 534.2596 | 0.10133 | 0 | 49.2744 | 0 | 0 | 0 | 0.10133 | 0 | 0 | 49.2744
5 | 19 | 18 | 0 | 0.015 | 0.015 | 48 | 6.9297 | 0.011776 | 0.011776 | 530.87 | 0.015 | 0 | 7.2431 | 0 | 0 | 0 | 0.015 | 0 | 0 | 7.2431
5 | 19 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 532.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 533.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 510.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 504.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 19 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 497.0513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 483.8211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 1 | 0.73833 | 0 | 0.73833 | 11 | 3.4384 | 0.25068 | 0.25068 | 479.1884 | 0.73833 | 0 | 345.6791 | 0 | 0 | 0 | 0.73833 | 0 | 0 | 345.6791
5 | 20 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 480.3199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 485.6333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 483.8343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 5 | 0 | 0.13917 | 0.13917 | 48 | 3.3706 | 0.046736 | 0.046736 | 492.5926 | 0.13917 | 0 | 61.8725 | 0 | 0 | 0 | 0.13917 | 0 | 0 | 61.8725
5 | 20 | 6 | 0.2425 | 20.7122 | 20.9547 | 47.5718 | 4.4638 | 8.5377 | 8.5377 | 507.2059 | 20.9547 | 0 | 9631.4979 | 0 | 0 | 0 | 20.9547 | 0 | 0 | 9631.4979
5 | 20 | 7 | 0.12833 | 285.8451 | 285.9734 | 47.9834 | 6.006 | 166.6513 | 166.6513 | 513.4446 | 285.9734 | 0 | 133109.5379 | 0 | 0 | 0 | 285.9734 | 0 | 0 | 133109.5379
5 | 20 | 8 | 0 | 158.0486 | 158.0486 | 48 | 6.6246 | 111.3147 | 111.3147 | 509.4349 | 158.0486 | 0 | 72929.1378 | 0 | 0 | 0 | 158.0486 | 0 | 0 | 72929.1378
5 | 20 | 9 | 0 | 108.1017 | 108.1017 | 48 | 7.1924 | 94.164 | 94.164 | 506.2785 | 108.1017 | 0 | 49540.6635 | 0 | 0 | 0 | 108.1017 | 0 | 0 | 49540.6635
5 | 20 | 10 | 0 | 11.5542 | 11.5542 | 48 | 7.0398 | 9.4626 | 9.4626 | 499.7934 | 11.5542 | 0 | 5220.1043 | 0 | 0 | 0 | 11.5542 | 0 | 0 | 5220.1043
5 | 20 | 11 | 0 | 16.0125 | 16.0125 | 48 | 7.2093 | 14.0473 | 14.0473 | 510.7711 | 16.0125 | 0 | 7410.1421 | 0 | 0 | 0 | 16.0125 | 0 | 0 | 7410.1421
5 | 20 | 12 | 0 | 55.9748 | 55.9748 | 48 | 7.9296 | 70.4038 | 70.4038 | 512.4222 | 55.9748 | 0 | 25995.943 | 0 | 0 | 0 | 55.9748 | 0 | 0 | 25995.943
5 | 20 | 13 | 0 | 27.411 | 27.411 | 48 | 8.2601 | 43.0429 | 43.0429 | 511.8943 | 27.411 | 0 | 12715.7982 | 0 | 0 | 0 | 27.411 | 0 | 0 | 12715.7982
5 | 20 | 14 | 0 | 24.2846 | 24.2846 | 48 | 8.5313 | 47.8982 | 47.8982 | 517.0906 | 24.2846 | 0 | 11391.683 | 0 | 0 | 0 | 24.2846 | 0 | 0 | 11391.683
5 | 20 | 15 | 0.76333 | 159.3479 | 160.1112 | 47.8236 | 8.4041 | 281.9552 | 281.9552 | 521.7364 | 160.1112 | 0 | 75878.749 | 0 | 0 | 0 | 160.1112 | 0 | 0 | 75878.749
5 | 20 | 16 | 0 | 0.24833 | 0.24833 | 48 | 9.1753 | 1.25 | 1.25 | 521.4029 | 0.24833 | 0 | 117.5617 | 0 | 0 | 0 | 0.24833 | 0 | 0 | 117.5617
5 | 20 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 522.8223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 18 | 0 | 0.029167 | 0.029167 | 48 | 9.0397 | 0.11065 | 0.11065 | 527.833 | 0.029167 | 0 | 13.9951 | 0 | 0 | 0 | 0.029167 | 0 | 0 | 13.9951
5 | 20 | 19 | 0 | 0.3975 | 0.3975 | 48 | 7.6754 | 0.43359 | 0.43359 | 525.2473 | 0.3975 | 0 | 189.7058 | 0 | 0 | 0 | 0.3975 | 0 | 0 | 189.7058
5 | 20 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 513.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 492.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 471.5654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 20 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 462.3876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 449.6581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 447.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 447.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 442.5101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 442.8844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 453.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 6 | 0.025 | 22.7527 | 22.7777 | 47.9594 | 4.1926 | 8.8142 | 8.8142 | 449.8889 | 22.7777 | 0 | 9155.0445 | 0 | 0 | 0 | 22.7777 | 0 | 0 | 9155.0445
5 | 21 | 7 | 0.073333 | 303.0731 | 303.1464 | 47.991 | 4.8705 | 134.157 | 134.157 | 464.2217 | 303.1464 | 0 | 126178.8505 | 0 | 0 | 0 | 303.1464 | 0 | 0 | 126178.8505
5 | 21 | 8 | 0 | 181.4558 | 181.4558 | 48 | 4.8451 | 79.8728 | 79.8728 | 467.3827 | 181.4558 | 0 | 76099.4214 | 0 | 0 | 0 | 181.4558 | 0 | 0 | 76099.4214
5 | 21 | 9 | 0 | 1.0453 | 1.0453 | 48 | 6.3789 | 0.67986 | 0.67986 | 472.2324 | 1.0453 | 0 | 443.4389 | 0 | 0 | 0 | 1.0453 | 0 | 0 | 443.4389
5 | 21 | 10 | 0 | 6.2061 | 6.2061 | 48 | 8.4804 | 11.6799 | 11.6799 | 474.6257 | 6.2061 | 0 | 2647.6756 | 0 | 0 | 0 | 6.2061 | 0 | 0 | 2647.6756
5 | 21 | 11 | 0 | 16.8253 | 16.8253 | 48 | 9.4549 | 259.6928 | 259.6928 | 472.8571 | 16.8253 | 0 | 7148.3636 | 0 | 0 | 0 | 16.8253 | 0 | 0 | 7148.3636
5 | 21 | 12 | 0 | 16.4235 | 16.4235 | 48 | 9.8362 | 0 | 0 | 472.1404 | 0 | 16.4235 | 0 | 1.7125 | 0 | 0 | 0 | 16.4235 | 0 | 0
5 | 21 | 13 | 0 | 9.3252 | 9.3252 | 48 | 9.6159 | 0 | 0 | 477.6055 | 0 | 9.3252 | 0 | 0.97236 | 0 | 0 | 0 | 9.3252 | 0 | 0
5 | 21 | 14 | 0 | 8.8613 | 8.8613 | 48 | 9.5227 | 274.0608 | 274.0608 | 483.9413 | 8.8613 | 0 | 3862.9882 | 0 | 0 | 0 | 8.8613 | 0 | 0 | 3862.9882
5 | 21 | 15 | 0 | 8.2253 | 8.2253 | 48 | 10.7175 | 0 | 0 | 490.7306 | 0 | 8.2253 | 0 | 0.85767 | 0 | 0 | 0 | 8.2253 | 0 | 0
5 | 21 | 16 | 0 | 7.3458 | 7.3458 | 48 | 12.0564 | 0 | 0 | 494.3073 | 0 | 7.3458 | 0 | 0.76597 | 0 | 0 | 0 | 7.3458 | 0 | 0
5 | 21 | 17 | 2.8959 | 1.4392 | 4.3351 | 23.2837 | 11.8107 | 0 | 0 | 492.9029 | 0 | 4.3351 | 0 | 0.45203 | 0 | 0 | 0 | 4.3351 | 0 | 0
5 | 21 | 18 | 0 | 0.59146 | 0.59146 | 48 | 12.3445 | 0 | 0 | 496.4347 | 0 | 0.59146 | 0 | 0.061673 | 0 | 0 | 0 | 0.59146 | 0 | 0
5 | 21 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 499.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 20 | 0 | 2.6091 | 2.6091 | 48 | 12.853 | 0 | 0 | 480.3285 | 0 | 2.6091 | 0 | 0.27206 | 0 | 0 | 0 | 2.6091 | 0 | 0
5 | 21 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 446.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 423.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 21 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 420.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 412.4878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 413.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 434.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 462.0936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 481.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 497.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 6 | 0 | 1.107 | 1.107 | 48 | 4.4722 | 0.45178 | 0.45178 | 502.0701 | 1.107 | 0 | 502.6556 | 0 | 0 | 0 | 1.107 | 0 | 0 | 502.6556
5 | 22 | 7 | 0 | 11.3726 | 11.3726 | 48 | 4.8281 | 4.9881 | 4.9881 | 502.2745 | 11.3726 | 0 | 5166.2767 | 0 | 0 | 0 | 11.3726 | 0 | 0 | 5166.2767
5 | 22 | 8 | 0 | 3.8669 | 3.8669 | 48 | 5.4976 | 1.9735 | 1.9735 | 499.6059 | 3.8669 | 0 | 1746.3025 | 0 | 0 | 0 | 3.8669 | 0 | 0 | 1746.3025
5 | 22 | 9 | 0 | 9.5649 | 9.5649 | 48 | 6.4043 | 6.2707 | 6.2707 | 489.9313 | 9.5649 | 0 | 4227.0101 | 0 | 0 | 0 | 9.5649 | 0 | 0 | 4227.0101
5 | 22 | 10 | 0 | 10.4332 | 10.4332 | 48 | 8.5991 | 21.9854 | 21.9854 | 484.6009 | 10.4332 | 0 | 4555.1287 | 0 | 0 | 0 | 10.4332 | 0 | 0 | 4555.1287
5 | 22 | 11 | 0 | 43.5046 | 43.5046 | 48 | 9.6413 | 0 | 0 | 482.065 | 0 | 43.5046 | 0 | 4.5363 | 0 | 0 | 0 | 43.5046 | 0 | 0
5 | 22 | 12 | 0 | 12.2312 | 12.2312 | 48 | 9.7176 | 0 | 0 | 478.1246 | 0 | 12.2312 | 0 | 1.2754 | 0 | 0 | 0 | 12.2312 | 0 | 0
5 | 22 | 13 | 0 | 4.9441 | 4.9441 | 48 | 9.7939 | 0 | 0 | 470.5539 | 0 | 4.9441 | 0 | 0.51554 | 0 | 0 | 0 | 4.9441 | 0 | 0
5 | 22 | 14 | 0 | 23.8958 | 23.8958 | 48 | 9.4634 | 393.4607 | 288 | 468.9636 | 17.4909 | 6.4049 | 7363.0391 | 0.66785 | 0 | 0 | 17.4909 | 6.4049 | 0 | 7363.0391
5 | 22 | 15 | 0 | 9.8904 | 9.8904 | 48 | 10.5311 | 0 | 0 | 473.4756 | 0 | 9.8904 | 0 | 1.0313 | 0 | 0 | 0 | 9.8904 | 0 | 0
5 | 22 | 16 | 0 | 4.4452 | 4.4452 | 48 | 11.0904 | 0 | 0 | 474.5025 | 0 | 4.4452 | 0 | 0.46352 | 0 | 0 | 0 | 4.4452 | 0 | 0
5 | 22 | 17 | 0 | 0.34029 | 0.34029 | 48 | 11.1073 | 0 | 0 | 478.7294 | 0 | 0.34029 | 0 | 0.035483 | 0 | 0 | 0 | 0.34029 | 0 | 0
5 | 22 | 18 | 0 | 0.48854 | 0.48854 | 48 | 11.4802 | 0 | 0 | 500.0544 | 0 | 0.48854 | 0 | 0.050942 | 0 | 0 | 0 | 0.48854 | 0 | 0
5 | 22 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 493.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 488.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 462.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 442.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 22 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 444.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 434.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 436.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 451.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 471.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 492.6821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 504.5011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 6 | 0 | 0.52621 | 0.52621 | 48 | 5.0061 | 0.23976 | 0.23976 | 514.2998 | 0.52621 | 0 | 245.3708 | 0 | 0 | 0 | 0.52621 | 0 | 0 | 245.3708
5 | 23 | 7 | 0 | 29.4964 | 29.4964 | 48 | 5.2518 | 14.2009 | 14.2009 | 511.4159 | 29.4964 | 0 | 13669.0916 | 0 | 0 | 0 | 29.4964 | 0 | 0 | 13669.0916
5 | 23 | 8 | 0 | 8.755 | 8.755 | 48 | 6.2094 | 5.4089 | 5.4089 | 507.57 | 8.755 | 0 | 4023.5548 | 0 | 0 | 0 | 8.755 | 0 | 0 | 4023.5548
5 | 23 | 9 | 0 | 11.7859 | 11.7859 | 48 | 7.328 | 10.8816 | 10.8816 | 515.017 | 11.7859 | 0 | 5504.2259 | 0 | 0 | 0 | 11.7859 | 0 | 0 | 5504.2259
5 | 23 | 10 | 0 | 5.5517 | 5.5517 | 48 | 8.5482 | 11.1282 | 11.1282 | 505.8774 | 5.5517 | 0 | 2542.0184 | 0 | 0 | 0 | 5.5517 | 0 | 0 | 2542.0184
5 | 23 | 11 | 0 | 13.2712 | 13.2712 | 48 | 9.1838 | 68.1924 | 68.1924 | 504.9728 | 13.2712 | 0 | 6064.5817 | 0 | 0 | 0 | 13.2712 | 0 | 0 | 6064.5817
5 | 23 | 12 | 0 | 8.8982 | 8.8982 | 48 | 9.8701 | 0 | 0 | 503.4753 | 0 | 8.8982 | 0 | 0.92784 | 0 | 0 | 0 | 8.8982 | 0 | 0
5 | 23 | 13 | 0 | 15.4503 | 15.4503 | 48 | 9.6668 | 0 | 0 | 507.7644 | 0 | 15.4503 | 0 | 1.611 | 0 | 0 | 0 | 15.4503 | 0 | 0
5 | 23 | 14 | 2.6575 | 3.623 | 6.2805 | 32.3439 | 10.2684 | 0 | 0 | 507.7012 | 0 | 6.2805 | 0 | 0.65488 | 0 | 0 | 0 | 6.2805 | 0 | 0
5 | 23 | 15 | 1.3492 | 11.7153 | 13.0645 | 44.179 | 11.226 | 0 | 0 | 506.5237 | 0 | 13.0645 | 0 | 1.3623 | 0 | 0 | 0 | 13.0645 | 0 | 0
5 | 23 | 16 | 4.5867 | 8.1383 | 12.725 | 34.6635 | 11.853 | 0 | 0 | 503.9743 | 0 | 12.725 | 0 | 1.3269 | 0 | 0 | 0 | 12.725 | 0 | 0
5 | 23 | 17 | 0.70996 | 0.084731 | 0.79469 | 14.945 | 11.7514 | 0 | 0 | 497.7158 | 0 | 0.79469 | 0 | 0.082864 | 0 | 0 | 0 | 0.79469 | 0 | 0
5 | 23 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 506.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 19 | 0 | 0.33 | 0.33 | 48 | 12.7428 | 0 | 0 | 508.552 | 0 | 0.33 | 0 | 0.03441 | 0 | 0 | 0 | 0.33 | 0 | 0
5 | 23 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 493.2411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 470.0915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 450.2501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 23 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 439.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 433.1143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 436.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 2 | 80.2041 | 0 | 80.2041 | 11 | 3.1842 | 26.1508 | 26.1508 | 449.4191 | 80.2041 | 0 | 35163.0304 | 0 | 0 | 0 | 80.2041 | 0 | 0 | 35163.0304
5 | 24 | 3 | 216.0735 | 0 | 216.0735 | 11 | 3.1249 | 69.805 | 69.805 | 472.4405 | 216.0735 | 0 | 99705.0363 | 0 | 0 | 0 | 216.0735 | 0 | 0 | 99705.0363
5 | 24 | 4 | 130.9775 | 0 | 130.9775 | 11 | 3.3028 | 43.5114 | 43.5114 | 485.8568 | 130.9775 | 0 | 62195.5404 | 0 | 0 | 0 | 130.9775 | 0 | 0 | 62195.5404
5 | 24 | 5 | 119.759 | 0 | 119.759 | 11 | 3.7096 | 42.5363 | 42.5363 | 497.0763 | 119.759 | 0 | 58212.0232 | 0 | 0 | 0 | 119.759 | 0 | 0 | 58212.0232
5 | 24 | 6 | 113.7884 | 0.61012 | 114.3985 | 11.1973 | 4.8366 | 50.2659 | 50.2659 | 500.925 | 114.3985 | 0 | 56024.1334 | 0 | 0 | 0 | 114.3985 | 0 | 0 | 56024.1334
5 | 24 | 7 | 131.3449 | 14.7188 | 146.0637 | 14.7285 | 5.0146 | 66.6753 | 66.6753 | 496.9223 | 146.0637 | 0 | 70430.9929 | 0 | 0 | 0 | 146.0637 | 0 | 0 | 70430.9929
5 | 24 | 8 | 73.6501 | 292.7127 | 366.3628 | 40.5619 | 6.2094 | 226.3413 | 226.3413 | 493.1368 | 366.3628 | 0 | 165806.6495 | 0 | 0 | 0 | 366.3628 | 0 | 0 | 165806.6495
5 | 24 | 9 | 67.8685 | 85.4536 | 153.322 | 31.6218 | 7.311 | 140.5056 | 140.5056 | 484.4056 | 153.322 | 0 | 69421.7284 | 0 | 0 | 0 | 153.322 | 0 | 0 | 69421.7284
5 | 24 | 10 | 24.7032 | 2.5408 | 27.2441 | 14.4507 | 8.0567 | 37.1072 | 37.1072 | 484.7871 | 27.2441 | 0 | 12813.8804 | 0 | 0 | 0 | 27.2441 | 0 | 0 | 12813.8804
5 | 24 | 11 | 64.6738 | 6.6042 | 71.2779 | 14.4282 | 9.3109 | 532.8842 | 288 | 483.8483 | 38.5225 | 32.7554 | 18083.249 | 3.4155 | 0 | 0 | 38.5225 | 32.7554 | 0 | 18083.249
5 | 24 | 12 | 30.2551 | 9.9867 | 40.2417 | 20.1822 | 9.0058 | 143.8173 | 143.8173 | 488.9578 | 40.2417 | 0 | 18864.3507 | 0 | 0 | 0 | 40.2417 | 0 | 0 | 18864.3507
5 | 24 | 13 | 41.0455 | 4.9633 | 46.0088 | 14.9915 | 8.4889 | 87.2552 | 87.2552 | 482.799 | 46.0088 | 0 | 21523.2776 | 0 | 0 | 0 | 46.0088 | 0 | 0 | 21523.2776
5 | 24 | 14 | 15.9334 | 3.6133 | 19.5467 | 17.8397 | 8.938 | 62.5959 | 62.5959 | 476.6745 | 19.5467 | 0 | 8968.7011 | 0 | 0 | 0 | 19.5467 | 0 | 0 | 8968.7011
5 | 24 | 15 | 9.9075 | 0 | 9.9075 | 11 | 9.6075 | 0 | 0 | 478.3158 | 0 | 9.9075 | 0 | 1.0331 | 0 | 0 | 0 | 9.9075 | 0 | 0
5 | 24 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 470.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 464.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 18 | 0 | 2.1299 | 2.1299 | 48 | 11.0734 | 0 | 0 | 476.303 | 0 | 2.1299 | 0 | 0.22209 | 0 | 0 | 0 | 2.1299 | 0 | 0
5 | 24 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 465.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 459.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 430.9726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 419.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 24 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 417.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 409.7852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 415.7081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 434.4572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 452.0818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 4 | 0.87235 | 0 | 0.87235 | 11 | 3.4045 | 0.29456 | 0.29456 | 466.4448 | 0.87235 | 0 | 397.3053 | 0 | 0 | 0 | 0.87235 | 0 | 0 | 397.3053
5 | 25 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 480.8613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 6 | 0 | 0.58621 | 0.58621 | 48 | 4.396 | 0.23572 | 0.23572 | 487.7514 | 0.58621 | 0 | 257.7859 | 0 | 0 | 0 | 0.58621 | 0 | 0 | 257.7859
5 | 25 | 7 | 0 | 85.9893 | 85.9893 | 48 | 4.6502 | 36.3573 | 36.3573 | 491.705 | 85.9893 | 0 | 38153.9051 | 0 | 0 | 0 | 85.9893 | 0 | 0 | 38153.9051
5 | 25 | 8 | 0.22556 | 47.3524 | 47.578 | 47.8246 | 5.1417 | 22.339 | 22.339 | 497.0773 | 47.578 | 0 | 21374.534 | 0 | 0 | 0 | 47.578 | 0 | 0 | 21374.534
5 | 25 | 9 | 0 | 14.1307 | 14.1307 | 48 | 6.6161 | 9.924 | 9.924 | 505.5826 | 14.1307 | 0 | 6465.9634 | 0 | 0 | 0 | 14.1307 | 0 | 0 | 6465.9634
5 | 25 | 10 | 81.8142 | 95.5509 | 177.3651 | 30.9328 | 6.9721 | 141.4962 | 141.4962 | 501.3402 | 177.3651 | 0 | 83433.8508 | 0 | 0 | 0 | 177.3651 | 0 | 0 | 83433.8508
5 | 25 | 11 | 0 | 14.2571 | 14.2571 | 48 | 8.5652 | 29.0501 | 29.0501 | 493.0337 | 14.2571 | 0 | 6344.8934 | 0 | 0 | 0 | 14.2571 | 0 | 0 | 6344.8934
5 | 25 | 12 | 0 | 202.4839 | 202.4839 | 48 | 7.8957 | 249.5852 | 249.5852 | 495.1185 | 202.4839 | 0 | 90534.3133 | 0 | 0 | 0 | 202.4839 | 0 | 0 | 90534.3133
5 | 25 | 13 | 0 | 90.4617 | 90.4617 | 48 | 7.4381 | 87.7961 | 87.7961 | 503.6683 | 90.4617 | 0 | 41220.5125 | 0 | 0 | 0 | 90.4617 | 0 | 0 | 41220.5125
5 | 25 | 14 | 0 | 52.1697 | 52.1697 | 48 | 7.2771 | 47.1082 | 47.1082 | 496.5179 | 52.1697 | 0 | 23399.0337 | 0 | 0 | 0 | 52.1697 | 0 | 0 | 23399.0337
5 | 25 | 15 | 0 | 36.9921 | 36.9921 | 48 | 7.3449 | 34.4116 | 34.4116 | 506.4715 | 36.9921 | 0 | 16959.8082 | 0 | 0 | 0 | 36.9921 | 0 | 0 | 16959.8082
5 | 25 | 16 | 0 | 11.0595 | 11.0595 | 48 | 6.9975 | 8.9095 | 8.9095 | 504.5809 | 11.0595 | 0 | 5049.5775 | 0 | 0 | 0 | 11.0595 | 0 | 0 | 5049.5775
5 | 25 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 487.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 495.8382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 495.6914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 477.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 451.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 435.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 25 | 23 | 3.5921 | 0 | 3.5921 | 11 | 4.2615 | 1.408 | 1.408 | 435.6714 | 3.5921 | 0 | 1525.4521 | 0 | 0 | 0 | 3.5921 | 0 | 0 | 1525.4521
5 | 26 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 426.9811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 1 | 0.63079 | 0 | 0.63079 | 11 | 3.1079 | 0.20325 | 0.20325 | 430.3901 | 0.63079 | 0 | 264.5478 | 0 | 0 | 0 | 0.63079 | 0 | 0 | 264.5478
5 | 26 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 439.0934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 450.8138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 466.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 476.8503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 6 | 0 | 0.57538 | 0.57538 | 48 | 4.6163 | 0.24162 | 0.24162 | 485.4788 | 0.57538 | 0 | 251.7144 | 0 | 0 | 0 | 0.57538 | 0 | 0 | 251.7144
5 | 26 | 7 | 0 | 4.2101 | 4.2101 | 48 | 6.1924 | 2.588 | 2.588 | 487.8837 | 4.2101 | 0 | 1851.9469 | 0 | 0 | 0 | 4.2101 | 0 | 0 | 1851.9469
5 | 26 | 8 | 0 | 18.7921 | 18.7921 | 48 | 6.8788 | 14.4763 | 14.4763 | 487.3806 | 18.7921 | 0 | 8256.884 | 0 | 0 | 0 | 18.7921 | 0 | 0 | 8256.884
5 | 26 | 9 | 0 | 0.92661 | 0.92661 | 48 | 7.3195 | 0.85232 | 0.85232 | 474.6058 | 0.92661 | 0 | 395.2955 | 0 | 0 | 0 | 0.92661 | 0 | 0 | 395.2955
5 | 26 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 473.3589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 11 | 0 | 0.0175 | 0.0175 | 48 | 7.2263 | 0.015462 | 0.015462 | 479.1179 | 0.0175 | 0 | 7.5446 | 0 | 0 | 0 | 0.0175 | 0 | 0 | 7.5446
5 | 26 | 12 | 0 | 15.106 | 15.106 | 48 | 7.8703 | 18.3447 | 18.3447 | 481.063 | 15.106 | 0 | 6541.8493 | 0 | 0 | 0 | 15.106 | 0 | 0 | 6541.8493
5 | 26 | 13 | 0 | 10.9518 | 10.9518 | 48 | 8.1754 | 16.1674 | 16.1674 | 483.4514 | 10.9518 | 0 | 4768.9762 | 0 | 0 | 0 | 10.9518 | 0 | 0 | 4768.9762
5 | 26 | 14 | 0 | 4.7275 | 4.7275 | 48 | 8.2431 | 7.3301 | 7.3301 | 484.6668 | 4.7275 | 0 | 2064.3425 | 0 | 0 | 0 | 4.7275 | 0 | 0 | 2064.3425
5 | 26 | 15 | 0 | 40.6334 | 40.6334 | 48 | 7.4212 | 39.1279 | 39.1279 | 495.7263 | 40.6334 | 0 | 18192.6291 | 0 | 0 | 0 | 40.6334 | 0 | 0 | 18192.6291
5 | 26 | 16 | 0 | 25.4156 | 25.4156 | 48 | 7.3195 | 23.378 | 23.378 | 490.3705 | 25.4156 | 0 | 11243.1003 | 0 | 0 | 0 | 25.4156 | 0 | 0 | 11243.1003
5 | 26 | 17 | 0 | 9.3523 | 9.3523 | 48 | 7.2686 | 8.4141 | 8.4141 | 484.9074 | 9.3523 | 0 | 4086.1053 | 0 | 0 | 0 | 9.3523 | 0 | 0 | 4086.1053
5 | 26 | 18 | 0 | 5.1925 | 5.1925 | 48 | 6.9297 | 4.0765 | 4.0765 | 498.5633 | 5.1925 | 0 | 2339.5687 | 0 | 0 | 0 | 5.1925 | 0 | 0 | 2339.5687
5 | 26 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 487.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 483.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 463.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 440.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 26 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 440.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 433.4585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 438.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 439.9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 438.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 443.1437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 448.3598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 6 | 0 | 16.9611 | 16.9611 | 48 | 4.4638 | 6.9106 | 6.9106 | 467.1573 | 16.9611 | 0 | 7109.3708 | 0 | 0 | 0 | 16.9611 | 0 | 0 | 7109.3708
5 | 27 | 7 | 5.7867 | 341.7719 | 347.5586 | 47.384 | 6.006 | 202.5402 | 202.5402 | 481.1138 | 347.5586 | 0 | 150746.546 | 0 | 0 | 0 | 347.5586 | 0 | 0 | 150746.546
5 | 27 | 8 | 0.69666 | 272.4667 | 273.1633 | 47.9056 | 6.6246 | 192.3908 | 192.3908 | 485.1832 | 273.1633 | 0 | 119448.1996 | 0 | 0 | 0 | 273.1633 | 0 | 0 | 119448.1996
5 | 27 | 9 | 0 | 279.4066 | 279.4066 | 48 | 7.1924 | 243.3824 | 243.3824 | 491.1213 | 279.4066 | 0 | 123811.0171 | 0 | 0 | 0 | 279.4066 | 0 | 0 | 123811.0171
5 | 27 | 10 | 0 | 47.1542 | 47.1542 | 48 | 7.0398 | 38.6181 | 38.6181 | 493.0232 | 47.1542 | 0 | 20984.7305 | 0 | 0 | 0 | 47.1542 | 0 | 0 | 20984.7305
5 | 27 | 11 | 0 | 288.3439 | 288.3439 | 48 | 7.2093 | 252.9552 | 252.9552 | 490.652 | 288.3439 | 0 | 127635.9929 | 0 | 0 | 0 | 288.3439 | 0 | 0 | 127635.9929
5 | 27 | 12 | 0 | 64.0227 | 64.0227 | 48 | 7.9296 | 80.5262 | 80.5262 | 487.0677 | 64.0227 | 0 | 28110.2776 | 0 | 0 | 0 | 64.0227 | 0 | 0 | 28110.2776
5 | 27 | 13 | 0 | 71.2578 | 71.2578 | 48 | 8.2601 | 111.8946 | 111.8946 | 480.9826 | 71.2578 | 0 | 30853.4038 | 0 | 0 | 0 | 71.2578 | 0 | 0 | 30853.4038
5 | 27 | 14 | 0 | 38.8566 | 38.8566 | 48 | 8.5313 | 76.6395 | 76.6395 | 484.3835 | 38.8566 | 0 | 16956.3779 | 0 | 0 | 0 | 38.8566 | 0 | 0 | 16956.3779
5 | 27 | 15 | 0 | 4.759 | 4.759 | 48 | 8.4041 | 8.3806 | 8.3806 | 485.2584 | 4.759 | 0 | 2080.9054 | 0 | 0 | 0 | 4.759 | 0 | 0 | 2080.9054
5 | 27 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 497.2437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 493.7802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 492.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 487.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 466.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 438.8928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 419.9853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 27 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 411.9772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 412.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 410.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 408.9711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 404.9422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 402.7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 5 | 0 | 0.26667 | 0.26667 | 48 | 3.4638 | 0.090916 | 0.090916 | 410.5089 | 0.26667 | 0 | 96.669 | 0 | 0 | 0 | 0.26667 | 0 | 0 | 96.669
5 | 28 | 6 | 0.74583 | 80.8716 | 81.6174 | 47.6619 | 4.1926 | 31.5832 | 31.5832 | 432.188 | 81.6174 | 0 | 31384.0163 | 0 | 0 | 0 | 81.6174 | 0 | 0 | 31384.0163
5 | 28 | 7 | 5.6258 | 464.2362 | 469.862 | 47.557 | 4.8705 | 207.9367 | 207.9367 | 456.9977 | 469.862 | 0 | 192380.639 | 0 | 0 | 0 | 469.862 | 0 | 0 | 192380.639
5 | 28 | 8 | 3.1058 | 488.0306 | 491.1364 | 47.766 | 4.8451 | 216.1872 | 216.1872 | 468.75 | 491.1364 | 0 | 206760.572 | 0 | 0 | 0 | 491.1364 | 0 | 0 | 206760.572
5 | 28 | 9 | 0.29496 | 330.0319 | 330.3269 | 47.967 | 6.3789 | 214.8483 | 214.8483 | 478.5152 | 330.3269 | 0 | 142221.6795 | 0 | 0 | 0 | 330.3269 | 0 | 0 | 142221.6795
5 | 28 | 10 | 0 | 273.1703 | 273.1703 | 48 | 8.4804 | 514.109 | 288 | 481.7547 | 153.028 | 120.1424 | 66376.6039 | 12.5276 | 0 | 0 | 153.028 | 120.1424 | 0 | 66376.6039
5 | 28 | 11 | 0 | 276.7634 | 276.7634 | 48 | 9.4549 | 4271.7407 | 288 | 476.3106 | 18.6593 | 258.1041 | 7991.9932 | 26.9132 | 0 | 0 | 18.6593 | 258.1041 | 0 | 7991.9932
5 | 28 | 12 | 0 | 74.9882 | 74.9882 | 48 | 9.8362 | 0 | 0 | 454.351 | 0 | 74.9882 | 0 | 7.8192 | 0 | 0 | 0 | 74.9882 | 0 | 0
5 | 28 | 13 | 0 | 26.2678 | 26.2678 | 48 | 9.6159 | 0 | 0 | 440.9902 | 0 | 26.2678 | 0 | 2.739 | 0 | 0 | 0 | 26.2678 | 0 | 0
5 | 28 | 14 | 0 | 64.4701 | 64.4701 | 48 | 9.5227 | 1993.931 | 288 | 436.9106 | 9.312 | 55.1582 | 3621.5184 | 5.7515 | 0 | 0 | 9.312 | 55.1582 | 0 | 3621.5184
5 | 28 | 15 | 0 | 0.17007 | 0.17007 | 48 | 10.7175 | 0 | 0 | 441.8255 | 0 | 0.17007 | 0 | 0.017734 | 0 | 0 | 0 | 0.17007 | 0 | 0
5 | 28 | 16 | 0 | 1.9158 | 1.9158 | 48 | 12.0564 | 0 | 0 | 447.3955 | 0 | 1.9158 | 0 | 0.19977 | 0 | 0 | 0 | 1.9158 | 0 | 0
5 | 28 | 17 | 0 | 0.8575 | 0.8575 | 48 | 11.8107 | 0 | 0 | 440.4429 | 0 | 0.8575 | 0 | 0.089414 | 0 | 0 | 0 | 0.8575 | 0 | 0
5 | 28 | 18 | 0 | 2.2825 | 2.2825 | 48 | 12.3445 | 0 | 0 | 446.3954 | 0 | 2.2825 | 0 | 0.238 | 0 | 0 | 0 | 2.2825 | 0 | 0
5 | 28 | 19 | 0 | 0.98667 | 0.98667 | 48 | 12.2767 | 0 | 0 | 452.1784 | 0 | 0.98667 | 0 | 0.10288 | 0 | 0 | 0 | 0.98667 | 0 | 0
5 | 28 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 446.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 412.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 390.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 28 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 380.5088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 377.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 372.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 374.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 375.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 379.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 5 | 0 | 0.2525 | 0.2525 | 48 | 3.6164 | 0.088284 | 0.088284 | 388.4873 | 0.2525 | 0 | 85.973 | 0 | 0 | 0 | 0.2525 | 0 | 0 | 85.973
5 | 29 | 6 | 0 | 2.8017 | 2.8017 | 48 | 4.4722 | 1.1434 | 1.1434 | 415.0133 | 2.8017 | 0 | 1028.2643 | 0 | 0 | 0 | 2.8017 | 0 | 0 | 1028.2643
5 | 29 | 7 | 4.955 | 405.5979 | 410.5529 | 47.5534 | 4.8281 | 180.073 | 180.073 | 431.4376 | 410.5529 | 0 | 157604.7461 | 0 | 0 | 0 | 410.5529 | 0 | 0 | 157604.7461
5 | 29 | 8 | 0 | 170.2488 | 170.2488 | 48 | 5.4976 | 86.8873 | 86.8873 | 446.6513 | 170.2488 | 0 | 67869.9024 | 0 | 0 | 0 | 170.2488 | 0 | 0 | 67869.9024
5 | 29 | 9 | 0 | 12.0257 | 12.0257 | 48 | 6.4043 | 7.884 | 7.884 | 453.8662 | 12.0257 | 0 | 4880.8055 | 0 | 0 | 0 | 12.0257 | 0 | 0 | 4880.8055
5 | 29 | 10 | 0 | 12.9456 | 12.9456 | 48 | 8.5991 | 27.2798 | 27.2798 | 450.9193 | 12.9456 | 0 | 5216.0259 | 0 | 0 | 0 | 12.9456 | 0 | 0 | 5216.0259
5 | 29 | 11 | 0 | 20.1049 | 20.1049 | 48 | 9.6413 | 0 | 0 | 450.1789 | 0 | 20.1049 | 0 | 2.0964 | 0 | 0 | 0 | 20.1049 | 0 | 0
5 | 29 | 12 | 0 | 16.1381 | 16.1381 | 48 | 9.7176 | 0 | 0 | 430.3278 | 0 | 16.1381 | 0 | 1.6828 | 0 | 0 | 0 | 16.1381 | 0 | 0
5 | 29 | 13 | 0 | 4.9949 | 4.9949 | 48 | 9.7939 | 0 | 0 | 443.1832 | 0 | 4.9949 | 0 | 0.52083 | 0 | 0 | 0 | 4.9949 | 0 | 0
5 | 29 | 14 | 0 | 8.8001 | 8.8001 | 48 | 9.4634 | 144.8995 | 144.8995 | 451.0701 | 8.8001 | 0 | 3547.0506 | 0 | 0 | 0 | 8.8001 | 0 | 0 | 3547.0506
5 | 29 | 15 | 0 | 8.3974 | 8.3974 | 48 | 10.5311 | 0 | 0 | 454.3716 | 0 | 8.3974 | 0 | 0.87562 | 0 | 0 | 0 | 8.3974 | 0 | 0
5 | 29 | 16 | 0 | 3.6475 | 3.6475 | 48 | 11.0904 | 0 | 0 | 466.6437 | 0 | 3.6475 | 0 | 0.38033 | 0 | 0 | 0 | 3.6475 | 0 | 0
5 | 29 | 17 | 0 | 0.0825 | 0.0825 | 48 | 11.1073 | 0 | 0 | 467.3796 | 0 | 0.0825 | 0 | 0.0086025 | 0 | 0 | 0 | 0.0825 | 0 | 0
5 | 29 | 18 | 0 | 2.1667 | 2.1667 | 48 | 11.4802 | 0 | 0 | 475.0696 | 0 | 2.1667 | 0 | 0.22592 | 0 | 0 | 0 | 2.1667 | 0 | 0
5 | 29 | 19 | 0 | 1.0142 | 1.0142 | 48 | 12.6496 | 0 | 0 | 474.1271 | 0 | 1.0142 | 0 | 0.10575 | 0 | 0 | 0 | 1.0142 | 0 | 0
5 | 29 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 456.5452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 425.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 413.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 29 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 398.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 388.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 391.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 408.9743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 433.2176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 452.8846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 5 | 0 | 0.16833 | 0.16833 | 48 | 3.8536 | 0.061291 | 0.061291 | 469.4825 | 0.16833 | 0 | 70.9496 | 0 | 0 | 0 | 0.16833 | 0 | 0 | 70.9496
5 | 30 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 481.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 483.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 8 | 22.5632 | 0 | 22.5632 | 11 | 6.2094 | 13.9397 | 13.9397 | 480.1817 | 22.5632 | 0 | 10586.2277 | 0 | 0 | 0 | 22.5632 | 0 | 0 | 10586.2277
5 | 30 | 9 | 2.2831 | 1.2067 | 3.4898 | 23.7937 | 7.328 | 3.2221 | 3.2221 | 473.7465 | 3.4898 | 0 | 1570.2581 | 0 | 0 | 0 | 3.4898 | 0 | 0 | 1570.2581
5 | 30 | 10 | 0.73067 | 2.889 | 3.6197 | 40.5311 | 8.5482 | 7.2554 | 7.2554 | 468.1974 | 3.6197 | 0 | 1548.0071 | 0 | 0 | 0 | 3.6197 | 0 | 0 | 1548.0071
5 | 30 | 11 | 0 | 8.6278 | 8.6278 | 48 | 9.1838 | 44.3326 | 44.3326 | 462.3679 | 8.6278 | 0 | 3575.0646 | 0 | 0 | 0 | 8.6278 | 0 | 0 | 3575.0646
5 | 30 | 12 | 0 | 6.4065 | 6.4065 | 48 | 9.8701 | 0 | 0 | 465.6521 | 0 | 6.4065 | 0 | 0.66802 | 0 | 0 | 0 | 6.4065 | 0 | 0
5 | 30 | 13 | 0 | 4.1676 | 4.1676 | 48 | 9.6668 | 0 | 0 | 469.8816 | 0 | 4.1676 | 0 | 0.43457 | 0 | 0 | 0 | 4.1676 | 0 | 0
5 | 30 | 14 | 1.8845 | 11.9411 | 13.8256 | 42.9568 | 10.2684 | 0 | 0 | 472.4307 | 0 | 13.8256 | 0 | 1.4416 | 0 | 0 | 0 | 13.8256 | 0 | 0
5 | 30 | 15 | 1.8153 | 4.3017 | 6.117 | 37.0196 | 11.226 | 0 | 0 | 483.3078 | 0 | 6.117 | 0 | 0.63784 | 0 | 0 | 0 | 6.117 | 0 | 0
5 | 30 | 16 | 9.3453 | 1.7383 | 11.0837 | 16.803 | 11.853 | 0 | 0 | 489.9885 | 0 | 11.0837 | 0 | 1.1557 | 0 | 0 | 0 | 11.0837 | 0 | 0
5 | 30 | 17 | 0 | 0.25667 | 0.25667 | 48 | 11.7514 | 0 | 0 | 487.555 | 0 | 0.25667 | 0 | 0.026763 | 0 | 0 | 0 | 0.25667 | 0 | 0
5 | 30 | 18 | 13.0439 | 0.1875 | 13.2314 | 11.5243 | 12.4971 | 0 | 0 | 497.1491 | 0 | 13.2314 | 0 | 1.3797 | 0 | 0 | 0 | 13.2314 | 0 | 0
5 | 30 | 19 | 48.587 | 0 | 48.587 | 11 | 12.7428 | 0 | 0 | 483.6928 | 0 | 48.587 | 0 | 5.0663 | 0 | 0 | 0 | 48.587 | 0 | 0
5 | 30 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 456.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 432.2039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 414.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 30 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 406.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 402.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 406.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 414.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 438.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 456.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 470.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 6 | 0 | 4.6867 | 4.6867 | 48 | 4.8366 | 2.0593 | 2.0593 | 480.7224 | 4.6867 | 0 | 2028.0255 | 0 | 0 | 0 | 4.6867 | 0 | 0 | 2028.0255
5 | 31 | 7 | 0 | 5 | 5 | 48 | 5.0146 | 2.2824 | 2.2824 | 474.1578 | 5 | 0 | 2130.789 | 0 | 0 | 0 | 5 | 0 | 0 | 2130.789
5 | 31 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 478.6292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 9 | 0.63583 | 82.3057 | 82.9415 | 47.7164 | 7.311 | 76.0083 | 76.0083 | 470.0225 | 82.9415 | 0 | 35026.708 | 0 | 0 | 0 | 82.9415 | 0 | 0 | 35026.708
5 | 31 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 475.1644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 11 | 0 | 0.22833 | 0.22833 | 48 | 9.3109 | 1.7071 | 1.7071 | 471.3475 | 0.22833 | 0 | 96.6644 | 0 | 0 | 0 | 0.22833 | 0 | 0 | 96.6644
5 | 31 | 12 | 0 | 0.80613 | 0.80613 | 48 | 9.0058 | 2.881 | 2.881 | 471.9162 | 0.80613 | 0 | 341.7336 | 0 | 0 | 0 | 0.80613 | 0 | 0 | 341.7336
5 | 31 | 13 | 0 | 0.27505 | 0.27505 | 48 | 8.4889 | 0.52163 | 0.52163 | 469.6474 | 0.27505 | 0 | 115.9732 | 0 | 0 | 0 | 0.27505 | 0 | 0 | 115.9732
5 | 31 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 472.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 15 | 0 | 0.0025 | 0.0025 | 48 | 9.6075 | 0 | 0 | 473.652 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
5 | 31 | 16 | 0 | 0.0025 | 0.0025 | 48 | 10.9718 | 0 | 0 | 484.093 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
5 | 31 | 17 | 0 | 0.10417 | 0.10417 | 48 | 10.3786 | 0 | 0 | 479.241 | 0 | 0.10417 | 0 | 0.010862 | 0 | 0 | 0 | 0.10417 | 0 | 0
5 | 31 | 18 | 0 | 2.1142 | 2.1142 | 48 | 11.0734 | 0 | 0 | 491.9835 | 0 | 2.1142 | 0 | 0.22045 | 0 | 0 | 0 | 2.1142 | 0 | 0
5 | 31 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 483.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 453.0927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 423.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 407.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 31 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 404.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 398.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 400.7055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 404.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 415.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 432.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 453.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 469.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 7 | 0 | 28.0577 | 28.0577 | 48 | 4.6502 | 11.8631 | 11.8631 | 472.8942 | 28.0577 | 0 | 11921.5446 | 0 | 0 | 0 | 28.0577 | 0 | 0 | 11921.5446
6 | 1 | 8 | 6.8962 | 865.2029 | 872.0991 | 47.7074 | 5.1417 | 409.4718 | 288 | 479.0048 | 613.3867 | 258.7124 | 264552.0402 | 26.9766 | 0 | 0 | 613.3867 | 258.7124 | 0 | 264552.0402
6 | 1 | 9 | 0 | 219.7267 | 219.7267 | 48 | 6.6161 | 154.3141 | 154.3141 | 485.7868 | 219.7267 | 0 | 96193.4494 | 0 | 0 | 0 | 219.7267 | 0 | 0 | 96193.4494
6 | 1 | 10 | 0 | 3.9954 | 3.9954 | 48 | 6.9721 | 3.1874 | 3.1874 | 477.0544 | 3.9954 | 0 | 1714.2559 | 0 | 0 | 0 | 3.9954 | 0 | 0 | 1714.2559
6 | 1 | 11 | 0 | 20.3124 | 20.3124 | 48 | 8.5652 | 41.3882 | 41.3882 | 482.1779 | 20.3124 | 0 | 8819.1901 | 0 | 0 | 0 | 20.3124 | 0 | 0 | 8819.1901
6 | 1 | 12 | 0 | 6.3445 | 6.3445 | 48 | 7.8957 | 7.8203 | 7.8203 | 485.5668 | 6.3445 | 0 | 2776.1293 | 0 | 0 | 0 | 6.3445 | 0 | 0 | 2776.1293
6 | 1 | 13 | 0 | 1.2533 | 1.2533 | 48 | 7.4381 | 1.2164 | 1.2164 | 484.2885 | 1.2533 | 0 | 546.803 | 0 | 0 | 0 | 1.2533 | 0 | 0 | 546.803
6 | 1 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 487.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 494.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 499.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 500.0688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 503.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 479.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 452.1626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 425.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 408.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 401.0827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 393.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 393.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 403.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 414.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 434.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 445.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 451.0954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 7 | 0 | 24.4966 | 24.4966 | 48 | 6.1924 | 15.0587 | 15.0587 | 471.5152 | 24.4966 | 0 | 10374.6852 | 0 | 0 | 0 | 24.4966 | 0 | 0 | 10374.6852
6 | 2 | 8 | 0.055833 | 16.4721 | 16.528 | 47.875 | 6.8788 | 12.7322 | 12.7322 | 478.2816 | 16.528 | 0 | 7113.751 | 0 | 0 | 0 | 16.528 | 0 | 0 | 7113.751
6 | 2 | 9 | 0.075 | 24.248 | 24.323 | 47.8859 | 7.3195 | 22.373 | 22.373 | 468.8639 | 24.323 | 0 | 10239.4407 | 0 | 0 | 0 | 24.323 | 0 | 0 | 10239.4407
6 | 2 | 10 | 0 | 15.3053 | 15.3053 | 48 | 7.4805 | 15.1526 | 15.1526 | 465.045 | 15.3053 | 0 | 6383.0093 | 0 | 0 | 0 | 15.3053 | 0 | 0 | 6383.0093
6 | 2 | 11 | 0 | 30.5579 | 30.5579 | 48 | 7.2263 | 26.9997 | 26.9997 | 469.8205 | 30.5579 | 0 | 12889.9467 | 0 | 0 | 0 | 30.5579 | 0 | 0 | 12889.9467
6 | 2 | 12 | 0 | 17.9755 | 17.9755 | 48 | 7.8703 | 21.8294 | 21.8294 | 471.7232 | 17.9755 | 0 | 7616.6202 | 0 | 0 | 0 | 17.9755 | 0 | 0 | 7616.6202
6 | 2 | 13 | 0 | 17.8791 | 17.8791 | 48 | 8.1754 | 26.3937 | 26.3937 | 474.6779 | 17.8791 | 0 | 7628.6232 | 0 | 0 | 0 | 17.8791 | 0 | 0 | 7628.6232
6 | 2 | 14 | 0 | 9.8733 | 9.8733 | 48 | 8.2431 | 15.3088 | 15.3088 | 478.1252 | 9.8733 | 0 | 4246.7698 | 0 | 0 | 0 | 9.8733 | 0 | 0 | 4246.7698
6 | 2 | 15 | 0 | 11.06 | 11.06 | 48 | 7.4212 | 10.6502 | 10.6502 | 481.4424 | 11.06 | 0 | 4793.873 | 0 | 0 | 0 | 11.06 | 0 | 0 | 4793.873
6 | 2 | 16 | 0 | 0.98167 | 0.98167 | 48 | 7.3195 | 0.90296 | 0.90296 | 489.5713 | 0.98167 | 0 | 433.4758 | 0 | 0 | 0 | 0.98167 | 0 | 0 | 433.4758
6 | 2 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 489.3157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 493.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 480.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 453.1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 427.3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 415.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 399.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 387.6771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 382.8268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 382.4052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 381.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 389.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 406.9376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 6 | 0 | 0.62371 | 0.62371 | 48 | 4.4638 | 0.25412 | 0.25412 | 426.9731 | 0.62371 | 0 | 236.3687 | 0 | 0 | 0 | 0.62371 | 0 | 0 | 236.3687
6 | 3 | 7 | 0 | 8.5668 | 8.5668 | 48 | 6.006 | 4.9923 | 4.9923 | 437.1129 | 8.5668 | 0 | 3333.4327 | 0 | 0 | 0 | 8.5668 | 0 | 0 | 3333.4327
6 | 3 | 8 | 0 | 82.8276 | 82.8276 | 48 | 6.6246 | 58.336 | 58.336 | 444.2291 | 82.8276 | 0 | 32818.6965 | 0 | 0 | 0 | 82.8276 | 0 | 0 | 32818.6965
6 | 3 | 9 | 0 | 19.2632 | 19.2632 | 48 | 7.1924 | 16.7796 | 16.7796 | 455.9535 | 19.2632 | 0 | 7858.5097 | 0 | 0 | 0 | 19.2632 | 0 | 0 | 7858.5097
6 | 3 | 10 | 0 | 0.66255 | 0.66255 | 48 | 7.0398 | 0.54261 | 0.54261 | 463.4553 | 0.66255 | 0 | 275.2617 | 0 | 0 | 0 | 0.66255 | 0 | 0 | 275.2617
6 | 3 | 11 | 0 | 7.2267 | 7.2267 | 48 | 7.2093 | 6.3397 | 6.3397 | 459.5573 | 7.2267 | 0 | 2974.1874 | 0 | 0 | 0 | 7.2267 | 0 | 0 | 2974.1874
6 | 3 | 12 | 0 | 1.3558 | 1.3558 | 48 | 7.9296 | 1.7053 | 1.7053 | 446.0433 | 1.3558 | 0 | 539.6805 | 0 | 0 | 0 | 1.3558 | 0 | 0 | 539.6805
6 | 3 | 13 | 0 | 0.235 | 0.235 | 48 | 8.2601 | 0.36902 | 0.36902 | 452.9424 | 0.235 | 0 | 95.1615 | 0 | 0 | 0 | 0.235 | 0 | 0 | 95.1615
6 | 3 | 14 | 0 | 0.10167 | 0.10167 | 48 | 8.5313 | 0.20052 | 0.20052 | 458.6557 | 0.10167 | 0 | 41.75 | 0 | 0 | 0 | 0.10167 | 0 | 0 | 41.75
6 | 3 | 15 | 0 | 0.1475 | 0.1475 | 48 | 8.4041 | 0.25975 | 0.25975 | 465.6089 | 0.1475 | 0 | 61.5973 | 0 | 0 | 0 | 0.1475 | 0 | 0 | 61.5973
6 | 3 | 16 | 0 | 1.4541 | 1.4541 | 48 | 9.1753 | 7.3193 | 7.3193 | 475.7911 | 1.4541 | 0 | 622.0617 | 0 | 0 | 0 | 1.4541 | 0 | 0 | 622.0617
6 | 3 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 481.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 480.6321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 463.0146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 450.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 434.7362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 419.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 3 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 405.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 396.2182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 387.4826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 2 | 31.7977 | 0 | 31.7977 | 11 | 2.8791 | 9.8965 | 9.8965 | 388.4342 | 31.7977 | 0 | 12001.5434 | 0 | 0 | 0 | 31.7977 | 0 | 0 | 12001.5434
6 | 4 | 3 | 50.6706 | 0 | 50.6706 | 11 | 3.0147 | 16.0955 | 16.0955 | 390.0084 | 50.6706 | 0 | 19204.5877 | 0 | 0 | 0 | 50.6706 | 0 | 0 | 19204.5877
6 | 4 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 391.4162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 5 | 2.9058 | 0.015 | 2.9208 | 11.19 | 3.4638 | 0.99582 | 0.99582 | 402.3125 | 2.9208 | 0 | 1142.4036 | 0 | 0 | 0 | 2.9208 | 0 | 0 | 1142.4036
6 | 4 | 6 | 66.0967 | 6.9025 | 72.9992 | 14.4986 | 4.1926 | 28.2483 | 28.2483 | 413.8036 | 72.9992 | 0 | 29148.958 | 0 | 0 | 0 | 72.9992 | 0 | 0 | 29148.958
6 | 4 | 7 | 18.2596 | 473.8508 | 492.1104 | 46.6271 | 4.8705 | 217.7827 | 217.7827 | 437.5697 | 492.1104 | 0 | 192386.8703 | 0 | 0 | 0 | 492.1104 | 0 | 0 | 192386.8703
6 | 4 | 8 | 27.8245 | 863.051 | 890.8755 | 46.8444 | 4.8451 | 392.1434 | 288 | 455.1361 | 654.2815 | 236.5941 | 267137.7262 | 24.6703 | 0 | 0 | 654.2815 | 236.5941 | 0 | 267137.7262
6 | 4 | 9 | 2.15 | 555.524 | 557.674 | 47.8574 | 6.3789 | 362.7173 | 288 | 473.0103 | 442.7969 | 114.8771 | 188256.4207 | 11.9785 | 0 | 0 | 442.7969 | 114.8771 | 0 | 188256.4207
6 | 4 | 10 | 0 | 324.1615 | 324.1615 | 48 | 8.4804 | 610.0748 | 288 | 477.3805 | 153.028 | 171.1335 | 65707.23 | 17.8445 | 0 | 0 | 153.028 | 171.1335 | 0 | 65707.23
6 | 4 | 11 | 0 | 287.4258 | 287.4258 | 48 | 9.4549 | 4436.3102 | 288 | 478.9281 | 18.6593 | 268.7664 | 8040.8332 | 28.025 | 0 | 0 | 18.6593 | 268.7664 | 0 | 8040.8332
6 | 4 | 12 | 0 | 54.848 | 54.848 | 48 | 9.8362 | 0 | 0 | 477.3999 | 0 | 54.848 | 0 | 5.7191 | 0 | 0 | 0 | 54.848 | 0 | 0
6 | 4 | 13 | 0 | 26.7894 | 26.7894 | 48 | 9.6159 | 0 | 0 | 478.9387 | 0 | 26.7894 | 0 | 2.7934 | 0 | 0 | 0 | 26.7894 | 0 | 0
6 | 4 | 14 | 0 | 6.5404 | 6.5404 | 48 | 9.5227 | 202.2826 | 202.2826 | 486.269 | 6.5404 | 0 | 2866.4718 | 0 | 0 | 0 | 6.5404 | 0 | 0 | 2866.4718
6 | 4 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 488.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 494.4065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 499.5182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 502.6252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 497.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 483.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 451.4655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 437.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4 | 23 | 5.0486 | 0 | 5.0486 | 11 | 3.3504 | 1.6899 | 1.6899 | 418.0596 | 5.0486 | 0 | 2055.082 | 0 | 0 | 0 | 5.0486 | 0 | 0 | 2055.082
6 | 5 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 412.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 410.6394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 421.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 440.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 454.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 5 | 0.31496 | 0 | 0.31496 | 11 | 3.6164 | 0.11012 | 0.11012 | 480.2572 | 0.31496 | 0 | 147.7965 | 0 | 0 | 0 | 0.31496 | 0 | 0 | 147.7965
6 | 5 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 491.8335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 7 | 0 | 14.379 | 14.379 | 48 | 4.8281 | 6.3068 | 6.3068 | 491.8038 | 14.379 | 0 | 6381.4749 | 0 | 0 | 0 | 14.379 | 0 | 0 | 6381.4749
6 | 5 | 8 | 0 | 68.7651 | 68.7651 | 48 | 5.4976 | 35.0946 | 35.0946 | 500.6579 | 68.7651 | 0 | 31127.0697 | 0 | 0 | 0 | 68.7651 | 0 | 0 | 31127.0697
6 | 5 | 9 | 0 | 41.746 | 41.746 | 48 | 6.4043 | 27.3687 | 27.3687 | 493.4648 | 41.746 | 0 | 18596.3511 | 0 | 0 | 0 | 41.746 | 0 | 0 | 18596.3511
6 | 5 | 10 | 0 | 124.3411 | 124.3411 | 48 | 8.5991 | 262.0196 | 262.0196 | 488.6983 | 124.3411 | 0 | 54796.9145 | 0 | 0 | 0 | 124.3411 | 0 | 0 | 54796.9145
6 | 5 | 11 | 0 | 4.8864 | 4.8864 | 48 | 9.6413 | 0 | 0 | 474.7711 | 0 | 4.8864 | 0 | 0.50952 | 0 | 0 | 0 | 4.8864 | 0 | 0
6 | 5 | 12 | 0 | 3.2445 | 3.2445 | 48 | 9.7176 | 0 | 0 | 474.7909 | 0 | 3.2445 | 0 | 0.33831 | 0 | 0 | 0 | 3.2445 | 0 | 0
6 | 5 | 13 | 0 | 0.055833 | 0.055833 | 48 | 9.7939 | 0 | 0 | 464.6711 | 0 | 0.055833 | 0 | 0.0058219 | 0 | 0 | 0 | 0.055833 | 0 | 0
6 | 5 | 14 | 0 | 1.9146 | 1.9146 | 48 | 9.4634 | 31.5251 | 31.5251 | 460.6572 | 1.9146 | 0 | 790.07 | 0 | 0 | 0 | 1.9146 | 0 | 0 | 790.07
6 | 5 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 469.2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 16 | 0 | 0.0091667 | 0.0091667 | 48 | 11.0904 | 0 | 0 | 472.1741 | 0 | 0.0091667 | 0 | 0.00095584 | 0 | 0 | 0 | 0.0091667 | 0 | 0
6 | 5 | 17 | 0 | 0.090792 | 0.090792 | 48 | 11.1073 | 0 | 0 | 470.847 | 0 | 0.090792 | 0 | 0.0094671 | 0 | 0 | 0 | 0.090792 | 0 | 0
6 | 5 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 477.1597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 462.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 434.9747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 410.2272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 401.7819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 5 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 394.7694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 387.8468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 388.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 391.0985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 399.6282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 419.4468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 440.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 6 | 0 | 0.49537 | 0.49537 | 48 | 5.0061 | 0.22571 | 0.22571 | 452.007 | 0.49537 | 0 | 200.135 | 0 | 0 | 0 | 0.49537 | 0 | 0 | 200.135
6 | 6 | 7 | 0 | 15.9289 | 15.9289 | 48 | 5.2518 | 7.6689 | 7.6689 | 461.3088 | 15.9289 | 0 | 6583.5443 | 0 | 0 | 0 | 15.9289 | 0 | 0 | 6583.5443
6 | 6 | 8 | 0 | 9.055 | 9.055 | 48 | 6.2094 | 5.5942 | 5.5942 | 470.4881 | 9.055 | 0 | 3825.6301 | 0 | 0 | 0 | 9.055 | 0 | 0 | 3825.6301
6 | 6 | 9 | 0 | 5.8328 | 5.8328 | 48 | 7.328 | 5.3853 | 5.3853 | 476.6577 | 5.8328 | 0 | 2500.2827 | 0 | 0 | 0 | 5.8328 | 0 | 0 | 2500.2827
6 | 6 | 10 | 0 | 60.4338 | 60.4338 | 48 | 8.5482 | 121.1363 | 121.1363 | 476.4653 | 60.4338 | 0 | 25893.7939 | 0 | 0 | 0 | 60.4338 | 0 | 0 | 25893.7939
6 | 6 | 11 | 0 | 106.0461 | 106.0461 | 48 | 9.1838 | 544.9041 | 288 | 469.1923 | 56.0489 | 49.9972 | 23607.3525 | 5.2133 | 0 | 0 | 56.0489 | 49.9972 | 0 | 23607.3525
6 | 6 | 12 | 0 | 111.0973 | 111.0973 | 48 | 9.8701 | 0 | 0 | 468.1853 | 0 | 111.0973 | 0 | 11.5844 | 0 | 0 | 0 | 111.0973 | 0 | 0
6 | 6 | 13 | 0 | 99.0504 | 99.0504 | 48 | 9.6668 | 0 | 0 | 459.7557 | 0 | 99.0504 | 0 | 10.3282 | 0 | 0 | 0 | 99.0504 | 0 | 0
6 | 6 | 14 | 0 | 97.93 | 97.93 | 48 | 10.2684 | 0 | 0 | 466.2807 | 0 | 97.93 | 0 | 10.2114 | 0 | 0 | 0 | 97.93 | 0 | 0
6 | 6 | 15 | 0 | 96.7919 | 96.7919 | 48 | 11.226 | 0 | 0 | 473.2517 | 0 | 96.7919 | 0 | 10.0927 | 0 | 0 | 0 | 96.7919 | 0 | 0
6 | 6 | 16 | 0 | 43.2522 | 43.2522 | 48 | 11.853 | 0 | 0 | 475.6503 | 0 | 43.2522 | 0 | 4.51 | 0 | 0 | 0 | 43.2522 | 0 | 0
6 | 6 | 17 | 0 | 1.7358 | 1.7358 | 48 | 11.7514 | 0 | 0 | 464.0705 | 0 | 1.7358 | 0 | 0.18099 | 0 | 0 | 0 | 1.7358 | 0 | 0
6 | 6 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 470.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 455.1934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 435.9805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 409.0946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 395.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 6 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 396.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 394.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 395.921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 403.4897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 416.1144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 434.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 450.3474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 451.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 7 | 0 | 0.005 | 0.005 | 48 | 5.0146 | 0.0022824 | 0.0022824 | 449.1001 | 0.005 | 0 | 2.0055 | 0 | 0 | 0 | 0.005 | 0 | 0 | 2.0055
6 | 7 | 8 | 0 | 14.4745 | 14.4745 | 48 | 6.2094 | 8.9425 | 8.9425 | 453.5444 | 14.4745 | 0 | 5870.0668 | 0 | 0 | 0 | 14.4745 | 0 | 0 | 5870.0668
6 | 7 | 9 | 0 | 7.2355 | 7.2355 | 48 | 7.311 | 6.6306 | 6.6306 | 453.1349 | 7.2355 | 0 | 2931.3346 | 0 | 0 | 0 | 7.2355 | 0 | 0 | 2931.3346
6 | 7 | 10 | 0 | 71.6448 | 71.6448 | 48 | 8.0567 | 97.5823 | 97.5823 | 458.6885 | 71.6448 | 0 | 29423.6792 | 0 | 0 | 0 | 71.6448 | 0 | 0 | 29423.6792
6 | 7 | 11 | 0 | 21.7614 | 21.7614 | 48 | 9.3109 | 162.6914 | 162.6914 | 457.5233 | 21.7614 | 0 | 8911.803 | 0 | 0 | 0 | 21.7614 | 0 | 0 | 8911.803
6 | 7 | 12 | 0 | 9.9327 | 9.9327 | 48 | 9.0058 | 35.4978 | 35.4978 | 455.3096 | 9.9327 | 0 | 4045.686 | 0 | 0 | 0 | 9.9327 | 0 | 0 | 4045.686
6 | 7 | 13 | 0 | 1.5825 | 1.5825 | 48 | 8.4889 | 3.0012 | 3.0012 | 456.9847 | 1.5825 | 0 | 647.212 | 0 | 0 | 0 | 1.5825 | 0 | 0 | 647.212
6 | 7 | 14 | 0 | 0.0015918 | 0.0015918 | 48 | 8.938 | 0.0050976 | 0.0050976 | 461.8405 | 0.0015918 | 0 | 0.65876 | 0 | 0 | 0 | 0.0015918 | 0 | 0 | 0.65876
6 | 7 | 15 | 0 | 0 | 0 | 0 | 9.6075 | 0 | 0 | 468.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 464.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 17 | 0 | 0.0075 | 0.0075 | 48 | 10.3786 | 0 | 0 | 470.4468 | 0 | 0.0075 | 0 | 0.00078205 | 0 | 0 | 0 | 0.0075 | 0 | 0
6 | 7 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 481.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 464.4694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 442.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 413.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 400.8145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 399.6686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 395.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 396.5723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 404.2886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 416.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 433.8535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 457.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 463.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 7 | 0.595 | 3.1333 | 3.7283 | 42.0952 | 4.6502 | 1.5764 | 1.5764 | 478.5079 | 3.7283 | 0 | 1627.0921 | 0 | 0 | 0 | 3.7283 | 0 | 0 | 1627.0921
6 | 8 | 8 | 0 | 82.1507 | 82.1507 | 48 | 5.1417 | 38.5718 | 38.5718 | 477.9213 | 82.1507 | 0 | 35318.3436 | 0 | 0 | 0 | 82.1507 | 0 | 0 | 35318.3436
6 | 8 | 9 | 0 | 308.844 | 308.844 | 48 | 6.6161 | 216.9012 | 216.9012 | 484.0656 | 308.844 | 0 | 134676.258 | 0 | 0 | 0 | 308.844 | 0 | 0 | 134676.258
6 | 8 | 10 | 0 | 422.8636 | 422.8636 | 48 | 6.9721 | 337.3469 | 288 | 488.3275 | 361.0073 | 61.8563 | 158961.4444 | 6.4499 | 0 | 0 | 361.0073 | 61.8563 | 0 | 158961.4444
6 | 8 | 11 | 0 | 210.2519 | 210.2519 | 48 | 8.5652 | 428.4062 | 288 | 487.2114 | 141.3438 | 68.9081 | 62079.7917 | 7.1852 | 0 | 0 | 141.3438 | 68.9081 | 0 | 62079.7917
6 | 8 | 12 | 0 | 58.0096 | 58.0096 | 48 | 7.8957 | 71.5037 | 71.5037 | 484.2045 | 58.0096 | 0 | 25304.0717 | 0 | 0 | 0 | 58.0096 | 0 | 0 | 25304.0717
6 | 8 | 13 | 0 | 53.3675 | 53.3675 | 48 | 7.4381 | 51.795 | 51.795 | 488.691 | 53.3675 | 0 | 23518.5948 | 0 | 0 | 0 | 53.3675 | 0 | 0 | 23518.5948
6 | 8 | 14 | 0 | 69.8457 | 69.8457 | 48 | 7.2771 | 63.0693 | 63.0693 | 494.7629 | 69.8457 | 0 | 31204.4758 | 0 | 0 | 0 | 69.8457 | 0 | 0 | 31204.4758
6 | 8 | 15 | 36.2323 | 241.5143 | 277.7466 | 43.1733 | 7.3449 | 258.3717 | 258.3717 | 496.9069 | 277.7466 | 0 | 126022.9875 | 0 | 0 | 0 | 277.7466 | 0 | 0 | 126022.9875
6 | 8 | 16 | 0 | 18.7379 | 18.7379 | 48 | 6.9975 | 15.0951 | 15.0951 | 500.6465 | 18.7379 | 0 | 8481.6411 | 0 | 0 | 0 | 18.7379 | 0 | 0 | 8481.6411
6 | 8 | 17 | 0 | 10.574 | 10.574 | 48 | 7.167 | 9.1141 | 9.1141 | 498.1497 | 10.574 | 0 | 4759.885 | 0 | 0 | 0 | 10.574 | 0 | 0 | 4759.885
6 | 8 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 504.6681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 19 | 0 | 0.0020417 | 0.0020417 | 48 | 7.3958 | 0.0019432 | 0.0019432 | 480.7011 | 0.0020417 | 0 | 0.88343 | 0 | 0 | 0 | 0.0020417 | 0 | 0 | 0.88343
6 | 8 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 454.2938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 424.4104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 403.7545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 399.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 396.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 391.7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 393.0768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 401.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 414.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 442.105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 454.7597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 7 | 0 | 4.622 | 4.622 | 48 | 6.1924 | 2.8413 | 2.8413 | 466.4074 | 4.622 | 0 | 1933.892 | 0 | 0 | 0 | 4.622 | 0 | 0 | 1933.892
6 | 9 | 8 | 0 | 0.16015 | 0.16015 | 48 | 6.8788 | 0.12337 | 0.12337 | 485.0599 | 0.16015 | 0 | 69.9957 | 0 | 0 | 0 | 0.16015 | 0 | 0 | 69.9957
6 | 9 | 9 | 0 | 4.6526 | 4.6526 | 48 | 7.3195 | 4.2796 | 4.2796 | 485.6341 | 4.6526 | 0 | 2036.1292 | 0 | 0 | 0 | 4.6526 | 0 | 0 | 2036.1292
6 | 9 | 10 | 0 | 27.6201 | 27.6201 | 48 | 7.4805 | 27.3446 | 27.3446 | 486.1835 | 27.6201 | 0 | 12102.6726 | 0 | 0 | 0 | 27.6201 | 0 | 0 | 12102.6726
6 | 9 | 11 | 0 | 35.8536 | 35.8536 | 48 | 7.2263 | 31.6788 | 31.6788 | 480.3466 | 35.8536 | 0 | 15501.1997 | 0 | 0 | 0 | 35.8536 | 0 | 0 | 15501.1997
6 | 9 | 12 | 0 | 18.046 | 18.046 | 48 | 7.8703 | 21.915 | 21.915 | 476.5149 | 18.046 | 0 | 7732.9826 | 0 | 0 | 0 | 18.046 | 0 | 0 | 7732.9826
6 | 9 | 13 | 0 | 2.0219 | 2.0219 | 48 | 8.1754 | 2.9848 | 2.9848 | 473.7058 | 2.0219 | 0 | 860.7386 | 0 | 0 | 0 | 2.0219 | 0 | 0 | 860.7386
6 | 9 | 14 | 0 | 21.8841 | 21.8841 | 48 | 8.2431 | 33.9318 | 33.9318 | 473.4634 | 21.8841 | 0 | 9310.8991 | 0 | 0 | 0 | 21.8841 | 0 | 0 | 9310.8991
6 | 9 | 15 | 0 | 1.1025 | 1.1025 | 48 | 7.4212 | 1.0617 | 1.0617 | 475.044 | 1.1025 | 0 | 470.8337 | 0 | 0 | 0 | 1.1025 | 0 | 0 | 470.8337
6 | 9 | 16 | 0 | 3.6592 | 3.6592 | 48 | 7.3195 | 3.3658 | 3.3658 | 476.15 | 3.6592 | 0 | 1566.6688 | 0 | 0 | 0 | 3.6592 | 0 | 0 | 1566.6688
6 | 9 | 17 | 0 | 5.0108 | 5.0108 | 48 | 7.2686 | 4.5081 | 4.5081 | 480.5629 | 5.0108 | 0 | 2167.4725 | 0 | 0 | 0 | 5.0108 | 0 | 0 | 2167.4725
6 | 9 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 488.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 482.8591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 455.6769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 435.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 408.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 9 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 390.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 383.8719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 379.9555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 380.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 387.7175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 390.2497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 402.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 10 | 6 | 0 | 142.157 | 142.157 | 48 | 4.4638 | 57.9198 | 57.9198 | 421.8097 | 142.157 | 0 | 53139.6626 | 0 | 0 | 0 | 142.157 | 0 | 0 | 53139.6626
6 | 10 | 7 | 5.0259 | 590.4447 | 595.4706 | 47.6877 | 6.006 | 347.0112 | 288 | 433.8718 | 494.2075 | 101.2631 | 190855.0598 | 10.559 | 0 | 0 | 494.2075 | 101.2631 | 0 | 190855.0598
6 | 10 | 8 | 6.4917 | 540.7095 | 547.2012 | 47.5611 | 6.6246 | 385.3976 | 288 | 450.5919 | 408.9126 | 138.2885 | 164804.4109 | 14.4197 | 0 | 0 | 408.9126 | 138.2885 | 0 | 164804.4109
6 | 10 | 9 | 2.6492 | 431.7373 | 434.3865 | 47.7743 | 7.1924 | 378.3806 | 288 | 476.8947 | 330.6283 | 103.7582 | 141879.3359 | 10.8191 | 0 | 0 | 330.6283 | 103.7582 | 0 | 141879.3359
6 | 10 | 10 | 2.145 | 501.7526 | 503.8976 | 47.8425 | 7.0398 | 412.6786 | 288 | 484.0148 | 351.6599 | 152.2377 | 153384.322 | 15.8742 | 0 | 0 | 351.6599 | 152.2377 | 0 | 153384.322
6 | 10 | 11 | 3.4725 | 461.2379 | 464.7104 | 47.7235 | 7.2093 | 407.6762 | 288 | 489.9267 | 328.2914 | 136.419 | 145171.5089 | 14.2248 | 0 | 0 | 328.2914 | 136.419 | 0 | 145171.5089
6 | 10 | 12 | 0 | 415.2641 | 415.2641 | 48 | 7.9296 | 522.3094 | 288 | 484.5674 | 228.9755 | 186.2886 | 99963.2424 | 19.4248 | 0 | 0 | 228.9755 | 186.2886 | 0 | 99963.2424
6 | 10 | 13 | 0.5725 | 351.5246 | 352.0971 | 47.9398 | 8.2601 | 552.8904 | 288 | 483.0885 | 183.407 | 168.6901 | 79809.3138 | 17.5898 | 0 | 0 | 183.407 | 168.6901 | 0 | 79809.3138
6 | 10 | 14 | 0 | 217.7987 | 217.7987 | 48 | 8.5313 | 429.579 | 288 | 484.3897 | 146.0175 | 71.7813 | 63720.5102 | 7.4848 | 0 | 0 | 146.0175 | 71.7813 | 0 | 63720.5102
6 | 10 | 15 | 0 | 30.996 | 30.996 | 48 | 8.4041 | 54.5839 | 54.5839 | 491.3627 | 30.996 | 0 | 13742.4934 | 0 | 0 | 0 | 30.996 | 0 | 0 | 13742.4934
6 | 10 | 16 | 0 | 9.1059 | 9.1059 | 48 | 9.1753 | 45.834 | 45.834 | 490.3201 | 9.1059 | 0 | 4027.7179 | 0 | 0 | 0 | 9.1059 | 0 | 0 | 4027.7179
6 | 10 | 17 | 0 | 34.7 | 34.7 | 48 | 8.6753 | 79.2173 | 79.2173 | 489.7384 | 34.7 | 0 | 15328.3221 | 0 | 0 | 0 | 34.7 | 0 | 0 | 15328.3221
6 | 10 | 18 | 0 | 2.215 | 2.215 | 48 | 9.0397 | 8.4034 | 8.4034 | 494.0904 | 2.215 | 0 | 988.0902 | 0 | 0 | 0 | 2.215 | 0 | 0 | 988.0902
6 | 10 | 19 | 0.59654 | 0 | 0.59654 | 11 | 7.6754 | 0.6507 | 0.6507 | 489.5367 | 0.59654 | 0 | 285.4663 | 0 | 0 | 0 | 0.59654 | 0 | 0 | 285.4663
6 | 10 | 20 | 143.9402 | 0 | 143.9402 | 11 | 10.8362 | 0 | 0 | 460.3094 | 0 | 143.9402 | 0 | 15.009 | 0 | 0 | 0 | 143.9402 | 0 | 0
6 | 10 | 21 | 109.6004 | 0 | 109.6004 | 11 | 8.7685 | 278.5918 | 278.5918 | 438.45 | 109.6004 | 0 | 46848.6674 | 0 | 0 | 0 | 109.6004 | 0 | 0 | 46848.6674
6 | 10 | 22 | 5.4306 | 0 | 5.4306 | 11 | 5.1247 | 2.5401 | 2.5401 | 421.5434 | 5.4306 | 0 | 2229.5038 | 0 | 0 | 0 | 5.4306 | 0 | 0 | 2229.5038
6 | 10 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 410.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 407.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 408.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 403.9717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 412.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 402.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 5 | 0 | 0.22037 | 0.22037 | 48 | 3.4638 | 0.075134 | 0.075134 | 411.6817 | 0.22037 | 0 | 80.1464 | 0 | 0 | 0 | 0.22037 | 0 | 0 | 80.1464
6 | 11 | 6 | 0.71213 | 200.5165 | 201.2286 | 47.8691 | 4.1926 | 77.8688 | 77.8688 | 429.0349 | 201.2286 | 0 | 76701.4803 | 0 | 0 | 0 | 201.2286 | 0 | 0 | 76701.4803
6 | 11 | 7 | 5.5575 | 611.9775 | 617.535 | 47.667 | 4.8705 | 273.2892 | 273.2892 | 453.5467 | 617.535 | 0 | 250644.9268 | 0 | 0 | 0 | 617.535 | 0 | 0 | 250644.9268
6 | 11 | 8 | 3.5075 | 499.9246 | 503.4321 | 47.7422 | 4.8451 | 221.5995 | 221.5995 | 478.7305 | 503.4321 | 0 | 216973.3278 | 0 | 0 | 0 | 503.4321 | 0 | 0 | 216973.3278
6 | 11 | 9 | 0 | 185.5349 | 185.5349 | 48 | 6.3789 | 120.674 | 120.674 | 504.8143 | 185.5349 | 0 | 84754.9963 | 0 | 0 | 0 | 185.5349 | 0 | 0 | 84754.9963
6 | 11 | 10 | 1.5084 | 207.9683 | 209.4767 | 47.7336 | 8.4804 | 394.237 | 288 | 517.4314 | 153.028 | 56.4487 | 71876.9207 | 5.8861 | 0 | 0 | 153.028 | 56.4487 | 0 | 71876.9207
6 | 11 | 11 | 0 | 178.9501 | 178.9501 | 48 | 9.4549 | 2762.0292 | 288 | 511.7698 | 18.6593 | 160.2908 | 8653.6379 | 16.7139 | 0 | 0 | 18.6593 | 160.2908 | 0 | 8653.6379
6 | 11 | 12 | 1.1558 | 237.2717 | 238.4276 | 47.8206 | 9.8362 | 0 | 0 | 510.0637 | 0 | 238.4276 | 0 | 24.8615 | 0 | 0 | 0 | 238.4276 | 0 | 0
6 | 11 | 13 | 0.735 | 104.7918 | 105.5268 | 47.7423 | 9.6159 | 0 | 0 | 511.9846 | 0 | 105.5268 | 0 | 11.0036 | 0 | 0 | 0 | 105.5268 | 0 | 0
6 | 11 | 14 | 0 | 164.7345 | 164.7345 | 48 | 9.5227 | 5094.9055 | 288 | 512.7724 | 9.312 | 155.4225 | 4327.9397 | 16.2063 | 0 | 0 | 9.312 | 155.4225 | 0 | 4327.9397
6 | 11 | 15 | 0.72333 | 272.5172 | 273.2406 | 47.9021 | 10.7175 | 0 | 0 | 521.456 | 0 | 273.2406 | 0 | 28.4915 | 0 | 0 | 0 | 273.2406 | 0 | 0
6 | 11 | 16 | 0 | 1.7444 | 1.7444 | 48 | 12.0564 | 0 | 0 | 527.7915 | 0 | 1.7444 | 0 | 0.18189 | 0 | 0 | 0 | 1.7444 | 0 | 0
6 | 11 | 17 | 0 | 8.3287 | 8.3287 | 48 | 11.8107 | 0 | 0 | 533.9819 | 0 | 8.3287 | 0 | 0.86845 | 0 | 0 | 0 | 8.3287 | 0 | 0
6 | 11 | 18 | 0 | 0.61917 | 0.61917 | 48 | 12.3445 | 0 | 0 | 538.3302 | 0 | 0.61917 | 0 | 0.064562 | 0 | 0 | 0 | 0.61917 | 0 | 0
6 | 11 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 534.2085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 504.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 492.6208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 467.3576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 11 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 455.0416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 450.7773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 449.9539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 450.9318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 454.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 478.8755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 514.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 6 | 0 | 3.8884 | 3.8884 | 48 | 4.4722 | 1.5869 | 1.5869 | 534.7996 | 3.8884 | 0 | 1892.8595 | 0 | 0 | 0 | 3.8884 | 0 | 0 | 1892.8595
6 | 12 | 7 | 1.4875 | 175.0303 | 176.5179 | 47.6882 | 4.8281 | 77.4227 | 77.4227 | 546.1197 | 176.5179 | 0 | 87982.0726 | 0 | 0 | 0 | 176.5179 | 0 | 0 | 87982.0726
6 | 12 | 8 | 5.985 | 548.3168 | 554.3018 | 47.6005 | 5.4976 | 282.8908 | 282.8908 | 552.7009 | 554.3018 | 0 | 279978.0587 | 0 | 0 | 0 | 554.3018 | 0 | 0 | 279978.0587
6 | 12 | 9 | 0 | 268.7252 | 268.7252 | 48 | 6.4043 | 176.1765 | 176.1765 | 551.8758 | 268.7252 | 0 | 135404.1118 | 0 | 0 | 0 | 268.7252 | 0 | 0 | 135404.1118
6 | 12 | 10 | 0 | 298.9052 | 298.9052 | 48 | 8.5991 | 629.8723 | 288 | 544.9325 | 136.6701 | 162.2351 | 67915.7979 | 16.9167 | 0 | 0 | 136.6701 | 162.2351 | 0 | 67915.7979
6 | 12 | 11 | 2.1858 | 624.8612 | 627.0471 | 47.871 | 9.6413 | 0 | 0 | 546.0107 | 0 | 627.0471 | 0 | 65.3838 | 0 | 0 | 0 | 627.0471 | 0 | 0
6 | 12 | 12 | 0.38417 | 810.882 | 811.2661 | 47.9825 | 9.7176 | 0 | 0 | 542.7085 | 0 | 811.2661 | 0 | 84.5928 | 0 | 0 | 0 | 811.2661 | 0 | 0
6 | 12 | 13 | 0.52417 | 625.58 | 626.1042 | 47.969 | 9.7939 | 0 | 0 | 542.9415 | 0 | 626.1042 | 0 | 65.2855 | 0 | 0 | 0 | 626.1042 | 0 | 0
6 | 12 | 14 | 0.325 | 452.7325 | 453.0575 | 47.9735 | 9.4634 | 7459.9054 | 288 | 542.9726 | 17.4909 | 435.5666 | 8657.9885 | 45.4177 | 0 | 0 | 17.4909 | 435.5666 | 0 | 8657.9885
6 | 12 | 15 | 0 | 340.1205 | 340.1205 | 48 | 10.5311 | 0 | 0 | 545.9824 | 0 | 340.1205 | 0 | 35.4653 | 0 | 0 | 0 | 340.1205 | 0 | 0
6 | 12 | 16 | 0 | 196.2206 | 196.2206 | 48 | 11.0904 | 0 | 0 | 550.4838 | 0 | 196.2206 | 0 | 20.4604 | 0 | 0 | 0 | 196.2206 | 0 | 0
6 | 12 | 17 | 0 | 125.7585 | 125.7585 | 48 | 11.1073 | 0 | 0 | 553.3403 | 0 | 125.7585 | 0 | 13.1132 | 0 | 0 | 0 | 125.7585 | 0 | 0
6 | 12 | 18 | 0 | 1.2742 | 1.2742 | 48 | 11.4802 | 0 | 0 | 560.2651 | 0 | 1.2742 | 0 | 0.13286 | 0 | 0 | 0 | 1.2742 | 0 | 0
6 | 12 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 564.1535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 558.5645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 553.9472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 524.0783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 12 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 508.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 488.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 480.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 490.1865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 507.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 534.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 559.9583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 567.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 7 | 0 | 165.9884 | 165.9884 | 48 | 5.2518 | 79.9146 | 79.9146 | 564.8416 | 165.9884 | 0 | 85789.7227 | 0 | 0 | 0 | 165.9884 | 0 | 0 | 85789.7227
6 | 13 | 8 | 0 | 368.8834 | 368.8834 | 48 | 6.2094 | 227.8985 | 227.8985 | 562.3383 | 368.8834 | 0 | 189730.8417 | 0 | 0 | 0 | 368.8834 | 0 | 0 | 189730.8417
6 | 13 | 9 | 0.14833 | 477.2589 | 477.4073 | 47.9885 | 7.328 | 440.7775 | 288 | 561.2119 | 311.9335 | 165.4737 | 160091.5906 | 17.2544 | 0 | 0 | 311.9335 | 165.4737 | 0 | 160091.5906
6 | 13 | 10 | 0.21917 | 419.3945 | 419.6136 | 47.9807 | 8.5482 | 841.0928 | 288 | 551.1174 | 143.6806 | 275.933 | 72290.9885 | 28.7723 | 0 | 0 | 143.6806 | 275.933 | 0 | 72290.9885
6 | 13 | 11 | 0.3925 | 391.8255 | 392.218 | 47.963 | 9.1838 | 2015.3621 | 288 | 549.1071 | 56.0489 | 336.1691 | 28088.5664 | 35.0532 | 0 | 0 | 56.0489 | 336.1691 | 0 | 28088.5664
6 | 13 | 12 | 0.3 | 132.3302 | 132.6302 | 47.9163 | 9.8701 | 0 | 0 | 549.8337 | 0 | 132.6302 | 0 | 13.8297 | 0 | 0 | 0 | 132.6302 | 0 | 0
6 | 13 | 13 | 0 | 13.5996 | 13.5996 | 48 | 9.6668 | 0 | 0 | 550.374 | 0 | 13.5996 | 0 | 1.4181 | 0 | 0 | 0 | 13.5996 | 0 | 0
6 | 13 | 14 | 0 | 34.383 | 34.383 | 48 | 10.2684 | 0 | 0 | 552.0016 | 0 | 34.383 | 0 | 3.5852 | 0 | 0 | 0 | 34.383 | 0 | 0
6 | 13 | 15 | 0 | 2.491 | 2.491 | 48 | 11.226 | 0 | 0 | 555.298 | 0 | 2.491 | 0 | 0.25974 | 0 | 0 | 0 | 2.491 | 0 | 0
6 | 13 | 16 | 0 | 12.17 | 12.17 | 48 | 11.853 | 0 | 0 | 562.1664 | 0 | 12.17 | 0 | 1.269 | 0 | 0 | 0 | 12.17 | 0 | 0
6 | 13 | 17 | 0 | 8.9353 | 8.9353 | 48 | 11.7514 | 0 | 0 | 561.2122 | 0 | 8.9353 | 0 | 0.93171 | 0 | 0 | 0 | 8.9353 | 0 | 0
6 | 13 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 553.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 555.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 554.4497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 523.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 501.7257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 13 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 492.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 482.7944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 472.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 478.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 506.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 527.0946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 540.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 550.5971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 7 | 0 | 23.83 | 23.83 | 48 | 5.0146 | 10.8779 | 10.8779 | 560.2148 | 23.83 | 0 | 12206.0567 | 0 | 0 | 0 | 23.83 | 0 | 0 | 12206.0567
6 | 14 | 8 | 0 | 55.6135 | 55.6135 | 48 | 6.2094 | 34.3584 | 34.3584 | 558.1213 | 55.6135 | 0 | 28369.6125 | 0 | 0 | 0 | 55.6135 | 0 | 0 | 28369.6125
6 | 14 | 9 | 0 | 23.1431 | 23.1431 | 48 | 7.311 | 21.2086 | 21.2086 | 551.0408 | 23.1431 | 0 | 11641.9445 | 0 | 0 | 0 | 23.1431 | 0 | 0 | 11641.9445
6 | 14 | 10 | 0 | 7.3791 | 7.3791 | 48 | 8.0567 | 10.0506 | 10.0506 | 543.6093 | 7.3791 | 0 | 3657.1533 | 0 | 0 | 0 | 7.3791 | 0 | 0 | 3657.1533
6 | 14 | 11 | 0 | 16.1291 | 16.1291 | 48 | 9.3109 | 120.5838 | 120.5838 | 540.8765 | 16.1291 | 0 | 7949.6722 | 0 | 0 | 0 | 16.1291 | 0 | 0 | 7949.6722
6 | 14 | 12 | 0 | 8.5839 | 8.5839 | 48 | 9.0058 | 30.6773 | 30.6773 | 539.3552 | 8.5839 | 0 | 4217.7309 | 0 | 0 | 0 | 8.5839 | 0 | 0 | 4217.7309
6 | 14 | 13 | 0 | 8.6366 | 8.6366 | 48 | 8.4889 | 16.3791 | 16.3791 | 535.4459 | 8.6366 | 0 | 4209.8518 | 0 | 0 | 0 | 8.6366 | 0 | 0 | 4209.8518
6 | 14 | 14 | 0 | 3.1146 | 3.1146 | 48 | 8.938 | 9.9742 | 9.9742 | 535.0347 | 3.1146 | 0 | 1516.9239 | 0 | 0 | 0 | 3.1146 | 0 | 0 | 1516.9239
6 | 14 | 15 | 0 | 0.06391 | 0.06391 | 48 | 9.6075 | 0 | 0 | 542.231 | 0 | 0.06391 | 0 | 0.006664 | 0 | 0 | 0 | 0.06391 | 0 | 0
6 | 14 | 16 | 0 | 0.12852 | 0.12852 | 48 | 10.9718 | 0 | 0 | 552.9325 | 0 | 0.12852 | 0 | 0.013401 | 0 | 0 | 0 | 0.12852 | 0 | 0
6 | 14 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 561.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 557.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 535.4983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 530.7829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 503.7075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 469.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 465.9933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 457.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 449.6103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 452.8868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 475.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 504.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 523.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 6 | 0 | 0.13917 | 0.13917 | 48 | 4.396 | 0.055961 | 0.055961 | 532.1002 | 0.13917 | 0 | 67.3706 | 0 | 0 | 0 | 0.13917 | 0 | 0 | 67.3706
6 | 15 | 7 | 0 | 23.9633 | 23.9633 | 48 | 4.6502 | 10.132 | 10.132 | 544.0537 | 23.9633 | 0 | 11887.0993 | 0 | 0 | 0 | 23.9633 | 0 | 0 | 11887.0993
6 | 15 | 8 | 0 | 23.8304 | 23.8304 | 48 | 5.1417 | 11.189 | 11.189 | 548.781 | 23.8304 | 0 | 11933.836 | 0 | 0 | 0 | 23.8304 | 0 | 0 | 11933.836
6 | 15 | 9 | 0 | 21.5876 | 21.5876 | 48 | 6.6161 | 15.161 | 15.161 | 550.3009 | 21.5876 | 0 | 10843.4711 | 0 | 0 | 0 | 21.5876 | 0 | 0 | 10843.4711
6 | 15 | 10 | 0 | 7.2376 | 7.2376 | 48 | 6.9721 | 5.7739 | 5.7739 | 547.7414 | 7.2376 | 0 | 3616.9358 | 0 | 0 | 0 | 7.2376 | 0 | 0 | 3616.9358
6 | 15 | 11 | 0 | 8.8844 | 8.8844 | 48 | 8.5652 | 18.1028 | 18.1028 | 536.0327 | 8.8844 | 0 | 4335.8888 | 0 | 0 | 0 | 8.8844 | 0 | 0 | 4335.8888
6 | 15 | 12 | 0 | 3.9713 | 3.9713 | 48 | 7.8957 | 4.8951 | 4.8951 | 532.7187 | 3.9713 | 0 | 1924.947 | 0 | 0 | 0 | 3.9713 | 0 | 0 | 1924.947
6 | 15 | 13 | 0 | 3.5807 | 3.5807 | 48 | 7.4381 | 3.4752 | 3.4752 | 531.9674 | 3.5807 | 0 | 1732.9511 | 0 | 0 | 0 | 3.5807 | 0 | 0 | 1732.9511
6 | 15 | 14 | 0 | 0.13897 | 0.13897 | 48 | 7.2771 | 0.12549 | 0.12549 | 533.1634 | 0.13897 | 0 | 67.4253 | 0 | 0 | 0 | 0.13897 | 0 | 0 | 67.4253
6 | 15 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 540.0472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 546.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 547.5753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 547.4519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 539.4445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 525.7524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 489.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 470.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 15 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 448.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 446.4663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 444.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 453.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 468.0605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 491.7409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 505.1138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 519.3374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 535.2207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 8 | 0 | 0.17769 | 0.17769 | 48 | 6.8788 | 0.13689 | 0.13689 | 538.9476 | 0.17769 | 0 | 87.2385 | 0 | 0 | 0 | 0.17769 | 0 | 0 | 87.2385
6 | 16 | 9 | 0 | 0.88441 | 0.88441 | 48 | 7.3195 | 0.8135 | 0.8135 | 533.5543 | 0.88441 | 0 | 429.4273 | 0 | 0 | 0 | 0.88441 | 0 | 0 | 429.4273
6 | 16 | 10 | 0 | 3.7433 | 3.7433 | 48 | 7.4805 | 3.706 | 3.706 | 529.1345 | 3.7433 | 0 | 1801.0464 | 0 | 0 | 0 | 3.7433 | 0 | 0 | 1801.0464
6 | 16 | 11 | 0 | 76.1967 | 76.1967 | 48 | 7.2263 | 67.3243 | 67.3243 | 527.0601 | 76.1967 | 0 | 36502.8217 | 0 | 0 | 0 | 76.1967 | 0 | 0 | 36502.8217
6 | 16 | 12 | 0 | 3.7863 | 3.7863 | 48 | 7.8703 | 4.5981 | 4.5981 | 527.0194 | 3.7863 | 0 | 1813.7018 | 0 | 0 | 0 | 3.7863 | 0 | 0 | 1813.7018
6 | 16 | 13 | 0 | 3.3218 | 3.3218 | 48 | 8.1754 | 4.9038 | 4.9038 | 525.5411 | 3.3218 | 0 | 1586.3084 | 0 | 0 | 0 | 3.3218 | 0 | 0 | 1586.3084
6 | 16 | 14 | 0 | 0.28428 | 0.28428 | 48 | 8.2431 | 0.44078 | 0.44078 | 527.8396 | 0.28428 | 0 | 136.4066 | 0 | 0 | 0 | 0.28428 | 0 | 0 | 136.4066
6 | 16 | 15 | 0 | 0.005 | 0.005 | 48 | 7.4212 | 0.0048148 | 0.0048148 | 527.9963 | 0.005 | 0 | 2.4 | 0 | 0 | 0 | 0.005 | 0 | 0 | 2.4
6 | 16 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 539.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 17 | 3.2556 | 0 | 3.2556 | 11 | 7.2686 | 2.929 | 2.929 | 543.515 | 3.2556 | 0 | 1733.6515 | 0 | 0 | 0 | 3.2556 | 0 | 0 | 1733.6515
6 | 16 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 544.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 531.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 516.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 21 | 1.8444 | 0 | 1.8444 | 11 | 5.6332 | 0.97356 | 0.97356 | 482.4405 | 1.8444 | 0 | 869.5364 | 0 | 0 | 0 | 1.8444 | 0 | 0 | 869.5364
6 | 16 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 464.1756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 16 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 448.0846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 433.6364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 425.3677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 423.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 424.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 439.255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 459.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 6 | 0 | 1.4534 | 1.4534 | 48 | 4.4638 | 0.59216 | 0.59216 | 483.9423 | 1.4534 | 0 | 633.5876 | 0 | 0 | 0 | 1.4534 | 0 | 0 | 633.5876
6 | 17 | 7 | 0 | 2.1358 | 2.1358 | 48 | 6.006 | 1.2447 | 1.2447 | 503.4062 | 2.1358 | 0 | 972.6717 | 0 | 0 | 0 | 2.1358 | 0 | 0 | 972.6717
6 | 17 | 8 | 0 | 75.1419 | 75.1419 | 48 | 6.6246 | 52.923 | 52.923 | 522.2455 | 75.1419 | 0 | 35635.7248 | 0 | 0 | 0 | 75.1419 | 0 | 0 | 35635.7248
6 | 17 | 9 | 0 | 5.3379 | 5.3379 | 48 | 7.1924 | 4.6497 | 4.6497 | 526.7327 | 5.3379 | 0 | 2555.4297 | 0 | 0 | 0 | 5.3379 | 0 | 0 | 2555.4297
6 | 17 | 10 | 0 | 1.5658 | 1.5658 | 48 | 7.0398 | 1.2824 | 1.2824 | 524.9637 | 1.5658 | 0 | 746.8458 | 0 | 0 | 0 | 1.5658 | 0 | 0 | 746.8458
6 | 17 | 11 | 0 | 1.4508 | 1.4508 | 48 | 7.2093 | 1.2728 | 1.2728 | 520.6586 | 1.4508 | 0 | 685.749 | 0 | 0 | 0 | 1.4508 | 0 | 0 | 685.749
6 | 17 | 12 | 0 | 0.3425 | 0.3425 | 48 | 7.9296 | 0.43079 | 0.43079 | 512.2015 | 0.3425 | 0 | 158.9891 | 0 | 0 | 0 | 0.3425 | 0 | 0 | 158.9891
6 | 17 | 13 | 0 | 0.099167 | 0.099167 | 48 | 8.2601 | 0.15572 | 0.15572 | 515.2901 | 0.099167 | 0 | 46.3396 | 0 | 0 | 0 | 0.099167 | 0 | 0 | 46.3396
6 | 17 | 14 | 0 | 0.0025 | 0.0025 | 48 | 8.5313 | 0.0049309 | 0.0049309 | 517.0602 | 0.0025 | 0 | 1.1727 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.1727
6 | 17 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 518.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 16 | 0 | 0.0025 | 0.0025 | 48 | 9.1753 | 0.012584 | 0.012584 | 522.0162 | 0.0025 | 0 | 1.185 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.185
6 | 17 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 524.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 529.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 523.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 508.5322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 483.3811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 471.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 17 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 453.2619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 441.1505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 438.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 427.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 420.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 425.2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 445.4889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 463.3061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 7 | 0 | 3.1433 | 3.1433 | 48 | 4.8705 | 1.3911 | 1.3911 | 488.797 | 3.1433 | 0 | 1385.5719 | 0 | 0 | 0 | 3.1433 | 0 | 0 | 1385.5719
6 | 18 | 8 | 0 | 8.9242 | 8.9242 | 48 | 4.8451 | 3.9282 | 3.9282 | 500.1288 | 8.9242 | 0 | 4034.8916 | 0 | 0 | 0 | 8.9242 | 0 | 0 | 4034.8916
6 | 18 | 9 | 0 | 1.8276 | 1.8276 | 48 | 6.3789 | 1.1887 | 1.1887 | 512.1186 | 1.8276 | 0 | 848.2155 | 0 | 0 | 0 | 1.8276 | 0 | 0 | 848.2155
6 | 18 | 10 | 0 | 5.6862 | 5.6862 | 48 | 8.4804 | 10.7014 | 10.7014 | 505.6061 | 5.6862 | 0 | 2602.028 | 0 | 0 | 0 | 5.6862 | 0 | 0 | 2602.028
6 | 18 | 11 | 0 | 20.7545 | 20.7545 | 48 | 9.4549 | 320.3384 | 288 | 503.6569 | 18.6593 | 2.0952 | 8502.2563 | 0.21847 | 0 | 0 | 18.6593 | 2.0952 | 0 | 8502.2563
6 | 18 | 12 | 0 | 13.8254 | 13.8254 | 48 | 9.8362 | 0 | 0 | 500.8823 | 0 | 13.8254 | 0 | 1.4416 | 0 | 0 | 0 | 13.8254 | 0 | 0
6 | 18 | 13 | 0 | 2.3267 | 2.3267 | 48 | 9.6159 | 0 | 0 | 498.8038 | 0 | 2.3267 | 0 | 0.24261 | 0 | 0 | 0 | 2.3267 | 0 | 0
6 | 18 | 14 | 0 | 2.5275 | 2.5275 | 48 | 9.5227 | 78.1705 | 78.1705 | 500.4453 | 2.5275 | 0 | 1143.5555 | 0 | 0 | 0 | 2.5275 | 0 | 0 | 1143.5555
6 | 18 | 15 | 0 | 2.1408 | 2.1408 | 48 | 10.7175 | 0 | 0 | 503.8642 | 0 | 2.1408 | 0 | 0.22323 | 0 | 0 | 0 | 2.1408 | 0 | 0
6 | 18 | 16 | 0 | 22.3092 | 22.3092 | 48 | 12.0564 | 0 | 0 | 516.3634 | 0 | 22.3092 | 0 | 2.3262 | 0 | 0 | 0 | 22.3092 | 0 | 0
6 | 18 | 17 | 0 | 1.8475 | 1.8475 | 48 | 11.8107 | 0 | 0 | 524.218 | 0 | 1.8475 | 0 | 0.19264 | 0 | 0 | 0 | 1.8475 | 0 | 0
6 | 18 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 525.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 528.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 512.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 493.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 474.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 18 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 464.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 449.7458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 449.2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 460.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 482.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 498.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 515.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 520.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 515.2567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 8 | 0 | 0.0066667 | 0.0066667 | 48 | 5.4976 | 0.0034024 | 0.0034024 | 505.6268 | 0.0066667 | 0 | 3.0509 | 0 | 0 | 0 | 0.0066667 | 0 | 0 | 3.0509
6 | 19 | 9 | 0 | 0.46 | 0.46 | 48 | 6.4043 | 0.30158 | 0.30158 | 494.4036 | 0.46 | 0 | 205.3458 | 0 | 0 | 0 | 0.46 | 0 | 0 | 205.3458
6 | 19 | 10 | 0 | 1.91 | 1.91 | 48 | 8.5991 | 4.0249 | 4.0249 | 490.9636 | 1.91 | 0 | 846.0606 | 0 | 0 | 0 | 1.91 | 0 | 0 | 846.0606
6 | 19 | 11 | 0 | 3.6275 | 3.6275 | 48 | 9.6413 | 0 | 0 | 482.6908 | 0 | 3.6275 | 0 | 0.37825 | 0 | 0 | 0 | 3.6275 | 0 | 0
6 | 19 | 12 | 0 | 2.1292 | 2.1292 | 48 | 9.7176 | 0 | 0 | 485.1297 | 0 | 2.1292 | 0 | 0.22201 | 0 | 0 | 0 | 2.1292 | 0 | 0
6 | 19 | 13 | 0 | 1.295 | 1.295 | 48 | 9.7939 | 0 | 0 | 481.2031 | 0 | 1.295 | 0 | 0.13503 | 0 | 0 | 0 | 1.295 | 0 | 0
6 | 19 | 14 | 0 | 2.4574 | 2.4574 | 48 | 9.4634 | 40.4624 | 40.4624 | 483.6651 | 2.4574 | 0 | 1070.5925 | 0 | 0 | 0 | 2.4574 | 0 | 0 | 1070.5925
6 | 19 | 15 | 0 | 17.1261 | 17.1261 | 48 | 10.5311 | 0 | 0 | 489.8334 | 0 | 17.1261 | 0 | 1.7858 | 0 | 0 | 0 | 17.1261 | 0 | 0
6 | 19 | 16 | 0 | 1.2483 | 1.2483 | 48 | 11.0904 | 0 | 0 | 496.0064 | 0 | 1.2483 | 0 | 0.13017 | 0 | 0 | 0 | 1.2483 | 0 | 0
6 | 19 | 17 | 0 | 0.030833 | 0.030833 | 48 | 11.1073 | 0 | 0 | 498.0216 | 0 | 0.030833 | 0 | 0.0032151 | 0 | 0 | 0 | 0.030833 | 0 | 0
6 | 19 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 512.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 498.9022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 478.5124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 464.4328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 444.3991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 19 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 435.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 432.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 433.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 438.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 451.5991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 469.6094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 491.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 502.3407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 516.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 8 | 0 | 0.0075 | 0.0075 | 48 | 6.2094 | 0.0046336 | 0.0046336 | 515.8693 | 0.0075 | 0 | 3.509 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.509
6 | 20 | 9 | 0 | 0.060834 | 0.060834 | 48 | 7.328 | 0.056166 | 0.056166 | 515.4603 | 0.060834 | 0 | 28.4373 | 0 | 0 | 0 | 0.060834 | 0 | 0 | 28.4373
6 | 20 | 10 | 0 | 1.2475 | 1.2475 | 48 | 8.5482 | 2.5005 | 2.5005 | 515.255 | 1.2475 | 0 | 582.9006 | 0 | 0 | 0 | 1.2475 | 0 | 0 | 582.9006
6 | 20 | 11 | 0 | 2.4317 | 2.4317 | 48 | 9.1838 | 12.4948 | 12.4948 | 518.3725 | 2.4317 | 0 | 1143.7892 | 0 | 0 | 0 | 2.4317 | 0 | 0 | 1143.7892
6 | 20 | 12 | 0 | 0.32 | 0.32 | 48 | 9.8701 | 0 | 0 | 515.9603 | 0 | 0.32 | 0 | 0.033367 | 0 | 0 | 0 | 0.32 | 0 | 0
6 | 20 | 13 | 0 | 0.1075 | 0.1075 | 48 | 9.6668 | 0 | 0 | 514.8866 | 0 | 0.1075 | 0 | 0.011209 | 0 | 0 | 0 | 0.1075 | 0 | 0
6 | 20 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 516.4868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 527.5057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 535.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 17 | 0 | 1.3775 | 1.3775 | 48 | 11.7514 | 0 | 0 | 539.6263 | 0 | 1.3775 | 0 | 0.14363 | 0 | 0 | 0 | 1.3775 | 0 | 0
6 | 20 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 538.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 525.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 506.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 475.2391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 458.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 20 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 452.3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 447.8769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 445.4459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 444.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 3 | 0.7375 | 0 | 0.7375 | 11 | 3.1249 | 0.23826 | 0.23826 | 461.6281 | 0.7375 | 0 | 332.3382 | 0 | 0 | 0 | 0.7375 | 0 | 0 | 332.3382
6 | 21 | 4 | 1.7059 | 0 | 1.7059 | 11 | 3.3028 | 0.5667 | 0.5667 | 475.4932 | 1.7059 | 0 | 792.3674 | 0 | 0 | 0 | 1.7059 | 0 | 0 | 792.3674
6 | 21 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 495.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 508.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 7 | 0 | 0.89917 | 0.89917 | 48 | 5.0146 | 0.41045 | 0.41045 | 528.968 | 0.89917 | 0 | 432.4704 | 0 | 0 | 0 | 0.89917 | 0 | 0 | 432.4704
6 | 21 | 8 | 0 | 0.0075 | 0.0075 | 48 | 6.2094 | 0.0046336 | 0.0046336 | 537.5455 | 0.0075 | 0 | 3.6716 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.6716
6 | 21 | 9 | 0 | 0.060834 | 0.060834 | 48 | 7.311 | 0.055748 | 0.055748 | 536.1125 | 0.060834 | 0 | 29.6936 | 0 | 0 | 0 | 0.060834 | 0 | 0 | 29.6936
6 | 21 | 10 | 0 | 1.4617 | 1.4617 | 48 | 8.0567 | 1.9908 | 1.9908 | 527.8979 | 1.4617 | 0 | 701.4508 | 0 | 0 | 0 | 1.4617 | 0 | 0 | 701.4508
6 | 21 | 11 | 0 | 2.09 | 2.09 | 48 | 9.3109 | 15.6251 | 15.6251 | 528.4101 | 2.09 | 0 | 1004.0572 | 0 | 0 | 0 | 2.09 | 0 | 0 | 1004.0572
6 | 21 | 12 | 0 | 0.85333 | 0.85333 | 48 | 9.0058 | 3.0497 | 3.0497 | 529.8086 | 0.85333 | 0 | 411.1434 | 0 | 0 | 0 | 0.85333 | 0 | 0 | 411.1434
6 | 21 | 13 | 0 | 0.5275 | 0.5275 | 48 | 8.4889 | 1.0004 | 1.0004 | 529.5989 | 0.5275 | 0 | 254.0434 | 0 | 0 | 0 | 0.5275 | 0 | 0 | 254.0434
6 | 21 | 14 | 0 | 0.24833 | 0.24833 | 48 | 8.938 | 0.79526 | 0.79526 | 531.4496 | 0.24833 | 0 | 120.0566 | 0 | 0 | 0 | 0.24833 | 0 | 0 | 120.0566
6 | 21 | 15 | 0 | 0 | 0 | 0 | 9.6075 | 0 | 0 | 537.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 546.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 546.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 548.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 536.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 502.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 471.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 447.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 21 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 437.9804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 425.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 421.8241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 440.8792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 456.3746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 490.0413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 508.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 7 | 0 | 0.87167 | 0.87167 | 48 | 4.6502 | 0.36855 | 0.36855 | 527.2003 | 0.87167 | 0 | 417.7029 | 0 | 0 | 0 | 0.87167 | 0 | 0 | 417.7029
6 | 22 | 8 | 0 | 0.5775 | 0.5775 | 48 | 5.1417 | 0.27115 | 0.27115 | 536.6041 | 0.5775 | 0 | 282.1689 | 0 | 0 | 0 | 0.5775 | 0 | 0 | 282.1689
6 | 22 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 535.066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 10 | 0 | 1.8519 | 1.8519 | 48 | 6.9721 | 1.4774 | 1.4774 | 524.2108 | 1.8519 | 0 | 881.8817 | 0 | 0 | 0 | 1.8519 | 0 | 0 | 881.8817
6 | 22 | 11 | 0 | 21.7095 | 21.7095 | 48 | 8.5652 | 44.2351 | 44.2351 | 515.4862 | 21.7095 | 0 | 10148.9142 | 0 | 0 | 0 | 21.7095 | 0 | 0 | 10148.9142
6 | 22 | 12 | 0 | 64.307 | 64.307 | 48 | 7.8957 | 79.266 | 79.266 | 519.2109 | 64.307 | 0 | 30302.184 | 0 | 0 | 0 | 64.307 | 0 | 0 | 30302.184
6 | 22 | 13 | 0 | 0.3925 | 0.3925 | 48 | 7.4381 | 0.38093 | 0.38093 | 522.1814 | 0.3925 | 0 | 186.1162 | 0 | 0 | 0 | 0.3925 | 0 | 0 | 186.1162
6 | 22 | 14 | 0 | 0.1375 | 0.1375 | 48 | 7.2771 | 0.12416 | 0.12416 | 526.1516 | 0.1375 | 0 | 65.7458 | 0 | 0 | 0 | 0.1375 | 0 | 0 | 65.7458
6 | 22 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 527.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 16 | 0 | 74.8208 | 74.8208 | 48 | 6.9975 | 60.2748 | 60.2748 | 528.6208 | 74.8208 | 0 | 35960.4105 | 0 | 0 | 0 | 74.8208 | 0 | 0 | 35960.4105
6 | 22 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 533.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 542.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 545.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 533.8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 510.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 502.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 22 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 488.6478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 474.6856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 470.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 480.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 501.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 503.1823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 511.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 524.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 537.2924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 538.9722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 9 | 0 | 1.1209 | 1.1209 | 48 | 7.3195 | 1.031 | 1.031 | 532.0403 | 1.1209 | 0 | 542.5486 | 0 | 0 | 0 | 1.1209 | 0 | 0 | 542.5486
6 | 23 | 10 | 0 | 1.1125 | 1.1125 | 48 | 7.4805 | 1.1014 | 1.1014 | 525.8897 | 1.1125 | 0 | 531.6523 | 0 | 0 | 0 | 1.1125 | 0 | 0 | 531.6523
6 | 23 | 11 | 0 | 2.1631 | 2.1631 | 48 | 7.2263 | 1.9112 | 1.9112 | 519.841 | 2.1631 | 0 | 1020.6289 | 0 | 0 | 0 | 2.1631 | 0 | 0 | 1020.6289
6 | 23 | 12 | 0 | 0.62667 | 0.62667 | 48 | 7.8703 | 0.76102 | 0.76102 | 518.4487 | 0.62667 | 0 | 294.8145 | 0 | 0 | 0 | 0.62667 | 0 | 0 | 294.8145
6 | 23 | 13 | 0 | 133.256 | 133.256 | 48 | 8.1754 | 196.7169 | 196.7169 | 517.4647 | 133.256 | 0 | 62558.9906 | 0 | 0 | 0 | 133.256 | 0 | 0 | 62558.9906
6 | 23 | 14 | 0 | 0.17833 | 0.17833 | 48 | 8.2431 | 0.27651 | 0.27651 | 517.6016 | 0.17833 | 0 | 83.7456 | 0 | 0 | 0 | 0.17833 | 0 | 0 | 83.7456
6 | 23 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 526.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 527.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 527.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 527.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 525.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 514.4831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 488.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 474.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 23 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 465.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 441.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 434.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 431.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 434.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 440.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 471.6396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 486.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 503.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 8 | 7.3241 | 0 | 7.3241 | 11 | 6.6246 | 5.1584 | 5.1584 | 507.7233 | 7.3241 | 0 | 3638.0432 | 0 | 0 | 0 | 7.3241 | 0 | 0 | 3638.0432
6 | 24 | 9 | 155.05 | 0.30917 | 155.3591 | 11.0736 | 7.1924 | 135.3285 | 135.3285 | 503.6369 | 155.3591 | 0 | 76524.2014 | 0 | 0 | 0 | 155.3591 | 0 | 0 | 76524.2014
6 | 24 | 10 | 72.7898 | 0.94833 | 73.7381 | 11.4759 | 7.0398 | 60.3896 | 60.3896 | 497.4953 | 73.7381 | 0 | 35838.1697 | 0 | 0 | 0 | 73.7381 | 0 | 0 | 35838.1697
6 | 24 | 11 | 0 | 2.7467 | 2.7467 | 48 | 7.2093 | 2.4096 | 2.4096 | 492.5101 | 2.7467 | 0 | 1220.9211 | 0 | 0 | 0 | 2.7467 | 0 | 0 | 1220.9211
6 | 24 | 12 | 0 | 0.7375 | 0.7375 | 48 | 7.9296 | 0.92761 | 0.92761 | 484.733 | 0.7375 | 0 | 322.0906 | 0 | 0 | 0 | 0.7375 | 0 | 0 | 322.0906
6 | 24 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 479.6351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 486.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 15 | 1.0414 | 0 | 1.0414 | 11 | 8.4041 | 1.8338 | 1.8338 | 496.5381 | 1.0414 | 0 | 505.619 | 0 | 0 | 0 | 1.0414 | 0 | 0 | 505.619
6 | 24 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 505.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 507.0824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 18 | 0 | 0.10392 | 0.10392 | 48 | 9.0397 | 0.39425 | 0.39425 | 505.6849 | 0.10392 | 0 | 47.5611 | 0 | 0 | 0 | 0.10392 | 0 | 0 | 47.5611
6 | 24 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 504.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 487.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 453.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 434.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 24 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 423.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 421.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 416.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 414.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 412.9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 412.3791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 5 | 25.226 | 0 | 25.226 | 11 | 3.4638 | 8.6004 | 8.6004 | 425.0682 | 25.226 | 0 | 10445.2677 | 0 | 0 | 0 | 25.226 | 0 | 0 | 10445.2677
6 | 25 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 434.6493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 7 | 0.75417 | 1.2725 | 2.0267 | 34.2315 | 4.8705 | 0.8969 | 0.8969 | 449.6647 | 2.0267 | 0 | 841.9458 | 0 | 0 | 0 | 2.0267 | 0 | 0 | 841.9458
6 | 25 | 8 | 0 | 0.6275 | 0.6275 | 48 | 4.8451 | 0.27621 | 0.27621 | 458.4988 | 0.6275 | 0 | 257.588 | 0 | 0 | 0 | 0.6275 | 0 | 0 | 257.588
6 | 25 | 9 | 0 | 0.0075 | 0.0075 | 48 | 6.3789 | 0.0048781 | 0.0048781 | 468.271 | 0.0075 | 0 | 3.1521 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.1521
6 | 25 | 10 | 0 | 1.1892 | 1.1892 | 48 | 8.4804 | 2.238 | 2.238 | 481.1399 | 1.1892 | 0 | 515.0756 | 0 | 0 | 0 | 1.1892 | 0 | 0 | 515.0756
6 | 25 | 11 | 0 | 2.6541 | 2.6541 | 48 | 9.4549 | 40.9648 | 40.9648 | 484.5196 | 2.6541 | 0 | 1158.5602 | 0 | 0 | 0 | 2.6541 | 0 | 0 | 1158.5602
6 | 25 | 12 | 0 | 1.3322 | 1.3322 | 48 | 9.8362 | 0 | 0 | 480.3847 | 0 | 1.3322 | 0 | 0.13891 | 0 | 0 | 0 | 1.3322 | 0 | 0
6 | 25 | 13 | 0 | 1.2112 | 1.2112 | 48 | 9.6159 | 0 | 0 | 475.9454 | 0 | 1.2112 | 0 | 0.12629 | 0 | 0 | 0 | 1.2112 | 0 | 0
6 | 25 | 14 | 0 | 0.65109 | 0.65109 | 48 | 9.5227 | 20.1368 | 20.1368 | 484.8414 | 0.65109 | 0 | 284.4213 | 0 | 0 | 0 | 0.65109 | 0 | 0 | 284.4213
6 | 25 | 15 | 0 | 4.2577 | 4.2577 | 48 | 10.7175 | 0 | 0 | 485.665 | 0 | 4.2577 | 0 | 0.44396 | 0 | 0 | 0 | 4.2577 | 0 | 0
6 | 25 | 16 | 0 | 3.7434 | 3.7434 | 48 | 12.0564 | 0 | 0 | 498.2213 | 0 | 3.7434 | 0 | 0.39033 | 0 | 0 | 0 | 3.7434 | 0 | 0
6 | 25 | 17 | 0 | 0.83 | 0.83 | 48 | 11.8107 | 0 | 0 | 489.0252 | 0 | 0.83 | 0 | 0.086546 | 0 | 0 | 0 | 0.83 | 0 | 0
6 | 25 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 491.6631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 479.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 458.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 438.3986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 426.7248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 25 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 423.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 420.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 421.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 421.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 423.9957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 437.8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 462.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 473.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 7 | 0 | 0.49079 | 0.49079 | 48 | 4.8281 | 0.21527 | 0.21527 | 476.0981 | 0.49079 | 0 | 210.107 | 0 | 0 | 0 | 0.49079 | 0 | 0 | 210.107
6 | 26 | 8 | 0 | 0.018333 | 0.018333 | 48 | 5.4976 | 0.0093566 | 0.0093566 | 470.2321 | 0.018333 | 0 | 7.741 | 0 | 0 | 0 | 0.018333 | 0 | 0 | 7.741
6 | 26 | 9 | 0 | 0.155 | 0.155 | 48 | 6.4043 | 0.10162 | 0.10162 | 480.2953 | 0.155 | 0 | 67.0058 | 0 | 0 | 0 | 0.155 | 0 | 0 | 67.0058
6 | 26 | 10 | 0 | 1.46 | 1.46 | 48 | 8.5991 | 3.0766 | 3.0766 | 488.4806 | 1.46 | 0 | 643.1017 | 0 | 0 | 0 | 1.46 | 0 | 0 | 643.1017
6 | 26 | 11 | 0 | 2.8529 | 2.8529 | 48 | 9.6413 | 0 | 0 | 498.247 | 0 | 2.8529 | 0 | 0.29747 | 0 | 0 | 0 | 2.8529 | 0 | 0
6 | 26 | 12 | 0 | 2.5196 | 2.5196 | 48 | 9.7176 | 0 | 0 | 500.4278 | 0 | 2.5196 | 0 | 0.26273 | 0 | 0 | 0 | 2.5196 | 0 | 0
6 | 26 | 13 | 3.0419 | 21.9501 | 24.992 | 43.4966 | 9.7939 | 0 | 0 | 501.0608 | 0 | 24.992 | 0 | 2.606 | 0 | 0 | 0 | 24.992 | 0 | 0
6 | 26 | 14 | 0 | 90.3541 | 90.3541 | 48 | 9.4634 | 1487.7423 | 288 | 508.7577 | 17.4909 | 72.8632 | 8059.0734 | 7.5976 | 0 | 0 | 17.4909 | 72.8632 | 0 | 8059.0734
6 | 26 | 15 | 0 | 26.4111 | 26.4111 | 48 | 10.5311 | 0 | 0 | 512.9817 | 0 | 26.4111 | 0 | 2.754 | 0 | 0 | 0 | 26.4111 | 0 | 0
6 | 26 | 16 | 0 | 45.6225 | 45.6225 | 48 | 11.0904 | 0 | 0 | 503.9397 | 0 | 45.6225 | 0 | 4.7572 | 0 | 0 | 0 | 45.6225 | 0 | 0
6 | 26 | 17 | 0 | 55.0642 | 55.0642 | 48 | 11.1073 | 0 | 0 | 501.0879 | 0 | 55.0642 | 0 | 5.7417 | 0 | 0 | 0 | 55.0642 | 0 | 0
6 | 26 | 18 | 0 | 2.7032 | 2.7032 | 48 | 11.4802 | 0 | 0 | 497.9388 | 0 | 2.7032 | 0 | 0.28187 | 0 | 0 | 0 | 2.7032 | 0 | 0
6 | 26 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 485.9618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 20 | 0.73417 | 0 | 0.73417 | 11 | 12.2428 | 0 | 0 | 468.4571 | 0 | 0.73417 | 0 | 0.076553 | 0 | 0 | 0 | 0.73417 | 0 | 0
6 | 26 | 21 | 18.4404 | 0 | 18.4404 | 11 | 9.4634 | 303.6341 | 288 | 451.1143 | 17.4909 | 0.94949 | 7698.0019 | 0.099006 | 0 | 0 | 17.4909 | 0.94949 | 0 | 7698.0019
6 | 26 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 439.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 26 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 436.4655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 432.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 435.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 447.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 457.7873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 465.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 489.4399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 501.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 7 | 0 | 65.1928 | 65.1928 | 48 | 5.2518 | 31.3869 | 31.3869 | 514.8724 | 65.1928 | 0 | 30436.7172 | 0 | 0 | 0 | 65.1928 | 0 | 0 | 30436.7172
6 | 27 | 8 | 0 | 184.3041 | 184.3041 | 48 | 6.2094 | 113.8642 | 113.8642 | 521.023 | 184.3041 | 0 | 87180.0521 | 0 | 0 | 0 | 184.3041 | 0 | 0 | 87180.0521
6 | 27 | 9 | 0 | 11.407 | 11.407 | 48 | 7.328 | 10.5318 | 10.5318 | 517.1624 | 11.407 | 0 | 5351.7308 | 0 | 0 | 0 | 11.407 | 0 | 0 | 5351.7308
6 | 27 | 10 | 3.1282 | 9.4051 | 12.5333 | 38.765 | 8.5482 | 25.1223 | 25.1223 | 516.6683 | 12.5333 | 0 | 5989.704 | 0 | 0 | 0 | 12.5333 | 0 | 0 | 5989.704
6 | 27 | 11 | 2.8698 | 6.3308 | 9.2006 | 36.4592 | 9.1838 | 47.2761 | 47.2761 | 527.2481 | 9.2006 | 0 | 4515.5527 | 0 | 0 | 0 | 9.2006 | 0 | 0 | 4515.5527
6 | 27 | 12 | 1.3771 | 1.7947 | 3.1718 | 31.9361 | 9.8701 | 0 | 0 | 522.2681 | 0 | 3.1718 | 0 | 0.33073 | 0 | 0 | 0 | 3.1718 | 0 | 0
6 | 27 | 13 | 0.14411 | 0.99921 | 1.1433 | 43.3364 | 9.6668 | 0 | 0 | 530.4303 | 0 | 1.1433 | 0 | 0.11922 | 0 | 0 | 0 | 1.1433 | 0 | 0
6 | 27 | 14 | 0 | 0.6874 | 0.6874 | 48 | 10.2684 | 0 | 0 | 531.3521 | 0 | 0.6874 | 0 | 0.071677 | 0 | 0 | 0 | 0.6874 | 0 | 0
6 | 27 | 15 | 0 | 0.013243 | 0.013243 | 48 | 11.226 | 0 | 0 | 528.297 | 0 | 0.013243 | 0 | 0.0013809 | 0 | 0 | 0 | 0.013243 | 0 | 0
6 | 27 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 523.5348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 521.0453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 516.9342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 494.0844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 466.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 432.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 428.1761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 27 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 418.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 420.0273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 419.7967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 419.6576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 423.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 438.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 453.7356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 467.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 7 | 0 | 63.8684 | 63.8684 | 48 | 5.0146 | 29.1547 | 29.1547 | 477.9826 | 63.8684 | 0 | 27462.3075 | 0 | 0 | 0 | 63.8684 | 0 | 0 | 27462.3075
6 | 28 | 8 | 0 | 265.0429 | 265.0429 | 48 | 6.2094 | 163.7452 | 163.7452 | 479.5611 | 265.0429 | 0 | 114382.1913 | 0 | 0 | 0 | 265.0429 | 0 | 0 | 114382.1913
6 | 28 | 9 | 3.7122 | 480.218 | 483.9302 | 47.7162 | 7.311 | 443.4777 | 288 | 489.1851 | 314.2704 | 169.6598 | 138740.6067 | 17.6909 | 0 | 0 | 314.2704 | 169.6598 | 0 | 138740.6067
6 | 28 | 10 | 2.9991 | 261.0857 | 264.0847 | 47.5798 | 8.0567 | 359.6913 | 288 | 497.8234 | 211.4491 | 52.6356 | 95203.6228 | 5.4885 | 0 | 0 | 211.4491 | 52.6356 | 0 | 95203.6228
6 | 28 | 11 | 0.0058294 | 184.2265 | 184.2324 | 47.9988 | 9.3109 | 1377.3477 | 288 | 490.4816 | 38.5225 | 145.7098 | 17045.5564 | 15.1935 | 0 | 0 | 38.5225 | 145.7098 | 0 | 17045.5564
6 | 28 | 12 | 0.35877 | 154.2135 | 154.5723 | 47.9141 | 9.0058 | 552.4155 | 288 | 491.5257 | 80.5858 | 73.9865 | 35748.7742 | 7.7148 | 0 | 0 | 80.5858 | 73.9865 | 0 | 35748.7742
6 | 28 | 13 | 0 | 13.0752 | 13.0752 | 48 | 8.4889 | 24.7969 | 24.7969 | 495.9962 | 13.0752 | 0 | 5857.6252 | 0 | 0 | 0 | 13.0752 | 0 | 0 | 5857.6252
6 | 28 | 14 | 0 | 10.7049 | 10.7049 | 48 | 8.938 | 34.2811 | 34.2811 | 507.8398 | 10.7049 | 0 | 4922.5277 | 0 | 0 | 0 | 10.7049 | 0 | 0 | 4922.5277
6 | 28 | 15 | 0 | 0.018712 | 0.018712 | 48 | 9.6075 | 0 | 0 | 510.6596 | 0 | 0.018712 | 0 | 0.0019512 | 0 | 0 | 0 | 0.018712 | 0 | 0
6 | 28 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 512.4701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 511.9464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 513.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 19 | 0 | 0.33246 | 0.33246 | 48 | 10.4633 | 0 | 0 | 492.8747 | 0 | 0.33246 | 0 | 0.034666 | 0 | 0 | 0 | 0.33246 | 0 | 0
6 | 28 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 462.5809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 436.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 423.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 28 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 425.3792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 425.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 422.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 427.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 441.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 466.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 476.4872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 494.8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 7 | 0 | 18.6799 | 18.6799 | 48 | 4.6502 | 7.8981 | 7.8981 | 506.0099 | 18.6799 | 0 | 8555.5663 | 0 | 0 | 0 | 18.6799 | 0 | 0 | 8555.5663
6 | 29 | 8 | 0 | 2.3901 | 2.3901 | 48 | 5.1417 | 1.1222 | 1.1222 | 516.4531 | 2.3901 | 0 | 1119.6615 | 0 | 0 | 0 | 2.3901 | 0 | 0 | 1119.6615
6 | 29 | 9 | 0 | 0.041667 | 0.041667 | 48 | 6.6161 | 0.029263 | 0.029263 | 525.0244 | 0.041667 | 0 | 19.876 | 0 | 0 | 0 | 0.041667 | 0 | 0 | 19.876
6 | 29 | 10 | 0 | 1.5198 | 1.5198 | 48 | 6.9721 | 1.2124 | 1.2124 | 527.4602 | 1.5198 | 0 | 728.6825 | 0 | 0 | 0 | 1.5198 | 0 | 0 | 728.6825
6 | 29 | 11 | 0 | 3.3985 | 3.3985 | 48 | 8.5652 | 6.9247 | 6.9247 | 525.6652 | 3.3985 | 0 | 1623.3415 | 0 | 0 | 0 | 3.3985 | 0 | 0 | 1623.3415
6 | 29 | 12 | 0 | 1.405 | 1.405 | 48 | 7.8957 | 1.7318 | 1.7318 | 520.4855 | 1.405 | 0 | 663.8409 | 0 | 0 | 0 | 1.405 | 0 | 0 | 663.8409
6 | 29 | 13 | 0 | 10.5781 | 10.5781 | 48 | 7.4381 | 10.2664 | 10.2664 | 523.3158 | 10.5781 | 0 | 5027.9182 | 0 | 0 | 0 | 10.5781 | 0 | 0 | 5027.9182
6 | 29 | 14 | 0 | 8.508 | 8.508 | 48 | 7.2771 | 7.6825 | 7.6825 | 531.1061 | 8.508 | 0 | 4110.2661 | 0 | 0 | 0 | 8.508 | 0 | 0 | 4110.2661
6 | 29 | 15 | 0 | 3.721 | 3.721 | 48 | 7.3449 | 3.4614 | 3.4614 | 533.979 | 3.721 | 0 | 1808.3278 | 0 | 0 | 0 | 3.721 | 0 | 0 | 1808.3278
6 | 29 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 541.0022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 17 | 0 | 0.86654 | 0.86654 | 48 | 7.167 | 0.7469 | 0.7469 | 551.0159 | 0.86654 | 0 | 435.8842 | 0 | 0 | 0 | 0.86654 | 0 | 0 | 435.8842
6 | 29 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 549.9218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 542.2675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 20 | 0 | 0.24413 | 0.24413 | 48 | 6.9721 | 0.19476 | 0.19476 | 527.9523 | 0.24413 | 0 | 117.1683 | 0 | 0 | 0 | 0.24413 | 0 | 0 | 117.1683
6 | 29 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 505.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 475.1523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 29 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 456.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 450.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 444.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 453.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 464.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 487.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 506.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 525.8809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 535.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 540.8502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 532.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 10 | 0 | 1.7825 | 1.7825 | 48 | 7.4805 | 1.7647 | 1.7647 | 529.9231 | 1.7825 | 0 | 859.028 | 0 | 0 | 0 | 1.7825 | 0 | 0 | 859.028
6 | 30 | 11 | 0 | 3.0883 | 3.0883 | 48 | 7.2263 | 2.7287 | 2.7287 | 529.8131 | 3.0883 | 0 | 1487.9994 | 0 | 0 | 0 | 3.0883 | 0 | 0 | 1487.9994
6 | 30 | 12 | 0 | 0.38329 | 0.38329 | 48 | 7.8703 | 0.46547 | 0.46547 | 529.0795 | 0.38329 | 0 | 184.3937 | 0 | 0 | 0 | 0.38329 | 0 | 0 | 184.3937
6 | 30 | 13 | 0 | 0.03 | 0.03 | 48 | 8.1754 | 0.044287 | 0.044287 | 528.7138 | 0.03 | 0 | 14.4214 | 0 | 0 | 0 | 0.03 | 0 | 0 | 14.4214
6 | 30 | 14 | 0 | 1.0333 | 1.0333 | 48 | 8.2431 | 1.6022 | 1.6022 | 530.9419 | 1.0333 | 0 | 499.0401 | 0 | 0 | 0 | 1.0333 | 0 | 0 | 499.0401
6 | 30 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 534.8091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 535.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 17 | 0 | 0.53987 | 0.53987 | 48 | 7.2686 | 0.48572 | 0.48572 | 543.8739 | 0.53987 | 0 | 267.7099 | 0 | 0 | 0 | 0.53987 | 0 | 0 | 267.7099
6 | 30 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 550.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 19 | 0 | 0.18537 | 0.18537 | 48 | 6.9382 | 0.146 | 0.146 | 545.8599 | 0.18537 | 0 | 92.2908 | 0 | 0 | 0 | 0.18537 | 0 | 0 | 92.2908
6 | 30 | 20 | 0 | 0.23329 | 0.23329 | 48 | 6.2772 | 0.14708 | 0.14708 | 527.012 | 0.23329 | 0 | 111.7495 | 0 | 0 | 0 | 0.23329 | 0 | 0 | 111.7495
6 | 30 | 21 | 0.20329 | 0 | 0.20329 | 11 | 5.6332 | 0.10731 | 0.10731 | 503.3215 | 0.20329 | 0 | 100.0848 | 0 | 0 | 0 | 0.20329 | 0 | 0 | 100.0848
6 | 30 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 495.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 30 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 482.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 459.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 451.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 448.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 449.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 460.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 480.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 6 | 0 | 0.32333 | 0.32333 | 48 | 4.4638 | 0.13174 | 0.13174 | 496.3543 | 0.32333 | 0 | 144.9679 | 0 | 0 | 0 | 0.32333 | 0 | 0 | 144.9679
7 | 1 | 7 | 0 | 2.9883 | 2.9883 | 48 | 6.006 | 1.7415 | 1.7415 | 517.1459 | 2.9883 | 0 | 1401.9643 | 0 | 0 | 0 | 2.9883 | 0 | 0 | 1401.9643
7 | 1 | 8 | 0 | 1.8358 | 1.8358 | 48 | 6.6246 | 1.293 | 1.293 | 529.7401 | 1.8358 | 0 | 884.3947 | 0 | 0 | 0 | 1.8358 | 0 | 0 | 884.3947
7 | 1 | 9 | 0 | 4.375 | 4.375 | 48 | 7.1924 | 3.8109 | 3.8109 | 532.7696 | 4.375 | 0 | 2120.8672 | 0 | 0 | 0 | 4.375 | 0 | 0 | 2120.8672
7 | 1 | 10 | 0 | 3.3783 | 3.3783 | 48 | 7.0398 | 2.7668 | 2.7668 | 530.9756 | 3.3783 | 0 | 1631.6526 | 0 | 0 | 0 | 3.3783 | 0 | 0 | 1631.6526
7 | 1 | 11 | 0 | 1.1592 | 1.1592 | 48 | 7.2093 | 1.0169 | 1.0169 | 523.2351 | 1.1592 | 0 | 550.8767 | 0 | 0 | 0 | 1.1592 | 0 | 0 | 550.8767
7 | 1 | 12 | 0 | 0.38933 | 0.38933 | 48 | 7.9296 | 0.48969 | 0.48969 | 518.8839 | 0.38933 | 0 | 183.3308 | 0 | 0 | 0 | 0.38933 | 0 | 0 | 183.3308
7 | 1 | 13 | 0 | 0.065 | 0.065 | 48 | 8.2601 | 0.10207 | 0.10207 | 516.7368 | 0.065 | 0 | 30.4679 | 0 | 0 | 0 | 0.065 | 0 | 0 | 30.4679
7 | 1 | 14 | 0 | 1.1325 | 1.1325 | 48 | 8.5313 | 2.2337 | 2.2337 | 518.6086 | 1.1325 | 0 | 532.9643 | 0 | 0 | 0 | 1.1325 | 0 | 0 | 532.9643
7 | 1 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 523.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 525.4146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 17 | 0 | 0.60654 | 0.60654 | 48 | 8.6753 | 1.3847 | 1.3847 | 532.3255 | 0.60654 | 0 | 293.7636 | 0 | 0 | 0 | 0.60654 | 0 | 0 | 293.7636
7 | 1 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 535.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 525.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 503.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 478.0347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 459.9693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 452.9262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 440.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 434.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 434.4933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 437.0271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 441.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 467.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 484.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 7 | 0 | 0.81667 | 0.81667 | 48 | 4.8705 | 0.36141 | 0.36141 | 507.4861 | 0.81667 | 0 | 375.2471 | 0 | 0 | 0 | 0.81667 | 0 | 0 | 375.2471
7 | 2 | 8 | 0 | 3.3383 | 3.3383 | 48 | 4.8451 | 1.4695 | 1.4695 | 527.4463 | 3.3383 | 0 | 1600.5518 | 0 | 0 | 0 | 3.3383 | 0 | 0 | 1600.5518
7 | 2 | 9 | 0 | 3.9392 | 3.9392 | 48 | 6.3789 | 2.5621 | 2.5621 | 531.8069 | 3.9392 | 0 | 1905.7963 | 0 | 0 | 0 | 3.9392 | 0 | 0 | 1905.7963
7 | 2 | 10 | 0 | 7.7649 | 7.7649 | 48 | 8.4804 | 14.6136 | 14.6136 | 536.1984 | 7.7649 | 0 | 3790.8068 | 0 | 0 | 0 | 7.7649 | 0 | 0 | 3790.8068
7 | 2 | 11 | 0 | 5.8026 | 5.8026 | 48 | 9.4549 | 89.5608 | 89.5608 | 532.6665 | 5.8026 | 0 | 2812.3212 | 0 | 0 | 0 | 5.8026 | 0 | 0 | 2812.3212
7 | 2 | 12 | 0 | 4.0466 | 4.0466 | 48 | 9.8362 | 0 | 0 | 524.4245 | 0 | 4.0466 | 0 | 0.42195 | 0 | 0 | 0 | 4.0466 | 0 | 0
7 | 2 | 13 | 0 | 2.3137 | 2.3137 | 48 | 9.6159 | 0 | 0 | 518.6919 | 0 | 2.3137 | 0 | 0.24126 | 0 | 0 | 0 | 2.3137 | 0 | 0
7 | 2 | 14 | 0 | 1.6103 | 1.6103 | 48 | 9.5227 | 49.8023 | 49.8023 | 520.4351 | 1.6103 | 0 | 760.7459 | 0 | 0 | 0 | 1.6103 | 0 | 0 | 760.7459
7 | 2 | 15 | 0 | 0.0091621 | 0.0091621 | 48 | 10.7175 | 0 | 0 | 523.0795 | 0 | 0.0091621 | 0 | 0.00095536 | 0 | 0 | 0 | 0.0091621 | 0 | 0
7 | 2 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 526.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 17 | 0 | 0.65238 | 0.65238 | 48 | 11.8107 | 0 | 0 | 535.0919 | 0 | 0.65238 | 0 | 0.068025 | 0 | 0 | 0 | 0.65238 | 0 | 0
7 | 2 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 537.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 527.261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 516.9807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 500.3446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 473.5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 445.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 432.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 429.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 434.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 453.1665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 472.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 494.4694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 513.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 7 | 0 | 0.67833 | 0.67833 | 48 | 4.8281 | 0.29752 | 0.29752 | 529.6626 | 0.67833 | 0 | 326.7279 | 0 | 0 | 0 | 0.67833 | 0 | 0 | 326.7279
7 | 3 | 8 | 0 | 0.91667 | 0.91667 | 48 | 5.4976 | 0.46783 | 0.46783 | 536.976 | 0.91667 | 0 | 448.2281 | 0 | 0 | 0 | 0.91667 | 0 | 0 | 448.2281
7 | 3 | 9 | 0 | 3.3075 | 3.3075 | 48 | 6.4043 | 2.1684 | 2.1684 | 527.0933 | 3.3075 | 0 | 1584.6014 | 0 | 0 | 0 | 3.3075 | 0 | 0 | 1584.6014
7 | 3 | 10 | 0 | 1.585 | 1.585 | 48 | 8.5991 | 3.34 | 3.34 | 528.8327 | 1.585 | 0 | 762.1125 | 0 | 0 | 0 | 1.585 | 0 | 0 | 762.1125
7 | 3 | 11 | 0 | 1.7532 | 1.7532 | 48 | 9.6413 | 0 | 0 | 527.5523 | 0 | 1.7532 | 0 | 0.18282 | 0 | 0 | 0 | 1.7532 | 0 | 0
7 | 3 | 12 | 0 | 2.4889 | 2.4889 | 48 | 9.7176 | 0 | 0 | 525.5559 | 0 | 2.4889 | 0 | 0.25953 | 0 | 0 | 0 | 2.4889 | 0 | 0
7 | 3 | 13 | 0 | 1.2813 | 1.2813 | 48 | 9.7939 | 0 | 0 | 525.2983 | 0 | 1.2813 | 0 | 0.13361 | 0 | 0 | 0 | 1.2813 | 0 | 0
7 | 3 | 14 | 0 | 2.9027 | 2.9027 | 48 | 9.4634 | 47.7942 | 47.7942 | 527.1945 | 2.9027 | 0 | 1390.9347 | 0 | 0 | 0 | 2.9027 | 0 | 0 | 1390.9347
7 | 3 | 15 | 0 | 0.63958 | 0.63958 | 48 | 10.5311 | 0 | 0 | 529.9726 | 0 | 0.63958 | 0 | 0.06669 | 0 | 0 | 0 | 0.63958 | 0 | 0
7 | 3 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 534.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 17 | 0 | 0.69321 | 0.69321 | 48 | 11.1073 | 0 | 0 | 542.295 | 0 | 0.69321 | 0 | 0.072283 | 0 | 0 | 0 | 0.69321 | 0 | 0
7 | 3 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 541.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 535.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 519.8812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 504.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 483.8568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 3 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 467.9862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 454.8248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 448.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 452.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 447.212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 449.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 464.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 6 | 0 | 0.99954 | 0.99954 | 48 | 5.0061 | 0.45543 | 0.45543 | 488.5887 | 0.99954 | 0 | 440.3868 | 0 | 0 | 0 | 0.99954 | 0 | 0 | 440.3868
7 | 4 | 7 | 0 | 1.0508 | 1.0508 | 48 | 5.2518 | 0.50592 | 0.50592 | 508.1639 | 1.0508 | 0 | 483.5556 | 0 | 0 | 0 | 1.0508 | 0 | 0 | 483.5556
7 | 4 | 8 | 0 | 17.2052 | 17.2052 | 48 | 6.2094 | 10.6295 | 10.6295 | 525.1316 | 17.2052 | 0 | 8209.1409 | 0 | 0 | 0 | 17.2052 | 0 | 0 | 8209.1409
7 | 4 | 9 | 0 | 3.4853 | 3.4853 | 48 | 7.328 | 3.2178 | 3.2178 | 537.6796 | 3.4853 | 0 | 1706.6598 | 0 | 0 | 0 | 3.4853 | 0 | 0 | 1706.6598
7 | 4 | 10 | 0 | 2.5658 | 2.5658 | 48 | 8.5482 | 5.143 | 5.143 | 541.1526 | 2.5658 | 0 | 1265.3354 | 0 | 0 | 0 | 2.5658 | 0 | 0 | 1265.3354
7 | 4 | 11 | 0 | 2.5818 | 2.5818 | 48 | 9.1838 | 13.2662 | 13.2662 | 531.4666 | 2.5818 | 0 | 1248.2055 | 0 | 0 | 0 | 2.5818 | 0 | 0 | 1248.2055
7 | 4 | 12 | 0 | 2.1124 | 2.1124 | 48 | 9.8701 | 0 | 0 | 532.1736 | 0 | 2.1124 | 0 | 0.22026 | 0 | 0 | 0 | 2.1124 | 0 | 0
7 | 4 | 13 | 0 | 1.6979 | 1.6979 | 48 | 9.6668 | 0 | 0 | 530.7656 | 0 | 1.6979 | 0 | 0.17705 | 0 | 0 | 0 | 1.6979 | 0 | 0
7 | 4 | 14 | 0 | 2.0827 | 2.0827 | 48 | 10.2684 | 0 | 0 | 531.7855 | 0 | 2.0827 | 0 | 0.21717 | 0 | 0 | 0 | 2.0827 | 0 | 0
7 | 4 | 15 | 0 | 0.46996 | 0.46996 | 48 | 11.226 | 0 | 0 | 535.0675 | 0 | 0.46996 | 0 | 0.049004 | 0 | 0 | 0 | 0.46996 | 0 | 0
7 | 4 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 537.0771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 17 | 0 | 0.66071 | 0.66071 | 48 | 11.7514 | 0 | 0 | 531.6513 | 0 | 0.66071 | 0 | 0.068894 | 0 | 0 | 0 | 0.66071 | 0 | 0
7 | 4 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 521.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 510.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 502.3391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 477.6169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 464.8261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 4 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 454.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 447.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 447.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 449.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 465.8941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 486.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 501.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 522.3395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 7 | 0 | 0.51833 | 0.51833 | 48 | 5.0146 | 0.23661 | 0.23661 | 540.4302 | 0.51833 | 0 | 255.243 | 0 | 0 | 0 | 0.51833 | 0 | 0 | 255.243
7 | 5 | 8 | 0 | 0.5775 | 0.5775 | 48 | 6.2094 | 0.35678 | 0.35678 | 553.4885 | 0.5775 | 0 | 291.9198 | 0 | 0 | 0 | 0.5775 | 0 | 0 | 291.9198
7 | 5 | 9 | 0 | 2.1176 | 2.1176 | 48 | 7.311 | 1.9406 | 1.9406 | 548.4646 | 2.1176 | 0 | 1059.7846 | 0 | 0 | 0 | 2.1176 | 0 | 0 | 1059.7846
7 | 5 | 10 | 0 | 1.3581 | 1.3581 | 48 | 8.0567 | 1.8497 | 1.8497 | 543.6395 | 1.3581 | 0 | 673.1122 | 0 | 0 | 0 | 1.3581 | 0 | 0 | 673.1122
7 | 5 | 11 | 0 | 0.37802 | 0.37802 | 48 | 9.3109 | 2.8262 | 2.8262 | 543.6391 | 0.37802 | 0 | 187.3634 | 0 | 0 | 0 | 0.37802 | 0 | 0 | 187.3634
7 | 5 | 12 | 0 | 0.47251 | 0.47251 | 48 | 9.0058 | 1.6887 | 1.6887 | 541.0076 | 0.47251 | 0 | 232.9517 | 0 | 0 | 0 | 0.47251 | 0 | 0 | 232.9517
7 | 5 | 13 | 0 | 0.21993 | 0.21993 | 48 | 8.4889 | 0.41709 | 0.41709 | 540.2672 | 0.21993 | 0 | 108.262 | 0 | 0 | 0 | 0.21993 | 0 | 0 | 108.262
7 | 5 | 14 | 0 | 21.2941 | 21.2941 | 48 | 8.938 | 68.1918 | 68.1918 | 538.7636 | 21.2941 | 0 | 10450.3791 | 0 | 0 | 0 | 21.2941 | 0 | 0 | 10450.3791
7 | 5 | 15 | 0 | 8.1773 | 8.1773 | 48 | 9.6075 | 0 | 0 | 544.3043 | 0 | 8.1773 | 0 | 0.85267 | 0 | 0 | 0 | 8.1773 | 0 | 0
7 | 5 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 545.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 17 | 0 | 0.50987 | 0.50987 | 48 | 10.3786 | 0 | 0 | 553.5717 | 0 | 0.50987 | 0 | 0.053166 | 0 | 0 | 0 | 0.50987 | 0 | 0
7 | 5 | 18 | 0 | 0.51562 | 0.51562 | 48 | 11.0734 | 0 | 0 | 559.8098 | 0 | 0.51562 | 0 | 0.053766 | 0 | 0 | 0 | 0.51562 | 0 | 0
7 | 5 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 553.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 539.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 513.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 490.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 480.3659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 472.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 471.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 479.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 497.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 516.1835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 533.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 6 | 0 | 0.57788 | 0.57788 | 48 | 4.396 | 0.23237 | 0.23237 | 540.7744 | 0.57788 | 0 | 284.762 | 0 | 0 | 0 | 0.57788 | 0 | 0 | 284.762
7 | 6 | 7 | 0 | 0.63246 | 0.63246 | 48 | 4.6502 | 0.26741 | 0.26741 | 548.8676 | 0.63246 | 0 | 316.7779 | 0 | 0 | 0 | 0.63246 | 0 | 0 | 316.7779
7 | 6 | 8 | 0 | 1.1797 | 1.1797 | 48 | 5.1417 | 0.55389 | 0.55389 | 556.5834 | 1.1797 | 0 | 599.9716 | 0 | 0 | 0 | 1.1797 | 0 | 0 | 599.9716
7 | 6 | 9 | 0 | 2.9652 | 2.9652 | 48 | 6.6161 | 2.0824 | 2.0824 | 546.8916 | 2.9652 | 0 | 1479.3043 | 0 | 0 | 0 | 2.9652 | 0 | 0 | 1479.3043
7 | 6 | 10 | 0 | 3.2652 | 3.2652 | 48 | 6.9721 | 2.6049 | 2.6049 | 546.1848 | 3.2652 | 0 | 1626.6963 | 0 | 0 | 0 | 3.2652 | 0 | 0 | 1626.6963
7 | 6 | 11 | 0 | 2.3501 | 2.3501 | 48 | 8.5652 | 4.7886 | 4.7886 | 545.052 | 2.3501 | 0 | 1168.1302 | 0 | 0 | 0 | 2.3501 | 0 | 0 | 1168.1302
7 | 6 | 12 | 0 | 2.0161 | 2.0161 | 48 | 7.8957 | 2.4851 | 2.4851 | 544.4025 | 2.0161 | 0 | 1000.8037 | 0 | 0 | 0 | 2.0161 | 0 | 0 | 1000.8037
7 | 6 | 13 | 0 | 2.1536 | 2.1536 | 48 | 7.4381 | 2.0901 | 2.0901 | 541.0784 | 2.1536 | 0 | 1061.8705 | 0 | 0 | 0 | 2.1536 | 0 | 0 | 1061.8705
7 | 6 | 14 | 0 | 0.46622 | 0.46622 | 48 | 7.2771 | 0.42099 | 0.42099 | 542.8981 | 0.46622 | 0 | 230.7325 | 0 | 0 | 0 | 0.46622 | 0 | 0 | 230.7325
7 | 6 | 15 | 0 | 1.1244 | 1.1244 | 48 | 7.3449 | 1.046 | 1.046 | 545.3664 | 1.1244 | 0 | 559.2583 | 0 | 0 | 0 | 1.1244 | 0 | 0 | 559.2583
7 | 6 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 542.1631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 17 | 0 | 0.43238 | 0.43238 | 48 | 7.167 | 0.37268 | 0.37268 | 548.2865 | 0.43238 | 0 | 216.3114 | 0 | 0 | 0 | 0.43238 | 0 | 0 | 216.3114
7 | 6 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 557.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 549.2942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 529.9023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 504.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 474.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 6 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 460.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 453.0443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 446.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 454.1875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 480.3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 491.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 509.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 6 | 0 | 0.59788 | 0.59788 | 48 | 4.6163 | 0.25107 | 0.25107 | 521.6941 | 0.59788 | 0 | 283.2099 | 0 | 0 | 0 | 0.59788 | 0 | 0 | 283.2099
7 | 7 | 7 | 0 | 0.55167 | 0.55167 | 48 | 6.1924 | 0.33912 | 0.33912 | 532.5864 | 0.55167 | 0 | 267.3302 | 0 | 0 | 0 | 0.55167 | 0 | 0 | 267.3302
7 | 7 | 8 | 0 | 0.70904 | 0.70904 | 48 | 6.8788 | 0.5462 | 0.5462 | 532.3866 | 0.70904 | 0 | 343.4504 | 0 | 0 | 0 | 0.70904 | 0 | 0 | 343.4504
7 | 7 | 9 | 0 | 4.2718 | 4.2718 | 48 | 7.3195 | 3.9293 | 3.9293 | 538.6405 | 4.2718 | 0 | 2095.9227 | 0 | 0 | 0 | 4.2718 | 0 | 0 | 2095.9227
7 | 7 | 10 | 0 | 1.4313 | 1.4313 | 48 | 7.4805 | 1.417 | 1.417 | 533.0262 | 1.4313 | 0 | 694.2054 | 0 | 0 | 0 | 1.4313 | 0 | 0 | 694.2054
7 | 7 | 11 | 0 | 1.7 | 1.7 | 48 | 7.2263 | 1.5021 | 1.5021 | 525.9291 | 1.7 | 0 | 812.4973 | 0 | 0 | 0 | 1.7 | 0 | 0 | 812.4973
7 | 7 | 12 | 0 | 1.2767 | 1.2767 | 48 | 7.8703 | 1.5504 | 1.5504 | 521.174 | 1.2767 | 0 | 604.1071 | 0 | 0 | 0 | 1.2767 | 0 | 0 | 604.1071
7 | 7 | 13 | 0 | 1.1033 | 1.1033 | 48 | 8.1754 | 1.6287 | 1.6287 | 526.3777 | 1.1033 | 0 | 527.7749 | 0 | 0 | 0 | 1.1033 | 0 | 0 | 527.7749
7 | 7 | 14 | 0 | 1.1649 | 1.1649 | 48 | 8.2431 | 1.8061 | 1.8061 | 530.7641 | 1.1649 | 0 | 562.3508 | 0 | 0 | 0 | 1.1649 | 0 | 0 | 562.3508
7 | 7 | 15 | 0 | 0.030833 | 0.030833 | 48 | 7.4212 | 0.029691 | 0.029691 | 532.3603 | 0.030833 | 0 | 14.9345 | 0 | 0 | 0 | 0.030833 | 0 | 0 | 14.9345
7 | 7 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 541.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 546.8007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 543.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 533.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 514.5481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 492.3723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 483.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 7 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 467.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 456.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 449.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 443.2986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 443.1977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 444.0978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 455.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 480.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 7 | 0 | 0.55417 | 0.55417 | 48 | 6.006 | 0.32294 | 0.32294 | 495.6912 | 0.55417 | 0 | 248.0956 | 0 | 0 | 0 | 0.55417 | 0 | 0 | 248.0956
7 | 8 | 8 | 0 | 0.62667 | 0.62667 | 48 | 6.6246 | 0.44137 | 0.44137 | 517.3535 | 0.62667 | 0 | 294.1283 | 0 | 0 | 0 | 0.62667 | 0 | 0 | 294.1283
7 | 8 | 9 | 0 | 2.9533 | 2.9533 | 48 | 7.1924 | 2.5726 | 2.5726 | 523.348 | 2.9533 | 0 | 1403.8614 | 0 | 0 | 0 | 2.9533 | 0 | 0 | 1403.8614
7 | 8 | 10 | 0 | 0.96785 | 0.96785 | 48 | 7.0398 | 0.79264 | 0.79264 | 525.9137 | 0.96785 | 0 | 462.5489 | 0 | 0 | 0 | 0.96785 | 0 | 0 | 462.5489
7 | 8 | 11 | 0 | 1.5623 | 1.5623 | 48 | 7.2093 | 1.3706 | 1.3706 | 534.7655 | 1.5623 | 0 | 760.483 | 0 | 0 | 0 | 1.5623 | 0 | 0 | 760.483
7 | 8 | 12 | 0 | 0.87051 | 0.87051 | 48 | 7.9296 | 1.0949 | 1.0949 | 531.8524 | 0.87051 | 0 | 421.2005 | 0 | 0 | 0 | 0.87051 | 0 | 0 | 421.2005
7 | 8 | 13 | 0 | 0.4942 | 0.4942 | 48 | 8.2601 | 0.77604 | 0.77604 | 528.6246 | 0.4942 | 0 | 237.5269 | 0 | 0 | 0 | 0.4942 | 0 | 0 | 237.5269
7 | 8 | 14 | 0 | 1.9883 | 1.9883 | 48 | 8.5313 | 3.9217 | 3.9217 | 533.9108 | 1.9883 | 0 | 966.1513 | 0 | 0 | 0 | 1.9883 | 0 | 0 | 966.1513
7 | 8 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 534.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 543.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 17 | 0 | 0.21988 | 0.21988 | 48 | 8.6753 | 0.50196 | 0.50196 | 547.6439 | 0.21988 | 0 | 109.8592 | 0 | 0 | 0 | 0.21988 | 0 | 0 | 109.8592
7 | 8 | 18 | 0 | 0.084042 | 0.084042 | 48 | 9.0397 | 0.31884 | 0.31884 | 533.051 | 0.084042 | 0 | 40.7645 | 0 | 0 | 0 | 0.084042 | 0 | 0 | 40.7645
7 | 8 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 523.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 509.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 492.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 473.3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 8 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 462.5155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 454.385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 446.2221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 440.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 433.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 433.7131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 443.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 452.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 7 | 0 | 0.039167 | 0.039167 | 48 | 4.8705 | 0.017333 | 0.017333 | 481.389 | 0.039167 | 0 | 16.9744 | 0 | 0 | 0 | 0.039167 | 0 | 0 | 16.9744
7 | 9 | 8 | 0 | 0.76917 | 0.76917 | 48 | 4.8451 | 0.33857 | 0.33857 | 493.9057 | 0.76917 | 0 | 342.9759 | 0 | 0 | 0 | 0.76917 | 0 | 0 | 342.9759
7 | 9 | 9 | 0 | 3.812 | 3.812 | 48 | 6.3789 | 2.4794 | 2.4794 | 508.5666 | 3.812 | 0 | 1755.6794 | 0 | 0 | 0 | 3.812 | 0 | 0 | 1755.6794
7 | 9 | 10 | 0 | 0.86486 | 0.86486 | 48 | 8.4804 | 1.6277 | 1.6277 | 517.6288 | 0.86486 | 0 | 406.1623 | 0 | 0 | 0 | 0.86486 | 0 | 0 | 406.1623
7 | 9 | 11 | 0 | 1.1653 | 1.1653 | 48 | 9.4549 | 17.9866 | 17.9866 | 531.4547 | 1.1653 | 0 | 563.3893 | 0 | 0 | 0 | 1.1653 | 0 | 0 | 563.3893
7 | 9 | 12 | 0 | 0.63757 | 0.63757 | 48 | 9.8362 | 0 | 0 | 530.8635 | 0 | 0.63757 | 0 | 0.066481 | 0 | 0 | 0 | 0.63757 | 0 | 0
7 | 9 | 13 | 0 | 0.44072 | 0.44072 | 48 | 9.6159 | 0 | 0 | 530.9978 | 0 | 0.44072 | 0 | 0.045955 | 0 | 0 | 0 | 0.44072 | 0 | 0
7 | 9 | 14 | 0 | 49.3837 | 49.3837 | 48 | 9.5227 | 1527.338 | 288 | 526.1281 | 9.312 | 40.0717 | 4452.3078 | 4.1784 | 0 | 0 | 9.312 | 40.0717 | 0 | 4452.3078
7 | 9 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 534.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 538.1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 550.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 544.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 534.8188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 514.2684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 481.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 453.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 9 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 443.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 442.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 444.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 446.5229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 454.6104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 463.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 479.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 488.1773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 508.0591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 8 | 0 | 1.1446 | 1.1446 | 48 | 5.4976 | 0.58416 | 0.58416 | 523.6503 | 1.1446 | 0 | 544.4342 | 0 | 0 | 0 | 1.1446 | 0 | 0 | 544.4342
7 | 10 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 536.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 10 | 0 | 0.27168 | 0.27168 | 48 | 8.5991 | 0.5725 | 0.5725 | 539.3721 | 0.27168 | 0 | 133.4964 | 0 | 0 | 0 | 0.27168 | 0 | 0 | 133.4964
7 | 10 | 11 | 0 | 0.095902 | 0.095902 | 48 | 9.6413 | 0 | 0 | 542.5322 | 0 | 0.095902 | 0 | 0.0099999 | 0 | 0 | 0 | 0.095902 | 0 | 0
7 | 10 | 12 | 0 | 0.43858 | 0.43858 | 48 | 9.7176 | 0 | 0 | 539.2844 | 0 | 0.43858 | 0 | 0.045732 | 0 | 0 | 0 | 0.43858 | 0 | 0
7 | 10 | 13 | 0 | 2.0668 | 2.0668 | 48 | 9.7939 | 0 | 0 | 541.7944 | 0 | 2.0668 | 0 | 0.21551 | 0 | 0 | 0 | 2.0668 | 0 | 0
7 | 10 | 14 | 0 | 0.27705 | 0.27705 | 48 | 9.4634 | 4.5618 | 4.5618 | 542.4972 | 0.27705 | 0 | 137.0004 | 0 | 0 | 0 | 0.27705 | 0 | 0 | 137.0004
7 | 10 | 15 | 0 | 0.0025 | 0.0025 | 48 | 10.5311 | 0 | 0 | 541.5866 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
7 | 10 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 547.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 555.2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 559.4837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 557.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 542.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 522.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 496.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 10 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 488.0884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 474.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 469.3402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 470.7425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 485.9362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 498.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 516.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 537.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 543.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 8 | 0 | 26.4 | 26.4 | 48 | 6.2094 | 16.3101 | 16.3101 | 550.758 | 26.4 | 0 | 13272.8006 | 0 | 0 | 0 | 26.4 | 0 | 0 | 13272.8006
7 | 11 | 9 | 0 | 16.4495 | 16.4495 | 48 | 7.328 | 15.1874 | 15.1874 | 551.8521 | 16.4495 | 0 | 8288.1113 | 0 | 0 | 0 | 16.4495 | 0 | 0 | 8288.1113
7 | 11 | 10 | 0 | 37.2109 | 37.2109 | 48 | 8.5482 | 74.5872 | 74.5872 | 548.0163 | 37.2109 | 0 | 18606.0363 | 0 | 0 | 0 | 37.2109 | 0 | 0 | 18606.0363
7 | 11 | 11 | 0 | 25.4104 | 25.4104 | 48 | 9.1838 | 130.5682 | 130.5682 | 550.166 | 25.4104 | 0 | 12760.2476 | 0 | 0 | 0 | 25.4104 | 0 | 0 | 12760.2476
7 | 11 | 12 | 0 | 17.9597 | 17.9597 | 48 | 9.8701 | 0 | 0 | 550.2976 | 0 | 17.9597 | 0 | 1.8727 | 0 | 0 | 0 | 17.9597 | 0 | 0
7 | 11 | 13 | 0 | 205.6186 | 205.6186 | 48 | 9.6668 | 0 | 0 | 547.5016 | 0 | 205.6186 | 0 | 21.4404 | 0 | 0 | 0 | 205.6186 | 0 | 0
7 | 11 | 14 | 0 | 169.5885 | 169.5885 | 48 | 10.2684 | 0 | 0 | 549.4128 | 0 | 169.5885 | 0 | 17.6834 | 0 | 0 | 0 | 169.5885 | 0 | 0
7 | 11 | 15 | 0 | 20.1857 | 20.1857 | 48 | 11.226 | 0 | 0 | 554.7047 | 0 | 20.1857 | 0 | 2.1048 | 0 | 0 | 0 | 20.1857 | 0 | 0
7 | 11 | 16 | 0 | 0.0025 | 0.0025 | 48 | 11.853 | 0 | 0 | 563.4532 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
7 | 11 | 17 | 0 | 26.578 | 26.578 | 48 | 11.7514 | 0 | 0 | 569.9775 | 0 | 26.578 | 0 | 2.7714 | 0 | 0 | 0 | 26.578 | 0 | 0
7 | 11 | 18 | 0 | 0.60069 | 0.60069 | 48 | 12.4971 | 0 | 0 | 571.8369 | 0 | 0.60069 | 0 | 0.062636 | 0 | 0 | 0 | 0.60069 | 0 | 0
7 | 11 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 575.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 557.9898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 538.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 526.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 11 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 500.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 477.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 471.7886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 476.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 499.5381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 522.8048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 530.8104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 535.9612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 544.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 8 | 0 | 67.3134 | 67.3134 | 48 | 6.2094 | 41.5866 | 41.5866 | 555.1277 | 67.3134 | 0 | 34136.4642 | 0 | 0 | 0 | 67.3134 | 0 | 0 | 34136.4642
7 | 12 | 9 | 0 | 170.346 | 170.346 | 48 | 7.311 | 156.1065 | 156.1065 | 555.6091 | 170.346 | 0 | 86469.1569 | 0 | 0 | 0 | 170.346 | 0 | 0 | 86469.1569
7 | 12 | 10 | 0 | 176.3382 | 176.3382 | 48 | 8.0567 | 240.1779 | 240.1779 | 554.4838 | 176.3382 | 0 | 89312.4553 | 0 | 0 | 0 | 176.3382 | 0 | 0 | 89312.4553
7 | 12 | 11 | 0 | 215.6488 | 215.6488 | 48 | 9.3109 | 1612.2215 | 288 | 553.086 | 38.5225 | 177.1263 | 19457.1924 | 18.4694 | 0 | 0 | 38.5225 | 177.1263 | 0 | 19457.1924
7 | 12 | 12 | 0 | 148.0957 | 148.0957 | 48 | 9.0058 | 529.2694 | 288 | 557.6515 | 80.5858 | 67.51 | 41070.6557 | 7.0394 | 0 | 0 | 80.5858 | 67.51 | 0 | 41070.6557
7 | 12 | 13 | 0 | 66.4047 | 66.4047 | 48 | 8.4889 | 125.9358 | 125.9358 | 559.1488 | 66.4047 | 0 | 33942.6728 | 0 | 0 | 0 | 66.4047 | 0 | 0 | 33942.6728
7 | 12 | 14 | 0 | 21.802 | 21.802 | 48 | 8.938 | 69.8183 | 69.8183 | 556.2869 | 21.802 | 0 | 11081.6689 | 0 | 0 | 0 | 21.802 | 0 | 0 | 11081.6689
7 | 12 | 15 | 0 | 4.2162 | 4.2162 | 48 | 9.6075 | 0 | 0 | 555.7977 | 0 | 4.2162 | 0 | 0.43964 | 0 | 0 | 0 | 4.2162 | 0 | 0
7 | 12 | 16 | 0 | 0.005 | 0.005 | 48 | 10.9718 | 0 | 0 | 560.7344 | 0 | 0.005 | 0 | 0.00052137 | 0 | 0 | 0 | 0.005 | 0 | 0
7 | 12 | 17 | 0 | 0.30654 | 0.30654 | 48 | 10.3786 | 0 | 0 | 567.4801 | 0 | 0.30654 | 0 | 0.031964 | 0 | 0 | 0 | 0.30654 | 0 | 0
7 | 12 | 18 | 0 | 4.931 | 4.931 | 48 | 11.0734 | 0 | 0 | 574.8292 | 0 | 4.931 | 0 | 0.51417 | 0 | 0 | 0 | 4.931 | 0 | 0
7 | 12 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 582.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 573.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 551.3022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 522.6811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 513.7677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 509.2094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 495.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 493.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 512.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 530.6939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 546.4827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 561.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 7 | 0 | 0.90167 | 0.90167 | 48 | 4.6502 | 0.38123 | 0.38123 | 569.1622 | 0.90167 | 0 | 469.9146 | 0 | 0 | 0 | 0.90167 | 0 | 0 | 469.9146
7 | 13 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 569.7568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 9 | 0 | 2.5967 | 2.5967 | 48 | 6.6161 | 1.8236 | 1.8236 | 563.8871 | 2.5967 | 0 | 1339.5869 | 0 | 0 | 0 | 2.5967 | 0 | 0 | 1339.5869
7 | 13 | 10 | 0 | 0.14932 | 0.14932 | 48 | 6.9721 | 0.11912 | 0.11912 | 561.0653 | 0.14932 | 0 | 76.611 | 0 | 0 | 0 | 0.14932 | 0 | 0 | 76.611
7 | 13 | 11 | 0 | 1.4657 | 1.4657 | 48 | 8.5652 | 2.9865 | 2.9865 | 557.4862 | 1.4657 | 0 | 746.7501 | 0 | 0 | 0 | 1.4657 | 0 | 0 | 746.7501
7 | 13 | 12 | 0 | 1.5095 | 1.5095 | 48 | 7.8957 | 1.8606 | 1.8606 | 556.341 | 1.5095 | 0 | 767.3276 | 0 | 0 | 0 | 1.5095 | 0 | 0 | 767.3276
7 | 13 | 13 | 0 | 2.1523 | 2.1523 | 48 | 7.4381 | 2.0889 | 2.0889 | 552.1563 | 2.1523 | 0 | 1085.1114 | 0 | 0 | 0 | 2.1523 | 0 | 0 | 1085.1114
7 | 13 | 14 | 0 | 0.37959 | 0.37959 | 48 | 7.2771 | 0.34276 | 0.34276 | 551.345 | 0.37959 | 0 | 191.0639 | 0 | 0 | 0 | 0.37959 | 0 | 0 | 191.0639
7 | 13 | 15 | 0 | 4.5591 | 4.5591 | 48 | 7.3449 | 4.2411 | 4.2411 | 554.9554 | 4.5591 | 0 | 2311.2528 | 0 | 0 | 0 | 4.5591 | 0 | 0 | 2311.2528
7 | 13 | 16 | 0 | 13.4955 | 13.4955 | 48 | 6.9975 | 10.8718 | 10.8718 | 557.8704 | 13.4955 | 0 | 6880.9337 | 0 | 0 | 0 | 13.4955 | 0 | 0 | 6880.9337
7 | 13 | 17 | 0 | 0.10163 | 0.10163 | 48 | 7.167 | 0.087594 | 0.087594 | 572.3497 | 0.10163 | 0 | 53.287 | 0 | 0 | 0 | 0.10163 | 0 | 0 | 53.287
7 | 13 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 575.4389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 577.7319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 568.254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 553.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 523.9127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 13 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 521.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 509.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 497.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 500.2527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 512.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 528.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 547.4013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 561.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 566.1496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 568.9134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 9 | 0 | 2.7506 | 2.7506 | 48 | 7.3195 | 2.5301 | 2.5301 | 562.862 | 2.7506 | 0 | 1416.2041 | 0 | 0 | 0 | 2.7506 | 0 | 0 | 1416.2041
7 | 14 | 10 | 0 | 0.73804 | 0.73804 | 48 | 7.4805 | 0.73068 | 0.73068 | 558.8209 | 0.73804 | 0 | 377.0087 | 0 | 0 | 0 | 0.73804 | 0 | 0 | 377.0087
7 | 14 | 11 | 0 | 1.9825 | 1.9825 | 48 | 7.2263 | 1.7517 | 1.7517 | 556.93 | 1.9825 | 0 | 1008.9627 | 0 | 0 | 0 | 1.9825 | 0 | 0 | 1008.9627
7 | 14 | 12 | 0 | 1.765 | 1.765 | 48 | 7.8703 | 2.1434 | 2.1434 | 553.7667 | 1.765 | 0 | 892.6547 | 0 | 0 | 0 | 1.765 | 0 | 0 | 892.6547
7 | 14 | 13 | 0 | 1.6838 | 1.6838 | 48 | 8.1754 | 2.4857 | 2.4857 | 551.2619 | 1.6838 | 0 | 847.3825 | 0 | 0 | 0 | 1.6838 | 0 | 0 | 847.3825
7 | 14 | 14 | 0 | 33.106 | 33.106 | 48 | 8.2431 | 51.3317 | 51.3317 | 550.595 | 33.106 | 0 | 16638.9315 | 0 | 0 | 0 | 33.106 | 0 | 0 | 16638.9315
7 | 14 | 15 | 0 | 0.54446 | 0.54446 | 48 | 7.4212 | 0.52429 | 0.52429 | 551.6789 | 0.54446 | 0 | 274.2354 | 0 | 0 | 0 | 0.54446 | 0 | 0 | 274.2354
7 | 14 | 16 | 0 | 0.0025 | 0.0025 | 48 | 7.3195 | 0.0022996 | 0.0022996 | 560.9131 | 0.0025 | 0 | 1.2823 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2823
7 | 14 | 17 | 0 | 0.12988 | 0.12988 | 48 | 7.2686 | 0.11685 | 0.11685 | 559.7421 | 0.12988 | 0 | 66.4625 | 0 | 0 | 0 | 0.12988 | 0 | 0 | 66.4625
7 | 14 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 562.1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 560.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 547.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 524.3838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 507.4114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 14 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 497.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 478.8213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 469.6094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 467.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 469.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 474.7044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 486.7881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 514.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 526.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 540.7568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 9 | 0 | 2.1937 | 2.1937 | 48 | 7.1924 | 1.9108 | 1.9108 | 549.8401 | 2.1937 | 0 | 1100.8674 | 0 | 0 | 0 | 2.1937 | 0 | 0 | 1100.8674
7 | 15 | 10 | 0 | 108.9534 | 108.9534 | 48 | 7.0398 | 89.2299 | 89.2299 | 555.8136 | 108.9534 | 0 | 55328.0289 | 0 | 0 | 0 | 108.9534 | 0 | 0 | 55328.0289
7 | 15 | 11 | 0.051667 | 4.4229 | 4.4745 | 47.5728 | 7.2093 | 3.9254 | 3.9254 | 561.0422 | 4.4745 | 0 | 2297.5423 | 0 | 0 | 0 | 4.4745 | 0 | 0 | 2297.5423
7 | 15 | 12 | 0 | 0.85998 | 0.85998 | 48 | 7.9296 | 1.0817 | 1.0817 | 549.7301 | 0.85998 | 0 | 431.478 | 0 | 0 | 0 | 0.85998 | 0 | 0 | 431.478
7 | 15 | 13 | 0 | 0.034106 | 0.034106 | 48 | 8.2601 | 0.053556 | 0.053556 | 548.5178 | 0.034106 | 0 | 17.0706 | 0 | 0 | 0 | 0.034106 | 0 | 0 | 17.0706
7 | 15 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 548.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 552.0864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 16 | 0 | 0.0016667 | 0.0016667 | 48 | 9.1753 | 0.0083891 | 0.0083891 | 556.4155 | 0.0016667 | 0 | 0.84736 | 0 | 0 | 0 | 0.0016667 | 0 | 0 | 0.84736
7 | 15 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 564.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 556.1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 552.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 532.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 510.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 484.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 15 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 478.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 457.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 457.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 455.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 447.8542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 444.8077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 455.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 483.2802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 494.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 510.5694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 9 | 0 | 2.822 | 2.822 | 48 | 6.3789 | 1.8354 | 1.8354 | 531.9935 | 2.822 | 0 | 1365.818 | 0 | 0 | 0 | 2.822 | 0 | 0 | 1365.818
7 | 16 | 10 | 0 | 1.3784 | 1.3784 | 48 | 8.4804 | 2.5942 | 2.5942 | 550.7661 | 1.3784 | 0 | 693.0339 | 0 | 0 | 0 | 1.3784 | 0 | 0 | 693.0339
7 | 16 | 11 | 0 | 1.4508 | 1.4508 | 48 | 9.4549 | 22.3921 | 22.3921 | 560.0768 | 1.4508 | 0 | 742.9052 | 0 | 0 | 0 | 1.4508 | 0 | 0 | 742.9052
7 | 16 | 12 | 0 | 0.73383 | 0.73383 | 48 | 9.8362 | 0 | 0 | 563.3133 | 0 | 0.73383 | 0 | 0.076519 | 0 | 0 | 0 | 0.73383 | 0 | 0
7 | 16 | 13 | 0 | 1.1533 | 1.1533 | 48 | 9.6159 | 0 | 0 | 556.3764 | 0 | 1.1533 | 0 | 0.12026 | 0 | 0 | 0 | 1.1533 | 0 | 0
7 | 16 | 14 | 0 | 0.36038 | 0.36038 | 48 | 9.5227 | 11.1457 | 11.1457 | 551.6291 | 0.36038 | 0 | 181.4961 | 0 | 0 | 0 | 0.36038 | 0 | 0 | 181.4961
7 | 16 | 15 | 0 | 0.72006 | 0.72006 | 48 | 10.7175 | 0 | 0 | 547.6935 | 0 | 0.72006 | 0 | 0.075083 | 0 | 0 | 0 | 0.72006 | 0 | 0
7 | 16 | 16 | 0 | 0.0058333 | 0.0058333 | 48 | 12.0564 | 0 | 0 | 547.3931 | 0 | 0.0058333 | 0 | 0.00060826 | 0 | 0 | 0 | 0.0058333 | 0 | 0
7 | 16 | 17 | 0 | 0.35654 | 0.35654 | 48 | 11.8107 | 0 | 0 | 557.7271 | 0 | 0.35654 | 0 | 0.037178 | 0 | 0 | 0 | 0.35654 | 0 | 0
7 | 16 | 18 | 0 | 0.87517 | 0.87517 | 48 | 12.3445 | 0 | 0 | 556.7247 | 0 | 0.87517 | 0 | 0.091256 | 0 | 0 | 0 | 0.87517 | 0 | 0
7 | 16 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 555.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 536.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 506.2888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 493.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 16 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 491.6518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 480.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 473.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 479.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 492.0154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 503.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 526.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 545.7775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 7 | 0 | 0.0225 | 0.0225 | 48 | 4.8281 | 0.0098688 | 0.0098688 | 563.3068 | 0.0225 | 0 | 11.5945 | 0 | 0 | 0 | 0.0225 | 0 | 0 | 11.5945
7 | 17 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 570.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 9 | 0 | 3.1121 | 3.1121 | 48 | 6.4043 | 2.0403 | 2.0403 | 566.3155 | 3.1121 | 0 | 1613.0738 | 0 | 0 | 0 | 3.1121 | 0 | 0 | 1613.0738
7 | 17 | 10 | 0 | 226.2727 | 226.2727 | 48 | 8.5991 | 476.8166 | 288 | 556.9182 | 136.6701 | 89.6027 | 69553.8816 | 9.3431 | 0 | 0 | 136.6701 | 89.6027 | 0 | 69553.8816
7 | 17 | 11 | 0 | 366.9428 | 366.9428 | 48 | 9.6413 | 0 | 0 | 557.0512 | 0 | 366.9428 | 0 | 38.2621 | 0 | 0 | 0 | 366.9428 | 0 | 0
7 | 17 | 12 | 0 | 258.2713 | 258.2713 | 48 | 9.7176 | 0 | 0 | 556.3763 | 0 | 258.2713 | 0 | 26.9306 | 0 | 0 | 0 | 258.2713 | 0 | 0
7 | 17 | 13 | 0 | 193.5993 | 193.5993 | 48 | 9.7939 | 0 | 0 | 553.3358 | 0 | 193.5993 | 0 | 20.1871 | 0 | 0 | 0 | 193.5993 | 0 | 0
7 | 17 | 14 | 0 | 37.5969 | 37.5969 | 48 | 9.4634 | 619.059 | 288 | 554.1366 | 17.4909 | 20.106 | 8852.793 | 2.0965 | 0 | 0 | 17.4909 | 20.106 | 0 | 8852.793
7 | 17 | 15 | 0 | 4.9589 | 4.9589 | 48 | 10.5311 | 0 | 0 | 555.748 | 0 | 4.9589 | 0 | 0.51708 | 0 | 0 | 0 | 4.9589 | 0 | 0
7 | 17 | 16 | 0 | 10.3315 | 10.3315 | 48 | 11.0904 | 0 | 0 | 560.6302 | 0 | 10.3315 | 0 | 1.0773 | 0 | 0 | 0 | 10.3315 | 0 | 0
7 | 17 | 17 | 0 | 0.37237 | 0.37237 | 48 | 11.1073 | 0 | 0 | 570.0929 | 0 | 0.37237 | 0 | 0.038829 | 0 | 0 | 0 | 0.37237 | 0 | 0
7 | 17 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 573.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 571.6806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 557.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 534.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 516.8871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 17 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 495.2849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 485.5426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 478.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 480.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 496.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 511.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 526.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 546.2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 7 | 0 | 0.0025 | 0.0025 | 48 | 5.2518 | 0.0012036 | 0.0012036 | 558.6005 | 0.0025 | 0 | 1.2765 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2765
7 | 18 | 8 | 0 | 12.4872 | 12.4872 | 48 | 6.2094 | 7.7147 | 7.7147 | 566.1807 | 12.4872 | 0 | 6470.6376 | 0 | 0 | 0 | 12.4872 | 0 | 0 | 6470.6376
7 | 18 | 9 | 0 | 0.21707 | 0.21707 | 48 | 7.328 | 0.20041 | 0.20041 | 558.7177 | 0.21707 | 0 | 110.8602 | 0 | 0 | 0 | 0.21707 | 0 | 0 | 110.8602
7 | 18 | 10 | 0 | 73.497 | 73.497 | 48 | 8.5482 | 147.3208 | 147.3208 | 555.9508 | 73.497 | 0 | 37332.8609 | 0 | 0 | 0 | 73.497 | 0 | 0 | 37332.8609
7 | 18 | 11 | 0 | 119.1447 | 119.1447 | 48 | 9.1838 | 612.2098 | 288 | 555.509 | 56.0489 | 63.0958 | 28445.31 | 6.5792 | 0 | 0 | 56.0489 | 63.0958 | 0 | 28445.31
7 | 18 | 12 | 0 | 67.4393 | 67.4393 | 48 | 9.8701 | 0 | 0 | 551.9503 | 0 | 67.4393 | 0 | 7.0321 | 0 | 0 | 0 | 67.4393 | 0 | 0
7 | 18 | 13 | 0 | 117.3944 | 117.3944 | 48 | 9.6668 | 0 | 0 | 549.872 | 0 | 117.3944 | 0 | 12.241 | 0 | 0 | 0 | 117.3944 | 0 | 0
7 | 18 | 14 | 0 | 247.6357 | 247.6357 | 48 | 10.2684 | 0 | 0 | 550.643 | 0 | 247.6357 | 0 | 25.8216 | 0 | 0 | 0 | 247.6357 | 0 | 0
7 | 18 | 15 | 0 | 182.0796 | 182.0796 | 48 | 11.226 | 0 | 0 | 549.7938 | 0 | 182.0796 | 0 | 18.9859 | 0 | 0 | 0 | 182.0796 | 0 | 0
7 | 18 | 16 | 0 | 120.9169 | 120.9169 | 48 | 11.853 | 0 | 0 | 552.3764 | 0 | 120.9169 | 0 | 12.6083 | 0 | 0 | 0 | 120.9169 | 0 | 0
7 | 18 | 17 | 0 | 13.1619 | 13.1619 | 48 | 11.7514 | 0 | 0 | 560.376 | 0 | 13.1619 | 0 | 1.3724 | 0 | 0 | 0 | 13.1619 | 0 | 0
7 | 18 | 18 | 0 | 55.2892 | 55.2892 | 48 | 12.4971 | 0 | 0 | 566.797 | 0 | 55.2892 | 0 | 5.7652 | 0 | 0 | 0 | 55.2892 | 0 | 0
7 | 18 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 569.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 20 | 3.9501 | 0 | 3.9501 | 11 | 12.2259 | 0 | 0 | 567.6403 | 0 | 3.9501 | 0 | 0.41189 | 0 | 0 | 0 | 3.9501 | 0 | 0
7 | 18 | 21 | 11.3704 | 0 | 11.3704 | 11 | 9.904 | 0 | 0 | 559.6112 | 0 | 11.3704 | 0 | 1.1856 | 0 | 0 | 0 | 11.3704 | 0 | 0
7 | 18 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 548.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 18 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 531.0157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 514.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 503.2713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 501.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 513.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 530.6595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 543.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 6 | 0 | 0.076208 | 0.076208 | 48 | 4.8366 | 0.033485 | 0.033485 | 556.8483 | 0.076208 | 0 | 38.7785 | 0 | 0 | 0 | 0.076208 | 0 | 0 | 38.7785
7 | 19 | 7 | 0 | 0.020833 | 0.020833 | 48 | 5.0146 | 0.0095101 | 0.0095101 | 563.3518 | 0.020833 | 0 | 10.7365 | 0 | 0 | 0 | 0.020833 | 0 | 0 | 10.7365
7 | 19 | 8 | 0 | 0.21583 | 0.21583 | 48 | 6.2094 | 0.13334 | 0.13334 | 562.415 | 0.21583 | 0 | 111.0279 | 0 | 0 | 0 | 0.21583 | 0 | 0 | 111.0279
7 | 19 | 9 | 0 | 0.22664 | 0.22664 | 48 | 7.311 | 0.20769 | 0.20769 | 561.4839 | 0.22664 | 0 | 116.3747 | 0 | 0 | 0 | 0.22664 | 0 | 0 | 116.3747
7 | 19 | 10 | 0 | 1.1128 | 1.1128 | 48 | 8.0567 | 1.5157 | 1.5157 | 548.8516 | 1.1128 | 0 | 557.3534 | 0 | 0 | 0 | 1.1128 | 0 | 0 | 557.3534
7 | 19 | 11 | 0 | 2.0331 | 2.0331 | 48 | 9.3109 | 15.2 | 15.2 | 545.3448 | 2.0331 | 0 | 1011.1668 | 0 | 0 | 0 | 2.0331 | 0 | 0 | 1011.1668
7 | 19 | 12 | 0 | 2.3075 | 2.3075 | 48 | 9.0058 | 8.2465 | 8.2465 | 543.2067 | 2.3075 | 0 | 1142.6683 | 0 | 0 | 0 | 2.3075 | 0 | 0 | 1142.6683
7 | 19 | 13 | 0 | 0.12167 | 0.12167 | 48 | 8.4889 | 0.23074 | 0.23074 | 545.0037 | 0.12167 | 0 | 60.4688 | 0 | 0 | 0 | 0.12167 | 0 | 0 | 60.4688
7 | 19 | 14 | 0.018333 | 8.44 | 8.4583 | 47.9198 | 8.938 | 27.0868 | 27.0868 | 549.3806 | 8.4583 | 0 | 4241.5224 | 0 | 0 | 0 | 8.4583 | 0 | 0 | 4241.5224
7 | 19 | 15 | 0 | 3.6406 | 3.6406 | 48 | 9.6075 | 0 | 0 | 551.0529 | 0 | 3.6406 | 0 | 0.37962 | 0 | 0 | 0 | 3.6406 | 0 | 0
7 | 19 | 16 | 0 | 1.4413 | 1.4413 | 48 | 10.9718 | 0 | 0 | 554.364 | 0 | 1.4413 | 0 | 0.15029 | 0 | 0 | 0 | 1.4413 | 0 | 0
7 | 19 | 17 | 0 | 0.28321 | 0.28321 | 48 | 10.3786 | 0 | 0 | 558.9591 | 0 | 0.28321 | 0 | 0.029531 | 0 | 0 | 0 | 0.28321 | 0 | 0
7 | 19 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 563.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 564.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 564.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 556.1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 554.3468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 538.5963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 524.0206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 511.2492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 505.424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 516.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 527.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 542.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 6 | 0 | 0.0087083 | 0.0087083 | 48 | 4.396 | 0.0035018 | 0.0035018 | 559.1238 | 0.0087083 | 0 | 4.451 | 0 | 0 | 0 | 0.0087083 | 0 | 0 | 4.451
7 | 20 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 564.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 561.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 9 | 0 | 0.031614 | 0.031614 | 48 | 6.6161 | 0.022203 | 0.022203 | 551.6206 | 0.031614 | 0 | 15.9215 | 0 | 0 | 0 | 0.031614 | 0 | 0 | 15.9215
7 | 20 | 10 | 0 | 14.5636 | 14.5636 | 48 | 6.9721 | 11.6184 | 11.6184 | 542.7807 | 14.5636 | 0 | 7205.8068 | 0 | 0 | 0 | 14.5636 | 0 | 0 | 7205.8068
7 | 20 | 11 | 0.035 | 15.4273 | 15.4623 | 47.9162 | 8.5652 | 31.5058 | 31.5058 | 545.4678 | 15.4623 | 0 | 7693.3097 | 0 | 0 | 0 | 15.4623 | 0 | 0 | 7693.3097
7 | 20 | 12 | 0 | 9.8053 | 9.8053 | 48 | 7.8957 | 12.0862 | 12.0862 | 548.807 | 9.8053 | 0 | 4910.5836 | 0 | 0 | 0 | 9.8053 | 0 | 0 | 4910.5836
7 | 20 | 13 | 0 | 0.63768 | 0.63768 | 48 | 7.4381 | 0.61889 | 0.61889 | 549.7852 | 0.63768 | 0 | 319.9773 | 0 | 0 | 0 | 0.63768 | 0 | 0 | 319.9773
7 | 20 | 14 | 0 | 4.5456 | 4.5456 | 48 | 7.2771 | 4.1046 | 4.1046 | 550.8893 | 4.5456 | 0 | 2285.9206 | 0 | 0 | 0 | 4.5456 | 0 | 0 | 2285.9206
7 | 20 | 15 | 0 | 0.048206 | 0.048206 | 48 | 7.3449 | 0.044843 | 0.044843 | 555.5622 | 0.048206 | 0 | 24.4675 | 0 | 0 | 0 | 0.048206 | 0 | 0 | 24.4675
7 | 20 | 16 | 0 | 0.016667 | 0.016667 | 48 | 6.9975 | 0.013426 | 0.013426 | 558.6265 | 0.016667 | 0 | 8.5104 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 8.5104
7 | 20 | 17 | 0 | 0.44988 | 0.44988 | 48 | 7.167 | 0.38776 | 0.38776 | 561.7506 | 0.44988 | 0 | 231.1235 | 0 | 0 | 0 | 0.44988 | 0 | 0 | 231.1235
7 | 20 | 18 | 0 | 2.9718 | 2.9718 | 48 | 6.7094 | 2.1546 | 2.1546 | 562.1091 | 2.9718 | 0 | 1527.8135 | 0 | 0 | 0 | 2.9718 | 0 | 0 | 1527.8135
7 | 20 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 571.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 570.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 21 | 1.8908 | 0 | 1.8908 | 11 | 6.1924 | 1.1623 | 1.1623 | 564.6413 | 1.8908 | 0 | 1046.8363 | 0 | 0 | 0 | 1.8908 | 0 | 0 | 1046.8363
7 | 20 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 554.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 20 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 537.5193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 520.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 508.188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 505.7227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 520.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 534.3271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 551.6142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 559.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 7 | 0 | 0.0025 | 0.0025 | 48 | 6.1924 | 0.0015368 | 0.0015368 | 566.1256 | 0.0025 | 0 | 1.2953 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2953
7 | 21 | 8 | 0 | 14.8487 | 14.8487 | 48 | 6.8788 | 11.4386 | 11.4386 | 566.9796 | 14.8487 | 0 | 7706.193 | 0 | 0 | 0 | 14.8487 | 0 | 0 | 7706.193
7 | 21 | 9 | 0 | 90.7178 | 90.7178 | 48 | 7.3195 | 83.4448 | 83.4448 | 559.8172 | 90.7178 | 0 | 46430.9485 | 0 | 0 | 0 | 90.7178 | 0 | 0 | 46430.9485
7 | 21 | 10 | 0.89 | 288.6844 | 289.5744 | 47.8863 | 7.4805 | 286.6857 | 286.6857 | 555.4984 | 289.5744 | 0 | 146991.4714 | 0 | 0 | 0 | 289.5744 | 0 | 0 | 146991.4714
7 | 21 | 11 | 0 | 145.2544 | 145.2544 | 48 | 7.2263 | 128.3408 | 128.3408 | 553.5894 | 145.2544 | 0 | 73439.083 | 0 | 0 | 0 | 145.2544 | 0 | 0 | 73439.083
7 | 21 | 12 | 0 | 159.0593 | 159.0593 | 48 | 7.8703 | 193.1613 | 193.1613 | 553.8169 | 159.0593 | 0 | 80454.8748 | 0 | 0 | 0 | 159.0593 | 0 | 0 | 80454.8748
7 | 21 | 13 | 0 | 272.7393 | 272.7393 | 48 | 8.1754 | 402.6266 | 288 | 552.7348 | 195.0912 | 77.648 | 98469.3187 | 8.0966 | 0 | 0 | 195.0912 | 77.648 | 0 | 98469.3187
7 | 21 | 14 | 0 | 201.8183 | 201.8183 | 48 | 8.2431 | 312.9239 | 288 | 549.6926 | 185.7438 | 16.0745 | 93186.313 | 1.6761 | 0 | 0 | 185.7438 | 16.0745 | 0 | 93186.313
7 | 21 | 15 | 0 | 36.7378 | 36.7378 | 48 | 7.4212 | 35.3766 | 35.3766 | 551.844 | 36.7378 | 0 | 18510.0987 | 0 | 0 | 0 | 36.7378 | 0 | 0 | 18510.0987
7 | 21 | 16 | 0 | 6.5217 | 6.5217 | 48 | 7.3195 | 5.9988 | 5.9988 | 553.4056 | 6.5217 | 0 | 3296.0822 | 0 | 0 | 0 | 6.5217 | 0 | 0 | 3296.0822
7 | 21 | 17 | 0 | 27.1515 | 27.1515 | 48 | 7.2686 | 24.4278 | 24.4278 | 559.1285 | 27.1515 | 0 | 13877.9106 | 0 | 0 | 0 | 27.1515 | 0 | 0 | 13877.9106
7 | 21 | 18 | 0 | 0.21062 | 0.21062 | 48 | 6.9297 | 0.16535 | 0.16535 | 566.3142 | 0.21062 | 0 | 109.1699 | 0 | 0 | 0 | 0.21062 | 0 | 0 | 109.1699
7 | 21 | 19 | 0 | 5.4308 | 5.4308 | 48 | 6.9382 | 4.2772 | 4.2772 | 571.7086 | 5.4308 | 0 | 2844.1744 | 0 | 0 | 0 | 5.4308 | 0 | 0 | 2844.1744
7 | 21 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 568.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 560.0493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 540.8433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 21 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 525.6619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 517.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 509.2965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 498.2249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 498.9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 502.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 519.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 6 | 0 | 0.13704 | 0.13704 | 48 | 4.4638 | 0.055836 | 0.055836 | 527.6634 | 0.13704 | 0 | 65.7339 | 0 | 0 | 0 | 0.13704 | 0 | 0 | 65.7339
7 | 22 | 7 | 0 | 0.032458 | 0.032458 | 48 | 6.006 | 0.018915 | 0.018915 | 541.6162 | 0.032458 | 0 | 16.022 | 0 | 0 | 0 | 0.032458 | 0 | 0 | 16.022
7 | 22 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 540.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 9 | 0 | 24.8333 | 24.8333 | 48 | 7.1924 | 21.6315 | 21.6315 | 550.649 | 24.8333 | 0 | 12482.4354 | 0 | 0 | 0 | 24.8333 | 0 | 0 | 12482.4354
7 | 22 | 10 | 0 | 23.715 | 23.715 | 48 | 7.0398 | 19.422 | 19.422 | 553.1753 | 23.715 | 0 | 11980.2368 | 0 | 0 | 0 | 23.715 | 0 | 0 | 11980.2368
7 | 22 | 11 | 0 | 59.6264 | 59.6264 | 48 | 7.2093 | 52.3084 | 52.3084 | 550.8786 | 59.6264 | 0 | 29984.843 | 0 | 0 | 0 | 59.6264 | 0 | 0 | 29984.843
7 | 22 | 12 | 0 | 199.6933 | 199.6933 | 48 | 7.9296 | 251.1696 | 251.1696 | 550.6038 | 199.6933 | 0 | 100366.6101 | 0 | 0 | 0 | 199.6933 | 0 | 0 | 100366.6101
7 | 22 | 13 | 0 | 118.838 | 118.838 | 48 | 8.2601 | 186.6087 | 186.6087 | 546.5276 | 118.838 | 0 | 59244.0226 | 0 | 0 | 0 | 118.838 | 0 | 0 | 59244.0226
7 | 22 | 14 | 0 | 75.0808 | 75.0808 | 48 | 8.5313 | 148.0869 | 148.0869 | 549.173 | 75.0808 | 0 | 37628.4658 | 0 | 0 | 0 | 75.0808 | 0 | 0 | 37628.4658
7 | 22 | 15 | 0 | 83.3674 | 83.3674 | 48 | 8.4041 | 146.8096 | 146.8096 | 550.9789 | 83.3674 | 0 | 41932.0286 | 0 | 0 | 0 | 83.3674 | 0 | 0 | 41932.0286
7 | 22 | 16 | 0 | 5.0734 | 5.0734 | 48 | 9.1753 | 25.5367 | 25.5367 | 552.4098 | 5.0734 | 0 | 2559.0774 | 0 | 0 | 0 | 5.0734 | 0 | 0 | 2559.0774
7 | 22 | 17 | 0 | 7.9985 | 7.9985 | 48 | 8.6753 | 18.26 | 18.26 | 553.3754 | 7.9985 | 0 | 4042.2545 | 0 | 0 | 0 | 7.9985 | 0 | 0 | 4042.2545
7 | 22 | 18 | 0 | 2.3938 | 2.3938 | 48 | 9.0397 | 9.0818 | 9.0818 | 558.2784 | 2.3938 | 0 | 1221.5167 | 0 | 0 | 0 | 2.3938 | 0 | 0 | 1221.5167
7 | 22 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 565.7359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 558.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 541.5684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 520.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 22 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 511.9254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 499.4402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 495.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 485.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 483.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 482.9669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 492.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 6 | 0 | 0.13204 | 0.13204 | 48 | 4.1926 | 0.051096 | 0.051096 | 512.2351 | 0.13204 | 0 | 61.2984 | 0 | 0 | 0 | 0.13204 | 0 | 0 | 61.2984
7 | 23 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 524.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 8 | 0 | 0.97087 | 0.97087 | 48 | 4.8451 | 0.42735 | 0.42735 | 540.8259 | 0.97087 | 0 | 478.4686 | 0 | 0 | 0 | 0.97087 | 0 | 0 | 478.4686
7 | 23 | 9 | 0 | 0.34486 | 0.34486 | 48 | 6.3789 | 0.2243 | 0.2243 | 548.3679 | 0.34486 | 0 | 172.5548 | 0 | 0 | 0 | 0.34486 | 0 | 0 | 172.5548
7 | 23 | 10 | 0 | 2.605 | 2.605 | 48 | 8.4804 | 4.9026 | 4.9026 | 549.8904 | 2.605 | 0 | 1307.4227 | 0 | 0 | 0 | 2.605 | 0 | 0 | 1307.4227
7 | 23 | 11 | 0 | 2.4383 | 2.4383 | 48 | 9.4549 | 37.6349 | 37.6349 | 542.3884 | 2.4383 | 0 | 1205.4875 | 0 | 0 | 0 | 2.4383 | 0 | 0 | 1205.4875
7 | 23 | 12 | 0 | 1.6246 | 1.6246 | 48 | 9.8362 | 0 | 0 | 539.4277 | 0 | 1.6246 | 0 | 0.1694 | 0 | 0 | 0 | 1.6246 | 0 | 0
7 | 23 | 13 | 0 | 2.5053 | 2.5053 | 48 | 9.6159 | 0 | 0 | 536.0271 | 0 | 2.5053 | 0 | 0.26124 | 0 | 0 | 0 | 2.5053 | 0 | 0
7 | 23 | 14 | 0 | 2.0624 | 2.0624 | 48 | 9.5227 | 63.7865 | 63.7865 | 537.6505 | 2.0624 | 0 | 1009.8654 | 0 | 0 | 0 | 2.0624 | 0 | 0 | 1009.8654
7 | 23 | 15 | 0 | 0.88991 | 0.88991 | 48 | 10.7175 | 0 | 0 | 534.9728 | 0 | 0.88991 | 0 | 0.092793 | 0 | 0 | 0 | 0.88991 | 0 | 0
7 | 23 | 16 | 0 | 0.85269 | 0.85269 | 48 | 12.0564 | 0 | 0 | 542.2165 | 0 | 0.85269 | 0 | 0.088912 | 0 | 0 | 0 | 0.85269 | 0 | 0
7 | 23 | 17 | 0 | 0.40225 | 0.40225 | 48 | 11.8107 | 0 | 0 | 550.1451 | 0 | 0.40225 | 0 | 0.041944 | 0 | 0 | 0 | 0.40225 | 0 | 0
7 | 23 | 18 | 0 | 0.032458 | 0.032458 | 48 | 12.3445 | 0 | 0 | 546.2054 | 0 | 0.032458 | 0 | 0.0033845 | 0 | 0 | 0 | 0.032458 | 0 | 0
7 | 23 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 548.2499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 539.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 518.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 502.4042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 23 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 473.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 464.5783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 463.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 469.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 481.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 504.3056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 515.0384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 6 | 0 | 0.026208 | 0.026208 | 48 | 4.4722 | 0.010696 | 0.010696 | 526.433 | 0.026208 | 0 | 12.5389 | 0 | 0 | 0 | 0.026208 | 0 | 0 | 12.5389
7 | 24 | 7 | 0 | 0.044958 | 0.044958 | 48 | 4.8281 | 0.019719 | 0.019719 | 541.5245 | 0.044958 | 0 | 22.188 | 0 | 0 | 0 | 0.044958 | 0 | 0 | 22.188
7 | 24 | 8 | 0 | 0.077212 | 0.077212 | 48 | 5.4976 | 0.039405 | 0.039405 | 543.4182 | 0.077212 | 0 | 38.252 | 0 | 0 | 0 | 0.077212 | 0 | 0 | 38.252
7 | 24 | 9 | 0 | 1.6367 | 1.6367 | 48 | 6.4043 | 1.073 | 1.073 | 535.0957 | 1.6367 | 0 | 797.2226 | 0 | 0 | 0 | 1.6367 | 0 | 0 | 797.2226
7 | 24 | 10 | 0 | 1.1214 | 1.1214 | 48 | 8.5991 | 2.3631 | 2.3631 | 538.5155 | 1.1214 | 0 | 550.0626 | 0 | 0 | 0 | 1.1214 | 0 | 0 | 550.0626
7 | 24 | 11 | 0 | 1.489 | 1.489 | 48 | 9.6413 | 0 | 0 | 534.4953 | 0 | 1.489 | 0 | 0.15526 | 0 | 0 | 0 | 1.489 | 0 | 0
7 | 24 | 12 | 0 | 1.3196 | 1.3196 | 48 | 9.7176 | 0 | 0 | 538.0306 | 0 | 1.3196 | 0 | 0.1376 | 0 | 0 | 0 | 1.3196 | 0 | 0
7 | 24 | 13 | 0 | 2.0708 | 2.0708 | 48 | 9.7939 | 0 | 0 | 538.6274 | 0 | 2.0708 | 0 | 0.21593 | 0 | 0 | 0 | 2.0708 | 0 | 0
7 | 24 | 14 | 0 | 1.713 | 1.713 | 48 | 9.4634 | 28.2057 | 28.2057 | 538.3954 | 1.713 | 0 | 840.0476 | 0 | 0 | 0 | 1.713 | 0 | 0 | 840.0476
7 | 24 | 15 | 0 | 0.24454 | 0.24454 | 48 | 10.5311 | 0 | 0 | 541.7601 | 0 | 0.24454 | 0 | 0.025499 | 0 | 0 | 0 | 0.24454 | 0 | 0
7 | 24 | 16 | 0 | 0.015833 | 0.015833 | 48 | 11.0904 | 0 | 0 | 545.3565 | 0 | 0.015833 | 0 | 0.001651 | 0 | 0 | 0 | 0.015833 | 0 | 0
7 | 24 | 17 | 0 | 0.92508 | 0.92508 | 48 | 11.1073 | 0 | 0 | 546.8761 | 0 | 0.92508 | 0 | 0.096461 | 0 | 0 | 0 | 0.92508 | 0 | 0
7 | 24 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 546.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 531.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 516.5297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 491.9361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 481.4189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 24 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 479.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 466.5518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 463.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 469.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 486.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 493.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 506.4864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 6 | 2.5292 | 0.044542 | 2.5737 | 11.6403 | 5.0061 | 1.1727 | 1.1727 | 514.3534 | 2.5737 | 0 | 1293.8369 | 0 | 0 | 0 | 2.5737 | 0 | 0 | 1293.8369
7 | 25 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 523.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 8 | 0 | 0.0083334 | 0.0083334 | 48 | 6.2094 | 0.0051484 | 0.0051484 | 525.4902 | 0.0083334 | 0 | 3.9791 | 0 | 0 | 0 | 0.0083334 | 0 | 0 | 3.9791
7 | 25 | 9 | 0 | 26.1483 | 26.1483 | 48 | 7.328 | 24.142 | 24.142 | 535.1033 | 26.1483 | 0 | 12736.9109 | 0 | 0 | 0 | 26.1483 | 0 | 0 | 12736.9109
7 | 25 | 10 | 0 | 0.21048 | 0.21048 | 48 | 8.5482 | 0.4219 | 0.4219 | 532.6655 | 0.21048 | 0 | 102.0142 | 0 | 0 | 0 | 0.21048 | 0 | 0 | 102.0142
7 | 25 | 11 | 0 | 39.8797 | 39.8797 | 48 | 9.1838 | 204.9169 | 204.9169 | 531.1898 | 39.8797 | 0 | 19269.4755 | 0 | 0 | 0 | 39.8797 | 0 | 0 | 19269.4755
7 | 25 | 12 | 0 | 78.8117 | 78.8117 | 48 | 9.8701 | 0 | 0 | 530.9164 | 0 | 78.8117 | 0 | 8.2179 | 0 | 0 | 0 | 78.8117 | 0 | 0
7 | 25 | 13 | 0 | 142.8073 | 142.8073 | 48 | 9.6668 | 0 | 0 | 531.3679 | 0 | 142.8073 | 0 | 14.8909 | 0 | 0 | 0 | 142.8073 | 0 | 0
7 | 25 | 14 | 0 | 0.79978 | 0.79978 | 48 | 10.2684 | 0 | 0 | 533.4562 | 0 | 0.79978 | 0 | 0.083395 | 0 | 0 | 0 | 0.79978 | 0 | 0
7 | 25 | 15 | 0 | 40.5721 | 40.5721 | 48 | 11.226 | 0 | 0 | 531.0635 | 0 | 40.5721 | 0 | 4.2306 | 0 | 0 | 0 | 40.5721 | 0 | 0
7 | 25 | 16 | 0 | 13.7659 | 13.7659 | 48 | 11.853 | 0 | 0 | 530.5083 | 0 | 13.7659 | 0 | 1.4354 | 0 | 0 | 0 | 13.7659 | 0 | 0
7 | 25 | 17 | 0 | 0.48904 | 0.48904 | 48 | 11.7514 | 0 | 0 | 541.2238 | 0 | 0.48904 | 0 | 0.050994 | 0 | 0 | 0 | 0.48904 | 0 | 0
7 | 25 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 544.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 539.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 518.0339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 489.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 462.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 25 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 447.5531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 446.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 441.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 445.4875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 459.2596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 475.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 488.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 6 | 0 | 0.10037 | 0.10037 | 48 | 4.8366 | 0.044104 | 0.044104 | 491.7182 | 0.10037 | 0 | 44.5382 | 0 | 0 | 0 | 0.10037 | 0 | 0 | 44.5382
7 | 26 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 512.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 8 | 0 | 9.1643 | 9.1643 | 48 | 6.2094 | 5.6618 | 5.6618 | 525.792 | 9.1643 | 0 | 4378.642 | 0 | 0 | 0 | 9.1643 | 0 | 0 | 4378.642
7 | 26 | 9 | 0 | 8.9263 | 8.9263 | 48 | 7.311 | 8.1801 | 8.1801 | 538.76 | 8.9263 | 0 | 4380.6491 | 0 | 0 | 0 | 8.9263 | 0 | 0 | 4380.6491
7 | 26 | 10 | 0.3875 | 0.010833 | 0.39833 | 12.0063 | 8.0567 | 0.54254 | 0.54254 | 536.4775 | 0.39833 | 0 | 208.9144 | 0 | 0 | 0 | 0.39833 | 0 | 0 | 208.9144
7 | 26 | 11 | 0.016615 | 0.39344 | 0.41005 | 46.5008 | 9.3109 | 3.0656 | 3.0656 | 531.3426 | 0.41005 | 0 | 198.8105 | 0 | 0 | 0 | 0.41005 | 0 | 0 | 198.8105
7 | 26 | 12 | 0 | 1.5876 | 1.5876 | 48 | 9.0058 | 5.674 | 5.674 | 531.7554 | 1.5876 | 0 | 768.0303 | 0 | 0 | 0 | 1.5876 | 0 | 0 | 768.0303
7 | 26 | 13 | 0 | 0.49437 | 0.49437 | 48 | 8.4889 | 0.93757 | 0.93757 | 529.4852 | 0.49437 | 0 | 238.0314 | 0 | 0 | 0 | 0.49437 | 0 | 0 | 238.0314
7 | 26 | 14 | 0 | 0.020833 | 0.020833 | 48 | 8.938 | 0.066716 | 0.066716 | 530.5077 | 0.020833 | 0 | 10.0522 | 0 | 0 | 0 | 0.020833 | 0 | 0 | 10.0522
7 | 26 | 15 | 0 | 0 | 0 | 0 | 9.6075 | 0 | 0 | 532.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 16 | 0 | 0.56492 | 0.56492 | 48 | 10.9718 | 0 | 0 | 537.6455 | 0 | 0.56492 | 0 | 0.058905 | 0 | 0 | 0 | 0.56492 | 0 | 0
7 | 26 | 17 | 0 | 0.80138 | 0.80138 | 48 | 10.3786 | 0 | 0 | 538.9075 | 0 | 0.80138 | 0 | 0.083561 | 0 | 0 | 0 | 0.80138 | 0 | 0
7 | 26 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 543.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 545.5073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 527.6029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 516.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 495.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 26 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 486.4267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 480.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 474.4974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 479.3701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 491.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 507.4459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 514.2775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 6 | 0 | 0.11704 | 0.11704 | 48 | 4.396 | 0.047065 | 0.047065 | 526.7021 | 0.11704 | 0 | 56.0281 | 0 | 0 | 0 | 0.11704 | 0 | 0 | 56.0281
7 | 27 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 539.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 8 | 0 | 0.016667 | 0.016667 | 48 | 5.1417 | 0.0078254 | 0.0078254 | 547.3586 | 0.016667 | 0 | 8.3227 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 8.3227
7 | 27 | 9 | 0 | 0.014167 | 0.014167 | 48 | 6.6161 | 0.0099493 | 0.0099493 | 533.6636 | 0.014167 | 0 | 6.8803 | 0 | 0 | 0 | 0.014167 | 0 | 0 | 6.8803
7 | 27 | 10 | 0 | 0.2375 | 0.2375 | 48 | 6.9721 | 0.18947 | 0.18947 | 535.2917 | 0.2375 | 0 | 115.7318 | 0 | 0 | 0 | 0.2375 | 0 | 0 | 115.7318
7 | 27 | 11 | 0 | 0.64771 | 0.64771 | 48 | 8.5652 | 1.3198 | 1.3198 | 536.1929 | 0.64771 | 0 | 316.2058 | 0 | 0 | 0 | 0.64771 | 0 | 0 | 316.2058
7 | 27 | 12 | 0 | 6.008 | 6.008 | 48 | 7.8957 | 7.4056 | 7.4056 | 534.4164 | 6.008 | 0 | 2922.4134 | 0 | 0 | 0 | 6.008 | 0 | 0 | 2922.4134
7 | 27 | 13 | 0 | 0.44 | 0.44 | 48 | 7.4381 | 0.42703 | 0.42703 | 530.3443 | 0.44 | 0 | 212.2298 | 0 | 0 | 0 | 0.44 | 0 | 0 | 212.2298
7 | 27 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 532.2306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 15 | 0 | 0.53205 | 0.53205 | 48 | 7.3449 | 0.49493 | 0.49493 | 533.0262 | 0.53205 | 0 | 258.0565 | 0 | 0 | 0 | 0.53205 | 0 | 0 | 258.0565
7 | 27 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 532.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 17 | 0 | 0.49321 | 0.49321 | 48 | 7.167 | 0.42511 | 0.42511 | 543.4991 | 0.49321 | 0 | 244.3843 | 0 | 0 | 0 | 0.49321 | 0 | 0 | 244.3843
7 | 27 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 543.8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 544.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 529.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 509.8782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 480.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 27 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 469.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 459.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 452.7226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 458.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 474.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 484.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 500.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 6 | 0 | 0.12287 | 0.12287 | 48 | 4.6163 | 0.051599 | 0.051599 | 516.3548 | 0.12287 | 0 | 57.5491 | 0 | 0 | 0 | 0.12287 | 0 | 0 | 57.5491
7 | 28 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 525.1985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 8 | 0 | 0.02 | 0.02 | 48 | 6.8788 | 0.015407 | 0.015407 | 526.3406 | 0.02 | 0 | 9.5668 | 0 | 0 | 0 | 0.02 | 0 | 0 | 9.5668
7 | 28 | 9 | 0 | 0.0175 | 0.0175 | 48 | 7.3195 | 0.016097 | 0.016097 | 519.6938 | 0.0175 | 0 | 8.2547 | 0 | 0 | 0 | 0.0175 | 0 | 0 | 8.2547
7 | 28 | 10 | 0 | 2.2962 | 2.2962 | 48 | 7.4805 | 2.2733 | 2.2733 | 517.4024 | 2.2962 | 0 | 1077.8473 | 0 | 0 | 0 | 2.2962 | 0 | 0 | 1077.8473
7 | 28 | 11 | 0 | 80.4778 | 80.4778 | 48 | 7.2263 | 71.1069 | 71.1069 | 514.7173 | 80.4778 | 0 | 37560.376 | 0 | 0 | 0 | 80.4778 | 0 | 0 | 37560.376
7 | 28 | 12 | 0 | 7.6573 | 7.6573 | 48 | 7.8703 | 9.299 | 9.299 | 514.7984 | 7.6573 | 0 | 3574.4295 | 0 | 0 | 0 | 7.6573 | 0 | 0 | 3574.4295
7 | 28 | 13 | 0 | 1.4396 | 1.4396 | 48 | 8.1754 | 2.1252 | 2.1252 | 511.612 | 1.4396 | 0 | 667.4091 | 0 | 0 | 0 | 1.4396 | 0 | 0 | 667.4091
7 | 28 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 516.5171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 15 | 0 | 38.5315 | 38.5315 | 48 | 7.4212 | 37.1039 | 37.1039 | 518.409 | 38.5315 | 0 | 18125.577 | 0 | 0 | 0 | 38.5315 | 0 | 0 | 18125.577
7 | 28 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 521.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 17 | 0 | 45.1887 | 45.1887 | 48 | 7.2686 | 40.6555 | 40.6555 | 526.0971 | 45.1887 | 0 | 21604.5775 | 0 | 0 | 0 | 45.1887 | 0 | 0 | 21604.5775
7 | 28 | 18 | 2.0034 | 11.0519 | 13.0552 | 42.3223 | 6.9297 | 10.2492 | 10.2492 | 516.3364 | 13.0552 | 0 | 6188.3723 | 0 | 0 | 0 | 13.0552 | 0 | 0 | 6188.3723
7 | 28 | 19 | 10.1403 | 0 | 10.1403 | 11 | 6.9382 | 7.9862 | 7.9862 | 501.5264 | 10.1403 | 0 | 4974.0997 | 0 | 0 | 0 | 10.1403 | 0 | 0 | 4974.0997
7 | 28 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 482.5247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 460.3098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 445.2164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 28 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 438.8674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 439.1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 426.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 422.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 424.0505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 418.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 427.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 6 | 0 | 0.077875 | 0.077875 | 48 | 4.4638 | 0.031729 | 0.031729 | 443.847 | 0.077875 | 0 | 30.8266 | 0 | 0 | 0 | 0.077875 | 0 | 0 | 30.8266
7 | 29 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 456.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 8 | 0 | 0.016667 | 0.016667 | 48 | 6.6246 | 0.011738 | 0.011738 | 463.4619 | 0.016667 | 0 | 6.9244 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 6.9244
7 | 29 | 9 | 0 | 0.0075 | 0.0075 | 48 | 7.1924 | 0.006533 | 0.006533 | 464.3057 | 0.0075 | 0 | 3.1223 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.1223
7 | 29 | 10 | 0 | 0.20583 | 0.20583 | 48 | 7.0398 | 0.16857 | 0.16857 | 469.9779 | 0.20583 | 0 | 86.8571 | 0 | 0 | 0 | 0.20583 | 0 | 0 | 86.8571
7 | 29 | 11 | 0 | 2.4025 | 2.4025 | 48 | 7.2093 | 2.1076 | 2.1076 | 467.3946 | 2.4025 | 0 | 1007.5956 | 0 | 0 | 0 | 2.4025 | 0 | 0 | 1007.5956
7 | 29 | 12 | 0 | 7.3558 | 7.3558 | 48 | 7.9296 | 9.252 | 9.252 | 469.7696 | 7.3558 | 0 | 3102.467 | 0 | 0 | 0 | 7.3558 | 0 | 0 | 3102.467
7 | 29 | 13 | 0 | 1.8222 | 1.8222 | 48 | 8.2601 | 2.8614 | 2.8614 | 472.8827 | 1.8222 | 0 | 774.2248 | 0 | 0 | 0 | 1.8222 | 0 | 0 | 774.2248
7 | 29 | 14 | 0 | 1.0934 | 1.0934 | 48 | 8.5313 | 2.1566 | 2.1566 | 475.8234 | 1.0934 | 0 | 467.7955 | 0 | 0 | 0 | 1.0934 | 0 | 0 | 467.7955
7 | 29 | 15 | 0 | 31.162 | 31.162 | 48 | 8.4041 | 54.8761 | 54.8761 | 484.5917 | 31.162 | 0 | 13605.0645 | 0 | 0 | 0 | 31.162 | 0 | 0 | 13605.0645
7 | 29 | 16 | 0 | 18.2598 | 18.2598 | 48 | 9.1753 | 91.9097 | 91.9097 | 486.8668 | 18.2598 | 0 | 8013.626 | 0 | 0 | 0 | 18.2598 | 0 | 0 | 8013.626
7 | 29 | 17 | 0 | 9.4786 | 9.4786 | 48 | 8.6753 | 21.6388 | 21.6388 | 488.6775 | 9.4786 | 0 | 4176.9852 | 0 | 0 | 0 | 9.4786 | 0 | 0 | 4176.9852
7 | 29 | 18 | 0 | 51.5951 | 51.5951 | 48 | 9.0397 | 195.7448 | 195.7448 | 483.3558 | 51.5951 | 0 | 22462.2355 | 0 | 0 | 0 | 51.5951 | 0 | 0 | 22462.2355
7 | 29 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 469.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 458.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 442.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 427.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 29 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 426.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 422.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 415.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 416.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 415.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 415.9388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 424.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 6 | 0 | 0.085375 | 0.085375 | 48 | 4.1926 | 0.033037 | 0.033037 | 433.6018 | 0.085375 | 0 | 32.9208 | 0 | 0 | 0 | 0.085375 | 0 | 0 | 32.9208
7 | 30 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 448.8789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 8 | 0 | 0.016667 | 0.016667 | 48 | 4.8451 | 0.0073363 | 0.0073363 | 460.9866 | 0.016667 | 0 | 6.8831 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 6.8831
7 | 30 | 9 | 0 | 0.0125 | 0.0125 | 48 | 6.3789 | 0.0081302 | 0.0081302 | 477.6333 | 0.0125 | 0 | 5.3704 | 0 | 0 | 0 | 0.0125 | 0 | 0 | 5.3704
7 | 30 | 10 | 0 | 0.2175 | 0.2175 | 48 | 8.4804 | 0.40934 | 0.40934 | 490.728 | 0.2175 | 0 | 96.2933 | 0 | 0 | 0 | 0.2175 | 0 | 0 | 96.2933
7 | 30 | 11 | 0 | 2.5194 | 2.5194 | 48 | 9.4549 | 38.8853 | 38.8853 | 500.7407 | 2.5194 | 0 | 1140.6152 | 0 | 0 | 0 | 2.5194 | 0 | 0 | 1140.6152
7 | 30 | 12 | 0 | 8.4946 | 8.4946 | 48 | 9.8362 | 0 | 0 | 495.1036 | 0 | 8.4946 | 0 | 0.88575 | 0 | 0 | 0 | 8.4946 | 0 | 0
7 | 30 | 13 | 0 | 1.4175 | 1.4175 | 48 | 9.6159 | 0 | 0 | 493.0296 | 0 | 1.4175 | 0 | 0.14781 | 0 | 0 | 0 | 1.4175 | 0 | 0
7 | 30 | 14 | 0 | 0.036667 | 0.036667 | 48 | 9.5227 | 1.134 | 1.134 | 500.7932 | 0.036667 | 0 | 16.6024 | 0 | 0 | 0 | 0.036667 | 0 | 0 | 16.6024
7 | 30 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 500.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 505.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 17 | 0 | 1.2519 | 1.2519 | 48 | 11.8107 | 0 | 0 | 509.208 | 0 | 1.2519 | 0 | 0.13054 | 0 | 0 | 0 | 1.2519 | 0 | 0
7 | 30 | 18 | 0 | 0.48737 | 0.48737 | 48 | 12.3445 | 0 | 0 | 516.4699 | 0 | 0.48737 | 0 | 0.05082 | 0 | 0 | 0 | 0.48737 | 0 | 0
7 | 30 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 512.4463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 470.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 453.4021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 30 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 445.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 439.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 434.9577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 442.1851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 460.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 468.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 482.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 6 | 0 | 0.062875 | 0.062875 | 48 | 4.4722 | 0.02566 | 0.02566 | 496.6871 | 0.062875 | 0 | 28.2112 | 0 | 0 | 0 | 0.062875 | 0 | 0 | 28.2112
7 | 31 | 7 | 0 | 6.9392 | 6.9392 | 48 | 4.8281 | 3.0436 | 3.0436 | 510.4883 | 6.9392 | 0 | 3209.2836 | 0 | 0 | 0 | 6.9392 | 0 | 0 | 3209.2836
7 | 31 | 8 | 0 | 1.6833 | 1.6833 | 48 | 5.4976 | 0.8591 | 0.8591 | 523.7508 | 1.6833 | 0 | 800.8473 | 0 | 0 | 0 | 1.6833 | 0 | 0 | 800.8473
7 | 31 | 9 | 0 | 0.020833 | 0.020833 | 48 | 6.4043 | 0.013658 | 0.013658 | 528.1793 | 0.020833 | 0 | 10.0038 | 0 | 0 | 0 | 0.020833 | 0 | 0 | 10.0038
7 | 31 | 10 | 0 | 0.2525 | 0.2525 | 48 | 8.5991 | 0.53208 | 0.53208 | 523.1187 | 0.2525 | 0 | 119.9675 | 0 | 0 | 0 | 0.2525 | 0 | 0 | 119.9675
7 | 31 | 11 | 0 | 2.4075 | 2.4075 | 48 | 9.6413 | 0 | 0 | 523.1005 | 0 | 2.4075 | 0 | 0.25104 | 0 | 0 | 0 | 2.4075 | 0 | 0
7 | 31 | 12 | 0 | 7.305 | 7.305 | 48 | 9.7176 | 0 | 0 | 523.8981 | 0 | 7.305 | 0 | 0.76171 | 0 | 0 | 0 | 7.305 | 0 | 0
7 | 31 | 13 | 0 | 1.2033 | 1.2033 | 48 | 9.7939 | 0 | 0 | 523.8066 | 0 | 1.2033 | 0 | 0.12547 | 0 | 0 | 0 | 1.2033 | 0 | 0
7 | 31 | 14 | 0 | 0.011667 | 0.011667 | 48 | 9.4634 | 0.1921 | 0.1921 | 524.7966 | 0.011667 | 0 | 5.5626 | 0 | 0 | 0 | 0.011667 | 0 | 0 | 5.5626
7 | 31 | 15 | 0 | 0.098333 | 0.098333 | 48 | 10.5311 | 0 | 0 | 528.5053 | 0 | 0.098333 | 0 | 0.010253 | 0 | 0 | 0 | 0.098333 | 0 | 0
7 | 31 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 530.9156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 17 | 0 | 0.19983 | 0.19983 | 48 | 11.1073 | 0 | 0 | 541.7006 | 0 | 0.19983 | 0 | 0.020837 | 0 | 0 | 0 | 0.19983 | 0 | 0
7 | 31 | 18 | 0 | 0.52246 | 0.52246 | 48 | 11.4802 | 0 | 0 | 547.4604 | 0 | 0.52246 | 0 | 0.054478 | 0 | 0 | 0 | 0.52246 | 0 | 0
7 | 31 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 542.6088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 536.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 520.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 494.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 31 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 479.7265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 467.084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 461.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 465.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 475.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 487.7842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 508.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 527.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 532.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 8 | 0 | 0.016667 | 0.016667 | 48 | 6.2094 | 0.010297 | 0.010297 | 538.4344 | 0.016667 | 0 | 8.1739 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 8.1739
8 | 1 | 9 | 0 | 0.0175 | 0.0175 | 48 | 7.328 | 0.016157 | 0.016157 | 535.7486 | 0.0175 | 0 | 8.5356 | 0 | 0 | 0 | 0.0175 | 0 | 0 | 8.5356
8 | 1 | 10 | 0 | 0.44579 | 0.44579 | 48 | 8.5482 | 0.89357 | 0.89357 | 533.0012 | 0.44579 | 0 | 216.2095 | 0 | 0 | 0 | 0.44579 | 0 | 0 | 216.2095
8 | 1 | 11 | 0 | 2.2919 | 2.2919 | 48 | 9.1838 | 11.7765 | 11.7765 | 534.945 | 2.2919 | 0 | 1116.0144 | 0 | 0 | 0 | 2.2919 | 0 | 0 | 1116.0144
8 | 1 | 12 | 0 | 49.886 | 49.886 | 48 | 9.8701 | 0 | 0 | 532.8802 | 0 | 49.886 | 0 | 5.2017 | 0 | 0 | 0 | 49.886 | 0 | 0
8 | 1 | 13 | 0 | 15.2943 | 15.2943 | 48 | 9.6668 | 0 | 0 | 532.5299 | 0 | 15.2943 | 0 | 1.5948 | 0 | 0 | 0 | 15.2943 | 0 | 0
8 | 1 | 14 | 0 | 17.1116 | 17.1116 | 48 | 10.2684 | 0 | 0 | 533.4552 | 0 | 17.1116 | 0 | 1.7843 | 0 | 0 | 0 | 17.1116 | 0 | 0
8 | 1 | 15 | 0 | 9.6836 | 9.6836 | 48 | 11.226 | 0 | 0 | 537.3556 | 0 | 9.6836 | 0 | 1.0097 | 0 | 0 | 0 | 9.6836 | 0 | 0
8 | 1 | 16 | 0 | 6.4063 | 6.4063 | 48 | 11.853 | 0 | 0 | 539.3122 | 0 | 6.4063 | 0 | 0.668 | 0 | 0 | 0 | 6.4063 | 0 | 0
8 | 1 | 17 | 0 | 3.8842 | 3.8842 | 48 | 11.7514 | 0 | 0 | 540.8552 | 0 | 3.8842 | 0 | 0.40502 | 0 | 0 | 0 | 3.8842 | 0 | 0
8 | 1 | 18 | 0 | 0.39071 | 0.39071 | 48 | 12.4971 | 0 | 0 | 550.3576 | 0 | 0.39071 | 0 | 0.04074 | 0 | 0 | 0 | 0.39071 | 0 | 0
8 | 1 | 19 | 0 | 0.0875 | 0.0875 | 48 | 12.7428 | 0 | 0 | 546.0862 | 0 | 0.0875 | 0 | 0.0091239 | 0 | 0 | 0 | 0.0875 | 0 | 0
8 | 1 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 540.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 527.2064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 501.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 487.2108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 474.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 468.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 476.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 499.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 514.7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 530.3985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 543.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 546.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 550.0924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 544.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 10 | 0 | 0.2125 | 0.2125 | 48 | 8.0567 | 0.28943 | 0.28943 | 542.1216 | 0.2125 | 0 | 105.0009 | 0 | 0 | 0 | 0.2125 | 0 | 0 | 105.0009
8 | 2 | 11 | 0 | 4.7322 | 4.7322 | 48 | 9.3109 | 35.379 | 35.379 | 544.5617 | 4.7322 | 0 | 2349.8535 | 0 | 0 | 0 | 4.7322 | 0 | 0 | 2349.8535
8 | 2 | 12 | 0 | 21.3284 | 21.3284 | 48 | 9.0058 | 76.2243 | 76.2243 | 542.7983 | 21.3284 | 0 | 10553.2781 | 0 | 0 | 0 | 21.3284 | 0 | 0 | 10553.2781
8 | 2 | 13 | 0 | 64.6597 | 64.6597 | 48 | 8.4889 | 122.6263 | 122.6263 | 541.0693 | 64.6597 | 0 | 31881.698 | 0 | 0 | 0 | 64.6597 | 0 | 0 | 31881.698
8 | 2 | 14 | 0 | 1.645 | 1.645 | 48 | 8.938 | 5.2679 | 5.2679 | 541.0195 | 1.645 | 0 | 811.0192 | 0 | 0 | 0 | 1.645 | 0 | 0 | 811.0192
8 | 2 | 15 | 0 | 0.74879 | 0.74879 | 48 | 9.6075 | 0 | 0 | 543.8039 | 0 | 0.74879 | 0 | 0.078078 | 0 | 0 | 0 | 0.74879 | 0 | 0
8 | 2 | 16 | 0 | 1.1852 | 1.1852 | 48 | 10.9718 | 0 | 0 | 544.8214 | 0 | 1.1852 | 0 | 0.12359 | 0 | 0 | 0 | 1.1852 | 0 | 0
8 | 2 | 17 | 2.8401 | 2.4031 | 5.2433 | 27.9581 | 10.3786 | 0 | 0 | 555.7083 | 0 | 5.2433 | 0 | 0.54673 | 0 | 0 | 0 | 5.2433 | 0 | 0
8 | 2 | 18 | 12.0557 | 1.4941 | 13.5498 | 15.0798 | 11.0734 | 0 | 0 | 553.8162 | 0 | 13.5498 | 0 | 1.4129 | 0 | 0 | 0 | 13.5498 | 0 | 0
8 | 2 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 550.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 536.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 517.9336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 495.6156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 470.6877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 464.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 463.6831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 466.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 478.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 498.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 515.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 530.185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 539.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 545.7355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 544.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 537.9021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 535.0182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 12 | 0 | 0.35833 | 0.35833 | 48 | 7.8957 | 0.44169 | 0.44169 | 530.752 | 0.35833 | 0 | 172.9861 | 0 | 0 | 0 | 0.35833 | 0 | 0 | 172.9861
8 | 3 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 534.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 535.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 538.7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 548.5672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 544.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 542.6625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 535.6928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 522.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 499.3875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 475.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 3 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 459.3206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 451.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 451.0647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 462.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 474.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 491.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 495.4008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 504.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 514.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 8 | 0 | 0.13167 | 0.13167 | 48 | 6.8788 | 0.10143 | 0.10143 | 517.2411 | 0.13167 | 0 | 61.7835 | 0 | 0 | 0 | 0.13167 | 0 | 0 | 61.7835
8 | 4 | 9 | 0 | 0.015833 | 0.015833 | 48 | 7.3195 | 0.014564 | 0.014564 | 512.5706 | 0.015833 | 0 | 7.3557 | 0 | 0 | 0 | 0.015833 | 0 | 0 | 7.3557
8 | 4 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 510.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 11 | 0 | 0.77026 | 0.77026 | 48 | 7.2263 | 0.68057 | 0.68057 | 507.5276 | 0.77026 | 0 | 353.9564 | 0 | 0 | 0 | 0.77026 | 0 | 0 | 353.9564
8 | 4 | 12 | 0 | 2.1284 | 2.1284 | 48 | 7.8703 | 2.5847 | 2.5847 | 503.5889 | 2.1284 | 0 | 969.6535 | 0 | 0 | 0 | 2.1284 | 0 | 0 | 969.6535
8 | 4 | 13 | 0 | 1.5761 | 1.5761 | 48 | 8.1754 | 2.3267 | 2.3267 | 506.4961 | 1.5761 | 0 | 722.6433 | 0 | 0 | 0 | 1.5761 | 0 | 0 | 722.6433
8 | 4 | 14 | 0.36167 | 35.8061 | 36.1678 | 47.63 | 8.2431 | 56.0789 | 56.0789 | 509.5711 | 36.1678 | 0 | 16707.3725 | 0 | 0 | 0 | 36.1678 | 0 | 0 | 16707.3725
8 | 4 | 15 | 0 | 8.7074 | 8.7074 | 48 | 7.4212 | 8.3848 | 8.3848 | 512.5866 | 8.7074 | 0 | 4045.3291 | 0 | 0 | 0 | 8.7074 | 0 | 0 | 4045.3291
8 | 4 | 16 | 0 | 0.050774 | 0.050774 | 48 | 7.3195 | 0.046703 | 0.046703 | 527.3304 | 0.050774 | 0 | 24.3375 | 0 | 0 | 0 | 0.050774 | 0 | 0 | 24.3375
8 | 4 | 17 | 0 | 19.2406 | 19.2406 | 48 | 7.2686 | 17.3104 | 17.3104 | 521.4723 | 19.2406 | 0 | 9109.8761 | 0 | 0 | 0 | 19.2406 | 0 | 0 | 9109.8761
8 | 4 | 18 | 0 | 0.42988 | 0.42988 | 48 | 6.9297 | 0.33748 | 0.33748 | 516.6821 | 0.42988 | 0 | 201.4747 | 0 | 0 | 0 | 0.42988 | 0 | 0 | 201.4747
8 | 4 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 505.8543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 487.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 469.2841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 451.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 447.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 436.0999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 418.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 419.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 420.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 422.9162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 431.0722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 444.7323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 467.1284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 8 | 0 | 11.2001 | 11.2001 | 48 | 6.6246 | 7.8883 | 7.8883 | 477.9719 | 11.2001 | 0 | 4815.7363 | 0 | 0 | 0 | 11.2001 | 0 | 0 | 4815.7363
8 | 5 | 9 | 0 | 94.1917 | 94.1917 | 48 | 7.1924 | 82.0475 | 82.0475 | 486.5516 | 94.1917 | 0 | 41307.9306 | 0 | 0 | 0 | 94.1917 | 0 | 0 | 41307.9306
8 | 5 | 10 | 0 | 3.7976 | 3.7976 | 48 | 7.0398 | 3.1101 | 3.1101 | 492.4145 | 3.7976 | 0 | 1687.7011 | 0 | 0 | 0 | 3.7976 | 0 | 0 | 1687.7011
8 | 5 | 11 | 0 | 1.39 | 1.39 | 48 | 7.2093 | 1.2194 | 1.2194 | 492.5861 | 1.39 | 0 | 617.9747 | 0 | 0 | 0 | 1.39 | 0 | 0 | 617.9747
8 | 5 | 12 | 0 | 3.8275 | 3.8275 | 48 | 7.9296 | 4.8141 | 4.8141 | 480.701 | 3.8275 | 0 | 1656.1631 | 0 | 0 | 0 | 3.8275 | 0 | 0 | 1656.1631
8 | 5 | 13 | 0 | 0.30917 | 0.30917 | 48 | 8.2601 | 0.48548 | 0.48548 | 485.257 | 0.30917 | 0 | 135.1853 | 0 | 0 | 0 | 0.30917 | 0 | 0 | 135.1853
8 | 5 | 14 | 0 | 0.089167 | 0.089167 | 48 | 8.5313 | 0.17587 | 0.17587 | 486.3123 | 0.089167 | 0 | 39.0829 | 0 | 0 | 0 | 0.089167 | 0 | 0 | 39.0829
8 | 5 | 15 | 0 | 27.4087 | 27.4087 | 48 | 8.4041 | 48.2666 | 48.2666 | 496.6667 | 27.4087 | 0 | 12297.3692 | 0 | 0 | 0 | 27.4087 | 0 | 0 | 12297.3692
8 | 5 | 16 | 0 | 1.4077 | 1.4077 | 48 | 9.1753 | 7.0857 | 7.0857 | 504.4271 | 1.4077 | 0 | 642.5233 | 0 | 0 | 0 | 1.4077 | 0 | 0 | 642.5233
8 | 5 | 17 | 0 | 0.039042 | 0.039042 | 48 | 8.6753 | 0.089129 | 0.089129 | 499.6534 | 0.039042 | 0 | 17.6333 | 0 | 0 | 0 | 0.039042 | 0 | 0 | 17.6333
8 | 5 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 504.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 490.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 471.5905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 457.4488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 446.0579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 442.9492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 436.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 434.6067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 430.6366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 434.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 429.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 444.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 439.7139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 459.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 8 | 0 | 1.7172 | 1.7172 | 48 | 4.8451 | 0.75587 | 0.75587 | 469.3001 | 1.7172 | 0 | 723.4571 | 0 | 0 | 0 | 1.7172 | 0 | 0 | 723.4571
8 | 6 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 481.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 10 | 0 | 24.7304 | 24.7304 | 48 | 8.4804 | 46.5427 | 46.5427 | 488.3316 | 24.7304 | 0 | 10889.5543 | 0 | 0 | 0 | 24.7304 | 0 | 0 | 10889.5543
8 | 6 | 11 | 0 | 1.7333 | 1.7333 | 48 | 9.4549 | 26.7534 | 26.7534 | 498.8285 | 1.7333 | 0 | 781.4361 | 0 | 0 | 0 | 1.7333 | 0 | 0 | 781.4361
8 | 6 | 12 | 0 | 0.57725 | 0.57725 | 48 | 9.8362 | 0 | 0 | 499.2026 | 0 | 0.57725 | 0 | 0.060191 | 0 | 0 | 0 | 0.57725 | 0 | 0
8 | 6 | 13 | 0 | 0.37167 | 0.37167 | 48 | 9.6159 | 0 | 0 | 491.0288 | 0 | 0.37167 | 0 | 0.038755 | 0 | 0 | 0 | 0.37167 | 0 | 0
8 | 6 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 488.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 494.9261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 16 | 0 | 0.076667 | 0.076667 | 48 | 12.0564 | 0 | 0 | 511.4839 | 0 | 0.076667 | 0 | 0.0079942 | 0 | 0 | 0 | 0.076667 | 0 | 0
8 | 6 | 17 | 0 | 0.32321 | 0.32321 | 48 | 11.8107 | 0 | 0 | 511.7574 | 0 | 0.32321 | 0 | 0.033702 | 0 | 0 | 0 | 0.32321 | 0 | 0
8 | 6 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 519.5692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 505.6676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 480.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 462.0033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 443.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 453.8107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 448.5892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 447.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 453.7144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 468.7668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 481.2329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 496.3503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 501.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 508.9705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 8 | 0 | 0.07 | 0.07 | 48 | 5.4976 | 0.035725 | 0.035725 | 516.5248 | 0.07 | 0 | 32.7968 | 0 | 0 | 0 | 0.07 | 0 | 0 | 32.7968
8 | 7 | 9 | 0 | 2.154 | 2.154 | 48 | 6.4043 | 1.4122 | 1.4122 | 507.9381 | 2.154 | 0 | 990.7259 | 0 | 0 | 0 | 2.154 | 0 | 0 | 990.7259
8 | 7 | 10 | 0 | 7.4429 | 7.4429 | 48 | 8.5991 | 15.6841 | 15.6841 | 513.8727 | 7.4429 | 0 | 3467.4324 | 0 | 0 | 0 | 7.4429 | 0 | 0 | 3467.4324
8 | 7 | 11 | 0 | 0.005 | 0.005 | 48 | 9.6413 | 0 | 0 | 504.7729 | 0 | 0.005 | 0 | 0.00052137 | 0 | 0 | 0 | 0.005 | 0 | 0
8 | 7 | 12 | 0 | 0.23237 | 0.23237 | 48 | 9.7176 | 0 | 0 | 506.8407 | 0 | 0.23237 | 0 | 0.02423 | 0 | 0 | 0 | 0.23237 | 0 | 0
8 | 7 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 507.8572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 14 | 0 | 7.5278 | 7.5278 | 48 | 9.4634 | 123.9498 | 123.9498 | 506.704 | 7.5278 | 0 | 3453.0136 | 0 | 0 | 0 | 7.5278 | 0 | 0 | 3453.0136
8 | 7 | 15 | 0 | 9.8576 | 9.8576 | 48 | 10.5311 | 0 | 0 | 510.9048 | 0 | 9.8576 | 0 | 1.0279 | 0 | 0 | 0 | 9.8576 | 0 | 0
8 | 7 | 16 | 0 | 0.065833 | 0.065833 | 48 | 11.0904 | 0 | 0 | 521.2492 | 0 | 0.065833 | 0 | 0.0068646 | 0 | 0 | 0 | 0.065833 | 0 | 0
8 | 7 | 17 | 0 | 0.29988 | 0.29988 | 48 | 11.1073 | 0 | 0 | 522.0972 | 0 | 0.29988 | 0 | 0.031269 | 0 | 0 | 0 | 0.29988 | 0 | 0
8 | 7 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 518.8178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 492.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 483.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 466.5081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 449.2651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 443.5852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 440.0489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 439.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 440.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 460.1824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 468.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 478.6364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 493.8336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 509.8181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 8 | 0 | 0.0091667 | 0.0091667 | 48 | 6.2094 | 0.0056633 | 0.0056633 | 514.0882 | 0.0091667 | 0 | 4.2725 | 0 | 0 | 0 | 0.0091667 | 0 | 0 | 4.2725
8 | 8 | 9 | 0 | 17.8098 | 17.8098 | 48 | 7.328 | 16.4433 | 16.4433 | 522.3029 | 17.8098 | 0 | 8447.2367 | 0 | 0 | 0 | 17.8098 | 0 | 0 | 8447.2367
8 | 8 | 10 | 0 | 0.060029 | 0.060029 | 48 | 8.5482 | 0.12033 | 0.12033 | 522.9411 | 0.060029 | 0 | 28.5105 | 0 | 0 | 0 | 0.060029 | 0 | 0 | 28.5105
8 | 8 | 11 | 0 | 0.1525 | 0.1525 | 48 | 9.1838 | 0.7836 | 0.7836 | 514.8967 | 0.1525 | 0 | 71.2018 | 0 | 0 | 0 | 0.1525 | 0 | 0 | 71.2018
8 | 8 | 12 | 0 | 16.9593 | 16.9593 | 48 | 9.8701 | 0 | 0 | 522.0471 | 0 | 16.9593 | 0 | 1.7684 | 0 | 0 | 0 | 16.9593 | 0 | 0
8 | 8 | 13 | 0 | 0.41837 | 0.41837 | 48 | 9.6668 | 0 | 0 | 523.9563 | 0 | 0.41837 | 0 | 0.043625 | 0 | 0 | 0 | 0.41837 | 0 | 0
8 | 8 | 14 | 0 | 28.4801 | 28.4801 | 48 | 10.2684 | 0 | 0 | 526.5906 | 0 | 28.4801 | 0 | 2.9697 | 0 | 0 | 0 | 28.4801 | 0 | 0
8 | 8 | 15 | 0 | 16.4037 | 16.4037 | 48 | 11.226 | 0 | 0 | 530.3866 | 0 | 16.4037 | 0 | 1.7105 | 0 | 0 | 0 | 16.4037 | 0 | 0
8 | 8 | 16 | 0 | 0.029167 | 0.029167 | 48 | 11.853 | 0 | 0 | 538.8606 | 0 | 0.029167 | 0 | 0.0030413 | 0 | 0 | 0 | 0.029167 | 0 | 0
8 | 8 | 17 | 0 | 0.35571 | 0.35571 | 48 | 11.7514 | 0 | 0 | 538.4104 | 0 | 0.35571 | 0 | 0.037091 | 0 | 0 | 0 | 0.35571 | 0 | 0
8 | 8 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 542.3936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 532.9062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 505.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 484.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 469.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 466.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 456.5472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 452.3858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 455.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 475.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 486.6418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 496.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 504.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 517.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 8 | 0 | 0.010833 | 0.010833 | 48 | 6.2094 | 0.006693 | 0.006693 | 526.7643 | 0.010833 | 0 | 5.1867 | 0 | 0 | 0 | 0.010833 | 0 | 0 | 5.1867
8 | 9 | 9 | 0 | 2.0276 | 2.0276 | 48 | 7.311 | 1.8581 | 1.8581 | 536.8878 | 2.0276 | 0 | 991.2806 | 0 | 0 | 0 | 2.0276 | 0 | 0 | 991.2806
8 | 9 | 10 | 0 | 2.9344 | 2.9344 | 48 | 8.0567 | 3.9967 | 3.9967 | 539.7379 | 2.9344 | 0 | 1442.9544 | 0 | 0 | 0 | 2.9344 | 0 | 0 | 1442.9544
8 | 9 | 11 | 0 | 0.20917 | 0.20917 | 48 | 9.3109 | 1.5638 | 1.5638 | 531.8893 | 0.20917 | 0 | 101.2136 | 0 | 0 | 0 | 0.20917 | 0 | 0 | 101.2136
8 | 9 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 530.601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 13 | 0 | 71.3273 | 71.3273 | 48 | 8.4889 | 135.2714 | 135.2714 | 526.8235 | 71.3273 | 0 | 34153.1731 | 0 | 0 | 0 | 71.3273 | 0 | 0 | 34153.1731
8 | 9 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 530.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 15 | 0 | 1.8963 | 1.8963 | 48 | 9.6075 | 0 | 0 | 532.2979 | 0 | 1.8963 | 0 | 0.19774 | 0 | 0 | 0 | 1.8963 | 0 | 0
8 | 9 | 16 | 0 | 6.655 | 6.655 | 48 | 10.9718 | 0 | 0 | 541.5027 | 0 | 6.655 | 0 | 0.69393 | 0 | 0 | 0 | 6.655 | 0 | 0
8 | 9 | 17 | 0 | 0.42817 | 0.42817 | 48 | 10.3786 | 0 | 0 | 541.5027 | 0 | 0.42817 | 0 | 0.044646 | 0 | 0 | 0 | 0.42817 | 0 | 0
8 | 9 | 18 | 0 | 0.82371 | 0.82371 | 48 | 11.0734 | 0 | 0 | 554.5778 | 0 | 0.82371 | 0 | 0.08589 | 0 | 0 | 0 | 0.82371 | 0 | 0
8 | 9 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 542.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 520.0898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 494.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 466.0775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 450.9582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 444.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 442.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 443.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 456.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 473.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 487.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 501.3233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 525.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 8 | 0 | 0.0041667 | 0.0041667 | 48 | 5.1417 | 0.0019564 | 0.0019564 | 538.081 | 0.0041667 | 0 | 2.042 | 0 | 0 | 0 | 0.0041667 | 0 | 0 | 2.042
8 | 10 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 532.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 10 | 0 | 0.025833 | 0.025833 | 48 | 6.9721 | 0.020609 | 0.020609 | 528.8638 | 0.025833 | 0 | 12.4223 | 0 | 0 | 0 | 0.025833 | 0 | 0 | 12.4223
8 | 10 | 11 | 0 | 0.26833 | 0.26833 | 48 | 8.5652 | 0.54675 | 0.54675 | 528.3519 | 0.26833 | 0 | 128.8945 | 0 | 0 | 0 | 0.26833 | 0 | 0 | 128.8945
8 | 10 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 532.351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 13 | 0 | 12.2515 | 12.2515 | 48 | 7.4381 | 11.8905 | 11.8905 | 532.7779 | 12.2515 | 0 | 5939.2612 | 0 | 0 | 0 | 12.2515 | 0 | 0 | 5939.2612
8 | 10 | 14 | 0 | 20.407 | 20.407 | 48 | 7.2771 | 18.4271 | 18.4271 | 534.1618 | 20.407 | 0 | 9921.0824 | 0 | 0 | 0 | 20.407 | 0 | 0 | 9921.0824
8 | 10 | 15 | 0 | 0.0025 | 0.0025 | 48 | 7.3449 | 0.0023256 | 0.0023256 | 537.8726 | 0.0025 | 0 | 1.2247 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2247
8 | 10 | 16 | 0 | 0.56329 | 0.56329 | 48 | 6.9975 | 0.45378 | 0.45378 | 546.8793 | 0.56329 | 0 | 281.0146 | 0 | 0 | 0 | 0.56329 | 0 | 0 | 281.0146
8 | 10 | 17 | 0 | 0.24821 | 0.24821 | 48 | 7.167 | 0.21394 | 0.21394 | 545.6848 | 0.24821 | 0 | 123.5295 | 0 | 0 | 0 | 0.24821 | 0 | 0 | 123.5295
8 | 10 | 18 | 0 | 0.77296 | 0.77296 | 48 | 6.7094 | 0.56041 | 0.56041 | 543.105 | 0.77296 | 0 | 382.6955 | 0 | 0 | 0 | 0.77296 | 0 | 0 | 382.6955
8 | 10 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 536.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 516.2245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 497.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 470.9794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 457.1253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 441.6892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 444.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 460.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 475.7632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 490.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 501.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 519.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 536.2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 8 | 0 | 0.0075 | 0.0075 | 48 | 6.8788 | 0.0057776 | 0.0057776 | 542.0386 | 0.0075 | 0 | 3.7053 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.7053
8 | 11 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 534.8024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 10 | 0 | 0.0375 | 0.0375 | 48 | 7.4805 | 0.037126 | 0.037126 | 535.6901 | 0.0375 | 0 | 18.2884 | 0 | 0 | 0 | 0.0375 | 0 | 0 | 18.2884
8 | 11 | 11 | 0 | 0.3575 | 0.3575 | 48 | 7.2263 | 0.31587 | 0.31587 | 528.3888 | 0.3575 | 0 | 171.7391 | 0 | 0 | 0 | 0.3575 | 0 | 0 | 171.7391
8 | 11 | 12 | 0 | 0.36583 | 0.36583 | 48 | 7.8703 | 0.44427 | 0.44427 | 527.5118 | 0.36583 | 0 | 175.4215 | 0 | 0 | 0 | 0.36583 | 0 | 0 | 175.4215
8 | 11 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 522.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 14 | 0 | 10.0717 | 10.0717 | 48 | 8.2431 | 15.6165 | 15.6165 | 522.7957 | 10.0717 | 0 | 4782.0184 | 0 | 0 | 0 | 10.0717 | 0 | 0 | 4782.0184
8 | 11 | 15 | 0 | 14.5246 | 14.5246 | 48 | 7.4212 | 13.9865 | 13.9865 | 528.2024 | 14.5246 | 0 | 6974.7395 | 0 | 0 | 0 | 14.5246 | 0 | 0 | 6974.7395
8 | 11 | 16 | 0 | 0.063333 | 0.063333 | 48 | 7.3195 | 0.058256 | 0.058256 | 535.1494 | 0.063333 | 0 | 30.8528 | 0 | 0 | 0 | 0.063333 | 0 | 0 | 30.8528
8 | 11 | 17 | 0 | 0.17404 | 0.17404 | 48 | 7.2686 | 0.15658 | 0.15658 | 541.1305 | 0.17404 | 0 | 85.8253 | 0 | 0 | 0 | 0.17404 | 0 | 0 | 85.8253
8 | 11 | 18 | 0 | 0.14033 | 0.14033 | 48 | 6.9297 | 0.11017 | 0.11017 | 540.4086 | 0.14033 | 0 | 69.1013 | 0 | 0 | 0 | 0.14033 | 0 | 0 | 69.1013
8 | 11 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 529.9975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 505.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 486.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 483.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 11 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 476.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 466.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 463.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 463.2382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 464.2201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 469.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 477.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 497.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 509.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 8 | 0 | 0.01 | 0.01 | 48 | 6.6246 | 0.0070431 | 0.0070431 | 523.8567 | 0.01 | 0 | 4.7586 | 0 | 0 | 0 | 0.01 | 0 | 0 | 4.7586
8 | 12 | 9 | 0 | 5.5999 | 5.5999 | 48 | 7.1924 | 4.8779 | 4.8779 | 527.4846 | 5.5999 | 0 | 2685.0571 | 0 | 0 | 0 | 5.5999 | 0 | 0 | 2685.0571
8 | 12 | 10 | 0 | 2.6476 | 2.6476 | 48 | 7.0398 | 2.1683 | 2.1683 | 522.808 | 2.6476 | 0 | 1257.1037 | 0 | 0 | 0 | 2.6476 | 0 | 0 | 1257.1037
8 | 12 | 11 | 0 | 0.30583 | 0.30583 | 48 | 7.2093 | 0.2683 | 0.2683 | 523.7891 | 0.30583 | 0 | 145.5122 | 0 | 0 | 0 | 0.30583 | 0 | 0 | 145.5122
8 | 12 | 12 | 0 | 0.35917 | 0.35917 | 48 | 7.9296 | 0.45175 | 0.45175 | 519.0663 | 0.35917 | 0 | 169.1914 | 0 | 0 | 0 | 0.35917 | 0 | 0 | 169.1914
8 | 12 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 515.2188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 517.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 520.2779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 16 | 0 | 0.033333 | 0.033333 | 48 | 9.1753 | 0.16778 | 0.16778 | 528.4915 | 0.033333 | 0 | 16.0164 | 0 | 0 | 0 | 0.033333 | 0 | 0 | 16.0164
8 | 12 | 17 | 0 | 0.20904 | 0.20904 | 48 | 8.6753 | 0.47723 | 0.47723 | 529.6397 | 0.20904 | 0 | 100.6828 | 0 | 0 | 0 | 0.20904 | 0 | 0 | 100.6828
8 | 12 | 18 | 0 | 1.9271 | 1.9271 | 48 | 9.0397 | 7.3111 | 7.3111 | 526.3873 | 1.9271 | 0 | 921.8924 | 0 | 0 | 0 | 1.9271 | 0 | 0 | 921.8924
8 | 12 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 511.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 488.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 476.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 467.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 12 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 456.0289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 445.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 438.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 435.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 433.9357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 435.4737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 446.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 459.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 472.2076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 8 | 0 | 78.4523 | 78.4523 | 48 | 4.8451 | 34.5329 | 34.5329 | 492.9617 | 78.4523 | 0 | 34908.2557 | 0 | 0 | 0 | 78.4523 | 0 | 0 | 34908.2557
8 | 13 | 9 | 0.7625 | 205.6465 | 206.409 | 47.8633 | 6.3789 | 134.2507 | 134.2507 | 510.0993 | 206.409 | 0 | 95409.6717 | 0 | 0 | 0 | 206.409 | 0 | 0 | 95409.6717
8 | 13 | 10 | 0 | 0.062298 | 0.062298 | 48 | 8.4804 | 0.11725 | 0.11725 | 517.4123 | 0.062298 | 0 | 29.2435 | 0 | 0 | 0 | 0.062298 | 0 | 0 | 29.2435
8 | 13 | 11 | 0 | 0.26179 | 0.26179 | 48 | 9.4549 | 4.0406 | 4.0406 | 523.8251 | 0.26179 | 0 | 124.5646 | 0 | 0 | 0 | 0.26179 | 0 | 0 | 124.5646
8 | 13 | 12 | 0 | 0.11417 | 0.11417 | 48 | 9.8362 | 0 | 0 | 519.3777 | 0 | 0.11417 | 0 | 0.011904 | 0 | 0 | 0 | 0.11417 | 0 | 0
8 | 13 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 511.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 512.4081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 518.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 16 | 0 | 0.035833 | 0.035833 | 48 | 12.0564 | 0 | 0 | 533.6759 | 0 | 0.035833 | 0 | 0.0037364 | 0 | 0 | 0 | 0.035833 | 0 | 0
8 | 13 | 17 | 0 | 0.27821 | 0.27821 | 48 | 11.8107 | 0 | 0 | 533.1974 | 0 | 0.27821 | 0 | 0.02901 | 0 | 0 | 0 | 0.27821 | 0 | 0
8 | 13 | 18 | 0 | 0.78842 | 0.78842 | 48 | 12.3445 | 0 | 0 | 536.5272 | 0 | 0.78842 | 0 | 0.08221 | 0 | 0 | 0 | 0.78842 | 0 | 0
8 | 13 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 517.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 491.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 476.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 463.3283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 13 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 449.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 444.6904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 447.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 451.5701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 463.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 476.4098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 485.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 508.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 7 | 0 | 0.014167 | 0.014167 | 48 | 4.8281 | 0.0062137 | 0.0062137 | 522.316 | 0.014167 | 0 | 6.7195 | 0 | 0 | 0 | 0.014167 | 0 | 0 | 6.7195
8 | 14 | 8 | 0 | 129.6192 | 129.6192 | 48 | 5.4976 | 66.1518 | 66.1518 | 529.9117 | 129.6192 | 0 | 62464.9903 | 0 | 0 | 0 | 129.6192 | 0 | 0 | 62464.9903
8 | 14 | 9 | 4.8633 | 332.7427 | 337.606 | 47.467 | 6.4043 | 221.3348 | 221.3348 | 531.925 | 337.606 | 0 | 163555.9127 | 0 | 0 | 0 | 337.606 | 0 | 0 | 163555.9127
8 | 14 | 10 | 0.63417 | 289.7725 | 290.4066 | 47.9192 | 8.5991 | 611.9637 | 288 | 528.011 | 136.6701 | 153.7366 | 65614.1716 | 16.0305 | 0 | 0 | 136.6701 | 153.7366 | 0 | 65614.1716
8 | 14 | 11 | 0 | 74.648 | 74.648 | 48 | 9.6413 | 0 | 0 | 527.4524 | 0 | 74.648 | 0 | 7.7837 | 0 | 0 | 0 | 74.648 | 0 | 0
8 | 14 | 12 | 0 | 102.9947 | 102.9947 | 48 | 9.7176 | 0 | 0 | 528.1527 | 0 | 102.9947 | 0 | 10.7395 | 0 | 0 | 0 | 102.9947 | 0 | 0
8 | 14 | 13 | 0 | 120.0394 | 120.0394 | 48 | 9.7939 | 0 | 0 | 531.6884 | 0 | 120.0394 | 0 | 12.5168 | 0 | 0 | 0 | 120.0394 | 0 | 0
8 | 14 | 14 | 0 | 164.807 | 164.807 | 48 | 9.4634 | 2713.6614 | 288 | 529.1091 | 17.4909 | 147.3161 | 8415.0388 | 15.361 | 0 | 0 | 17.4909 | 147.3161 | 0 | 8415.0388
8 | 14 | 15 | 0 | 0.0425 | 0.0425 | 48 | 10.5311 | 0 | 0 | 529.3007 | 0 | 0.0425 | 0 | 0.0044316 | 0 | 0 | 0 | 0.0425 | 0 | 0
8 | 14 | 16 | 0 | 0.58404 | 0.58404 | 48 | 11.0904 | 0 | 0 | 541.3845 | 0 | 0.58404 | 0 | 0.0609 | 0 | 0 | 0 | 0.58404 | 0 | 0
8 | 14 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 549.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 18 | 0 | 0.65279 | 0.65279 | 48 | 11.4802 | 0 | 0 | 551.3525 | 0 | 0.65279 | 0 | 0.068068 | 0 | 0 | 0 | 0.65279 | 0 | 0
8 | 14 | 19 | 3.7533 | 0 | 3.7533 | 11 | 12.6496 | 0 | 0 | 549.4217 | 0 | 3.7533 | 0 | 0.39137 | 0 | 0 | 0 | 3.7533 | 0 | 0
8 | 14 | 20 | 3.4627 | 0 | 3.4627 | 11 | 12.2428 | 0 | 0 | 532.4274 | 0 | 3.4627 | 0 | 0.36106 | 0 | 0 | 0 | 3.4627 | 0 | 0
8 | 14 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 517.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 495.067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 14 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 490.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 479.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 474.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 491.7194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 508.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 517.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 530.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 539.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 7 | 0 | 0.011625 | 0.011625 | 48 | 5.2518 | 0.0055968 | 0.0055968 | 547.6087 | 0.011625 | 0 | 5.808 | 0 | 0 | 0 | 0.011625 | 0 | 0 | 5.808
8 | 15 | 8 | 0 | 0.0175 | 0.0175 | 48 | 6.2094 | 0.010812 | 0.010812 | 552.5629 | 0.0175 | 0 | 8.8299 | 0 | 0 | 0 | 0.0175 | 0 | 0 | 8.8299
8 | 15 | 9 | 0.9675 | 82.7236 | 83.6911 | 47.5723 | 7.328 | 77.2698 | 77.2698 | 549.8312 | 83.6911 | 0 | 42034.5842 | 0 | 0 | 0 | 83.6911 | 0 | 0 | 42034.5842
8 | 15 | 10 | 0 | 34.3143 | 34.3143 | 48 | 8.5482 | 68.7811 | 68.7811 | 545.1967 | 34.3143 | 0 | 17060.9323 | 0 | 0 | 0 | 34.3143 | 0 | 0 | 17060.9323
8 | 15 | 11 | 1.46 | 0.23083 | 1.6908 | 16.0514 | 9.1838 | 8.6879 | 8.6879 | 546.3858 | 1.6908 | 0 | 896.6851 | 0 | 0 | 0 | 1.6908 | 0 | 0 | 896.6851
8 | 15 | 12 | 0 | 0.0033333 | 0.0033333 | 48 | 9.8701 | 0 | 0 | 542.0573 | 0 | 0.0033333 | 0 | 0.00034758 | 0 | 0 | 0 | 0.0033333 | 0 | 0
8 | 15 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 539.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 537.7049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 15 | 0.175 | 10.461 | 10.636 | 47.3912 | 11.226 | 0 | 0 | 541.2195 | 0 | 10.636 | 0 | 1.109 | 0 | 0 | 0 | 10.636 | 0 | 0
8 | 15 | 16 | 0 | 4.2121 | 4.2121 | 48 | 11.853 | 0 | 0 | 549.8889 | 0 | 4.2121 | 0 | 0.43921 | 0 | 0 | 0 | 4.2121 | 0 | 0
8 | 15 | 17 | 0 | 0.088958 | 0.088958 | 48 | 11.7514 | 0 | 0 | 554.3287 | 0 | 0.088958 | 0 | 0.0092759 | 0 | 0 | 0 | 0.088958 | 0 | 0
8 | 15 | 18 | 0 | 1.3357 | 1.3357 | 48 | 12.4971 | 0 | 0 | 564.7221 | 0 | 1.3357 | 0 | 0.13927 | 0 | 0 | 0 | 1.3357 | 0 | 0
8 | 15 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 562.5664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 540.2001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 515.7451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 491.3567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 15 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 476.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 464.099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 459.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 464.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 487.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 505.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 515.2663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 531.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 548.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 8 | 0 | 47.6781 | 47.6781 | 48 | 6.2094 | 29.4558 | 29.4558 | 555.7801 | 47.6781 | 0 | 24209.9807 | 0 | 0 | 0 | 47.6781 | 0 | 0 | 24209.9807
8 | 16 | 9 | 0 | 209.1349 | 209.1349 | 48 | 7.311 | 191.653 | 191.653 | 549.1034 | 209.1349 | 0 | 104798.2066 | 0 | 0 | 0 | 209.1349 | 0 | 0 | 104798.2066
8 | 16 | 10 | 0 | 5.0341 | 5.0341 | 48 | 8.0567 | 6.8566 | 6.8566 | 546.8501 | 5.0341 | 0 | 2511.2597 | 0 | 0 | 0 | 5.0341 | 0 | 0 | 2511.2597
8 | 16 | 11 | 0 | 0.59189 | 0.59189 | 48 | 9.3109 | 4.4251 | 4.4251 | 541.6397 | 0.59189 | 0 | 292.182 | 0 | 0 | 0 | 0.59189 | 0 | 0 | 292.182
8 | 16 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 540.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 541.9276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 544.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 15 | 0 | 0 | 0 | 0 | 9.6075 | 0 | 0 | 544.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | 16 | 0 | 0.57904 | 0.57904 | 48 | 10.9718 | 0 | 0 | 548.5672 | 0 | 0.57904 | 0 | 0.060378 | 0 | 0 | 0 | 0.57904 | 0 | 0
8 | 16 | 17 | 0 | 0.066583 | 0.066583 | 48 | 10.3786 | 0 | 0 | 553.1601 | 0 | 0.066583 | 0 | 0.0069428 | 0 | 0 | 0 | 0.066583 | 0 | 0
8 | 16 | 18 | 0 | 1.0744 | 1.0744 | 48 | 11.0734 | 0 | 0 | 561.6642 | 0 | 1.0744 | 0 | 0.11203 | 0 | 0 | 0 | 1.0744 | 0 | 0
8 | 16 | 19 | 3.5438 | 0 | 3.5438 | 11 | 10.4633 | 0 | 0 | 562.2878 | 0 | 3.5438 | 0 | 0.36952 | 0 | 0 | 0 | 3.5438 | 0 | 0
8 | 16 | 20 | 50.7218 | 0 | 50.7218 | 11 | 8.0228 | 67.5906 | 67.5906 | 547.7559 | 50.7218 | 0 | 27225.2296 | 0 | 0 | 0 | 50.7218 | 0 | 0 | 27225.2296
8 | 16 | 21 | 99.8367 | 0 | 99.8367 | 11 | 7.1076 | 83.9962 | 83.9962 | 533.2937 | 99.8367 | 0 | 52144.0563 | 0 | 0 | 0 | 99.8367 | 0 | 0 | 52144.0563
8 | 16 | 22 | 135.1707 | 0 | 135.1707 | 11 | 5.2264 | 64.6984 | 64.6984 | 508.2225 | 135.1707 | 0 | 67209.9122 | 0 | 0 | 0 | 135.1707 | 0 | 0 | 67209.9122
8 | 16 | 23 | 4.8775 | 0 | 4.8775 | 11 | 4.2265 | 1.8994 | 1.8994 | 497.57 | 4.8775 | 0 | 2373.2519 | 0 | 0 | 0 | 4.8775 | 0 | 0 | 2373.2519
8 | 17 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 484.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 477.6663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 2 | 39.2017 | 0 | 39.2017 | 11 | 3.8197 | 14.1896 | 14.1896 | 481.4447 | 39.2017 | 0 | 18442.2144 | 0 | 0 | 0 | 39.2017 | 0 | 0 | 18442.2144
8 | 17 | 3 | 132.4267 | 0 | 132.4267 | 11 | 3.4638 | 45.149 | 45.149 | 502.2595 | 132.4267 | 0 | 65055.9031 | 0 | 0 | 0 | 132.4267 | 0 | 0 | 65055.9031
8 | 17 | 4 | 17.7407 | 0 | 17.7407 | 11 | 3.4045 | 5.9904 | 5.9904 | 525.1137 | 17.7407 | 0 | 9120.7124 | 0 | 0 | 0 | 17.7407 | 0 | 0 | 9120.7124
8 | 17 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 533.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 542.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 550.7511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 8 | 0 | 0.0075 | 0.0075 | 48 | 5.1417 | 0.0035215 | 0.0035215 | 554.1971 | 0.0075 | 0 | 3.7965 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.7965
8 | 17 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 546.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 542.9784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 11 | 0 | 0.3625 | 0.3625 | 48 | 8.5652 | 0.73863 | 0.73863 | 538.937 | 0.3625 | 0 | 177.9647 | 0 | 0 | 0 | 0.3625 | 0 | 0 | 177.9647
8 | 17 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 535.9479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 13 | 0 | 0.018333 | 0.018333 | 48 | 7.4381 | 0.017793 | 0.017793 | 534.0936 | 0.018333 | 0 | 8.9117 | 0 | 0 | 0 | 0.018333 | 0 | 0 | 8.9117
8 | 17 | 14 | 0 | 0.15333 | 0.15333 | 48 | 7.2771 | 0.13846 | 0.13846 | 535.8223 | 0.15333 | 0 | 74.7994 | 0 | 0 | 0 | 0.15333 | 0 | 0 | 74.7994
8 | 17 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 543.7188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 16 | 0.32446 | 0 | 0.32446 | 11 | 6.9975 | 0.26138 | 0.26138 | 549.842 | 0.32446 | 0 | 174.8317 | 0 | 0 | 0 | 0.32446 | 0 | 0 | 174.8317
8 | 17 | 17 | 1.0775 | 12.0343 | 13.1118 | 44.9594 | 7.167 | 11.3014 | 11.3014 | 554.8415 | 13.1118 | 0 | 6685.4556 | 0 | 0 | 0 | 13.1118 | 0 | 0 | 6685.4556
8 | 17 | 18 | 0 | 1.2455 | 1.2455 | 48 | 6.7094 | 0.90305 | 0.90305 | 554.5035 | 1.2455 | 0 | 630.8712 | 0 | 0 | 0 | 1.2455 | 0 | 0 | 630.8712
8 | 17 | 19 | 0.78611 | 0 | 0.78611 | 11 | 7.3958 | 0.74822 | 0.74822 | 552.4301 | 0.78611 | 0 | 425.6241 | 0 | 0 | 0 | 0.78611 | 0 | 0 | 425.6241
8 | 17 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 540.1542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 533.4269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 508.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 491.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 485.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 482.0128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 501.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 523.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 532.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 546.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 551.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 553.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 8 | 0 | 0.0058334 | 0.0058334 | 48 | 6.8788 | 0.0044937 | 0.0044937 | 547.7623 | 0.0058334 | 0 | 2.9153 | 0 | 0 | 0 | 0.0058334 | 0 | 0 | 2.9153
8 | 18 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 537.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 536.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 533.6768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 531.4237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 532.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 535.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 540.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 549.0393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 17 | 0 | 0.0025 | 0.0025 | 48 | 7.2686 | 0.0022492 | 0.0022492 | 551.0993 | 0.0025 | 0 | 1.2578 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2578
8 | 18 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 558.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 553.9478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 535.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 513.1588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 492.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 18 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 479.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 467.2796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 465.241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 467.2291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 469.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 469.3654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 491.497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 511.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 526.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 8 | 0 | 0.0058334 | 0.0058334 | 48 | 6.6246 | 0.0041085 | 0.0041085 | 540.6757 | 0.0058334 | 0 | 2.874 | 0 | 0 | 0 | 0.0058334 | 0 | 0 | 2.874
8 | 19 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 546.5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 543.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 540.2269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 537.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 537.1025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 539.7565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 541.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 16 | 0 | 18.7799 | 18.7799 | 48 | 9.1753 | 94.5274 | 94.5274 | 550.5823 | 18.7799 | 0 | 9438.4308 | 0 | 0 | 0 | 18.7799 | 0 | 0 | 9438.4308
8 | 19 | 17 | 0 | 0.0075 | 0.0075 | 48 | 8.6753 | 0.017122 | 0.017122 | 555.3901 | 0.0075 | 0 | 3.8054 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.8054
8 | 19 | 18 | 0 | 0.85342 | 0.85342 | 48 | 9.0397 | 3.2377 | 3.2377 | 558.1901 | 0.85342 | 0 | 435.4047 | 0 | 0 | 0 | 0.85342 | 0 | 0 | 435.4047
8 | 19 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 538.071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 512.1622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 490.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 481.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 19 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 466.2756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 456.3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 446.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 445.5539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 445.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 447.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 459.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 478.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 499.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 8 | 0 | 0.005 | 0.005 | 48 | 4.8451 | 0.0022009 | 0.0022009 | 521.3891 | 0.005 | 0 | 2.367 | 0 | 0 | 0 | 0.005 | 0 | 0 | 2.367
8 | 20 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 535.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 545.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 543.1291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 533.4217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 531.3514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 534.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 540.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 547.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 17 | 0 | 0.0075 | 0.0075 | 48 | 11.8107 | 0 | 0 | 553.6586 | 0 | 0.0075 | 0 | 0.00078205 | 0 | 0 | 0 | 0.0075 | 0 | 0
8 | 20 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 555.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 550.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 531.2524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 511.2793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 485.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 20 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 476.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 471.8868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 466.1142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 477.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 491.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 515.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 522.6169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 543.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 7 | 0 | 0.10954 | 0.10954 | 48 | 4.8281 | 0.048046 | 0.048046 | 555.4378 | 0.10954 | 0 | 55.5856 | 0 | 0 | 0 | 0.10954 | 0 | 0 | 55.5856
8 | 21 | 8 | 0 | 37.6354 | 37.6354 | 48 | 5.4976 | 19.2074 | 19.2074 | 554.2701 | 37.6354 | 0 | 19053.6771 | 0 | 0 | 0 | 37.6354 | 0 | 0 | 19053.6771
8 | 21 | 9 | 0 | 68.5543 | 68.5543 | 48 | 6.4043 | 44.9443 | 44.9443 | 548.0561 | 68.5543 | 0 | 34281.0015 | 0 | 0 | 0 | 68.5543 | 0 | 0 | 34281.0015
8 | 21 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 552.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 11 | 4.5983 | 789.7135 | 794.3118 | 47.7858 | 9.6413 | 0 | 0 | 550.7238 | 0 | 794.3118 | 0 | 82.825 | 0 | 0 | 0 | 794.3118 | 0 | 0
8 | 21 | 12 | 0.10917 | 47.8988 | 48.0079 | 47.9159 | 9.7176 | 0 | 0 | 542.6335 | 0 | 48.0079 | 0 | 5.0059 | 0 | 0 | 0 | 48.0079 | 0 | 0
8 | 21 | 13 | 0 | 1.449 | 1.449 | 48 | 9.7939 | 0 | 0 | 543.4694 | 0 | 1.449 | 0 | 0.15109 | 0 | 0 | 0 | 1.449 | 0 | 0
8 | 21 | 14 | 0 | 3.1177 | 3.1177 | 48 | 9.4634 | 51.3357 | 51.3357 | 550.5475 | 3.1177 | 0 | 1566.812 | 0 | 0 | 0 | 3.1177 | 0 | 0 | 1566.812
8 | 21 | 15 | 0 | 0.65804 | 0.65804 | 48 | 10.5311 | 0 | 0 | 556.0027 | 0 | 0.65804 | 0 | 0.068616 | 0 | 0 | 0 | 0.65804 | 0 | 0
8 | 21 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 563.5177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 17 | 0 | 0.0025 | 0.0025 | 48 | 11.1073 | 0 | 0 | 565.0343 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
8 | 21 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 571.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 565.7261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 546.862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 524.3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 492.8814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 21 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 482.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 478.7812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 476.1189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 498.0789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 524.4907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 542.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 546.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 559.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 564.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 8 | 0 | 0.005 | 0.005 | 48 | 6.2094 | 0.0030891 | 0.0030891 | 554.9825 | 0.005 | 0 | 2.5349 | 0 | 0 | 0 | 0.005 | 0 | 0 | 2.5349
8 | 22 | 9 | 0 | 1.6316 | 1.6316 | 48 | 7.328 | 1.5064 | 1.5064 | 559.2113 | 1.6316 | 0 | 834.0689 | 0 | 0 | 0 | 1.6316 | 0 | 0 | 834.0689
8 | 22 | 10 | 0 | 20.1208 | 20.1208 | 48 | 8.5482 | 40.331 | 40.331 | 552.8622 | 20.1208 | 0 | 10158.21 | 0 | 0 | 0 | 20.1208 | 0 | 0 | 10158.21
8 | 22 | 11 | 0 | 11.5677 | 11.5677 | 48 | 9.1838 | 59.4389 | 59.4389 | 549.6632 | 11.5677 | 0 | 5803.0668 | 0 | 0 | 0 | 11.5677 | 0 | 0 | 5803.0668
8 | 22 | 12 | 0 | 2.8 | 2.8 | 48 | 9.8701 | 0 | 0 | 551.3943 | 0 | 2.8 | 0 | 0.29197 | 0 | 0 | 0 | 2.8 | 0 | 0
8 | 22 | 13 | 0 | 0.28699 | 0.28699 | 48 | 9.6668 | 0 | 0 | 549.2382 | 0 | 0.28699 | 0 | 0.029925 | 0 | 0 | 0 | 0.28699 | 0 | 0
8 | 22 | 14 | 0 | 6.4604 | 6.4604 | 48 | 10.2684 | 0 | 0 | 551.311 | 0 | 6.4604 | 0 | 0.67364 | 0 | 0 | 0 | 6.4604 | 0 | 0
8 | 22 | 15 | 0 | 3.0019 | 3.0019 | 48 | 11.226 | 0 | 0 | 557.2893 | 0 | 3.0019 | 0 | 0.31302 | 0 | 0 | 0 | 3.0019 | 0 | 0
8 | 22 | 16 | 0 | 14.8846 | 14.8846 | 48 | 11.853 | 0 | 0 | 562.646 | 0 | 14.8846 | 0 | 1.5521 | 0 | 0 | 0 | 14.8846 | 0 | 0
8 | 22 | 17 | 0 | 0.0025 | 0.0025 | 48 | 11.7514 | 0 | 0 | 570.1207 | 0 | 0.0025 | 0 | 0.00026068 | 0 | 0 | 0 | 0.0025 | 0 | 0
8 | 22 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 573.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 562.6029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 536.2729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 520.9203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 515.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 22 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 504.3775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 491.5688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 488.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 498.4525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 520.3372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 529.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 532.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 543.4995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 7 | 0 | 1.0862 | 1.0862 | 48 | 5.0146 | 0.49583 | 0.49583 | 552.673 | 1.0862 | 0 | 548.18 | 0 | 0 | 0 | 1.0862 | 0 | 0 | 548.18
8 | 23 | 8 | 0 | 28.4377 | 28.4377 | 48 | 6.2094 | 17.569 | 17.569 | 554.5527 | 28.4377 | 0 | 14405.1785 | 0 | 0 | 0 | 28.4377 | 0 | 0 | 14405.1785
8 | 23 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 555.4139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 544.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 11 | 0 | 0 | 0 | 0 | 9.3109 | 0 | 0 | 539.0548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 12 | 0 | 0.57104 | 0.57104 | 48 | 9.0058 | 2.0408 | 2.0408 | 537.4651 | 0.57104 | 0 | 279.5049 | 0 | 0 | 0 | 0.57104 | 0 | 0 | 279.5049
8 | 23 | 13 | 0 | 0.032437 | 0.032437 | 48 | 8.4889 | 0.061517 | 0.061517 | 538.1363 | 0.032437 | 0 | 15.8988 | 0 | 0 | 0 | 0.032437 | 0 | 0 | 15.8988
8 | 23 | 14 | 0 | 8.0938 | 8.0938 | 48 | 8.938 | 25.9193 | 25.9193 | 540.6531 | 8.0938 | 0 | 3987.4167 | 0 | 0 | 0 | 8.0938 | 0 | 0 | 3987.4167
8 | 23 | 15 | 0 | 0.94163 | 0.94163 | 48 | 9.6075 | 0 | 0 | 549.4344 | 0 | 0.94163 | 0 | 0.098186 | 0 | 0 | 0 | 0.94163 | 0 | 0
8 | 23 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 557.1898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 17 | 0 | 0.0075 | 0.0075 | 48 | 10.3786 | 0 | 0 | 558.2056 | 0 | 0.0075 | 0 | 0.00078205 | 0 | 0 | 0 | 0.0075 | 0 | 0
8 | 23 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 552.8338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 528.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 505.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 490.1709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 474.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 23 | 23 | 4.2386 | 0 | 4.2386 | 11 | 4.2265 | 1.6506 | 1.6506 | 469.6939 | 4.2386 | 0 | 1944.2057 | 0 | 0 | 0 | 4.2386 | 0 | 0 | 1944.2057
8 | 24 | 0 | 155.1133 | 0 | 155.1133 | 11 | 4.1757 | 59.8358 | 59.8358 | 462.2234 | 155.1133 | 0 | 69990.7422 | 0 | 0 | 0 | 155.1133 | 0 | 0 | 69990.7422
8 | 24 | 1 | 79.1167 | 0 | 79.1167 | 11 | 3.8791 | 28.9348 | 28.9348 | 458.1965 | 79.1167 | 0 | 35380.7316 | 0 | 0 | 0 | 79.1167 | 0 | 0 | 35380.7316
8 | 24 | 2 | 149.3134 | 0 | 149.3134 | 11 | 3.8197 | 54.046 | 54.046 | 463.4326 | 149.3134 | 0 | 67554.2529 | 0 | 0 | 0 | 149.3134 | 0 | 0 | 67554.2529
8 | 24 | 3 | 129.7696 | 0 | 129.7696 | 11 | 3.4638 | 44.2431 | 44.2431 | 488.2743 | 129.7696 | 0 | 61935.6902 | 0 | 0 | 0 | 129.7696 | 0 | 0 | 61935.6902
8 | 24 | 4 | 125.4066 | 0 | 125.4066 | 11 | 3.4045 | 42.3456 | 42.3456 | 493.7704 | 125.4066 | 0 | 60542.6172 | 0 | 0 | 0 | 125.4066 | 0 | 0 | 60542.6172
8 | 24 | 5 | 122.6924 | 0 | 122.6924 | 11 | 3.6418 | 43.0816 | 43.0816 | 494.0506 | 122.6924 | 0 | 59266.6122 | 0 | 0 | 0 | 122.6924 | 0 | 0 | 59266.6122
8 | 24 | 6 | 108.5946 | 0 | 108.5946 | 11 | 4.396 | 43.6678 | 43.6678 | 505.6766 | 108.5946 | 0 | 53719.2207 | 0 | 0 | 0 | 108.5946 | 0 | 0 | 53719.2207
8 | 24 | 7 | 67.2452 | 0 | 67.2452 | 11 | 4.6502 | 28.432 | 28.432 | 516.6767 | 67.2452 | 0 | 34004.3448 | 0 | 0 | 0 | 67.2452 | 0 | 0 | 34004.3448
8 | 24 | 8 | 40.0978 | 0.005 | 40.1028 | 11.0046 | 5.1417 | 18.8292 | 18.8292 | 528.9921 | 40.1028 | 0 | 20772.751 | 0 | 0 | 0 | 40.1028 | 0 | 0 | 20772.751
8 | 24 | 9 | 6.6135 | 0 | 6.6135 | 11 | 6.6161 | 4.6447 | 4.6447 | 533.2694 | 6.6135 | 0 | 3454.0406 | 0 | 0 | 0 | 6.6135 | 0 | 0 | 3454.0406
8 | 24 | 10 | 0 | 0.04797 | 0.04797 | 48 | 6.9721 | 0.038269 | 0.038269 | 525.5343 | 0.04797 | 0 | 22.9075 | 0 | 0 | 0 | 0.04797 | 0 | 0 | 22.9075
8 | 24 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 517.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 12 | 0 | 0.10062 | 0.10062 | 48 | 7.8957 | 0.12402 | 0.12402 | 520.35 | 0.10062 | 0 | 47.5262 | 0 | 0 | 0 | 0.10062 | 0 | 0 | 47.5262
8 | 24 | 13 | 0 | 41.9181 | 41.9181 | 48 | 7.4381 | 40.6829 | 40.6829 | 518.2288 | 41.9181 | 0 | 19711.0976 | 0 | 0 | 0 | 41.9181 | 0 | 0 | 19711.0976
8 | 24 | 14 | 0 | 19.8958 | 19.8958 | 48 | 7.2771 | 17.9655 | 17.9655 | 525.7132 | 19.8958 | 0 | 9504.4875 | 0 | 0 | 0 | 19.8958 | 0 | 0 | 9504.4875
8 | 24 | 15 | 0 | 37.1169 | 37.1169 | 48 | 7.3449 | 34.5277 | 34.5277 | 531.8951 | 37.1169 | 0 | 17960.6679 | 0 | 0 | 0 | 37.1169 | 0 | 0 | 17960.6679
8 | 24 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 527.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 17 | 0 | 0.0025 | 0.0025 | 48 | 7.167 | 0.0021548 | 0.0021548 | 530.8917 | 0.0025 | 0 | 1.2072 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.2072
8 | 24 | 18 | 0 | 0.068292 | 0.068292 | 48 | 6.7094 | 0.049513 | 0.049513 | 521.77 | 0.068292 | 0 | 32.3545 | 0 | 0 | 0 | 0.068292 | 0 | 0 | 32.3545
8 | 24 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 500.6753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 481.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 456.6585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 443.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 442.5461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 434.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 433.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 435.7191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 453.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 463.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 474.2391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 493.6627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 7 | 0.1 | 62.2031 | 62.3031 | 47.9406 | 6.1924 | 38.2993 | 38.2993 | 503.5312 | 62.3031 | 0 | 28384.7103 | 0 | 0 | 0 | 62.3031 | 0 | 0 | 28384.7103
8 | 25 | 8 | 0 | 18.0034 | 18.0034 | 48 | 6.8788 | 13.8688 | 13.8688 | 510.1651 | 18.0034 | 0 | 8320.5526 | 0 | 0 | 0 | 18.0034 | 0 | 0 | 8320.5526
8 | 25 | 9 | 0 | 103.7584 | 103.7584 | 48 | 7.3195 | 95.4399 | 95.4399 | 513.9061 | 103.7584 | 0 | 48341.6685 | 0 | 0 | 0 | 103.7584 | 0 | 0 | 48341.6685
8 | 25 | 10 | 0 | 199.4165 | 199.4165 | 48 | 7.4805 | 197.4272 | 197.4272 | 503.3039 | 199.4165 | 0 | 90795.1116 | 0 | 0 | 0 | 199.4165 | 0 | 0 | 90795.1116
8 | 25 | 11 | 0 | 170.989 | 170.989 | 48 | 7.2263 | 151.0788 | 151.0788 | 501.9624 | 170.989 | 0 | 77622.5565 | 0 | 0 | 0 | 170.989 | 0 | 0 | 77622.5565
8 | 25 | 12 | 0 | 44.8511 | 44.8511 | 48 | 7.8703 | 54.4671 | 54.4671 | 496.1297 | 44.8511 | 0 | 20099.1232 | 0 | 0 | 0 | 44.8511 | 0 | 0 | 20099.1232
8 | 25 | 13 | 0 | 4.78 | 4.78 | 48 | 8.1754 | 7.0564 | 7.0564 | 494.6761 | 4.78 | 0 | 2135.1291 | 0 | 0 | 0 | 4.78 | 0 | 0 | 2135.1291
8 | 25 | 14 | 0 | 55.1343 | 55.1343 | 48 | 8.2431 | 85.487 | 85.487 | 498.3056 | 55.1343 | 0 | 24827.2757 | 0 | 0 | 0 | 55.1343 | 0 | 0 | 24827.2757
8 | 25 | 15 | 0 | 5.7227 | 5.7227 | 48 | 7.4212 | 5.5107 | 5.5107 | 511.9435 | 5.7227 | 0 | 2655.0002 | 0 | 0 | 0 | 5.7227 | 0 | 0 | 2655.0002
8 | 25 | 16 | 0 | 29.502 | 29.502 | 48 | 7.3195 | 27.1368 | 27.1368 | 502.2926 | 29.502 | 0 | 13402.5349 | 0 | 0 | 0 | 29.502 | 0 | 0 | 13402.5349
8 | 25 | 17 | 0 | 0.096245 | 0.096245 | 48 | 7.2686 | 0.08659 | 0.08659 | 499.3853 | 0.096245 | 0 | 43.4435 | 0 | 0 | 0 | 0.096245 | 0 | 0 | 43.4435
8 | 25 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 500.4248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 485.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 458.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 434.0538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 420.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 25 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 420.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 411.7477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 408.6827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 406.0911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 424.3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 421.8142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 419.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 439.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 457.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 467.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 477.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 481.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 11 | 0 | 0.48198 | 0.48198 | 48 | 7.2093 | 0.42283 | 0.42283 | 486.4108 | 0.48198 | 0 | 211.3058 | 0 | 0 | 0 | 0.48198 | 0 | 0 | 211.3058
8 | 26 | 12 | 0 | 1.944 | 1.944 | 48 | 7.9296 | 2.4451 | 2.4451 | 484.8933 | 1.944 | 0 | 849.3014 | 0 | 0 | 0 | 1.944 | 0 | 0 | 849.3014
8 | 26 | 13 | 0 | 1.8795 | 1.8795 | 48 | 8.2601 | 2.9513 | 2.9513 | 483.7037 | 1.8795 | 0 | 818.8967 | 0 | 0 | 0 | 1.8795 | 0 | 0 | 818.8967
8 | 26 | 14 | 0 | 0.61471 | 0.61471 | 48 | 8.5313 | 1.2124 | 1.2124 | 485.4041 | 0.61471 | 0 | 268.8779 | 0 | 0 | 0 | 0.61471 | 0 | 0 | 268.8779
8 | 26 | 15 | 0 | 0.22871 | 0.22871 | 48 | 8.4041 | 0.40275 | 0.40275 | 487.0403 | 0.22871 | 0 | 100.4122 | 0 | 0 | 0 | 0.22871 | 0 | 0 | 100.4122
8 | 26 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 490.4462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 488.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 477.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 457.0334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 447.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 426.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 413.4675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 407.243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 394.1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 393.0197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 395.8398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 397.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 395.4443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 398.1847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 410.8966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 427.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 8 | 0 | 0.11394 | 0.11394 | 48 | 4.8451 | 0.050152 | 0.050152 | 441.3278 | 0.11394 | 0 | 44.8145 | 0 | 0 | 0 | 0.11394 | 0 | 0 | 44.8145
8 | 27 | 9 | 0 | 1.0873 | 1.0873 | 48 | 6.3789 | 0.7072 | 0.7072 | 455.7945 | 1.0873 | 0 | 443.3993 | 0 | 0 | 0 | 1.0873 | 0 | 0 | 443.3993
8 | 27 | 10 | 0 | 1.1352 | 1.1352 | 48 | 8.4804 | 2.1365 | 2.1365 | 466.1372 | 1.1352 | 0 | 474.6746 | 0 | 0 | 0 | 1.1352 | 0 | 0 | 474.6746
8 | 27 | 11 | 0 | 1.5557 | 1.5557 | 48 | 9.4549 | 24.011 | 24.011 | 471.2721 | 1.5557 | 0 | 658.4669 | 0 | 0 | 0 | 1.5557 | 0 | 0 | 658.4669
8 | 27 | 12 | 0 | 4.4019 | 4.4019 | 48 | 9.8362 | 0 | 0 | 466.4645 | 0 | 4.4019 | 0 | 0.459 | 0 | 0 | 0 | 4.4019 | 0 | 0
8 | 27 | 13 | 0 | 1.7523 | 1.7523 | 48 | 9.6159 | 0 | 0 | 465.8617 | 0 | 1.7523 | 0 | 0.18272 | 0 | 0 | 0 | 1.7523 | 0 | 0
8 | 27 | 14 | 0 | 1.7752 | 1.7752 | 48 | 9.5227 | 54.9028 | 54.9028 | 472.8195 | 1.7752 | 0 | 754.1317 | 0 | 0 | 0 | 1.7752 | 0 | 0 | 754.1317
8 | 27 | 15 | 0 | 0.024147 | 0.024147 | 48 | 10.7175 | 0 | 0 | 478.9194 | 0 | 0.024147 | 0 | 0.0025179 | 0 | 0 | 0 | 0.024147 | 0 | 0
8 | 27 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 483.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 484.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 479.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 475.3229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 456.7371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 431.6794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 422.3858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 411.4411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 408.5016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 413.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 417.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 449.2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 463.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 470.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 477.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 484.3107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 8 | 0 | 0.016667 | 0.016667 | 48 | 5.4976 | 0.008506 | 0.008506 | 492.9042 | 0.016667 | 0 | 7.4151 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 7.4151
8 | 28 | 9 | 0 | 0.37789 | 0.37789 | 48 | 6.4043 | 0.24774 | 0.24774 | 494.8707 | 0.37789 | 0 | 168.8669 | 0 | 0 | 0 | 0.37789 | 0 | 0 | 168.8669
8 | 28 | 10 | 0 | 3.7037 | 3.7037 | 48 | 8.5991 | 7.8047 | 7.8047 | 481.5821 | 3.7037 | 0 | 1605.8641 | 0 | 0 | 0 | 3.7037 | 0 | 0 | 1605.8641
8 | 28 | 11 | 0 | 3.5677 | 3.5677 | 48 | 9.6413 | 0 | 0 | 480.317 | 0 | 3.5677 | 0 | 0.37202 | 0 | 0 | 0 | 3.5677 | 0 | 0
8 | 28 | 12 | 0 | 1.29 | 1.29 | 48 | 9.7176 | 0 | 0 | 485.6035 | 0 | 1.29 | 0 | 0.13452 | 0 | 0 | 0 | 1.29 | 0 | 0
8 | 28 | 13 | 0 | 0.57276 | 0.57276 | 48 | 9.7939 | 0 | 0 | 487.7378 | 0 | 0.57276 | 0 | 0.059724 | 0 | 0 | 0 | 0.57276 | 0 | 0
8 | 28 | 14 | 0 | 13.1831 | 13.1831 | 48 | 9.4634 | 217.0689 | 217.0689 | 484.9986 | 13.1831 | 0 | 5760.9991 | 0 | 0 | 0 | 13.1831 | 0 | 0 | 5760.9991
8 | 28 | 15 | 0 | 14.3731 | 14.3731 | 48 | 10.5311 | 0 | 0 | 488.0017 | 0 | 14.3731 | 0 | 1.4987 | 0 | 0 | 0 | 14.3731 | 0 | 0
8 | 28 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 479.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 17 | 0 | 0.059958 | 0.059958 | 48 | 11.1073 | 0 | 0 | 490.3883 | 0 | 0.059958 | 0 | 0.006252 | 0 | 0 | 0 | 0.059958 | 0 | 0
8 | 28 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 494.9489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 483.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 468.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 447.9002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 441.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 431.5501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 426.4152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 429.558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 441.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 463.3816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 474.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 480.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 489.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 7 | 0 | 1.5529 | 1.5529 | 48 | 5.2518 | 0.74763 | 0.74763 | 496.4938 | 1.5529 | 0 | 696.4549 | 0 | 0 | 0 | 1.5529 | 0 | 0 | 696.4549
8 | 29 | 8 | 0 | 0.037523 | 0.037523 | 48 | 6.2094 | 0.023182 | 0.023182 | 498.3875 | 0.037523 | 0 | 16.8998 | 0 | 0 | 0 | 0.037523 | 0 | 0 | 16.8998
8 | 29 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 504.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 10 | 0 | 1.4723 | 1.4723 | 48 | 8.5482 | 2.9512 | 2.9512 | 503.9765 | 1.4723 | 0 | 671.3478 | 0 | 0 | 0 | 1.4723 | 0 | 0 | 671.3478
8 | 29 | 11 | 0 | 3.4803 | 3.4803 | 48 | 9.1838 | 17.883 | 17.883 | 498.8151 | 3.4803 | 0 | 1568.9691 | 0 | 0 | 0 | 3.4803 | 0 | 0 | 1568.9691
8 | 29 | 12 | 0 | 3.4117 | 3.4117 | 48 | 9.8701 | 0 | 0 | 496.7018 | 0 | 3.4117 | 0 | 0.35575 | 0 | 0 | 0 | 3.4117 | 0 | 0
8 | 29 | 13 | 0 | 14.0919 | 14.0919 | 48 | 9.6668 | 0 | 0 | 497.6244 | 0 | 14.0919 | 0 | 1.4694 | 0 | 0 | 0 | 14.0919 | 0 | 0
8 | 29 | 14 | 0 | 13.726 | 13.726 | 48 | 10.2684 | 0 | 0 | 495.4781 | 0 | 13.726 | 0 | 1.4312 | 0 | 0 | 0 | 13.726 | 0 | 0
8 | 29 | 15 | 0 | 3.6042 | 3.6042 | 48 | 11.226 | 0 | 0 | 509.0677 | 0 | 3.6042 | 0 | 0.37582 | 0 | 0 | 0 | 3.6042 | 0 | 0
8 | 29 | 16 | 0 | 12.2061 | 12.2061 | 48 | 11.853 | 0 | 0 | 504.5527 | 0 | 12.2061 | 0 | 1.2728 | 0 | 0 | 0 | 12.2061 | 0 | 0
8 | 29 | 17 | 0 | 6.7035 | 6.7035 | 48 | 11.7514 | 0 | 0 | 497.377 | 0 | 6.7035 | 0 | 0.69899 | 0 | 0 | 0 | 6.7035 | 0 | 0
8 | 29 | 18 | 0 | 0.31162 | 0.31162 | 48 | 12.4971 | 0 | 0 | 501.9419 | 0 | 0.31162 | 0 | 0.032494 | 0 | 0 | 0 | 0.31162 | 0 | 0
8 | 29 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 487.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 465.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 21 | 1.3725 | 0 | 1.3725 | 11 | 9.904 | 0 | 0 | 451.0072 | 0 | 1.3725 | 0 | 0.14312 | 0 | 0 | 0 | 1.3725 | 0 | 0
8 | 29 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 443.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 29 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 435.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 429.3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 428.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 441.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 465.6139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 472.7925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 478.4531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 486.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 492.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 503.4201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 513.0883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 10 | 0 | 0.016667 | 0.016667 | 48 | 8.0567 | 0.022701 | 0.022701 | 519.4248 | 0.016667 | 0 | 7.8571 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 7.8571
8 | 30 | 11 | 0 | 0 | 0 | 0 | 9.3109 | 0 | 0 | 510.5009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 505.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 505.9526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 506.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 15 | 0 | 0.0075 | 0.0075 | 48 | 9.6075 | 0 | 0 | 511.271 | 0 | 0.0075 | 0 | 0.00078205 | 0 | 0 | 0 | 0.0075 | 0 | 0
8 | 30 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 511.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 518.6542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 523.6538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 514.9108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 489.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 465.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 443.854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 30 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 433.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 427.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 426.3468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 439.5661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 465.4584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 476.2821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 480.7661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 489.4068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 500.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 507.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 9 | 0 | 0.0075 | 0.0075 | 48 | 6.6161 | 0.0052673 | 0.0052673 | 502.1176 | 0.0075 | 0 | 3.4059 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.4059
8 | 31 | 10 | 0 | 0.023333 | 0.023333 | 48 | 6.9721 | 0.018615 | 0.018615 | 497.7893 | 0.023333 | 0 | 10.4951 | 0 | 0 | 0 | 0.023333 | 0 | 0 | 10.4951
8 | 31 | 11 | 0 | 0.064167 | 0.064167 | 48 | 8.5652 | 0.13075 | 0.13075 | 496.2604 | 0.064167 | 0 | 28.7634 | 0 | 0 | 0 | 0.064167 | 0 | 0 | 28.7634
8 | 31 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 494.5905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 13 | 0 | 0.31083 | 0.31083 | 48 | 7.4381 | 0.30167 | 0.30167 | 488.7089 | 0.31083 | 0 | 136.987 | 0 | 0 | 0 | 0.31083 | 0 | 0 | 136.987
8 | 31 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 489.1397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 15 | 0 | 0.0075 | 0.0075 | 48 | 7.3449 | 0.0069769 | 0.0069769 | 489.5934 | 0.0075 | 0 | 3.312 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.312
8 | 31 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 487.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 494.2191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 499.1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 481.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 449.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 432.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 420.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 31 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 405.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 397.5993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 399.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 410.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 433.0335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 444.8255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 449.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 449.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 448.2474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 8 | 0 | 3.605 | 3.605 | 48 | 6.8788 | 2.7771 | 2.7771 | 447.1683 | 3.605 | 0 | 1438.9852 | 0 | 0 | 0 | 3.605 | 0 | 0 | 1438.9852
9 | 1 | 9 | 0 | 0.74058 | 0.74058 | 48 | 7.3195 | 0.68121 | 0.68121 | 436.2097 | 0.74058 | 0 | 287.5011 | 0 | 0 | 0 | 0.74058 | 0 | 0 | 287.5011
9 | 1 | 10 | 0 | 3.7036 | 3.7036 | 48 | 7.4805 | 3.6666 | 3.6666 | 442.4646 | 3.7036 | 0 | 1460.9282 | 0 | 0 | 0 | 3.7036 | 0 | 0 | 1460.9282
9 | 1 | 11 | 0 | 1.3925 | 1.3925 | 48 | 7.2263 | 1.2303 | 1.2303 | 440.7197 | 1.3925 | 0 | 546.8519 | 0 | 0 | 0 | 1.3925 | 0 | 0 | 546.8519
9 | 1 | 12 | 0 | 0.6274 | 0.6274 | 48 | 7.8703 | 0.76191 | 0.76191 | 444.5583 | 0.6274 | 0 | 248.8005 | 0 | 0 | 0 | 0.6274 | 0 | 0 | 248.8005
9 | 1 | 13 | 0 | 0.84158 | 0.84158 | 48 | 8.1754 | 1.2424 | 1.2424 | 443.4993 | 0.84158 | 0 | 332.8458 | 0 | 0 | 0 | 0.84158 | 0 | 0 | 332.8458
9 | 1 | 14 | 0 | 1.451 | 1.451 | 48 | 8.2431 | 2.2499 | 2.2499 | 440.0919 | 1.451 | 0 | 568.9447 | 0 | 0 | 0 | 1.451 | 0 | 0 | 568.9447
9 | 1 | 15 | 0 | 0.73996 | 0.73996 | 48 | 7.4212 | 0.71254 | 0.71254 | 440.6954 | 0.73996 | 0 | 290.5782 | 0 | 0 | 0 | 0.73996 | 0 | 0 | 290.5782
9 | 1 | 16 | 0 | 4.1183 | 4.1183 | 48 | 7.3195 | 3.7882 | 3.7882 | 440.9572 | 4.1183 | 0 | 1618.3285 | 0 | 0 | 0 | 4.1183 | 0 | 0 | 1618.3285
9 | 1 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 443.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 438.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 19 | 0 | 0.31162 | 0.31162 | 48 | 6.9382 | 0.24543 | 0.24543 | 421.3191 | 0.31162 | 0 | 116.3356 | 0 | 0 | 0 | 0.31162 | 0 | 0 | 116.3356
9 | 1 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 408.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 394.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 389.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 387.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 393.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 392.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 404.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 407.2079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 408.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 413.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 430.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 7 | 0 | 1.2479 | 1.2479 | 48 | 6.006 | 0.7272 | 0.7272 | 436.9114 | 1.2479 | 0 | 485.3128 | 0 | 0 | 0 | 1.2479 | 0 | 0 | 485.3128
9 | 2 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 450.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 9 | 0 | 0.0075 | 0.0075 | 48 | 7.1924 | 0.0065331 | 0.0065331 | 453.1105 | 0.0075 | 0 | 3.0383 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.0383
9 | 2 | 10 | 0 | 0.57928 | 0.57928 | 48 | 7.0398 | 0.47442 | 0.47442 | 448.2304 | 0.57928 | 0 | 231.8464 | 0 | 0 | 0 | 0.57928 | 0 | 0 | 231.8464
9 | 2 | 11 | 0 | 0.76239 | 0.76239 | 48 | 7.2093 | 0.66882 | 0.66882 | 449.0908 | 0.76239 | 0 | 305.7862 | 0 | 0 | 0 | 0.76239 | 0 | 0 | 305.7862
9 | 2 | 12 | 0 | 0.56433 | 0.56433 | 48 | 7.9296 | 0.7098 | 0.7098 | 446.9131 | 0.56433 | 0 | 225.1181 | 0 | 0 | 0 | 0.56433 | 0 | 0 | 225.1181
9 | 2 | 13 | 0 | 0.49131 | 0.49131 | 48 | 8.2601 | 0.77149 | 0.77149 | 446.2891 | 0.49131 | 0 | 195.6832 | 0 | 0 | 0 | 0.49131 | 0 | 0 | 195.6832
9 | 2 | 14 | 0 | 10.9495 | 10.9495 | 48 | 8.5313 | 21.5965 | 21.5965 | 445.161 | 10.9495 | 0 | 4348.7316 | 0 | 0 | 0 | 10.9495 | 0 | 0 | 4348.7316
9 | 2 | 15 | 0 | 36.5301 | 36.5301 | 48 | 8.4041 | 64.3295 | 64.3295 | 444.1175 | 36.5301 | 0 | 14470.2333 | 0 | 0 | 0 | 36.5301 | 0 | 0 | 14470.2333
9 | 2 | 16 | 0 | 6.6229 | 6.6229 | 48 | 9.1753 | 33.3359 | 33.3359 | 442.9819 | 6.6229 | 0 | 2615.9156 | 0 | 0 | 0 | 6.6229 | 0 | 0 | 2615.9156
9 | 2 | 17 | 0 | 2.4583 | 2.4583 | 48 | 8.6753 | 5.6121 | 5.6121 | 451.4501 | 2.4583 | 0 | 991.798 | 0 | 0 | 0 | 2.4583 | 0 | 0 | 991.798
9 | 2 | 18 | 0 | 1.5173 | 1.5173 | 48 | 9.0397 | 5.7564 | 5.7564 | 455.1219 | 1.5173 | 0 | 617.7227 | 0 | 0 | 0 | 1.5173 | 0 | 0 | 617.7227
9 | 2 | 19 | 0 | 0.31162 | 0.31162 | 48 | 7.6754 | 0.33992 | 0.33992 | 447.891 | 0.31162 | 0 | 124.616 | 0 | 0 | 0 | 0.31162 | 0 | 0 | 124.616
9 | 2 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 431.8047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 427.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 424.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 420.8397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 414.1329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 410.2806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 414.8801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 425.8069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 417.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 411.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 418.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 434.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 8 | 0 | 4.68 | 4.68 | 48 | 4.8451 | 2.06 | 2.06 | 440.3954 | 4.68 | 0 | 1836.4104 | 0 | 0 | 0 | 4.68 | 0 | 0 | 1836.4104
9 | 3 | 9 | 0 | 24.8117 | 24.8117 | 48 | 6.3789 | 16.1378 | 16.1378 | 445.7421 | 24.8117 | 0 | 9868.6772 | 0 | 0 | 0 | 24.8117 | 0 | 0 | 9868.6772
9 | 3 | 10 | 0 | 0.85 | 0.85 | 48 | 8.4804 | 1.5997 | 1.5997 | 459.5034 | 0.85 | 0 | 349.7779 | 0 | 0 | 0 | 0.85 | 0 | 0 | 349.7779
9 | 3 | 11 | 0 | 4.6731 | 4.6731 | 48 | 9.4549 | 72.1282 | 72.1282 | 461.4797 | 4.6731 | 0 | 1932.2481 | 0 | 0 | 0 | 4.6731 | 0 | 0 | 1932.2481
9 | 3 | 12 | 0 | 0.028512 | 0.028512 | 48 | 9.8362 | 0 | 0 | 461.4392 | 0 | 0.028512 | 0 | 0.002973 | 0 | 0 | 0 | 0.028512 | 0 | 0
9 | 3 | 13 | 0 | 0.014879 | 0.014879 | 48 | 9.6159 | 0 | 0 | 453.9734 | 0 | 0.014879 | 0 | 0.0015515 | 0 | 0 | 0 | 0.014879 | 0 | 0
9 | 3 | 14 | 0 | 0.12353 | 0.12353 | 48 | 9.5227 | 3.8204 | 3.8204 | 459.9745 | 0.12353 | 0 | 50.8899 | 0 | 0 | 0 | 0.12353 | 0 | 0 | 50.8899
9 | 3 | 15 | 0 | 0.03 | 0.03 | 48 | 10.7175 | 0 | 0 | 463.9651 | 0 | 0.03 | 0 | 0.0031282 | 0 | 0 | 0 | 0.03 | 0 | 0
9 | 3 | 16 | 0 | 0.014792 | 0.014792 | 48 | 12.0564 | 0 | 0 | 464.9648 | 0 | 0.014792 | 0 | 0.0015424 | 0 | 0 | 0 | 0.014792 | 0 | 0
9 | 3 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 464.4606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 18 | 0 | 1.0574 | 1.0574 | 48 | 12.3445 | 0 | 0 | 464.8333 | 0 | 1.0574 | 0 | 0.11026 | 0 | 0 | 0 | 1.0574 | 0 | 0
9 | 3 | 19 | 0 | 0.19079 | 0.19079 | 48 | 12.2767 | 0 | 0 | 442.4102 | 0 | 0.19079 | 0 | 0.019894 | 0 | 0 | 0 | 0.19079 | 0 | 0
9 | 3 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 423.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 409.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 398.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 3 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 392.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 387.2481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 382.4081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 382.2695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 383.6943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 383.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 385.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 393.5008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 410.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 427.0412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 444.5437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 454.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 11 | 0 | 0.0058333 | 0.0058333 | 48 | 9.6413 | 0 | 0 | 458.4589 | 0 | 0.0058333 | 0 | 0.00060826 | 0 | 0 | 0 | 0.0058333 | 0 | 0
9 | 4 | 12 | 0 | 0.039167 | 0.039167 | 48 | 9.7176 | 0 | 0 | 461.0018 | 0 | 0.039167 | 0 | 0.004084 | 0 | 0 | 0 | 0.039167 | 0 | 0
9 | 4 | 13 | 0 | 0.31641 | 0.31641 | 48 | 9.7939 | 0 | 0 | 461.3788 | 0 | 0.31641 | 0 | 0.032993 | 0 | 0 | 0 | 0.31641 | 0 | 0
9 | 4 | 14 | 0 | 2.3682 | 2.3682 | 48 | 9.4634 | 38.9942 | 38.9942 | 469.5051 | 2.3682 | 0 | 998.212 | 0 | 0 | 0 | 2.3682 | 0 | 0 | 998.212
9 | 4 | 15 | 0 | 4.0162 | 4.0162 | 48 | 10.5311 | 0 | 0 | 472.8029 | 0 | 4.0162 | 0 | 0.41878 | 0 | 0 | 0 | 4.0162 | 0 | 0
9 | 4 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 472.1687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 474.9859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 485.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 19 | 0 | 0.49071 | 0.49071 | 48 | 12.6496 | 0 | 0 | 473.6207 | 0 | 0.49071 | 0 | 0.051167 | 0 | 0 | 0 | 0.49071 | 0 | 0
9 | 4 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 456.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 436.7983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 421.1277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 4 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 418.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 417.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 420.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 429.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 456.5412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 460.437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 455.0537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 472.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 481.3472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 479.4962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 9 | 0 | 0.0058334 | 0.0058334 | 48 | 7.328 | 0.0053858 | 0.0053858 | 469.975 | 0.0058334 | 0 | 2.4615 | 0 | 0 | 0 | 0.0058334 | 0 | 0 | 2.4615
9 | 5 | 10 | 0 | 0.16 | 0.16 | 48 | 8.5482 | 0.32071 | 0.32071 | 469.5568 | 0.16 | 0 | 67.4491 | 0 | 0 | 0 | 0.16 | 0 | 0 | 67.4491
9 | 5 | 11 | 0 | 0.19876 | 0.19876 | 48 | 9.1838 | 1.0213 | 1.0213 | 469.9099 | 0.19876 | 0 | 83.8586 | 0 | 0 | 0 | 0.19876 | 0 | 0 | 83.8586
9 | 5 | 12 | 0 | 3.6861 | 3.6861 | 48 | 9.8701 | 0 | 0 | 471.5329 | 0 | 3.6861 | 0 | 0.38436 | 0 | 0 | 0 | 3.6861 | 0 | 0
9 | 5 | 13 | 0 | 0.36013 | 0.36013 | 48 | 9.6668 | 0 | 0 | 475.5891 | 0 | 0.36013 | 0 | 0.037552 | 0 | 0 | 0 | 0.36013 | 0 | 0
9 | 5 | 14 | 0 | 22.35 | 22.35 | 48 | 10.2684 | 0 | 0 | 475.2663 | 0 | 22.35 | 0 | 2.3305 | 0 | 0 | 0 | 22.35 | 0 | 0
9 | 5 | 15 | 0 | 23.44 | 23.44 | 48 | 11.226 | 0 | 0 | 479.6261 | 0 | 23.44 | 0 | 2.4442 | 0 | 0 | 0 | 23.44 | 0 | 0
9 | 5 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 489.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 17 | 0 | 0.29212 | 0.29212 | 48 | 11.7514 | 0 | 0 | 486.599 | 0 | 0.29212 | 0 | 0.030461 | 0 | 0 | 0 | 0.29212 | 0 | 0
9 | 5 | 18 | 0 | 0.29975 | 0.29975 | 48 | 12.4971 | 0 | 0 | 493.1171 | 0 | 0.29975 | 0 | 0.031256 | 0 | 0 | 0 | 0.29975 | 0 | 0
9 | 5 | 19 | 0 | 0.31162 | 0.31162 | 48 | 12.7428 | 0 | 0 | 477.6172 | 0 | 0.31162 | 0 | 0.032494 | 0 | 0 | 0 | 0.31162 | 0 | 0
9 | 5 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 458.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 439.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 434.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 437.7697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 432.0362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 435.4293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 441.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 464.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 480.3708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 484.7436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 495.7949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 7 | 0 | 0.055792 | 0.055792 | 48 | 5.0146 | 0.025468 | 0.025468 | 496.1282 | 0.055792 | 0 | 25.0018 | 0 | 0 | 0 | 0.055792 | 0 | 0 | 25.0018
9 | 6 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 490.7696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 9 | 0 | 0.05543 | 0.05543 | 48 | 7.311 | 0.050796 | 0.050796 | 488.5641 | 0.05543 | 0 | 24.4203 | 0 | 0 | 0 | 0.05543 | 0 | 0 | 24.4203
9 | 6 | 10 | 0 | 1.6758 | 1.6758 | 48 | 8.0567 | 2.2825 | 2.2825 | 487.6984 | 1.6758 | 0 | 736.84 | 0 | 0 | 0 | 1.6758 | 0 | 0 | 736.84
9 | 6 | 11 | 0 | 0.41961 | 0.41961 | 48 | 9.3109 | 3.137 | 3.137 | 480.8147 | 0.41961 | 0 | 181.612 | 0 | 0 | 0 | 0.41961 | 0 | 0 | 181.612
9 | 6 | 12 | 0 | 3.1791 | 3.1791 | 48 | 9.0058 | 11.3615 | 11.3615 | 475.5737 | 3.1791 | 0 | 1359.2907 | 0 | 0 | 0 | 3.1791 | 0 | 0 | 1359.2907
9 | 6 | 13 | 0 | 4.241 | 4.241 | 48 | 8.4889 | 8.043 | 8.043 | 474.3346 | 4.241 | 0 | 1808.0816 | 0 | 0 | 0 | 4.241 | 0 | 0 | 1808.0816
9 | 6 | 14 | 0 | 1.0319 | 1.0319 | 48 | 8.938 | 3.3044 | 3.3044 | 479.2359 | 1.0319 | 0 | 444.9761 | 0 | 0 | 0 | 1.0319 | 0 | 0 | 444.9761
9 | 6 | 15 | 0 | 0.023333 | 0.023333 | 48 | 9.6075 | 0 | 0 | 476.8965 | 0 | 0.023333 | 0 | 0.002433 | 0 | 0 | 0 | 0.023333 | 0 | 0
9 | 6 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 472.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 485.3935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 18 | 0 | 1.2499 | 1.2499 | 48 | 11.0734 | 0 | 0 | 478.6887 | 0 | 1.2499 | 0 | 0.13033 | 0 | 0 | 0 | 1.2499 | 0 | 0
9 | 6 | 19 | 0 | 0.31162 | 0.31162 | 48 | 10.4633 | 0 | 0 | 459.7465 | 0 | 0.31162 | 0 | 0.032494 | 0 | 0 | 0 | 0.31162 | 0 | 0
9 | 6 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 434.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 419.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 408.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 6 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 412.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 408.7541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 408.9346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 412.8219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 438.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 463.9551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 464.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 6 | 0 | 3.695 | 3.695 | 48 | 4.396 | 1.4858 | 1.4858 | 462.9079 | 3.695 | 0 | 1533.0848 | 0 | 0 | 0 | 3.695 | 0 | 0 | 1533.0848
9 | 7 | 7 | 0 | 0.14037 | 0.14037 | 48 | 4.6502 | 0.059352 | 0.059352 | 477.2777 | 0.14037 | 0 | 60.2599 | 0 | 0 | 0 | 0.14037 | 0 | 0 | 60.2599
9 | 7 | 8 | 0 | 8.9248 | 8.9248 | 48 | 5.1417 | 4.1904 | 4.1904 | 478.5488 | 8.9248 | 0 | 3842.5713 | 0 | 0 | 0 | 8.9248 | 0 | 0 | 3842.5713
9 | 7 | 9 | 0 | 0.0075 | 0.0075 | 48 | 6.6161 | 0.0052673 | 0.0052673 | 462.6272 | 0.0075 | 0 | 3.1097 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.1097
9 | 7 | 10 | 0 | 95.3122 | 95.3122 | 48 | 6.9721 | 76.037 | 76.037 | 463.2895 | 95.3122 | 0 | 39582.169 | 0 | 0 | 0 | 95.3122 | 0 | 0 | 39582.169
9 | 7 | 11 | 0.04 | 109.3463 | 109.3863 | 47.9865 | 8.5652 | 222.8839 | 222.8839 | 464.9829 | 109.3863 | 0 | 45613.6796 | 0 | 0 | 0 | 109.3863 | 0 | 0 | 45613.6796
9 | 7 | 12 | 0 | 3.5827 | 3.5827 | 48 | 7.8957 | 4.4161 | 4.4161 | 461.8515 | 3.5827 | 0 | 1482.6952 | 0 | 0 | 0 | 3.5827 | 0 | 0 | 1482.6952
9 | 7 | 13 | 0 | 5.3721 | 5.3721 | 48 | 7.4381 | 5.2138 | 5.2138 | 465.52 | 5.3721 | 0 | 2242.977 | 0 | 0 | 0 | 5.3721 | 0 | 0 | 2242.977
9 | 7 | 14 | 0 | 0.698 | 0.698 | 48 | 7.2771 | 0.63028 | 0.63028 | 466.6921 | 0.698 | 0 | 292.2456 | 0 | 0 | 0 | 0.698 | 0 | 0 | 292.2456
9 | 7 | 15 | 0 | 0.0025 | 0.0025 | 48 | 7.3449 | 0.0023256 | 0.0023256 | 479.768 | 0.0025 | 0 | 1.0794 | 0 | 0 | 0 | 0.0025 | 0 | 0 | 1.0794
9 | 7 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 479.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 478.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 18 | 0 | 1.2499 | 1.2499 | 48 | 6.7094 | 0.90622 | 0.90622 | 483.0346 | 1.2499 | 0 | 543.757 | 0 | 0 | 0 | 1.2499 | 0 | 0 | 543.757
9 | 7 | 19 | 0 | 0.31162 | 0.31162 | 48 | 7.3958 | 0.2966 | 0.2966 | 462.5407 | 0.31162 | 0 | 129.1813 | 0 | 0 | 0 | 0.31162 | 0 | 0 | 129.1813
9 | 7 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 439.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 415.3371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 407.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 401.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 396.5115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 394.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 400.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 428.5709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 445.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 452.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 455.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 7 | 0 | 0.83788 | 0.83788 | 48 | 6.1924 | 0.51506 | 0.51506 | 469.1319 | 0.83788 | 0 | 352.8559 | 0 | 0 | 0 | 0.83788 | 0 | 0 | 352.8559
9 | 8 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 470.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 9 | 0 | 0.0083334 | 0.0083334 | 48 | 7.3195 | 0.0076653 | 0.0076653 | 466.3421 | 0.0083334 | 0 | 3.4862 | 0 | 0 | 0 | 0.0083334 | 0 | 0 | 3.4862
9 | 8 | 10 | 0 | 1.3865 | 1.3865 | 48 | 7.4805 | 1.3727 | 1.3727 | 462.036 | 1.3865 | 0 | 574.0664 | 0 | 0 | 0 | 1.3865 | 0 | 0 | 574.0664
9 | 8 | 11 | 0 | 59.9654 | 59.9654 | 48 | 7.2263 | 52.9829 | 52.9829 | 466.5667 | 59.9654 | 0 | 25099.5171 | 0 | 0 | 0 | 59.9654 | 0 | 0 | 25099.5171
9 | 8 | 12 | 0 | 2.5595 | 2.5595 | 48 | 7.8703 | 3.1082 | 3.1082 | 465.0256 | 2.5595 | 0 | 1067.3588 | 0 | 0 | 0 | 2.5595 | 0 | 0 | 1067.3588
9 | 8 | 13 | 0 | 2.1537 | 2.1537 | 48 | 8.1754 | 3.1793 | 3.1793 | 472.0265 | 2.1537 | 0 | 913.2192 | 0 | 0 | 0 | 2.1537 | 0 | 0 | 913.2192
9 | 8 | 14 | 0 | 1.2111 | 1.2111 | 48 | 8.2431 | 1.8779 | 1.8779 | 475.9601 | 1.2111 | 0 | 518.3227 | 0 | 0 | 0 | 1.2111 | 0 | 0 | 518.3227
9 | 8 | 15 | 0 | 0.22841 | 0.22841 | 48 | 7.4212 | 0.21994 | 0.21994 | 481.2697 | 0.22841 | 0 | 98.9611 | 0 | 0 | 0 | 0.22841 | 0 | 0 | 98.9611
9 | 8 | 16 | 0 | 0.005 | 0.005 | 48 | 7.3195 | 0.0045992 | 0.0045992 | 470.1812 | 0.005 | 0 | 2.1109 | 0 | 0 | 0 | 0.005 | 0 | 0 | 2.1109
9 | 8 | 17 | 0 | 0.017458 | 0.017458 | 48 | 7.2686 | 0.015707 | 0.015707 | 475.2576 | 0.017458 | 0 | 7.4592 | 0 | 0 | 0 | 0.017458 | 0 | 0 | 7.4592
9 | 8 | 18 | 0 | 1.2499 | 1.2499 | 48 | 6.9297 | 0.98126 | 0.98126 | 464.2745 | 1.2499 | 0 | 520.3084 | 0 | 0 | 0 | 1.2499 | 0 | 0 | 520.3084
9 | 8 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 449.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 436.1468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 403.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 391.1477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 8 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 391.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 386.9367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 384.9421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 385.2193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 399.9248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 396.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 396.4312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 410.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 421.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 434.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 9 | 0 | 1.612 | 1.612 | 48 | 7.1924 | 1.4042 | 1.4042 | 440.6431 | 1.612 | 0 | 632.957 | 0 | 0 | 0 | 1.612 | 0 | 0 | 632.957
9 | 9 | 10 | 0 | 1.3371 | 1.3371 | 48 | 7.0398 | 1.095 | 1.095 | 447.6472 | 1.3371 | 0 | 534.3509 | 0 | 0 | 0 | 1.3371 | 0 | 0 | 534.3509
9 | 9 | 11 | 0 | 0.8316 | 0.8316 | 48 | 7.2093 | 0.72954 | 0.72954 | 445.975 | 0.8316 | 0 | 330.9551 | 0 | 0 | 0 | 0.8316 | 0 | 0 | 330.9551
9 | 9 | 12 | 0 | 1.2259 | 1.2259 | 48 | 7.9296 | 1.5419 | 1.5419 | 450.1808 | 1.2259 | 0 | 493.0424 | 0 | 0 | 0 | 1.2259 | 0 | 0 | 493.0424
9 | 9 | 13 | 0 | 1.7862 | 1.7862 | 48 | 8.2601 | 2.8049 | 2.8049 | 444.7048 | 1.7862 | 0 | 708.6075 | 0 | 0 | 0 | 1.7862 | 0 | 0 | 708.6075
9 | 9 | 14 | 0 | 0.68594 | 0.68594 | 48 | 8.5313 | 1.3529 | 1.3529 | 445.3567 | 0.68594 | 0 | 272.5613 | 0 | 0 | 0 | 0.68594 | 0 | 0 | 272.5613
9 | 9 | 15 | 0 | 0.41392 | 0.41392 | 48 | 8.4041 | 0.72892 | 0.72892 | 448.1226 | 0.41392 | 0 | 165.62 | 0 | 0 | 0 | 0.41392 | 0 | 0 | 165.62
9 | 9 | 16 | 0 | 4.3516 | 4.3516 | 48 | 9.1753 | 21.9036 | 21.9036 | 440.0743 | 4.3516 | 0 | 1706.1526 | 0 | 0 | 0 | 4.3516 | 0 | 0 | 1706.1526
9 | 9 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 437.9812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 428.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 416.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 404.6956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 379.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 378.0168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 9 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 384.6275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 386.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 389.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 391.3141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 396.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 395.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 399.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 406.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 7 | 0 | 0.76121 | 0.76121 | 48 | 4.8705 | 0.33687 | 0.33687 | 418.9258 | 0.76121 | 0 | 282.3518 | 0 | 0 | 0 | 0.76121 | 0 | 0 | 282.3518
9 | 10 | 8 | 0.21167 | 178.0509 | 178.2626 | 47.9561 | 4.8451 | 78.4672 | 78.4672 | 427.3216 | 178.2626 | 0 | 67626.671 | 0 | 0 | 0 | 178.2626 | 0 | 0 | 67626.671
9 | 10 | 9 | 0 | 5.5098 | 5.5098 | 48 | 6.3789 | 3.5836 | 3.5836 | 439.6328 | 5.5098 | 0 | 2157.818 | 0 | 0 | 0 | 5.5098 | 0 | 0 | 2157.818
9 | 10 | 10 | 0 | 74.5468 | 74.5468 | 48 | 8.4804 | 140.2977 | 140.2977 | 446.3878 | 74.5468 | 0 | 29698.5293 | 0 | 0 | 0 | 74.5468 | 0 | 0 | 29698.5293
9 | 10 | 11 | 0 | 21.5072 | 21.5072 | 48 | 9.4549 | 331.9553 | 288 | 453.6143 | 18.6593 | 2.8478 | 7568.4943 | 0.29695 | 0 | 0 | 18.6593 | 2.8478 | 0 | 7568.4943
9 | 10 | 12 | 0 | 0.75379 | 0.75379 | 48 | 9.8362 | 0 | 0 | 450.6199 | 0 | 0.75379 | 0 | 0.0786 | 0 | 0 | 0 | 0.75379 | 0 | 0
9 | 10 | 13 | 0.0091667 | 0.38003 | 0.38919 | 47.1285 | 9.6159 | 0 | 0 | 451.9633 | 0 | 0.38919 | 0 | 0.040582 | 0 | 0 | 0 | 0.38919 | 0 | 0
9 | 10 | 14 | 1.7212 | 21.4493 | 23.1705 | 45.2515 | 9.5227 | 716.6173 | 288 | 452.6779 | 9.312 | 13.8586 | 3793.9361 | 1.4451 | 0 | 0 | 9.312 | 13.8586 | 0 | 3793.9361
9 | 10 | 15 | 0 | 4.9501 | 4.9501 | 48 | 10.7175 | 0 | 0 | 452.2752 | 0 | 4.9501 | 0 | 0.51616 | 0 | 0 | 0 | 4.9501 | 0 | 0
9 | 10 | 16 | 0 | 0.047083 | 0.047083 | 48 | 12.0564 | 0 | 0 | 442.0901 | 0 | 0.047083 | 0 | 0.0049095 | 0 | 0 | 0 | 0.047083 | 0 | 0
9 | 10 | 17 | 0 | 5.6256 | 5.6256 | 48 | 11.8107 | 0 | 0 | 446.9305 | 0 | 5.6256 | 0 | 0.58659 | 0 | 0 | 0 | 5.6256 | 0 | 0
9 | 10 | 18 | 0 | 0.93408 | 0.93408 | 48 | 12.3445 | 0 | 0 | 450.0026 | 0 | 0.93408 | 0 | 0.097399 | 0 | 0 | 0 | 0.93408 | 0 | 0
9 | 10 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 435.5017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 409.4847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 385.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 392.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 10 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 401.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 394.1479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 392.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 408.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 439.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 462.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 460.1561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 462.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 7 | 0 | 3.8297 | 3.8297 | 48 | 4.8281 | 1.6797 | 1.6797 | 472.909 | 3.8297 | 0 | 1627.2609 | 0 | 0 | 0 | 3.8297 | 0 | 0 | 1627.2609
9 | 11 | 8 | 0 | 25.1381 | 25.1381 | 48 | 5.4976 | 12.8294 | 12.8294 | 478.7049 | 25.1381 | 0 | 10827.1104 | 0 | 0 | 0 | 25.1381 | 0 | 0 | 10827.1104
9 | 11 | 9 | 0 | 9.6841 | 9.6841 | 48 | 6.4043 | 6.3489 | 6.3489 | 472.9737 | 9.6841 | 0 | 4115.4982 | 0 | 0 | 0 | 9.6841 | 0 | 0 | 4115.4982
9 | 11 | 10 | 0 | 3.8249 | 3.8249 | 48 | 8.5991 | 8.0601 | 8.0601 | 467.5931 | 3.8249 | 0 | 1604.9081 | 0 | 0 | 0 | 3.8249 | 0 | 0 | 1604.9081
9 | 11 | 11 | 0 | 6.1954 | 6.1954 | 48 | 9.6413 | 0 | 0 | 460.3393 | 0 | 6.1954 | 0 | 0.64601 | 0 | 0 | 0 | 6.1954 | 0 | 0
9 | 11 | 12 | 0 | 7.1579 | 7.1579 | 48 | 9.7176 | 0 | 0 | 455.6542 | 0 | 7.1579 | 0 | 0.74637 | 0 | 0 | 0 | 7.1579 | 0 | 0
9 | 11 | 13 | 0 | 0.14478 | 0.14478 | 48 | 9.7939 | 0 | 0 | 455.0426 | 0 | 0.14478 | 0 | 0.015096 | 0 | 0 | 0 | 0.14478 | 0 | 0
9 | 11 | 14 | 0 | 0.010833 | 0.010833 | 48 | 9.4634 | 0.17838 | 0.17838 | 453.1555 | 0.010833 | 0 | 4.3892 | 0 | 0 | 0 | 0.010833 | 0 | 0 | 4.3892
9 | 11 | 15 | 0 | 0.4825 | 0.4825 | 48 | 10.5311 | 0 | 0 | 455.9005 | 0 | 0.4825 | 0 | 0.050312 | 0 | 0 | 0 | 0.4825 | 0 | 0
9 | 11 | 16 | 0 | 0.8525 | 0.8525 | 48 | 11.0904 | 0 | 0 | 455.9582 | 0 | 0.8525 | 0 | 0.088892 | 0 | 0 | 0 | 0.8525 | 0 | 0
9 | 11 | 17 | 0 | 0.68029 | 0.68029 | 48 | 11.1073 | 0 | 0 | 458.2987 | 0 | 0.68029 | 0 | 0.070936 | 0 | 0 | 0 | 0.68029 | 0 | 0
9 | 11 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 467.0725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 464.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 446.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 430.1769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 408.8699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 391.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 386.8778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 392.5713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 404.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 434.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 448.2526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 450.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 456.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 466.9012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 8 | 0 | 12.105 | 12.105 | 48 | 6.2094 | 7.4785 | 7.4785 | 468.397 | 12.105 | 0 | 5088.8938 | 0 | 0 | 0 | 12.105 | 0 | 0 | 5088.8938
9 | 12 | 9 | 0 | 0.87802 | 0.87802 | 48 | 7.328 | 0.81065 | 0.81065 | 464.7982 | 0.87802 | 0 | 365.9558 | 0 | 0 | 0 | 0.87802 | 0 | 0 | 365.9558
9 | 12 | 10 | 0 | 1.2869 | 1.2869 | 48 | 8.5482 | 2.5796 | 2.5796 | 463.8715 | 1.2869 | 0 | 535.2029 | 0 | 0 | 0 | 1.2869 | 0 | 0 | 535.2029
9 | 12 | 11 | 0 | 5.7075 | 5.7075 | 48 | 9.1838 | 29.3275 | 29.3275 | 458.4794 | 5.7075 | 0 | 2342.8271 | 0 | 0 | 0 | 5.7075 | 0 | 0 | 2342.8271
9 | 12 | 12 | 0 | 6.6152 | 6.6152 | 48 | 9.8701 | 0 | 0 | 459.1969 | 0 | 6.6152 | 0 | 0.68979 | 0 | 0 | 0 | 6.6152 | 0 | 0
9 | 12 | 13 | 0 | 6.1385 | 6.1385 | 48 | 9.6668 | 0 | 0 | 460.245 | 0 | 6.1385 | 0 | 0.64008 | 0 | 0 | 0 | 6.1385 | 0 | 0
9 | 12 | 14 | 0 | 4.5903 | 4.5903 | 48 | 10.2684 | 0 | 0 | 466.1348 | 0 | 4.5903 | 0 | 0.47864 | 0 | 0 | 0 | 4.5903 | 0 | 0
9 | 12 | 15 | 0 | 1.6551 | 1.6551 | 48 | 11.226 | 0 | 0 | 466.3552 | 0 | 1.6551 | 0 | 0.17258 | 0 | 0 | 0 | 1.6551 | 0 | 0
9 | 12 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 472.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 474.4048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 481.0961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 466.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 461.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 446.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 430.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 420.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 415.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 422.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 443.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 465.7635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 476.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 475.7457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 482.4398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 7 | 0 | 0.51454 | 0.51454 | 48 | 5.0146 | 0.23488 | 0.23488 | 489.9458 | 0.51454 | 0 | 227.3995 | 0 | 0 | 0 | 0.51454 | 0 | 0 | 227.3995
9 | 13 | 8 | 0.68172 | 0.016667 | 0.69839 | 11.883 | 6.2094 | 0.43147 | 0.43147 | 492.7645 | 0.69839 | 0 | 335.8407 | 0 | 0 | 0 | 0.69839 | 0 | 0 | 335.8407
9 | 13 | 9 | 0 | 0.84583 | 0.84583 | 48 | 7.311 | 0.77513 | 0.77513 | 488.0215 | 0.84583 | 0 | 372.1849 | 0 | 0 | 0 | 0.84583 | 0 | 0 | 372.1849
9 | 13 | 10 | 0 | 0.21333 | 0.21333 | 48 | 8.0567 | 0.29057 | 0.29057 | 483.6104 | 0.21333 | 0 | 92.9303 | 0 | 0 | 0 | 0.21333 | 0 | 0 | 92.9303
9 | 13 | 11 | 0 | 0.10417 | 0.10417 | 48 | 9.3109 | 0.77877 | 0.77877 | 478.5619 | 0.10417 | 0 | 44.8502 | 0 | 0 | 0 | 0.10417 | 0 | 0 | 44.8502
9 | 13 | 12 | 0 | 3.086 | 3.086 | 48 | 9.0058 | 11.0287 | 11.0287 | 475.9599 | 3.086 | 0 | 1320.6659 | 0 | 0 | 0 | 3.086 | 0 | 0 | 1320.6659
9 | 13 | 13 | 0 | 3.9419 | 3.9419 | 48 | 8.4889 | 7.4758 | 7.4758 | 472.8639 | 3.9419 | 0 | 1674.7878 | 0 | 0 | 0 | 3.9419 | 0 | 0 | 1674.7878
9 | 13 | 14 | 0 | 3.5341 | 3.5341 | 48 | 8.938 | 11.3177 | 11.3177 | 477.4585 | 3.5341 | 0 | 1517.7666 | 0 | 0 | 0 | 3.5341 | 0 | 0 | 1517.7666
9 | 13 | 15 | 0 | 2.1217 | 2.1217 | 48 | 9.6075 | 0 | 0 | 498.5921 | 0 | 2.1217 | 0 | 0.22124 | 0 | 0 | 0 | 2.1217 | 0 | 0
9 | 13 | 16 | 0 | 0.042797 | 0.042797 | 48 | 10.9718 | 0 | 0 | 499.4338 | 0 | 0.042797 | 0 | 0.0044625 | 0 | 0 | 0 | 0.042797 | 0 | 0
9 | 13 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 505.0689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 503.9429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 13 | 19 | 42.9769 | 0 | 42.9769 | 11 | 10.4633 | 0 | 0 | 497.0729 | 0 | 42.9769 | 0 | 4.4813 | 0 | 0 | 0 | 42.9769 | 0 | 0
9 | 13 | 20 | 118.4633 | 0 | 118.4633 | 11 | 8.0228 | 157.8613 | 157.8613 | 485.18 | 118.4633 | 0 | 56172.9171 | 0 | 0 | 0 | 118.4633 | 0 | 0 | 56172.9171
9 | 13 | 21 | 57.0886 | 0 | 57.0886 | 11 | 7.1076 | 48.0307 | 48.0307 | 469.6719 | 57.0886 | 0 | 26184.9443 | 0 | 0 | 0 | 57.0886 | 0 | 0 | 26184.9443
9 | 13 | 22 | 87.9538 | 0 | 87.9538 | 11 | 5.2264 | 42.0984 | 42.0984 | 452.6983 | 87.9538 | 0 | 38849.0563 | 0 | 0 | 0 | 87.9538 | 0 | 0 | 38849.0563
9 | 13 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 445.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 441.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 442.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 452.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 480.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 491.3106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 493.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 496.6924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 7 | 0 | 0.24083 | 0.24083 | 48 | 4.6502 | 0.10183 | 0.10183 | 503.2529 | 0.24083 | 0 | 109.6401 | 0 | 0 | 0 | 0.24083 | 0 | 0 | 109.6401
9 | 14 | 8 | 7.0117 | 352.384 | 359.3956 | 47.2781 | 5.1417 | 168.745 | 168.745 | 505.3071 | 359.3956 | 0 | 164613.6207 | 0 | 0 | 0 | 359.3956 | 0 | 0 | 164613.6207
9 | 14 | 9 | 4.0667 | 652.6237 | 656.6903 | 47.7709 | 6.6161 | 461.1937 | 288 | 504.7022 | 410.0811 | 246.6093 | 187378.8648 | 25.7146 | 0 | 0 | 410.0811 | 246.6093 | 0 | 187378.8648
9 | 14 | 10 | 0 | 340.1878 | 340.1878 | 48 | 6.9721 | 271.3909 | 271.3909 | 498.8712 | 340.1878 | 0 | 153380.8868 | 0 | 0 | 0 | 340.1878 | 0 | 0 | 153380.8868
9 | 14 | 11 | 1.3025 | 178.6992 | 180.0017 | 47.7323 | 8.5652 | 366.7689 | 288 | 495.6735 | 141.3438 | 38.658 | 63313.6926 | 4.031 | 0 | 0 | 141.3438 | 38.658 | 0 | 63313.6926
9 | 14 | 12 | 0.42917 | 118.5576 | 118.9868 | 47.8665 | 7.8957 | 146.6651 | 146.6651 | 494.3596 | 118.9868 | 0 | 53126.7608 | 0 | 0 | 0 | 118.9868 | 0 | 0 | 53126.7608
9 | 14 | 13 | 0.21667 | 22.852 | 23.0687 | 47.6525 | 7.4381 | 22.3889 | 22.3889 | 492.3313 | 23.0687 | 0 | 10258.1496 | 0 | 0 | 0 | 23.0687 | 0 | 0 | 10258.1496
9 | 14 | 14 | 5.2025 | 210.9058 | 216.1083 | 47.1093 | 7.2771 | 195.1414 | 195.1414 | 493.4527 | 216.1083 | 0 | 96458.5172 | 0 | 0 | 0 | 216.1083 | 0 | 0 | 96458.5172
9 | 14 | 15 | 17.9395 | 801.8752 | 819.8147 | 47.1904 | 7.3449 | 762.6265 | 288 | 499.3692 | 309.5967 | 510.218 | 139993.0701 | 53.2018 | 0 | 0 | 309.5967 | 510.218 | 0 | 139993.0701
9 | 14 | 16 | 5.8151 | 207.7893 | 213.6044 | 46.9927 | 6.9975 | 172.0775 | 172.0775 | 495.6253 | 213.6044 | 0 | 95829.8847 | 0 | 0 | 0 | 213.6044 | 0 | 0 | 95829.8847
9 | 14 | 17 | 0 | 14.3084 | 14.3084 | 48 | 7.167 | 12.3329 | 12.3329 | 500.7184 | 14.3084 | 0 | 6477.6833 | 0 | 0 | 0 | 14.3084 | 0 | 0 | 6477.6833
9 | 14 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 506.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 496.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 480.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 459.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 433.8097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 419.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 410.2674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 415.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 421.5555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 458.8492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 477.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 481.5903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 490.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 7 | 0 | 2.0595 | 2.0595 | 48 | 6.1924 | 1.266 | 1.266 | 502.0209 | 2.0595 | 0 | 935.0456 | 0 | 0 | 0 | 2.0595 | 0 | 0 | 935.0456
9 | 15 | 8 | 0 | 9.5157 | 9.5157 | 48 | 6.8788 | 7.3304 | 7.3304 | 506.9193 | 9.5157 | 0 | 4366.9554 | 0 | 0 | 0 | 9.5157 | 0 | 0 | 4366.9554
9 | 15 | 9 | 1.6058 | 465.6565 | 467.2624 | 47.8728 | 7.3195 | 429.8011 | 288 | 505.467 | 313.1019 | 154.1604 | 143273.6309 | 16.0747 | 0 | 0 | 313.1019 | 154.1604 | 0 | 143273.6309
9 | 15 | 10 | 1.9608 | 415.3289 | 417.2897 | 47.8261 | 7.4805 | 413.127 | 288 | 498.9587 | 290.9019 | 126.3878 | 131235.3107 | 13.1788 | 0 | 0 | 290.9019 | 126.3878 | 0 | 131235.3107
9 | 15 | 11 | 3.4183 | 808.0439 | 811.4623 | 47.8441 | 7.2263 | 716.9745 | 288 | 494.9104 | 325.9546 | 485.5077 | 145723.3112 | 50.6252 | 0 | 0 | 325.9546 | 485.5077 | 0 | 145723.3112
9 | 15 | 12 | 2.2975 | 399.7481 | 402.0456 | 47.7886 | 7.8703 | 488.2436 | 288 | 492.4265 | 237.1544 | 164.8912 | 105447.8754 | 17.1936 | 0 | 0 | 237.1544 | 164.8912 | 0 | 105447.8754
9 | 15 | 13 | 2.28 | 342.7563 | 345.0363 | 47.7555 | 8.1754 | 509.3538 | 288 | 495.1648 | 195.0912 | 149.9451 | 87285.6276 | 15.6352 | 0 | 0 | 195.0912 | 149.9451 | 0 | 87285.6276
9 | 15 | 14 | 2.0725 | 299.7108 | 301.7833 | 47.7459 | 8.2431 | 467.9218 | 288 | 499.4414 | 185.7438 | 116.0395 | 83899.6571 | 12.0997 | 0 | 0 | 185.7438 | 116.0395 | 0 | 83899.6571
9 | 15 | 15 | 3.79 | 499.994 | 503.784 | 47.7216 | 7.4212 | 485.1189 | 288 | 509.1595 | 299.0809 | 204.7031 | 138007.2247 | 21.3449 | 0 | 0 | 299.0809 | 204.7031 | 0 | 138007.2247
9 | 15 | 16 | 4.8483 | 390.8047 | 395.653 | 47.5466 | 7.3195 | 363.9328 | 288 | 505.3302 | 313.1019 | 82.5511 | 143332.9376 | 8.6078 | 0 | 0 | 313.1019 | 82.5511 | 0 | 143332.9376
9 | 15 | 17 | 0.1925 | 11.8554 | 12.0479 | 47.4088 | 7.2686 | 10.8393 | 10.8393 | 508.7147 | 12.0479 | 0 | 5557.7542 | 0 | 0 | 0 | 12.0479 | 0 | 0 | 5557.7542
9 | 15 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 506.8115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 493.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 481.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 464.5167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 443.1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 15 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 434.7853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 424.3281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 417.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 425.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 439.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 442.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 453.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 473.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 488.9954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 8 | 0 | 0.88333 | 0.88333 | 48 | 6.6246 | 0.62214 | 0.62214 | 499.7972 | 0.88333 | 0 | 399.0873 | 0 | 0 | 0 | 0.88333 | 0 | 0 | 399.0873
9 | 16 | 9 | 0 | 3.1663 | 3.1663 | 48 | 7.1924 | 2.758 | 2.758 | 500.8451 | 3.1663 | 0 | 1433.8346 | 0 | 0 | 0 | 3.1663 | 0 | 0 | 1433.8346
9 | 16 | 10 | 0 | 5.5798 | 5.5798 | 48 | 7.0398 | 4.5697 | 4.5697 | 498.6287 | 5.5798 | 0 | 2514.4122 | 0 | 0 | 0 | 5.5798 | 0 | 0 | 2514.4122
9 | 16 | 11 | 0 | 6.54 | 6.54 | 48 | 7.2093 | 5.7373 | 5.7373 | 494.2005 | 6.54 | 0 | 2918.1297 | 0 | 0 | 0 | 6.54 | 0 | 0 | 2918.1297
9 | 16 | 12 | 0 | 5.6239 | 5.6239 | 48 | 7.9296 | 7.0736 | 7.0736 | 494.0553 | 5.6239 | 0 | 2508.5633 | 0 | 0 | 0 | 5.6239 | 0 | 0 | 2508.5633
9 | 16 | 13 | 0 | 6.3566 | 6.3566 | 48 | 8.2601 | 9.9816 | 9.9816 | 493.8987 | 6.3566 | 0 | 2834.3886 | 0 | 0 | 0 | 6.3566 | 0 | 0 | 2834.3886
9 | 16 | 14 | 0 | 5.2637 | 5.2637 | 48 | 8.5313 | 10.3819 | 10.3819 | 492.6122 | 5.2637 | 0 | 2340.302 | 0 | 0 | 0 | 5.2637 | 0 | 0 | 2340.302
9 | 16 | 15 | 0 | 1.6333 | 1.6333 | 48 | 8.4041 | 2.8762 | 2.8762 | 497.2984 | 1.6333 | 0 | 733.8185 | 0 | 0 | 0 | 1.6333 | 0 | 0 | 733.8185
9 | 16 | 16 | 0 | 0.079496 | 0.079496 | 48 | 9.1753 | 0.40014 | 0.40014 | 500.695 | 0.079496 | 0 | 35.9876 | 0 | 0 | 0 | 0.079496 | 0 | 0 | 35.9876
9 | 16 | 17 | 0 | 4.9726 | 4.9726 | 48 | 8.6753 | 11.352 | 11.352 | 501.1128 | 4.9726 | 0 | 2253.1412 | 0 | 0 | 0 | 4.9726 | 0 | 0 | 2253.1412
9 | 16 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 504.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 491.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 483.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 466.9479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 448.1997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 16 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 432.1976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 420.8189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 412.4472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 416.6363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 427.3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 423.9587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 428.8549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 455.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 478.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 8 | 0 | 0.38639 | 0.38639 | 48 | 4.8451 | 0.17008 | 0.17008 | 491.6285 | 0.38639 | 0 | 171.415 | 0 | 0 | 0 | 0.38639 | 0 | 0 | 171.415
9 | 17 | 9 | 0 | 62.3172 | 62.3172 | 48 | 6.3789 | 40.5318 | 40.5318 | 503.9003 | 62.3172 | 0 | 28410.4251 | 0 | 0 | 0 | 62.3172 | 0 | 0 | 28410.4251
9 | 17 | 10 | 0 | 6.8581 | 6.8581 | 48 | 8.4804 | 12.907 | 12.907 | 506.413 | 6.8581 | 0 | 3143.8384 | 0 | 0 | 0 | 6.8581 | 0 | 0 | 3143.8384
9 | 17 | 11 | 0 | 7.1797 | 7.1797 | 48 | 9.4549 | 110.8163 | 110.8163 | 507.9779 | 7.1797 | 0 | 3302.511 | 0 | 0 | 0 | 7.1797 | 0 | 0 | 3302.511
9 | 17 | 12 | 0 | 6.8727 | 6.8727 | 48 | 9.8362 | 0 | 0 | 503.8933 | 0 | 6.8727 | 0 | 0.71664 | 0 | 0 | 0 | 6.8727 | 0 | 0
9 | 17 | 13 | 0 | 7.6026 | 7.6026 | 48 | 9.6159 | 0 | 0 | 499.4455 | 0 | 7.6026 | 0 | 0.79275 | 0 | 0 | 0 | 7.6026 | 0 | 0
9 | 17 | 14 | 0.15583 | 63.0734 | 63.2292 | 47.9088 | 9.5227 | 1955.5513 | 288 | 497.3302 | 9.312 | 53.9172 | 4184.9913 | 5.6221 | 0 | 0 | 9.312 | 53.9172 | 0 | 4184.9913
9 | 17 | 15 | 0 | 5.7601 | 5.7601 | 48 | 10.7175 | 0 | 0 | 504.3361 | 0 | 5.7601 | 0 | 0.60062 | 0 | 0 | 0 | 5.7601 | 0 | 0
9 | 17 | 16 | 0 | 2.2574 | 2.2574 | 48 | 12.0564 | 0 | 0 | 501.8993 | 0 | 2.2574 | 0 | 0.23539 | 0 | 0 | 0 | 2.2574 | 0 | 0
9 | 17 | 17 | 0 | 0.51833 | 0.51833 | 48 | 11.8107 | 0 | 0 | 503.3736 | 0 | 0.51833 | 0 | 0.054048 | 0 | 0 | 0 | 0.51833 | 0 | 0
9 | 17 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 510.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 500.2552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 492.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 468.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 447.6948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 17 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 441.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 440.8618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 442.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 457.9101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 489.0932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 501.5014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 5 | 3.4249 | 0 | 3.4249 | 11 | 3.6164 | 1.1975 | 1.1975 | 505.4685 | 3.4249 | 0 | 1693.5133 | 0 | 0 | 0 | 3.4249 | 0 | 0 | 1693.5133
9 | 18 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 514.4835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 518.2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 8 | 0 | 1.1693 | 1.1693 | 48 | 5.4976 | 0.59674 | 0.59674 | 520.6819 | 1.1693 | 0 | 552.6915 | 0 | 0 | 0 | 1.1693 | 0 | 0 | 552.6915
9 | 18 | 9 | 0 | 203.9749 | 203.9749 | 48 | 6.4043 | 133.7261 | 133.7261 | 522.8778 | 203.9749 | 0 | 96863.1466 | 0 | 0 | 0 | 203.9749 | 0 | 0 | 96863.1466
9 | 18 | 10 | 0 | 4.9637 | 4.9637 | 48 | 8.5991 | 10.4598 | 10.4598 | 519.033 | 4.9637 | 0 | 2338.0632 | 0 | 0 | 0 | 4.9637 | 0 | 0 | 2338.0632
9 | 18 | 11 | 0 | 6.059 | 6.059 | 48 | 9.6413 | 0 | 0 | 515.0922 | 0 | 6.059 | 0 | 0.63178 | 0 | 0 | 0 | 6.059 | 0 | 0
9 | 18 | 12 | 0 | 22.5493 | 22.5493 | 48 | 9.7176 | 0 | 0 | 508.1148 | 0 | 22.5493 | 0 | 2.3513 | 0 | 0 | 0 | 22.5493 | 0 | 0
9 | 18 | 13 | 0 | 24.2361 | 24.2361 | 48 | 9.7939 | 0 | 0 | 508.8606 | 0 | 24.2361 | 0 | 2.5272 | 0 | 0 | 0 | 24.2361 | 0 | 0
9 | 18 | 14 | 0 | 11.9311 | 11.9311 | 48 | 9.4634 | 196.4541 | 196.4541 | 510.3254 | 11.9311 | 0 | 5516.0597 | 0 | 0 | 0 | 11.9311 | 0 | 0 | 5516.0597
9 | 18 | 15 | 0 | 4.5533 | 4.5533 | 48 | 10.5311 | 0 | 0 | 522.0641 | 0 | 4.5533 | 0 | 0.47479 | 0 | 0 | 0 | 4.5533 | 0 | 0
9 | 18 | 16 | 0 | 0.98978 | 0.98978 | 48 | 11.0904 | 0 | 0 | 519.5129 | 0 | 0.98978 | 0 | 0.10321 | 0 | 0 | 0 | 0.98978 | 0 | 0
9 | 18 | 17 | 0 | 0.20304 | 0.20304 | 48 | 11.1073 | 0 | 0 | 523.3939 | 0 | 0.20304 | 0 | 0.021172 | 0 | 0 | 0 | 0.20304 | 0 | 0
9 | 18 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 522.3529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 507.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 490.515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 474.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 474.6064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 18 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 462.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 460.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 460.9882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 475.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 501.3908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 517.4324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 5 | 0.26663 | 0 | 0.26663 | 11 | 3.8536 | 0.097079 | 0.097079 | 521.7677 | 0.26662 | 0 | 136.1834 | 0 | 0 | 0 | 0.26662 | 0 | 0 | 136.1834
9 | 19 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 523.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 521.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 8 | 0 | 2.4494 | 2.4494 | 48 | 6.2094 | 1.5132 | 1.5132 | 527.304 | 2.4494 | 0 | 1174.0021 | 0 | 0 | 0 | 2.4494 | 0 | 0 | 1174.0021
9 | 19 | 9 | 0 | 144.0633 | 144.0633 | 48 | 7.328 | 133.0099 | 133.0099 | 520.15 | 144.0633 | 0 | 68019.5091 | 0 | 0 | 0 | 144.0633 | 0 | 0 | 68019.5091
9 | 19 | 10 | 0.60417 | 364.3244 | 364.9286 | 47.9387 | 8.5482 | 731.4797 | 288 | 515.7001 | 143.6806 | 221.248 | 67208.2329 | 23.0701 | 0 | 0 | 143.6806 | 221.248 | 0 | 67208.2329
9 | 19 | 11 | 0.61167 | 273.0599 | 273.6716 | 47.9173 | 9.1838 | 1406.2264 | 288 | 514.8903 | 56.0489 | 217.6227 | 26173.3101 | 22.6921 | 0 | 0 | 56.0489 | 217.6227 | 0 | 26173.3101
9 | 19 | 12 | 0 | 268.1452 | 268.1452 | 48 | 9.8701 | 0 | 0 | 514.7006 | 0 | 268.1452 | 0 | 27.9602 | 0 | 0 | 0 | 268.1452 | 0 | 0
9 | 19 | 13 | 0 | 280.516 | 280.516 | 48 | 9.6668 | 0 | 0 | 515.4752 | 0 | 280.516 | 0 | 29.2501 | 0 | 0 | 0 | 280.516 | 0 | 0
9 | 19 | 14 | 0 | 60.9741 | 60.9741 | 48 | 10.2684 | 0 | 0 | 515.2735 | 0 | 60.9741 | 0 | 6.3579 | 0 | 0 | 0 | 60.9741 | 0 | 0
9 | 19 | 15 | 0 | 12.1163 | 12.1163 | 48 | 11.226 | 0 | 0 | 520.289 | 0 | 12.1163 | 0 | 1.2634 | 0 | 0 | 0 | 12.1163 | 0 | 0
9 | 19 | 16 | 0 | 6.3111 | 6.3111 | 48 | 11.853 | 0 | 0 | 518.5823 | 0 | 6.3111 | 0 | 0.65807 | 0 | 0 | 0 | 6.3111 | 0 | 0
9 | 19 | 17 | 0 | 0.071625 | 0.071625 | 48 | 11.7514 | 0 | 0 | 523.8129 | 0 | 0.071625 | 0 | 0.0074685 | 0 | 0 | 0 | 0.071625 | 0 | 0
9 | 19 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 530.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 524.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 513.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 494.4863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 475.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 458.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 449.5499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 451.6991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 465.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 492.0158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 510.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 505.2795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 518.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 528.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 8 | 0 | 3.9328 | 3.9328 | 48 | 6.2094 | 2.4297 | 2.4297 | 526.3539 | 3.9328 | 0 | 1881.289 | 0 | 0 | 0 | 3.9328 | 0 | 0 | 1881.289
9 | 20 | 9 | 0 | 7.185 | 7.185 | 48 | 7.311 | 6.5844 | 6.5844 | 529.0053 | 7.185 | 0 | 3456.0228 | 0 | 0 | 0 | 7.185 | 0 | 0 | 3456.0228
9 | 20 | 10 | 0 | 151.2711 | 151.2711 | 48 | 8.0567 | 206.0357 | 206.0357 | 522.2271 | 151.2711 | 0 | 71736.8497 | 0 | 0 | 0 | 151.2711 | 0 | 0 | 71736.8497
9 | 20 | 11 | 0 | 152.2168 | 152.2168 | 48 | 9.3109 | 1137.9945 | 288 | 523.1564 | 38.5225 | 113.6942 | 18304.2257 | 11.8552 | 0 | 0 | 38.5225 | 113.6942 | 0 | 18304.2257
9 | 20 | 12 | 0 | 20.1294 | 20.1294 | 48 | 9.0058 | 71.9391 | 71.9391 | 522.4021 | 20.1294 | 0 | 9549.4352 | 0 | 0 | 0 | 20.1294 | 0 | 0 | 9549.4352
9 | 20 | 13 | 0 | 216.1934 | 216.1934 | 48 | 8.4889 | 410.0084 | 288 | 521.3535 | 151.8596 | 64.3338 | 71883.2545 | 6.7083 | 0 | 0 | 151.8596 | 64.3338 | 0 | 71883.2545
9 | 20 | 14 | 0 | 13.6717 | 13.6717 | 48 | 8.938 | 43.782 | 43.782 | 520.3734 | 13.6717 | 0 | 6458.1581 | 0 | 0 | 0 | 13.6717 | 0 | 0 | 6458.1581
9 | 20 | 15 | 0 | 5.9185 | 5.9185 | 48 | 9.6075 | 0 | 0 | 521.7901 | 0 | 5.9185 | 0 | 0.61714 | 0 | 0 | 0 | 5.9185 | 0 | 0
9 | 20 | 16 | 0 | 3.9401 | 3.9401 | 48 | 10.9718 | 0 | 0 | 523.7432 | 0 | 3.9401 | 0 | 0.41084 | 0 | 0 | 0 | 3.9401 | 0 | 0
9 | 20 | 17 | 0 | 1.2205 | 1.2205 | 48 | 10.3786 | 0 | 0 | 523.5465 | 0 | 1.2205 | 0 | 0.12726 | 0 | 0 | 0 | 1.2205 | 0 | 0
9 | 20 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 525.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 19 | 36.6225 | 0 | 36.6225 | 11 | 10.4633 | 0 | 0 | 514.2158 | 0 | 36.6225 | 0 | 3.8187 | 0 | 0 | 0 | 36.6225 | 0 | 0
9 | 20 | 20 | 4.0959 | 0 | 4.0959 | 11 | 8.0228 | 5.4581 | 5.4581 | 507.1312 | 4.0959 | 0 | 2032.0924 | 0 | 0 | 0 | 4.0959 | 0 | 0 | 2032.0924
9 | 20 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 497.5432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 481.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 20 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 470.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 462.7382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 461.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 472.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 494.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 518.9097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 523.2535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 536.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 542.0151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 8 | 0 | 30.7378 | 30.7378 | 48 | 5.1417 | 14.4322 | 14.4322 | 543.1247 | 30.7378 | 0 | 15219.0571 | 0 | 0 | 0 | 30.7378 | 0 | 0 | 15219.0571
9 | 21 | 9 | 0 | 29.0994 | 29.0994 | 48 | 6.6161 | 20.4365 | 20.4365 | 543.2794 | 29.0994 | 0 | 14412.3458 | 0 | 0 | 0 | 29.0994 | 0 | 0 | 14412.3458
9 | 21 | 10 | 0 | 29.6386 | 29.6386 | 48 | 6.9721 | 23.6448 | 23.6448 | 534.9657 | 29.6386 | 0 | 14433.0025 | 0 | 0 | 0 | 29.6386 | 0 | 0 | 14433.0025
9 | 21 | 11 | 0 | 26.2482 | 26.2482 | 48 | 8.5652 | 53.4829 | 53.4829 | 534.4745 | 26.2482 | 0 | 12769.0554 | 0 | 0 | 0 | 26.2482 | 0 | 0 | 12769.0554
9 | 21 | 12 | 0 | 17.7986 | 17.7986 | 48 | 7.8957 | 21.9388 | 21.9388 | 535.6659 | 17.7986 | 0 | 8679.7504 | 0 | 0 | 0 | 17.7986 | 0 | 0 | 8679.7504
9 | 21 | 13 | 0 | 21.5613 | 21.5613 | 48 | 7.4381 | 20.926 | 20.926 | 536.6786 | 21.5613 | 0 | 10536.5449 | 0 | 0 | 0 | 21.5613 | 0 | 0 | 10536.5449
9 | 21 | 14 | 0 | 7.3133 | 7.3133 | 48 | 7.2771 | 6.6037 | 6.6037 | 542.9096 | 7.3133 | 0 | 3619.4108 | 0 | 0 | 0 | 7.3133 | 0 | 0 | 3619.4108
9 | 21 | 15 | 0 | 7.842 | 7.842 | 48 | 7.3449 | 7.295 | 7.295 | 541.6329 | 7.842 | 0 | 3871.0683 | 0 | 0 | 0 | 7.842 | 0 | 0 | 3871.0683
9 | 21 | 16 | 0 | 6.2672 | 6.2672 | 48 | 6.9975 | 5.0488 | 5.0488 | 547.1211 | 6.2672 | 0 | 3128.0675 | 0 | 0 | 0 | 6.2672 | 0 | 0 | 3128.0675
9 | 21 | 17 | 0 | 1.5235 | 1.5235 | 48 | 7.167 | 1.3132 | 1.3132 | 548.5763 | 1.5235 | 0 | 762.628 | 0 | 0 | 0 | 1.5235 | 0 | 0 | 762.628
9 | 21 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 551.7411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 543.1706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 537.3439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 513.107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 493.706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 21 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 481.8622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 473.7209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 468.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 485.7229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 506.7473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 4 | 0.94996 | 0 | 0.94996 | 11 | 2.9469 | 0.29867 | 0.29867 | 530.6021 | 0.94996 | 0 | 493.6004 | 0 | 0 | 0 | 0.94996 | 0 | 0 | 493.6004
9 | 22 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 532.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 538.2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 541.5537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 8 | 1.4542 | 136.7869 | 138.241 | 47.6108 | 6.8788 | 106.4929 | 106.4929 | 540.1836 | 138.241 | 0 | 68093.7804 | 0 | 0 | 0 | 138.241 | 0 | 0 | 68093.7804
9 | 22 | 9 | 0 | 130.1952 | 130.1952 | 48 | 7.3195 | 119.7572 | 119.7572 | 539.2607 | 130.1952 | 0 | 63959.7934 | 0 | 0 | 0 | 130.1952 | 0 | 0 | 63959.7934
9 | 22 | 10 | 0 | 124.0435 | 124.0435 | 48 | 7.4805 | 122.8061 | 122.8061 | 531.944 | 124.0435 | 0 | 60030.1007 | 0 | 0 | 0 | 124.0435 | 0 | 0 | 60030.1007
9 | 22 | 11 | 0 | 185.7771 | 185.7771 | 48 | 7.2263 | 164.145 | 164.145 | 532.3138 | 185.7771 | 0 | 89974.4197 | 0 | 0 | 0 | 185.7771 | 0 | 0 | 89974.4197
9 | 22 | 12 | 0 | 261.4288 | 261.4288 | 48 | 7.8703 | 317.4788 | 288 | 529.0043 | 237.1544 | 24.2744 | 114072.2973 | 2.5312 | 0 | 0 | 237.1544 | 24.2744 | 0 | 114072.2973
9 | 22 | 13 | 0 | 330.2749 | 330.2749 | 48 | 8.1754 | 487.5625 | 288 | 527.9968 | 195.0912 | 135.1837 | 93643.1598 | 14.096 | 0 | 0 | 195.0912 | 135.1837 | 0 | 93643.1598
9 | 22 | 14 | 0 | 337.018 | 337.018 | 48 | 8.2431 | 522.554 | 288 | 529.8827 | 185.7438 | 151.2742 | 89506.7415 | 15.7738 | 0 | 0 | 185.7438 | 151.2742 | 0 | 89506.7415
9 | 22 | 15 | 0 | 45.5735 | 45.5735 | 48 | 7.4212 | 43.885 | 43.885 | 538.6033 | 45.5735 | 0 | 22358.5103 | 0 | 0 | 0 | 45.5735 | 0 | 0 | 22358.5103
9 | 22 | 16 | 0 | 8.1689 | 8.1689 | 48 | 7.3195 | 7.514 | 7.514 | 537.0305 | 8.1689 | 0 | 3994.8274 | 0 | 0 | 0 | 8.1689 | 0 | 0 | 3994.8274
9 | 22 | 17 | 0 | 3.369 | 3.369 | 48 | 7.2686 | 3.0311 | 3.0311 | 539.819 | 3.369 | 0 | 1656.95 | 0 | 0 | 0 | 3.369 | 0 | 0 | 1656.95
9 | 22 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 537.1524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 534.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 521.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 502.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 482.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 22 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 470.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 458.8497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 451.4099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 452.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 459.7385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 470.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 479.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 504.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 7 | 0 | 0.40704 | 0.40704 | 48 | 6.006 | 0.2372 | 0.2372 | 521.7628 | 0.40704 | 0 | 192.8412 | 0 | 0 | 0 | 0.40704 | 0 | 0 | 192.8412
9 | 23 | 8 | 0.37917 | 122.3171 | 122.6963 | 47.8857 | 6.6246 | 86.4158 | 86.4158 | 532.3541 | 122.6963 | 0 | 59442.4789 | 0 | 0 | 0 | 122.6963 | 0 | 0 | 59442.4789
9 | 23 | 9 | 0.2625 | 177.324 | 177.5865 | 47.9453 | 7.1924 | 154.6901 | 154.6901 | 537.1566 | 177.5865 | 0 | 86877.3259 | 0 | 0 | 0 | 177.5865 | 0 | 0 | 86877.3259
9 | 23 | 10 | 1.4883 | 518.365 | 519.8533 | 47.8941 | 7.0398 | 425.7459 | 288 | 535.7042 | 351.6599 | 168.1934 | 171543.2522 | 17.538 | 0 | 0 | 351.6599 | 168.1934 | 0 | 171543.2522
9 | 23 | 11 | 0.21583 | 666.2066 | 666.4224 | 47.988 | 7.2093 | 584.6319 | 288 | 527.9781 | 328.2914 | 338.131 | 157576.6531 | 35.2578 | 0 | 0 | 328.2914 | 338.131 | 0 | 157576.6531
9 | 23 | 12 | 0.18083 | 577.2808 | 577.4616 | 47.9884 | 7.9296 | 726.3177 | 288 | 528.1457 | 228.9755 | 348.4861 | 109944.2565 | 36.3376 | 0 | 0 | 228.9755 | 348.4861 | 0 | 109944.2565
9 | 23 | 13 | 0.11833 | 162.125 | 162.2433 | 47.973 | 8.2601 | 254.7671 | 254.7671 | 528.4256 | 162.2433 | 0 | 77950.22 | 0 | 0 | 0 | 162.2433 | 0 | 0 | 77950.22
9 | 23 | 14 | 0 | 12.6707 | 12.6707 | 48 | 8.5313 | 24.9913 | 24.9913 | 528.9753 | 12.6707 | 0 | 6094.3125 | 0 | 0 | 0 | 12.6707 | 0 | 0 | 6094.3125
9 | 23 | 15 | 0.3375 | 59.4408 | 59.7783 | 47.7911 | 8.4041 | 105.2694 | 105.2694 | 532.5217 | 59.7783 | 0 | 28976.386 | 0 | 0 | 0 | 59.7783 | 0 | 0 | 28976.386
9 | 23 | 16 | 0 | 7.8631 | 7.8631 | 48 | 9.1753 | 39.5786 | 39.5786 | 535.9926 | 7.8631 | 0 | 3837.1443 | 0 | 0 | 0 | 7.8631 | 0 | 0 | 3837.1443
9 | 23 | 17 | 0 | 6.9268 | 6.9268 | 48 | 8.6753 | 15.8132 | 15.8132 | 535.3222 | 6.9268 | 0 | 3375.565 | 0 | 0 | 0 | 6.9268 | 0 | 0 | 3375.565
9 | 23 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 532.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 530.6225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 509.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 489.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 476.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 23 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 465.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 457.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 451.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 448.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 452.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 454.4313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 457.8078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 483.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 512.5165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 8 | 0.26833 | 199.1039 | 199.3722 | 47.9502 | 4.8451 | 87.7592 | 87.7592 | 531.1126 | 199.3722 | 0 | 96329.1462 | 0 | 0 | 0 | 199.3722 | 0 | 0 | 96329.1462
9 | 24 | 9 | 0.6075 | 419.0316 | 419.6391 | 47.9464 | 6.3789 | 272.9379 | 272.9379 | 536.5762 | 419.6391 | 0 | 205048.1403 | 0 | 0 | 0 | 419.6391 | 0 | 0 | 205048.1403
9 | 24 | 10 | 0.705 | 326.4911 | 327.1961 | 47.9203 | 8.4804 | 615.7859 | 288 | 542.4952 | 153.028 | 174.1681 | 75683.8087 | 18.161 | 0 | 0 | 153.028 | 174.1681 | 0 | 75683.8087
9 | 24 | 11 | 0 | 7.2578 | 7.2578 | 48 | 9.4549 | 112.0218 | 112.0218 | 533.8734 | 7.2578 | 0 | 3526.3824 | 0 | 0 | 0 | 7.2578 | 0 | 0 | 3526.3824
9 | 24 | 12 | 0 | 6.4727 | 6.4727 | 48 | 9.8362 | 0 | 0 | 529.8884 | 0 | 6.4727 | 0 | 0.67492 | 0 | 0 | 0 | 6.4727 | 0 | 0
9 | 24 | 13 | 0 | 6.8175 | 6.8175 | 48 | 9.6159 | 0 | 0 | 533.5459 | 0 | 6.8175 | 0 | 0.71088 | 0 | 0 | 0 | 6.8175 | 0 | 0
9 | 24 | 14 | 0 | 24.7465 | 24.7465 | 48 | 9.5227 | 765.3579 | 288 | 535.0249 | 9.312 | 15.4345 | 4535.1537 | 1.6094 | 0 | 0 | 9.312 | 15.4345 | 0 | 4535.1537
9 | 24 | 15 | 0 | 8.1874 | 8.1874 | 48 | 10.7175 | 0 | 0 | 543.8965 | 0 | 8.1874 | 0 | 0.85372 | 0 | 0 | 0 | 8.1874 | 0 | 0
9 | 24 | 16 | 0 | 2.9772 | 2.9772 | 48 | 12.0564 | 0 | 0 | 545.6918 | 0 | 2.9772 | 0 | 0.31044 | 0 | 0 | 0 | 2.9772 | 0 | 0
9 | 24 | 17 | 0 | 2.5545 | 2.5545 | 48 | 11.8107 | 0 | 0 | 549.4029 | 0 | 2.5545 | 0 | 0.26637 | 0 | 0 | 0 | 2.5545 | 0 | 0
9 | 24 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 553.6329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 547.5092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 529.7397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 498.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 475.1202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 24 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 461.0053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 455.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 458.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 469.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 503.9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 524.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 527.6129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 543.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 550.1681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 8 | 0 | 20.196 | 20.196 | 48 | 5.4976 | 10.3071 | 10.3071 | 545.0728 | 20.196 | 0 | 10038.8607 | 0 | 0 | 0 | 20.196 | 0 | 0 | 10038.8607
9 | 25 | 9 | 0 | 99.5586 | 99.5586 | 48 | 6.4043 | 65.2707 | 65.2707 | 542.2685 | 99.5586 | 0 | 49208.6861 | 0 | 0 | 0 | 99.5586 | 0 | 0 | 49208.6861
9 | 25 | 10 | 0 | 16.4701 | 16.4701 | 48 | 8.5991 | 34.7069 | 34.7069 | 541.277 | 16.4701 | 0 | 8124.3249 | 0 | 0 | 0 | 16.4701 | 0 | 0 | 8124.3249
9 | 25 | 11 | 0.091667 | 169.0222 | 169.1139 | 47.9799 | 9.6413 | 0 | 0 | 542.0565 | 0 | 169.1139 | 0 | 17.6339 | 0 | 0 | 0 | 169.1139 | 0 | 0
9 | 25 | 12 | 0.23833 | 95.9769 | 96.2153 | 47.9083 | 9.7176 | 0 | 0 | 542.7832 | 0 | 96.2153 | 0 | 10.0326 | 0 | 0 | 0 | 96.2153 | 0 | 0
9 | 25 | 13 | 0.14333 | 51.6736 | 51.8169 | 47.8977 | 9.7939 | 0 | 0 | 546.5386 | 0 | 51.8169 | 0 | 5.4031 | 0 | 0 | 0 | 51.8169 | 0 | 0
9 | 25 | 14 | 0 | 2.7952 | 2.7952 | 48 | 9.4634 | 46.0242 | 46.0242 | 549.3084 | 2.7952 | 0 | 1401.2368 | 0 | 0 | 0 | 2.7952 | 0 | 0 | 1401.2368
9 | 25 | 15 | 0 | 7.0683 | 7.0683 | 48 | 10.5311 | 0 | 0 | 550.1016 | 0 | 7.0683 | 0 | 0.73703 | 0 | 0 | 0 | 7.0683 | 0 | 0
9 | 25 | 16 | 0 | 5.8862 | 5.8862 | 48 | 11.0904 | 0 | 0 | 548.4865 | 0 | 5.8862 | 0 | 0.61377 | 0 | 0 | 0 | 5.8862 | 0 | 0
9 | 25 | 17 | 0 | 0.72113 | 0.72113 | 48 | 11.1073 | 0 | 0 | 551.7231 | 0 | 0.72113 | 0 | 0.075194 | 0 | 0 | 0 | 0.72113 | 0 | 0
9 | 25 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 557.1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 556.9004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 549.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 528.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 499.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 25 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 484.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 473.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 469.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 478.7815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 518.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 540.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 543.2275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 548.8876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 554.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 8 | 0 | 0.37864 | 0.37864 | 48 | 6.2094 | 0.23393 | 0.23393 | 555.863 | 0.37864 | 0 | 192.2996 | 0 | 0 | 0 | 0.37864 | 0 | 0 | 192.2996
9 | 26 | 9 | 0 | 9.8783 | 9.8783 | 48 | 7.328 | 9.1204 | 9.1204 | 549.6654 | 9.8783 | 0 | 4955.5941 | 0 | 0 | 0 | 9.8783 | 0 | 0 | 4955.5941
9 | 26 | 10 | 0 | 4.3116 | 4.3116 | 48 | 8.5482 | 8.6423 | 8.6423 | 540.863 | 4.3116 | 0 | 2125.0148 | 0 | 0 | 0 | 4.3116 | 0 | 0 | 2125.0148
9 | 26 | 11 | 0 | 5.0414 | 5.0414 | 48 | 9.1838 | 25.9044 | 25.9044 | 538.7231 | 5.0414 | 0 | 2473.9088 | 0 | 0 | 0 | 5.0414 | 0 | 0 | 2473.9088
9 | 26 | 12 | 0 | 3.3421 | 3.3421 | 48 | 9.8701 | 0 | 0 | 543.0659 | 0 | 3.3421 | 0 | 0.34849 | 0 | 0 | 0 | 3.3421 | 0 | 0
9 | 26 | 13 | 0 | 4.6295 | 4.6295 | 48 | 9.6668 | 0 | 0 | 544.6 | 0 | 4.6295 | 0 | 0.48273 | 0 | 0 | 0 | 4.6295 | 0 | 0
9 | 26 | 14 | 0 | 5.2222 | 5.2222 | 48 | 10.2684 | 0 | 0 | 547.2582 | 0 | 5.2222 | 0 | 0.54453 | 0 | 0 | 0 | 5.2222 | 0 | 0
9 | 26 | 15 | 0 | 23.953 | 23.953 | 48 | 11.226 | 0 | 0 | 551.2969 | 0 | 23.953 | 0 | 2.4976 | 0 | 0 | 0 | 23.953 | 0 | 0
9 | 26 | 16 | 0 | 0.61294 | 0.61294 | 48 | 11.853 | 0 | 0 | 552.6925 | 0 | 0.61294 | 0 | 0.063913 | 0 | 0 | 0 | 0.61294 | 0 | 0
9 | 26 | 17 | 0 | 0.0066667 | 0.0066667 | 48 | 11.7514 | 0 | 0 | 559.0262 | 0 | 0.0066667 | 0 | 0.00069515 | 0 | 0 | 0 | 0.0066667 | 0 | 0
9 | 26 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 558.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 556.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 550.8039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 529.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 508.9125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 26 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 494.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 487.2327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 486.1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 499.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 527.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 542.9296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 541.5531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 546.4677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 7 | 0 | 6.7156 | 6.7156 | 48 | 5.0146 | 3.0656 | 3.0656 | 547.8524 | 6.7156 | 0 | 3356.825 | 0 | 0 | 0 | 6.7156 | 0 | 0 | 3356.825
9 | 27 | 8 | 0.26 | 543.4506 | 543.7106 | 47.9823 | 6.2094 | 335.908 | 288 | 549.5781 | 466.1654 | 77.5453 | 233826.5687 | 8.0858 | 0 | 0 | 466.1654 | 77.5453 | 0 | 233826.5687
9 | 27 | 9 | 0.22833 | 831.6216 | 831.8499 | 47.9898 | 7.311 | 762.3143 | 288 | 539.7074 | 314.2704 | 517.5796 | 154532.2421 | 53.9694 | 0 | 0 | 314.2704 | 517.5796 | 0 | 154532.2421
9 | 27 | 10 | 0 | 332.4154 | 332.4154 | 48 | 8.0567 | 452.7596 | 288 | 538.571 | 211.4491 | 120.9663 | 103730.8104 | 12.6135 | 0 | 0 | 211.4491 | 120.9663 | 0 | 103730.8104
9 | 27 | 11 | 0 | 146.3531 | 146.3531 | 48 | 9.3109 | 1094.1573 | 288 | 538.0307 | 38.5225 | 107.8306 | 18877.2218 | 11.2438 | 0 | 0 | 38.5225 | 107.8306 | 0 | 18877.2218
9 | 27 | 12 | 0 | 50.3937 | 50.3937 | 48 | 9.0058 | 180.0985 | 180.0985 | 536.5577 | 50.3937 | 0 | 24620.2124 | 0 | 0 | 0 | 50.3937 | 0 | 0 | 24620.2124
9 | 27 | 13 | 0 | 4.0917 | 4.0917 | 48 | 8.4889 | 7.7599 | 7.7599 | 536.4082 | 4.0917 | 0 | 1998.4243 | 0 | 0 | 0 | 4.0917 | 0 | 0 | 1998.4243
9 | 27 | 14 | 0 | 4.3474 | 4.3474 | 48 | 8.938 | 13.9221 | 13.9221 | 538.8631 | 4.3474 | 0 | 2133.9902 | 0 | 0 | 0 | 4.3474 | 0 | 0 | 2133.9902
9 | 27 | 15 | 0 | 3.8444 | 3.8444 | 48 | 9.6075 | 0 | 0 | 541.2627 | 0 | 3.8444 | 0 | 0.40087 | 0 | 0 | 0 | 3.8444 | 0 | 0
9 | 27 | 16 | 0 | 6.5286 | 6.5286 | 48 | 10.9718 | 0 | 0 | 541.6048 | 0 | 6.5286 | 0 | 0.68075 | 0 | 0 | 0 | 6.5286 | 0 | 0
9 | 27 | 17 | 0 | 0.50404 | 0.50404 | 48 | 10.3786 | 0 | 0 | 542.3434 | 0 | 0.50404 | 0 | 0.052558 | 0 | 0 | 0 | 0.50404 | 0 | 0
9 | 27 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 549.0606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 543.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 535.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 514.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 496.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 27 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 484.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 472.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 472.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 483.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 504.9387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 515.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 513.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 518.711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 526.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 8 | 0 | 2.8584 | 2.8584 | 48 | 5.1417 | 1.3421 | 1.3421 | 526.2508 | 2.8584 | 0 | 1367.0397 | 0 | 0 | 0 | 2.8584 | 0 | 0 | 1367.0397
9 | 28 | 9 | 0 | 2.1565 | 2.1565 | 48 | 6.6161 | 1.5145 | 1.5145 | 519.4381 | 2.1565 | 0 | 1016.6686 | 0 | 0 | 0 | 2.1565 | 0 | 0 | 1016.6686
9 | 28 | 10 | 0 | 2.6852 | 2.6852 | 48 | 6.9721 | 2.1422 | 2.1422 | 513.6223 | 2.6852 | 0 | 1250.3045 | 0 | 0 | 0 | 2.6852 | 0 | 0 | 1250.3045
9 | 28 | 11 | 0 | 12.7912 | 12.7912 | 48 | 8.5652 | 26.0631 | 26.0631 | 514.2627 | 12.7912 | 0 | 5964.0497 | 0 | 0 | 0 | 12.7912 | 0 | 0 | 5964.0497
9 | 28 | 12 | 0 | 2.4841 | 2.4841 | 48 | 7.8957 | 3.062 | 3.062 | 516.2962 | 2.4841 | 0 | 1163.3017 | 0 | 0 | 0 | 2.4841 | 0 | 0 | 1163.3017
9 | 28 | 13 | 0 | 3.3585 | 3.3585 | 48 | 7.4381 | 3.2595 | 3.2595 | 518.4541 | 3.3585 | 0 | 1580.0056 | 0 | 0 | 0 | 3.3585 | 0 | 0 | 1580.0056
9 | 28 | 14 | 0 | 66.9987 | 66.9987 | 48 | 7.2771 | 60.4985 | 60.4985 | 520.6197 | 66.9987 | 0 | 31664.9278 | 0 | 0 | 0 | 66.9987 | 0 | 0 | 31664.9278
9 | 28 | 15 | 0 | 42.9773 | 42.9773 | 48 | 7.3449 | 39.9793 | 39.9793 | 525.8371 | 42.9773 | 0 | 20536.1357 | 0 | 0 | 0 | 42.9773 | 0 | 0 | 20536.1357
9 | 28 | 16 | 0 | 14.027 | 14.027 | 48 | 6.9975 | 11.3 | 11.3 | 531.1383 | 14.027 | 0 | 6776.9896 | 0 | 0 | 0 | 14.027 | 0 | 0 | 6776.9896
9 | 28 | 17 | 0 | 0.8065 | 0.8065 | 48 | 7.167 | 0.69515 | 0.69515 | 535.8966 | 0.8065 | 0 | 393.4886 | 0 | 0 | 0 | 0.8065 | 0 | 0 | 393.4886
9 | 28 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 526.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 505.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 491.5761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 472.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 461.3407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 28 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 455.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 444.1092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 437.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 441.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 459.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 474.0788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 471.4831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 474.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 483.3442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 483.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 9 | 0 | 0.1463 | 0.1463 | 48 | 7.3195 | 0.13457 | 0.13457 | 483.565 | 0.1463 | 0 | 63.7244 | 0 | 0 | 0 | 0.1463 | 0 | 0 | 63.7244
9 | 29 | 10 | 0 | 0.32419 | 0.32419 | 48 | 7.4805 | 0.32096 | 0.32096 | 479.8278 | 0.32419 | 0 | 139.996 | 0 | 0 | 0 | 0.32419 | 0 | 0 | 139.996
9 | 29 | 11 | 0 | 1.2667 | 1.2667 | 48 | 7.2263 | 1.1192 | 1.1192 | 474.627 | 1.2667 | 0 | 540.4031 | 0 | 0 | 0 | 1.2667 | 0 | 0 | 540.4031
9 | 29 | 12 | 0 | 0.1301 | 0.1301 | 48 | 7.8703 | 0.15799 | 0.15799 | 468.8561 | 0.1301 | 0 | 54.7529 | 0 | 0 | 0 | 0.1301 | 0 | 0 | 54.7529
9 | 29 | 13 | 0 | 0.3567 | 0.3567 | 48 | 8.1754 | 0.52657 | 0.52657 | 474.5566 | 0.3567 | 0 | 152.1527 | 0 | 0 | 0 | 0.3567 | 0 | 0 | 152.1527
9 | 29 | 14 | 0 | 0.076848 | 0.076848 | 48 | 8.2431 | 0.11915 | 0.11915 | 479.9243 | 0.076848 | 0 | 33.1925 | 0 | 0 | 0 | 0.076848 | 0 | 0 | 33.1925
9 | 29 | 15 | 0 | 10.2501 | 10.2501 | 48 | 7.4212 | 9.8703 | 9.8703 | 482.2801 | 10.2501 | 0 | 4451.4201 | 0 | 0 | 0 | 10.2501 | 0 | 0 | 4451.4201
9 | 29 | 16 | 0 | 1.1561 | 1.1561 | 48 | 7.3195 | 1.0634 | 1.0634 | 486.2416 | 1.1561 | 0 | 506.6438 | 0 | 0 | 0 | 1.1561 | 0 | 0 | 506.6438
9 | 29 | 17 | 0 | 0.75813 | 0.75813 | 48 | 7.2686 | 0.68207 | 0.68207 | 477.0282 | 0.75813 | 0 | 325.257 | 0 | 0 | 0 | 0.75813 | 0 | 0 | 325.257
9 | 29 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 466.4328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 449.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 436.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 425.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 420.8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 29 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 410.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 410.8039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 405.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 404.1761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 411.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 414.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 421.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 434.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 446.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 8 | 0.70833 | 56.3504 | 57.0587 | 47.5407 | 6.6246 | 40.1868 | 40.1868 | 450.5085 | 57.0587 | 0 | 22992.8169 | 0 | 0 | 0 | 57.0587 | 0 | 0 | 22992.8169
9 | 30 | 9 | 0.59583 | 215.1716 | 215.7675 | 47.8978 | 7.1924 | 187.9483 | 187.9483 | 455.632 | 215.7675 | 0 | 87975.7643 | 0 | 0 | 0 | 215.7675 | 0 | 0 | 87975.7643
9 | 30 | 10 | 0 | 106.8009 | 106.8009 | 48 | 7.0398 | 87.4671 | 87.4671 | 460.4077 | 106.8009 | 0 | 44045.5089 | 0 | 0 | 0 | 106.8009 | 0 | 0 | 44045.5089
9 | 30 | 11 | 0 | 4.6437 | 4.6437 | 48 | 7.2093 | 4.0738 | 4.0738 | 460.245 | 4.6437 | 0 | 1914.3365 | 0 | 0 | 0 | 4.6437 | 0 | 0 | 1914.3365
9 | 30 | 12 | 0 | 59.3431 | 59.3431 | 48 | 7.9296 | 74.6403 | 74.6403 | 460.8522 | 59.3431 | 0 | 24499.9263 | 0 | 0 | 0 | 59.3431 | 0 | 0 | 24499.9263
9 | 30 | 13 | 0 | 3.2988 | 3.2988 | 48 | 8.2601 | 5.1801 | 5.1801 | 460.8721 | 3.2988 | 0 | 1361.9898 | 0 | 0 | 0 | 3.2988 | 0 | 0 | 1361.9898
9 | 30 | 14 | 0 | 0.326 | 0.326 | 48 | 8.5313 | 0.643 | 0.643 | 461.4165 | 0.326 | 0 | 134.7757 | 0 | 0 | 0 | 0.326 | 0 | 0 | 134.7757
9 | 30 | 15 | 0 | 29.9369 | 29.9369 | 48 | 8.4041 | 52.7187 | 52.7187 | 463.0931 | 29.9369 | 0 | 12426.5861 | 0 | 0 | 0 | 29.9369 | 0 | 0 | 12426.5861
9 | 30 | 16 | 0 | 26.4401 | 26.4401 | 48 | 9.1753 | 133.0847 | 133.0847 | 460.3396 | 26.4401 | 0 | 10902.2948 | 0 | 0 | 0 | 26.4401 | 0 | 0 | 10902.2948
9 | 30 | 17 | 0 | 0.025 | 0.025 | 48 | 8.6753 | 0.057073 | 0.057073 | 464.8766 | 0.025 | 0 | 10.4219 | 0 | 0 | 0 | 0.025 | 0 | 0 | 10.4219
9 | 30 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 443.2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 424.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 405.8435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 394.6527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 381.4805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 30 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 373.8039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 376.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 373.2064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 378.1813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 387.6441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 394.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 397.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 405.5421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 7 | 0 | 0.19704 | 0.19704 | 48 | 4.8705 | 0.0872 | 0.0872 | 423.0638 | 0.19704 | 0 | 73.9032 | 0 | 0 | 0 | 0.19704 | 0 | 0 | 73.9032
10 | 1 | 8 | 0 | 0.016667 | 0.016667 | 48 | 4.8451 | 0.0073363 | 0.0073363 | 421.7724 | 0.016667 | 0 | 6.2296 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 6.2296
10 | 1 | 9 | 2.2208 | 198.1085 | 200.3293 | 47.5898 | 6.3789 | 130.2964 | 130.2964 | 424.5743 | 200.3293 | 0 | 75521.0483 | 0 | 0 | 0 | 200.3293 | 0 | 0 | 75521.0483
10 | 1 | 10 | 11.3166 | 986.9198 | 998.2364 | 47.5805 | 8.4804 | 1878.6895 | 288 | 427.0438 | 153.028 | 845.2084 | 58068.4947 | 88.1321 | 0 | 0 | 153.028 | 845.2084 | 0 | 58068.4947
10 | 1 | 11 | 2.3142 | 335.6867 | 338.0009 | 47.7467 | 9.4549 | 5216.919 | 288 | 431.4358 | 18.6593 | 319.3416 | 7159.386 | 33.2986 | 0 | 0 | 18.6593 | 319.3416 | 0 | 7159.386
10 | 1 | 12 | 0 | 1.1565 | 1.1565 | 48 | 9.8362 | 0 | 0 | 435.9345 | 0 | 1.1565 | 0 | 0.12059 | 0 | 0 | 0 | 1.1565 | 0 | 0
10 | 1 | 13 | 0 | 5.8224 | 5.8224 | 48 | 9.6159 | 0 | 0 | 440.7581 | 0 | 5.8224 | 0 | 0.60712 | 0 | 0 | 0 | 5.8224 | 0 | 0
10 | 1 | 14 | 0 | 21.7848 | 21.7848 | 48 | 9.5227 | 673.7587 | 288 | 452.3368 | 9.312 | 12.4728 | 3765.1658 | 1.3006 | 0 | 0 | 9.312 | 12.4728 | 0 | 3765.1658
10 | 1 | 15 | 0.86333 | 181.6158 | 182.4792 | 47.8249 | 10.7175 | 0 | 0 | 448.0752 | 0 | 182.4792 | 0 | 19.0276 | 0 | 0 | 0 | 182.4792 | 0 | 0
10 | 1 | 16 | 0 | 3.3659 | 3.3659 | 48 | 12.0564 | 0 | 0 | 446.6082 | 0 | 3.3659 | 0 | 0.35097 | 0 | 0 | 0 | 3.3659 | 0 | 0
10 | 1 | 17 | 0 | 0.047907 | 0.047907 | 48 | 11.8107 | 0 | 0 | 450.2404 | 0 | 0.047907 | 0 | 0.0049954 | 0 | 0 | 0 | 0.047907 | 0 | 0
10 | 1 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 442.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 423.9435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 397.7815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 388.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 387.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 388.6603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 391.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 395.4683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 416.4922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 444.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 474.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 5 | 1.3575 | 0 | 1.3575 | 11 | 3.6164 | 0.47462 | 0.47462 | 473.3175 | 1.3575 | 0 | 627.5767 | 0 | 0 | 0 | 1.3575 | 0 | 0 | 627.5767
10 | 2 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 477.1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 485.7619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 8 | 0 | 0.74941 | 0.74941 | 48 | 5.4976 | 0.38247 | 0.38247 | 494.4743 | 0.74941 | 0 | 334.5921 | 0 | 0 | 0 | 0.74941 | 0 | 0 | 334.5921
10 | 2 | 9 | 0 | 5.847 | 5.847 | 48 | 6.4043 | 3.8333 | 3.8333 | 494.7589 | 5.847 | 0 | 2612.1812 | 0 | 0 | 0 | 5.847 | 0 | 0 | 2612.1812
10 | 2 | 10 | 0 | 23.6022 | 23.6022 | 48 | 8.5991 | 49.7362 | 49.7362 | 490.5308 | 23.6022 | 0 | 10444.7162 | 0 | 0 | 0 | 23.6022 | 0 | 0 | 10444.7162
10 | 2 | 11 | 0 | 79.5887 | 79.5887 | 48 | 9.6413 | 0 | 0 | 490.7601 | 0 | 79.5887 | 0 | 8.2989 | 0 | 0 | 0 | 79.5887 | 0 | 0
10 | 2 | 12 | 0 | 38.4261 | 38.4261 | 48 | 9.7176 | 0 | 0 | 489.2355 | 0 | 38.4261 | 0 | 4.0068 | 0 | 0 | 0 | 38.4261 | 0 | 0
10 | 2 | 13 | 0 | 0.33637 | 0.33637 | 48 | 9.7939 | 0 | 0 | 481.6371 | 0 | 0.33637 | 0 | 0.035074 | 0 | 0 | 0 | 0.33637 | 0 | 0
10 | 2 | 14 | 0 | 0.095155 | 0.095155 | 48 | 9.4634 | 1.5668 | 1.5668 | 485.5289 | 0.095155 | 0 | 41.6332 | 0 | 0 | 0 | 0.095155 | 0 | 0 | 41.6332
10 | 2 | 15 | 0 | 0.95955 | 0.95955 | 48 | 10.5311 | 0 | 0 | 492.0314 | 0 | 0.95955 | 0 | 0.10005 | 0 | 0 | 0 | 0.95955 | 0 | 0
10 | 2 | 16 | 0.1725 | 50.9856 | 51.1581 | 47.8752 | 11.0904 | 0 | 0 | 488.8316 | 0 | 51.1581 | 0 | 5.3344 | 0 | 0 | 0 | 51.1581 | 0 | 0
10 | 2 | 17 | 0 | 0.0091667 | 0.0091667 | 48 | 11.1073 | 0 | 0 | 487.8381 | 0 | 0.0091667 | 0 | 0.00095584 | 0 | 0 | 0 | 0.0091667 | 0 | 0
10 | 2 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 490.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 466.8552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 446.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 422.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 407.6445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 397.9878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 398.0326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 402.8344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 424.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 447.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 468.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 469.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 472.4584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 7 | 0 | 0.22667 | 0.22667 | 48 | 5.2518 | 0.10913 | 0.10913 | 482.4413 | 0.22667 | 0 | 98.4734 | 0 | 0 | 0 | 0.22667 | 0 | 0 | 98.4734
10 | 3 | 8 | 0 | 0.016667 | 0.016667 | 48 | 6.2094 | 0.010297 | 0.010297 | 489.631 | 0.016667 | 0 | 7.3605 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 7.3605
10 | 3 | 9 | 0 | 4.6062 | 4.6062 | 48 | 7.328 | 4.2528 | 4.2528 | 491.568 | 4.6062 | 0 | 2043.1563 | 0 | 0 | 0 | 4.6062 | 0 | 0 | 2043.1563
10 | 3 | 10 | 0 | 58.6486 | 58.6486 | 48 | 8.5482 | 117.5579 | 117.5579 | 487.4159 | 58.6486 | 0 | 25771.1124 | 0 | 0 | 0 | 58.6486 | 0 | 0 | 25771.1124
10 | 3 | 11 | 0 | 12.7234 | 12.7234 | 48 | 9.1838 | 65.3776 | 65.3776 | 476.9933 | 12.7234 | 0 | 5458.2522 | 0 | 0 | 0 | 12.7234 | 0 | 0 | 5458.2522
10 | 3 | 12 | 0 | 0.13417 | 0.13417 | 48 | 9.8701 | 0 | 0 | 477.5615 | 0 | 0.13417 | 0 | 0.01399 | 0 | 0 | 0 | 0.13417 | 0 | 0
10 | 3 | 13 | 0 | 0.55243 | 0.55243 | 48 | 9.6668 | 0 | 0 | 481.9518 | 0 | 0.55243 | 0 | 0.057603 | 0 | 0 | 0 | 0.55243 | 0 | 0
10 | 3 | 14 | 0 | 0.061667 | 0.061667 | 48 | 10.2684 | 0 | 0 | 483.1921 | 0 | 0.061667 | 0 | 0.0064301 | 0 | 0 | 0 | 0.061667 | 0 | 0
10 | 3 | 15 | 0 | 0.033333 | 0.033333 | 48 | 11.226 | 0 | 0 | 487.2164 | 0 | 0.033333 | 0 | 0.0034758 | 0 | 0 | 0 | 0.033333 | 0 | 0
10 | 3 | 16 | 0 | 3.3009 | 3.3009 | 48 | 11.853 | 0 | 0 | 489.2353 | 0 | 3.3009 | 0 | 0.34419 | 0 | 0 | 0 | 3.3009 | 0 | 0
10 | 3 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 491.8522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 502.2464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 486.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 467.6859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 443.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 430.0597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 3 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 424.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 421.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 425.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 449.6644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 468.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 485.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 478.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 483.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 7 | 0 | 1.0788 | 1.0788 | 48 | 5.0146 | 0.49244 | 0.49244 | 493.8609 | 1.0788 | 0 | 480.986 | 0 | 0 | 0 | 1.0788 | 0 | 0 | 480.986
10 | 4 | 8 | 0 | 3.6154 | 3.6154 | 48 | 6.2094 | 2.2336 | 2.2336 | 501.6268 | 3.6154 | 0 | 1640.0485 | 0 | 0 | 0 | 3.6154 | 0 | 0 | 1640.0485
10 | 4 | 9 | 0 | 0.47636 | 0.47636 | 48 | 7.311 | 0.43654 | 0.43654 | 498.4739 | 0.47636 | 0 | 214.586 | 0 | 0 | 0 | 0.47636 | 0 | 0 | 214.586
10 | 4 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 499.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 11 | 0 | 16.7482 | 16.7482 | 48 | 9.3109 | 125.2117 | 125.2117 | 494.867 | 16.7482 | 0 | 7484.2057 | 0 | 0 | 0 | 16.7482 | 0 | 0 | 7484.2057
10 | 4 | 12 | 0 | 1.0878 | 1.0878 | 48 | 9.0058 | 3.8875 | 3.8875 | 493.1799 | 1.0878 | 0 | 484.2479 | 0 | 0 | 0 | 1.0878 | 0 | 0 | 484.2479
10 | 4 | 13 | 0 | 0.041022 | 0.041022 | 48 | 8.4889 | 0.077797 | 0.077797 | 493.2979 | 0.041022 | 0 | 18.2668 | 0 | 0 | 0 | 0.041022 | 0 | 0 | 18.2668
10 | 4 | 14 | 0 | 0.084167 | 0.084167 | 48 | 8.938 | 0.26953 | 0.26953 | 497.2759 | 0.084167 | 0 | 37.8141 | 0 | 0 | 0 | 0.084167 | 0 | 0 | 37.8141
10 | 4 | 15 | 0 | 0.031667 | 0.031667 | 48 | 9.6075 | 0 | 0 | 498.9125 | 0 | 0.031667 | 0 | 0.003302 | 0 | 0 | 0 | 0.031667 | 0 | 0
10 | 4 | 16 | 0 | 2.7364 | 2.7364 | 48 | 10.9718 | 0 | 0 | 498.7061 | 0 | 2.7364 | 0 | 0.28533 | 0 | 0 | 0 | 2.7364 | 0 | 0
10 | 4 | 17 | 0 | 0.18654 | 0.18654 | 48 | 10.3786 | 0 | 0 | 501.3761 | 0 | 0.18654 | 0 | 0.019451 | 0 | 0 | 0 | 0.18654 | 0 | 0
10 | 4 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 495.6754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 502.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 494.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 474.3298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 449.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 4 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 438.839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 431.616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 432.7723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 449.9158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 476.7677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 495.8262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 491.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 492.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 493.2393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 8 | 0.15 | 66.2512 | 66.4012 | 47.9164 | 5.1417 | 31.177 | 31.177 | 494.6196 | 66.4012 | 0 | 29661.6092 | 0 | 0 | 0 | 66.4012 | 0 | 0 | 29661.6092
10 | 5 | 9 | 0.13417 | 277.3514 | 277.4856 | 47.9821 | 6.6161 | 194.8782 | 194.8782 | 489.4296 | 277.4856 | 0 | 122495.3167 | 0 | 0 | 0 | 277.4856 | 0 | 0 | 122495.3167
10 | 5 | 10 | 0.085833 | 214.2303 | 214.3161 | 47.9852 | 6.9721 | 170.9745 | 170.9745 | 493.2246 | 214.3161 | 0 | 95421.9789 | 0 | 0 | 0 | 214.3161 | 0 | 0 | 95421.9789
10 | 5 | 11 | 0 | 0.0075 | 0.0075 | 48 | 8.5652 | 0.015282 | 0.015282 | 488.2776 | 0.0075 | 0 | 3.3021 | 0 | 0 | 0 | 0.0075 | 0 | 0 | 3.3021
10 | 5 | 12 | 0 | 0.85487 | 0.85487 | 48 | 7.8957 | 1.0537 | 1.0537 | 487.116 | 0.85487 | 0 | 375.3885 | 0 | 0 | 0 | 0.85487 | 0 | 0 | 375.3885
10 | 5 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 486.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 14 | 0 | 0.7315 | 0.7315 | 48 | 7.2771 | 0.66053 | 0.66053 | 488.619 | 0.7315 | 0 | 322.312 | 0 | 0 | 0 | 0.7315 | 0 | 0 | 322.312
10 | 5 | 15 | 0 | 2.6483 | 2.6483 | 48 | 7.3449 | 2.4636 | 2.4636 | 489.8189 | 2.6483 | 0 | 1170.0852 | 0 | 0 | 0 | 2.6483 | 0 | 0 | 1170.0852
10 | 5 | 16 | 0 | 0.45652 | 0.45652 | 48 | 6.9975 | 0.36777 | 0.36777 | 490.9021 | 0.45652 | 0 | 202.1921 | 0 | 0 | 0 | 0.45652 | 0 | 0 | 202.1921
10 | 5 | 17 | 0 | 0.051625 | 0.051625 | 48 | 7.167 | 0.044497 | 0.044497 | 493.334 | 0.051625 | 0 | 22.9904 | 0 | 0 | 0 | 0.051625 | 0 | 0 | 22.9904
10 | 5 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 497.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 498.1201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 491.9276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 475.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 455.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 443.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 439.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 441.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 456.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 479.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 488.2068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 486.7026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 487.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 489.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 8 | 0 | 13.1979 | 13.1979 | 48 | 6.8788 | 10.1669 | 10.1669 | 494.1122 | 13.1979 | 0 | 5887.754 | 0 | 0 | 0 | 13.1979 | 0 | 0 | 5887.754
10 | 6 | 9 | 0 | 188.8625 | 188.8625 | 48 | 7.3195 | 173.7211 | 173.7211 | 491.2604 | 188.8625 | 0 | 83715.2819 | 0 | 0 | 0 | 188.8625 | 0 | 0 | 83715.2819
10 | 6 | 10 | 0 | 281.3621 | 281.3621 | 48 | 7.4805 | 278.5554 | 278.5554 | 489.4951 | 281.3621 | 0 | 124219.995 | 0 | 0 | 0 | 281.3621 | 0 | 0 | 124219.995
10 | 6 | 11 | 0 | 96.0685 | 96.0685 | 48 | 7.2263 | 84.8821 | 84.8821 | 485.137 | 96.0685 | 0 | 41995.0772 | 0 | 0 | 0 | 96.0685 | 0 | 0 | 41995.0772
10 | 6 | 12 | 0 | 2.8467 | 2.8467 | 48 | 7.8703 | 3.457 | 3.457 | 485.7224 | 2.8467 | 0 | 1246.0718 | 0 | 0 | 0 | 2.8467 | 0 | 0 | 1246.0718
10 | 6 | 13 | 0 | 0.097486 | 0.097486 | 48 | 8.1754 | 0.14391 | 0.14391 | 485.7428 | 0.097486 | 0 | 42.6737 | 0 | 0 | 0 | 0.097486 | 0 | 0 | 42.6737
10 | 6 | 14 | 0 | 6.074 | 6.074 | 48 | 8.2431 | 9.4179 | 9.4179 | 487.4544 | 6.074 | 0 | 2669.2563 | 0 | 0 | 0 | 6.074 | 0 | 0 | 2669.2563
10 | 6 | 15 | 0 | 1.4923 | 1.4923 | 48 | 7.4212 | 1.437 | 1.437 | 490.9896 | 1.4923 | 0 | 661.0762 | 0 | 0 | 0 | 1.4923 | 0 | 0 | 661.0762
10 | 6 | 16 | 0 | 0.93454 | 0.93454 | 48 | 7.3195 | 0.85962 | 0.85962 | 489.3074 | 0.93454 | 0 | 412.4201 | 0 | 0 | 0 | 0.93454 | 0 | 0 | 412.4201
10 | 6 | 17 | 0 | 0.054993 | 0.054993 | 48 | 7.2686 | 0.049476 | 0.049476 | 490.8146 | 0.054993 | 0 | 24.3518 | 0 | 0 | 0 | 0.054993 | 0 | 0 | 24.3518
10 | 6 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 493.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 482.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 472.6712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 452.1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 429.0004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 6 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 409.5729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 397.4973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 396.1996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 398.8898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 408.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 416.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 424.9431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 443.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 7 | 0 | 0.66083 | 0.66083 | 48 | 6.006 | 0.3851 | 0.3851 | 447.9569 | 0.66083 | 0 | 264.3049 | 0 | 0 | 0 | 0.66083 | 0 | 0 | 264.3049
10 | 7 | 8 | 0 | 2.9383 | 2.9383 | 48 | 6.6246 | 2.0695 | 2.0695 | 459.9629 | 2.9383 | 0 | 1210.4842 | 0 | 0 | 0 | 2.9383 | 0 | 0 | 1210.4842
10 | 7 | 9 | 0 | 1.213 | 1.213 | 48 | 7.1924 | 1.0566 | 1.0566 | 458.0685 | 1.213 | 0 | 497.4029 | 0 | 0 | 0 | 1.213 | 0 | 0 | 497.4029
10 | 7 | 10 | 0 | 3.4611 | 3.4611 | 48 | 7.0398 | 2.8346 | 2.8346 | 462.4056 | 3.4611 | 0 | 1434.312 | 0 | 0 | 0 | 3.4611 | 0 | 0 | 1434.312
10 | 7 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 462.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 12 | 0 | 0.17151 | 0.17151 | 48 | 7.9296 | 0.21573 | 0.21573 | 468.92 | 0.17151 | 0 | 72.1934 | 0 | 0 | 0 | 0.17151 | 0 | 0 | 72.1934
10 | 7 | 13 | 0 | 0.075698 | 0.075698 | 48 | 8.2601 | 0.11887 | 0.11887 | 466.3475 | 0.075698 | 0 | 31.6679 | 0 | 0 | 0 | 0.075698 | 0 | 0 | 31.6679
10 | 7 | 14 | 0 | 0.19161 | 0.19161 | 48 | 8.5313 | 0.37792 | 0.37792 | 467.1427 | 0.19161 | 0 | 80.3099 | 0 | 0 | 0 | 0.19161 | 0 | 0 | 80.3099
10 | 7 | 15 | 0 | 0.80676 | 0.80676 | 48 | 8.4041 | 1.4207 | 1.4207 | 468.1979 | 0.80676 | 0 | 339.0005 | 0 | 0 | 0 | 0.80676 | 0 | 0 | 339.0005
10 | 7 | 16 | 0 | 0.038083 | 0.038083 | 48 | 9.1753 | 0.19169 | 0.19169 | 467.3363 | 0.038083 | 0 | 15.9697 | 0 | 0 | 0 | 0.038083 | 0 | 0 | 15.9697
10 | 7 | 17 | 0 | 4.5066 | 4.5066 | 48 | 8.6753 | 10.2882 | 10.2882 | 470.3199 | 4.5066 | 0 | 1903.2199 | 0 | 0 | 0 | 4.5066 | 0 | 0 | 1903.2199
10 | 7 | 18 | 0 | 0.2175 | 0.2175 | 48 | 9.0397 | 0.82517 | 0.82517 | 481.2898 | 0.2175 | 0 | 94.2405 | 0 | 0 | 0 | 0.2175 | 0 | 0 | 94.2405
10 | 7 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 474.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 469.9228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 459.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 443.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 7 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 439.3983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 434.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 433.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 440.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 444.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 452.8425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 460.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 478.0312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 496.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 8 | 0 | 0.96719 | 0.96719 | 48 | 4.8451 | 0.42573 | 0.42573 | 503.7362 | 0.96719 | 0 | 440.7829 | 0 | 0 | 0 | 0.96719 | 0 | 0 | 440.7829
10 | 8 | 9 | 0 | 94.4516 | 94.4516 | 48 | 6.3789 | 61.4323 | 61.4323 | 507.1018 | 94.4516 | 0 | 43362.8842 | 0 | 0 | 0 | 94.4516 | 0 | 0 | 43362.8842
10 | 8 | 10 | 0 | 126.9385 | 126.9385 | 48 | 8.4804 | 238.8993 | 238.8993 | 509.5036 | 126.9385 | 0 | 58582.5587 | 0 | 0 | 0 | 126.9385 | 0 | 0 | 58582.5587
10 | 8 | 11 | 0 | 190.7592 | 190.7592 | 48 | 9.4549 | 2944.2979 | 288 | 503.2994 | 18.6593 | 172.0999 | 8495.5853 | 17.9453 | 0 | 0 | 18.6593 | 172.0999 | 0 | 8495.5853
10 | 8 | 12 | 0 | 194.0769 | 194.0769 | 48 | 9.8362 | 0 | 0 | 501.8885 | 0 | 194.0769 | 0 | 20.2369 | 0 | 0 | 0 | 194.0769 | 0 | 0
10 | 8 | 13 | 0 | 55.2298 | 55.2298 | 48 | 9.6159 | 0 | 0 | 503.2048 | 0 | 55.2298 | 0 | 5.759 | 0 | 0 | 0 | 55.2298 | 0 | 0
10 | 8 | 14 | 0 | 33.909 | 33.909 | 48 | 9.5227 | 1048.7377 | 288 | 508.8748 | 9.312 | 24.5971 | 4291.6451 | 2.5648 | 0 | 0 | 9.312 | 24.5971 | 0 | 4291.6451
10 | 8 | 15 | 0 | 13.4118 | 13.4118 | 48 | 10.7175 | 0 | 0 | 514.1331 | 0 | 13.4118 | 0 | 1.3985 | 0 | 0 | 0 | 13.4118 | 0 | 0
10 | 8 | 16 | 0 | 0.28128 | 0.28128 | 48 | 12.0564 | 0 | 0 | 516.5784 | 0 | 0.28128 | 0 | 0.02933 | 0 | 0 | 0 | 0.28128 | 0 | 0
10 | 8 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 519.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 18 | 0.80812 | 0 | 0.80812 | 11 | 12.3445 | 0 | 0 | 518.0978 | 0 | 0.80812 | 0 | 0.084264 | 0 | 0 | 0 | 0.80812 | 0 | 0
10 | 8 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 515.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 507.3933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 501.745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 8 | 22 | 0.22568 | 0 | 0.22568 | 11 | 5.04 | 0.1036 | 0.1036 | 484.7131 | 0.22568 | 0 | 106.9087 | 0 | 0 | 0 | 0.22568 | 0 | 0 | 106.9087
10 | 8 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 474.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 469.6408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 472.3407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 483.9041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 505.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 520.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 524.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 530.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 529.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 8 | 0 | 31.4183 | 31.4183 | 48 | 5.4976 | 16.0345 | 16.0345 | 526.6611 | 31.4183 | 0 | 15038.7249 | 0 | 0 | 0 | 31.4183 | 0 | 0 | 15038.7249
10 | 9 | 9 | 0 | 352.2084 | 352.2084 | 48 | 6.4043 | 230.9082 | 230.9082 | 521.6388 | 352.2084 | 0 | 166819.5715 | 0 | 0 | 0 | 352.2084 | 0 | 0 | 166819.5715
10 | 9 | 10 | 0 | 542.5191 | 542.5191 | 48 | 8.5991 | 1143.2312 | 288 | 517.6087 | 136.6701 | 405.849 | 64181.4556 | 42.3189 | 0 | 0 | 136.6701 | 405.849 | 0 | 64181.4556
10 | 9 | 11 | 0 | 349.4891 | 349.4891 | 48 | 9.6413 | 0 | 0 | 519.1874 | 0 | 349.4891 | 0 | 36.4421 | 0 | 0 | 0 | 349.4891 | 0 | 0
10 | 9 | 12 | 0 | 109.033 | 109.033 | 48 | 9.7176 | 0 | 0 | 519.0002 | 0 | 109.033 | 0 | 11.3692 | 0 | 0 | 0 | 109.033 | 0 | 0
10 | 9 | 13 | 0.24083 | 128.4812 | 128.722 | 47.9308 | 9.7939 | 0 | 0 | 521.2947 | 0 | 128.722 | 0 | 13.4222 | 0 | 0 | 0 | 128.722 | 0 | 0
10 | 9 | 14 | 0.26833 | 112.4256 | 112.6939 | 47.9119 | 9.4634 | 1855.5827 | 288 | 524.6294 | 17.4909 | 95.203 | 8338.2257 | 9.9271 | 0 | 0 | 17.4909 | 95.203 | 0 | 8338.2257
10 | 9 | 15 | 0.11417 | 7.2318 | 7.3459 | 47.425 | 10.5311 | 0 | 0 | 527.1853 | 0 | 7.3459 | 0 | 0.76598 | 0 | 0 | 0 | 7.3459 | 0 | 0
10 | 9 | 16 | 0 | 6.7858 | 6.7858 | 48 | 11.0904 | 0 | 0 | 527.9136 | 0 | 6.7858 | 0 | 0.70757 | 0 | 0 | 0 | 6.7858 | 0 | 0
10 | 9 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 524.1564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 523.1716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 521.895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 508.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 504.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 507.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 9 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 498.8945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 490.9622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 487.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 501.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 518.3459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 528.9317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 529.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 531.845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 7 | 0.063333 | 27.6495 | 27.7128 | 47.9154 | 5.2518 | 13.3423 | 13.3423 | 529.9123 | 27.7128 | 0 | 13357.5037 | 0 | 0 | 0 | 27.7128 | 0 | 0 | 13357.5037
10 | 10 | 8 | 0.02 | 35.8059 | 35.8259 | 47.9793 | 6.2094 | 22.1335 | 22.1335 | 532.4307 | 35.8259 | 0 | 17355.8884 | 0 | 0 | 0 | 35.8259 | 0 | 0 | 17355.8884
10 | 10 | 9 | 0.018333 | 153.5321 | 153.5505 | 47.9956 | 7.328 | 141.7691 | 141.7691 | 528.8042 | 153.5505 | 0 | 73828.3869 | 0 | 0 | 0 | 153.5505 | 0 | 0 | 73828.3869
10 | 10 | 10 | 0 | 120.0758 | 120.0758 | 48 | 8.5482 | 240.6855 | 240.6855 | 525.8578 | 120.0758 | 0 | 57379.1699 | 0 | 0 | 0 | 120.0758 | 0 | 0 | 57379.1699
10 | 10 | 11 | 0 | 193.3051 | 193.3051 | 48 | 9.1838 | 993.2735 | 288 | 520.1525 | 56.0489 | 137.2562 | 26463.6172 | 14.3121 | 0 | 0 | 56.0489 | 137.2562 | 0 | 26463.6172
10 | 10 | 12 | 0.0058333 | 3.9173 | 3.9232 | 47.945 | 9.8701 | 0 | 0 | 519.4744 | 0 | 3.9232 | 0 | 0.40908 | 0 | 0 | 0 | 3.9232 | 0 | 0
10 | 10 | 13 | 0.038333 | 66.4727 | 66.5111 | 47.9787 | 9.6668 | 0 | 0 | 515.1285 | 0 | 66.5111 | 0 | 6.9353 | 0 | 0 | 0 | 66.5111 | 0 | 0
10 | 10 | 14 | 0.27342 | 50.0615 | 50.3349 | 47.799 | 10.2684 | 0 | 0 | 513.2631 | 0 | 50.3349 | 0 | 5.2485 | 0 | 0 | 0 | 50.3349 | 0 | 0
10 | 10 | 15 | 0.0175 | 16.9398 | 16.9573 | 47.9618 | 11.226 | 0 | 0 | 506.9595 | 0 | 16.9573 | 0 | 1.7682 | 0 | 0 | 0 | 16.9573 | 0 | 0
10 | 10 | 16 | 0 | 1.2466 | 1.2466 | 48 | 11.853 | 0 | 0 | 504.3198 | 0 | 1.2466 | 0 | 0.12999 | 0 | 0 | 0 | 1.2466 | 0 | 0
10 | 10 | 17 | 0 | 0.51704 | 0.51704 | 48 | 11.7514 | 0 | 0 | 509.5722 | 0 | 0.51704 | 0 | 0.053913 | 0 | 0 | 0 | 0.51704 | 0 | 0
10 | 10 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 519.8858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 511.5371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 503.9309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 492.521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 477.3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 10 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 462.5942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 464.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 464.6402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 476.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 499.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 521.3397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 513.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 514.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 516.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 8 | 0 | 1.223 | 1.223 | 48 | 6.2094 | 0.75559 | 0.75559 | 517.0915 | 1.223 | 0 | 573.705 | 0 | 0 | 0 | 1.223 | 0 | 0 | 573.705
10 | 11 | 9 | 0 | 69.7592 | 69.7592 | 48 | 7.311 | 63.9279 | 63.9279 | 520.124 | 69.7592 | 0 | 32934.9742 | 0 | 0 | 0 | 69.7592 | 0 | 0 | 32934.9742
10 | 11 | 10 | 0 | 3.7068 | 3.7068 | 48 | 8.0567 | 5.0488 | 5.0488 | 523.4658 | 3.7068 | 0 | 1762.4591 | 0 | 0 | 0 | 3.7068 | 0 | 0 | 1762.4591
10 | 11 | 11 | 0.02 | 78.3608 | 78.3808 | 47.9906 | 9.3109 | 585.986 | 288 | 522.1319 | 38.5225 | 39.8582 | 18265.1224 | 4.1561 | 0 | 0 | 38.5225 | 39.8582 | 0 | 18265.1224
10 | 11 | 12 | 0 | 3.8823 | 3.8823 | 48 | 9.0058 | 13.8747 | 13.8747 | 517.36 | 3.8823 | 0 | 1822.1955 | 0 | 0 | 0 | 3.8823 | 0 | 0 | 1822.1955
10 | 11 | 13 | 0 | 5.1921 | 5.1921 | 48 | 8.4889 | 9.8468 | 9.8468 | 519.2474 | 5.1921 | 0 | 2446.7624 | 0 | 0 | 0 | 5.1921 | 0 | 0 | 2446.7624
10 | 11 | 14 | 0 | 6.102 | 6.102 | 48 | 8.938 | 19.5409 | 19.5409 | 521.1223 | 6.102 | 0 | 2886.9898 | 0 | 0 | 0 | 6.102 | 0 | 0 | 2886.9898
10 | 11 | 15 | 0 | 1.9148 | 1.9148 | 48 | 9.6075 | 0 | 0 | 519.244 | 0 | 1.9148 | 0 | 0.19966 | 0 | 0 | 0 | 1.9148 | 0 | 0
10 | 11 | 16 | 0 | 2.1612 | 2.1612 | 48 | 10.9718 | 0 | 0 | 521.1433 | 0 | 2.1612 | 0 | 0.22536 | 0 | 0 | 0 | 2.1612 | 0 | 0
10 | 11 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 521.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 522.5491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 517.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 501.1978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 487.8739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 483.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 481.5066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 471.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 474.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 484.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 506.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 521.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 523.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 525.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 524.1388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 8 | 0 | 2.3548 | 2.3548 | 48 | 5.1417 | 1.1056 | 1.1056 | 525.3468 | 2.3548 | 0 | 1124.0671 | 0 | 0 | 0 | 2.3548 | 0 | 0 | 1124.0671
10 | 12 | 9 | 0 | 146.1078 | 146.1078 | 48 | 6.6161 | 102.6116 | 102.6116 | 521.689 | 146.1078 | 0 | 69209.6832 | 0 | 0 | 0 | 146.1078 | 0 | 0 | 69209.6832
10 | 12 | 10 | 0 | 5.5101 | 5.5101 | 48 | 6.9721 | 4.3958 | 4.3958 | 524.4883 | 5.5101 | 0 | 2625.4895 | 0 | 0 | 0 | 5.5101 | 0 | 0 | 2625.4895
10 | 12 | 11 | 0 | 4.9921 | 4.9921 | 48 | 8.5652 | 10.1719 | 10.1719 | 522.053 | 4.9921 | 0 | 2366.5302 | 0 | 0 | 0 | 4.9921 | 0 | 0 | 2366.5302
10 | 12 | 12 | 0 | 5.9317 | 5.9317 | 48 | 7.8957 | 7.3116 | 7.3116 | 519.4143 | 5.9317 | 0 | 2796.3114 | 0 | 0 | 0 | 5.9317 | 0 | 0 | 2796.3114
10 | 12 | 13 | 0.005 | 52.1221 | 52.1271 | 47.9965 | 7.4381 | 50.5911 | 50.5911 | 515.2342 | 52.1271 | 0 | 24355.7708 | 0 | 0 | 0 | 52.1271 | 0 | 0 | 24355.7708
10 | 12 | 14 | 0 | 6.1293 | 6.1293 | 48 | 7.2771 | 5.5346 | 5.5346 | 517.1731 | 6.1293 | 0 | 2875.6845 | 0 | 0 | 0 | 6.1293 | 0 | 0 | 2875.6845
10 | 12 | 15 | 0 | 15.0378 | 15.0378 | 48 | 7.3449 | 13.9888 | 13.9888 | 518.9454 | 15.0378 | 0 | 7081.9849 | 0 | 0 | 0 | 15.0378 | 0 | 0 | 7081.9849
10 | 12 | 16 | 0 | 87.8317 | 87.8317 | 48 | 6.9975 | 70.7563 | 70.7563 | 512.4049 | 87.8317 | 0 | 40789.4513 | 0 | 0 | 0 | 87.8317 | 0 | 0 | 40789.4513
10 | 12 | 17 | 0 | 0.055106 | 0.055106 | 48 | 7.167 | 0.047497 | 0.047497 | 515.7637 | 0.055106 | 0 | 25.7765 | 0 | 0 | 0 | 0.055106 | 0 | 0 | 25.7765
10 | 12 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 517.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 499.0403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 470.2652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 447.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 436.3874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 435.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 425.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 428.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 439.3974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 467.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 491.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 495.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 503.5606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 507.3259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 509.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 9 | 0 | 2.006 | 2.006 | 48 | 7.3195 | 1.8452 | 1.8452 | 509.7484 | 2.006 | 0 | 926.268 | 0 | 0 | 0 | 2.006 | 0 | 0 | 926.268
10 | 13 | 10 | 0 | 3.6176 | 3.6176 | 48 | 7.4805 | 3.5815 | 3.5815 | 514.6395 | 3.6176 | 0 | 1688.1297 | 0 | 0 | 0 | 3.6176 | 0 | 0 | 1688.1297
10 | 13 | 11 | 0 | 45.0341 | 45.0341 | 48 | 7.2263 | 39.7903 | 39.7903 | 514.746 | 45.0341 | 0 | 21019.4886 | 0 | 0 | 0 | 45.0341 | 0 | 0 | 21019.4886
10 | 13 | 12 | 0 | 77.002 | 77.002 | 48 | 7.8703 | 93.5111 | 93.5111 | 518.7859 | 77.002 | 0 | 36251.4681 | 0 | 0 | 0 | 77.002 | 0 | 0 | 36251.4681
10 | 13 | 13 | 0 | 6.0819 | 6.0819 | 48 | 8.1754 | 8.9782 | 8.9782 | 518.663 | 6.0819 | 0 | 2862.5081 | 0 | 0 | 0 | 6.0819 | 0 | 0 | 2862.5081
10 | 13 | 14 | 0 | 56.7517 | 56.7517 | 48 | 8.2431 | 87.9948 | 87.9948 | 519.1617 | 56.7517 | 0 | 26739.2197 | 0 | 0 | 0 | 56.7517 | 0 | 0 | 26739.2197
10 | 13 | 15 | 0 | 67.4643 | 67.4643 | 48 | 7.4212 | 64.9647 | 64.9647 | 516.6009 | 67.4643 | 0 | 31613.8255 | 0 | 0 | 0 | 67.4643 | 0 | 0 | 31613.8255
10 | 13 | 16 | 0 | 11.7214 | 11.7214 | 48 | 7.3195 | 10.7816 | 10.7816 | 508.8833 | 11.7214 | 0 | 5402.1829 | 0 | 0 | 0 | 11.7214 | 0 | 0 | 5402.1829
10 | 13 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 510.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 508.774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 491.3685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 473.4884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 452.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 444.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 440.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 441.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 440.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 442.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 455.6267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 468.8053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 473.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 486.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 493.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 8 | 0 | 1.2291 | 1.2291 | 48 | 6.6246 | 0.86565 | 0.86565 | 499.9182 | 1.2291 | 0 | 555.4421 | 0 | 0 | 0 | 1.2291 | 0 | 0 | 555.4421
10 | 14 | 9 | 0 | 74.7841 | 74.7841 | 48 | 7.1924 | 65.1421 | 65.1421 | 505.8077 | 74.7841 | 0 | 34236.7415 | 0 | 0 | 0 | 74.7841 | 0 | 0 | 34236.7415
10 | 14 | 10 | 0 | 15.0073 | 15.0073 | 48 | 7.0398 | 12.2906 | 12.2906 | 494.8922 | 15.0073 | 0 | 6706.662 | 0 | 0 | 0 | 15.0073 | 0 | 0 | 6706.662
10 | 14 | 11 | 0 | 23.4949 | 23.4949 | 48 | 7.2093 | 20.6113 | 20.6113 | 494.6458 | 23.4949 | 0 | 10493.8926 | 0 | 0 | 0 | 23.4949 | 0 | 0 | 10493.8926
10 | 14 | 12 | 0 | 4.0276 | 4.0276 | 48 | 7.9296 | 5.0659 | 5.0659 | 485.7668 | 4.0276 | 0 | 1763.1616 | 0 | 0 | 0 | 4.0276 | 0 | 0 | 1763.1616
10 | 14 | 13 | 0 | 5.6104 | 5.6104 | 48 | 8.2601 | 8.8098 | 8.8098 | 489.949 | 5.6104 | 0 | 2479.4925 | 0 | 0 | 0 | 5.6104 | 0 | 0 | 2479.4925
10 | 14 | 14 | 0 | 3.8845 | 3.8845 | 48 | 8.5313 | 7.6617 | 7.6617 | 490.0276 | 3.8845 | 0 | 1717.0639 | 0 | 0 | 0 | 3.8845 | 0 | 0 | 1717.0639
10 | 14 | 15 | 0 | 1.9789 | 1.9789 | 48 | 8.4041 | 3.4848 | 3.4848 | 489.4129 | 1.9789 | 0 | 873.5142 | 0 | 0 | 0 | 1.9789 | 0 | 0 | 873.5142
10 | 14 | 16 | 0 | 3.0045 | 3.0045 | 48 | 9.1753 | 15.1229 | 15.1229 | 488.5291 | 3.0045 | 0 | 1323.5661 | 0 | 0 | 0 | 3.0045 | 0 | 0 | 1323.5661
10 | 14 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 489.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 491.9212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 481.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 463.6541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 444.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 430.9532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 14 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 423.7476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 409.0337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 408.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 416.9165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 421.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 418.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 419.8257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 428.7136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 7 | 0 | 25.7491 | 25.7491 | 48 | 4.8705 | 11.3952 | 11.3952 | 443.9601 | 25.7491 | 0 | 10195.626 | 0 | 0 | 0 | 25.7491 | 0 | 0 | 10195.626
10 | 15 | 8 | 0 | 87.0029 | 87.0029 | 48 | 4.8451 | 38.2967 | 38.2967 | 442.9049 | 87.0029 | 0 | 34357.8651 | 0 | 0 | 0 | 87.0029 | 0 | 0 | 34357.8651
10 | 15 | 9 | 0.21583 | 384.0416 | 384.2575 | 47.9792 | 6.3789 | 249.9253 | 249.9253 | 444.683 | 384.2575 | 0 | 152436.3881 | 0 | 0 | 0 | 384.2575 | 0 | 0 | 152436.3881
10 | 15 | 10 | 0 | 20.6455 | 20.6455 | 48 | 8.4804 | 38.8551 | 38.8551 | 454.9518 | 20.6455 | 0 | 8401.7411 | 0 | 0 | 0 | 20.6455 | 0 | 0 | 8401.7411
10 | 15 | 11 | 0 | 3.1771 | 3.1771 | 48 | 9.4549 | 49.0369 | 49.0369 | 439.1281 | 3.1771 | 0 | 1242.6417 | 0 | 0 | 0 | 3.1771 | 0 | 0 | 1242.6417
10 | 15 | 12 | 0 | 4.1114 | 4.1114 | 48 | 9.8362 | 0 | 0 | 444.2376 | 0 | 4.1114 | 0 | 0.42871 | 0 | 0 | 0 | 4.1114 | 0 | 0
10 | 15 | 13 | 0 | 5.3015 | 5.3015 | 48 | 9.6159 | 0 | 0 | 453.3575 | 0 | 5.3015 | 0 | 0.5528 | 0 | 0 | 0 | 5.3015 | 0 | 0
10 | 15 | 14 | 0 | 5.0661 | 5.0661 | 48 | 9.5227 | 156.6831 | 156.6831 | 459.3722 | 5.0661 | 0 | 2084.038 | 0 | 0 | 0 | 5.0661 | 0 | 0 | 2084.038
10 | 15 | 15 | 0 | 9.0622 | 9.0622 | 48 | 10.7175 | 0 | 0 | 469.7945 | 0 | 9.0622 | 0 | 0.94494 | 0 | 0 | 0 | 9.0622 | 0 | 0
10 | 15 | 16 | 0 | 23.1495 | 23.1495 | 48 | 12.0564 | 0 | 0 | 476.798 | 0 | 23.1495 | 0 | 2.4139 | 0 | 0 | 0 | 23.1495 | 0 | 0
10 | 15 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 475.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 481.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 471.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 454.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 446.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 445.1729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 15 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 437.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 437.6008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 437.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 444.3131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 458.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 480.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 484.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 495.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 7 | 0 | 22.2047 | 22.2047 | 48 | 4.8281 | 9.7392 | 9.7392 | 499.0149 | 22.2047 | 0 | 10014.6313 | 0 | 0 | 0 | 22.2047 | 0 | 0 | 10014.6313
10 | 16 | 8 | 0 | 152.0046 | 152.0046 | 48 | 5.4976 | 77.5763 | 77.5763 | 500.2855 | 152.0046 | 0 | 68749.4822 | 0 | 0 | 0 | 152.0046 | 0 | 0 | 68749.4822
10 | 16 | 9 | 0 | 100.6265 | 100.6265 | 48 | 6.4043 | 65.9708 | 65.9708 | 488.2467 | 100.6265 | 0 | 44300.4759 | 0 | 0 | 0 | 100.6265 | 0 | 0 | 44300.4759
10 | 16 | 10 | 0 | 218.34 | 218.34 | 48 | 8.5991 | 460.1001 | 288 | 482.9828 | 136.6701 | 81.6699 | 59449.1274 | 8.5159 | 0 | 0 | 136.6701 | 81.6699 | 0 | 59449.1274
10 | 16 | 11 | 0 | 277.9572 | 277.9572 | 48 | 9.6413 | 0 | 0 | 483.0636 | 0 | 277.9572 | 0 | 28.9833 | 0 | 0 | 0 | 277.9572 | 0 | 0
10 | 16 | 12 | 0 | 231.5633 | 231.5633 | 48 | 9.7176 | 0 | 0 | 479.5325 | 0 | 231.5633 | 0 | 24.1457 | 0 | 0 | 0 | 231.5633 | 0 | 0
10 | 16 | 13 | 0 | 158.8144 | 158.8144 | 48 | 9.7939 | 0 | 0 | 479.5325 | 0 | 158.8144 | 0 | 16.56 | 0 | 0 | 0 | 158.8144 | 0 | 0
10 | 16 | 14 | 0 | 44.5662 | 44.5662 | 48 | 9.4634 | 733.814 | 288 | 479.5325 | 17.4909 | 27.0753 | 7547.8989 | 2.8232 | 0 | 0 | 17.4909 | 27.0753 | 0 | 7547.8989
10 | 16 | 15 | 0 | 32.8851 | 32.8851 | 48 | 10.5311 | 0 | 0 | 479.5325 | 0 | 32.8851 | 0 | 3.429 | 0 | 0 | 0 | 32.8851 | 0 | 0
10 | 16 | 16 | 0 | 20.1821 | 20.1821 | 48 | 11.0904 | 0 | 0 | 479.5325 | 0 | 20.1821 | 0 | 2.1044 | 0 | 0 | 0 | 20.1821 | 0 | 0
10 | 16 | 17 | 0.14083 | 2.5433 | 2.6842 | 46.0587 | 11.1073 | 0 | 0 | 479.5325 | 0 | 2.6842 | 0 | 0.27989 | 0 | 0 | 0 | 2.6842 | 0 | 0
10 | 16 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 475.9734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 472.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 455.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 430.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 405.7073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 16 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 398.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 397.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 401.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 408.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 435.1973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 460.7948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 466.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 476.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 7 | 0 | 1.1752 | 1.1752 | 48 | 5.2518 | 0.56579 | 0.56579 | 480.3041 | 1.1752 | 0 | 508.0415 | 0 | 0 | 0 | 1.1752 | 0 | 0 | 508.0415
10 | 17 | 8 | 0.005 | 18.755 | 18.76 | 47.9901 | 6.2094 | 11.5901 | 11.5901 | 471.7587 | 18.76 | 0 | 7949.8989 | 0 | 0 | 0 | 18.76 | 0 | 0 | 7949.8989
10 | 17 | 9 | 0 | 1.6081 | 1.6081 | 48 | 7.328 | 1.4847 | 1.4847 | 464.4037 | 1.6081 | 0 | 669.6284 | 0 | 0 | 0 | 1.6081 | 0 | 0 | 669.6284
10 | 17 | 10 | 0 | 0 | 0 | 0 | 8.5482 | 0 | 0 | 467.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 11 | 0 | 6.904 | 6.904 | 48 | 9.1838 | 35.4755 | 35.4755 | 462.3787 | 6.904 | 0 | 2860.8846 | 0 | 0 | 0 | 6.904 | 0 | 0 | 2860.8846
10 | 17 | 12 | 0 | 6.5627 | 6.5627 | 48 | 9.8701 | 0 | 0 | 472.0576 | 0 | 6.5627 | 0 | 0.68431 | 0 | 0 | 0 | 6.5627 | 0 | 0
10 | 17 | 13 | 0 | 1.1903 | 1.1903 | 48 | 9.6668 | 0 | 0 | 473.6781 | 0 | 1.1903 | 0 | 0.12412 | 0 | 0 | 0 | 1.1903 | 0 | 0
10 | 17 | 14 | 0 | 0.071667 | 0.071667 | 48 | 10.2684 | 0 | 0 | 478.2172 | 0 | 0.071667 | 0 | 0.0074729 | 0 | 0 | 0 | 0.071667 | 0 | 0
10 | 17 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 476.5372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 16 | 0 | 0.36442 | 0.36442 | 48 | 11.853 | 0 | 0 | 487.2405 | 0 | 0.36442 | 0 | 0.037999 | 0 | 0 | 0 | 0.36442 | 0 | 0
10 | 17 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 481.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 475.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 454.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 438.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 417.9119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 406.2142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 17 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 401.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 403.3711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 420.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 429.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 469.1621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 482.3161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 482.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 488.3707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 483.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 9 | 0 | 9.4178 | 9.4178 | 48 | 7.311 | 8.6305 | 8.6305 | 487.0882 | 9.4178 | 0 | 4135.2321 | 0 | 0 | 0 | 9.4178 | 0 | 0 | 4135.2321
10 | 18 | 10 | 0 | 59.4672 | 59.4672 | 48 | 8.0567 | 80.996 | 80.996 | 486.7521 | 59.4672 | 0 | 26091.3421 | 0 | 0 | 0 | 59.4672 | 0 | 0 | 26091.3421
10 | 18 | 11 | 0 | 0.13 | 0.13 | 48 | 9.3109 | 0.9719 | 0.9719 | 481.0064 | 0.13 | 0 | 56.2909 | 0 | 0 | 0 | 0.13 | 0 | 0 | 56.2909
10 | 18 | 12 | 0 | 5.4614 | 5.4614 | 48 | 9.0058 | 19.5183 | 19.5183 | 479.0818 | 5.4614 | 0 | 2354.3304 | 0 | 0 | 0 | 5.4614 | 0 | 0 | 2354.3304
10 | 18 | 13 | 0 | 41.895 | 41.895 | 48 | 8.4889 | 79.4533 | 79.4533 | 481.0698 | 41.895 | 0 | 18143.4418 | 0 | 0 | 0 | 41.895 | 0 | 0 | 18143.4418
10 | 18 | 14 | 0 | 84.7286 | 84.7286 | 48 | 8.938 | 271.3332 | 271.3332 | 479.7757 | 84.7286 | 0 | 36583.7748 | 0 | 0 | 0 | 84.7286 | 0 | 0 | 36583.7748
10 | 18 | 15 | 0 | 74.0559 | 74.0559 | 48 | 9.6075 | 0 | 0 | 478.3726 | 0 | 74.0559 | 0 | 7.722 | 0 | 0 | 0 | 74.0559 | 0 | 0
10 | 18 | 16 | 0 | 1.3719 | 1.3719 | 48 | 10.9718 | 0 | 0 | 480.8007 | 0 | 1.3719 | 0 | 0.14305 | 0 | 0 | 0 | 1.3719 | 0 | 0
10 | 18 | 17 | 0 | 2.4284 | 2.4284 | 48 | 10.3786 | 0 | 0 | 470.7735 | 0 | 2.4284 | 0 | 0.25321 | 0 | 0 | 0 | 2.4284 | 0 | 0
10 | 18 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 472.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 453.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 436.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 420.1616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 404.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 18 | 23 | 0.1753 | 0 | 0.1753 | 11 | 4.2265 | 0.068263 | 0.068263 | 398.6501 | 0.1753 | 0 | 67.954 | 0 | 0 | 0 | 0.1753 | 0 | 0 | 67.954
10 | 19 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 398.2873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 398.2066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 406.5907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 435.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 469.7317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 481.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 484.0261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 7 | 0 | 0.675 | 0.675 | 48 | 4.6502 | 0.2854 | 0.2854 | 491.0676 | 0.675 | 0 | 299.0706 | 0 | 0 | 0 | 0.675 | 0 | 0 | 299.0706
10 | 19 | 8 | 0 | 3.6742 | 3.6742 | 48 | 5.1417 | 1.7251 | 1.7251 | 491.803 | 3.6742 | 0 | 1630.6061 | 0 | 0 | 0 | 3.6742 | 0 | 0 | 1630.6061
10 | 19 | 9 | 0 | 10.1024 | 10.1024 | 48 | 6.6161 | 7.0949 | 7.0949 | 490.7538 | 10.1024 | 0 | 4472.8595 | 0 | 0 | 0 | 10.1024 | 0 | 0 | 4472.8595
10 | 19 | 10 | 0 | 16.8577 | 16.8577 | 48 | 6.9721 | 13.4486 | 13.4486 | 498.7286 | 16.8577 | 0 | 7598.2662 | 0 | 0 | 0 | 16.8577 | 0 | 0 | 7598.2662
10 | 19 | 11 | 0.66917 | 180.8161 | 181.4853 | 47.8636 | 8.5652 | 369.7918 | 288 | 494.3329 | 141.3438 | 40.1415 | 63105.6486 | 4.1857 | 0 | 0 | 141.3438 | 40.1415 | 0 | 63105.6486
10 | 19 | 12 | 0.45417 | 74.9747 | 75.4289 | 47.7772 | 7.8957 | 92.9749 | 92.9749 | 496.5981 | 75.4289 | 0 | 33854.0533 | 0 | 0 | 0 | 75.4289 | 0 | 0 | 33854.0533
10 | 19 | 13 | 0 | 8.2485 | 8.2485 | 48 | 7.4381 | 8.0054 | 8.0054 | 493.1466 | 8.2485 | 0 | 3671.7701 | 0 | 0 | 0 | 8.2485 | 0 | 0 | 3671.7701
10 | 19 | 14 | 0 | 6.8268 | 6.8268 | 48 | 7.2771 | 6.1645 | 6.1645 | 499.5047 | 6.8268 | 0 | 3082.3476 | 0 | 0 | 0 | 6.8268 | 0 | 0 | 3082.3476
10 | 19 | 15 | 0 | 4.5258 | 4.5258 | 48 | 7.3449 | 4.2101 | 4.2101 | 489.4581 | 4.5258 | 0 | 1997.9428 | 0 | 0 | 0 | 4.5258 | 0 | 0 | 1997.9428
10 | 19 | 16 | 0 | 7.418 | 7.418 | 48 | 6.9975 | 5.9758 | 5.9758 | 490.036 | 7.418 | 0 | 3279.0044 | 0 | 0 | 0 | 7.418 | 0 | 0 | 3279.0044
10 | 19 | 17 | 0 | 2.1083 | 2.1083 | 48 | 7.167 | 1.8172 | 1.8172 | 481.8998 | 2.1083 | 0 | 914.8055 | 0 | 0 | 0 | 2.1083 | 0 | 0 | 914.8055
10 | 19 | 18 | 0 | 0.016667 | 0.016667 | 48 | 6.7094 | 0.012084 | 0.012084 | 478.8917 | 0.016667 | 0 | 7.1815 | 0 | 0 | 0 | 0.016667 | 0 | 0 | 7.1815
10 | 19 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 452.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 427.5579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 416.1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 408.6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 402.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 396.4064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 400.5063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 411.9891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 449.8217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 478.2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 477.2202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 477.9388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 7 | 0 | 0.54167 | 0.54167 | 48 | 6.1924 | 0.33298 | 0.33298 | 485.1321 | 0.54167 | 0 | 236.7799 | 0 | 0 | 0 | 0.54167 | 0 | 0 | 236.7799
10 | 20 | 8 | 0 | 86.3431 | 86.3431 | 48 | 6.8788 | 66.5137 | 66.5137 | 485.922 | 86.3431 | 0 | 37811.535 | 0 | 0 | 0 | 86.3431 | 0 | 0 | 37811.535
10 | 20 | 9 | 0.19167 | 212.6785 | 212.8701 | 47.9667 | 7.3195 | 195.804 | 195.804 | 487.1248 | 212.8701 | 0 | 93483.6579 | 0 | 0 | 0 | 212.8701 | 0 | 0 | 93483.6579
10 | 20 | 10 | 0 | 229.3666 | 229.3666 | 48 | 7.4805 | 227.0786 | 227.0786 | 486.377 | 229.3666 | 0 | 100549.0392 | 0 | 0 | 0 | 229.3666 | 0 | 0 | 100549.0392
10 | 20 | 11 | 0.595 | 334.4675 | 335.0625 | 47.9343 | 7.2263 | 296.0473 | 288 | 476.1685 | 325.9546 | 9.1079 | 139584.9197 | 0.9497 | 0 | 0 | 325.9546 | 9.1079 | 0 | 139584.9197
10 | 20 | 12 | 0 | 56.3145 | 56.3145 | 48 | 7.8703 | 68.3883 | 68.3883 | 479.1798 | 56.3145 | 0 | 24281.6773 | 0 | 0 | 0 | 56.3145 | 0 | 0 | 24281.6773
10 | 20 | 13 | 0 | 9.6349 | 9.6349 | 48 | 8.1754 | 14.2234 | 14.2234 | 479.3479 | 9.6349 | 0 | 4155.9934 | 0 | 0 | 0 | 9.6349 | 0 | 0 | 4155.9934
10 | 20 | 14 | 0 | 60.107 | 60.107 | 48 | 8.2431 | 93.1972 | 93.1972 | 477.2107 | 60.107 | 0 | 25798.5477 | 0 | 0 | 0 | 60.107 | 0 | 0 | 25798.5477
10 | 20 | 15 | 0 | 114.5126 | 114.5126 | 48 | 7.4212 | 110.27 | 110.27 | 480.0781 | 114.5126 | 0 | 49478.4002 | 0 | 0 | 0 | 114.5126 | 0 | 0 | 49478.4002
10 | 20 | 16 | 0 | 119.0929 | 119.0929 | 48 | 7.3195 | 109.545 | 109.545 | 477.7142 | 119.0929 | 0 | 51175.9049 | 0 | 0 | 0 | 119.0929 | 0 | 0 | 51175.9049
10 | 20 | 17 | 0 | 4.4469 | 4.4469 | 48 | 7.2686 | 4.0008 | 4.0008 | 465.1193 | 4.4469 | 0 | 1854.8727 | 0 | 0 | 0 | 4.4469 | 0 | 0 | 1854.8727
10 | 20 | 18 | 0 | 0.014167 | 0.014167 | 48 | 6.9297 | 0.011122 | 0.011122 | 454.7416 | 0.014167 | 0 | 5.7622 | 0 | 0 | 0 | 0.014167 | 0 | 0 | 5.7622
10 | 20 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 442.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 420.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 405.2971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 391.2846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 20 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 391.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 384.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 388.6864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 394.6199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 406.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 423.1696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 423.7189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 426.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 7 | 0 | 0.365 | 0.365 | 48 | 6.006 | 0.2127 | 0.2127 | 440.9638 | 0.365 | 0 | 143.4318 | 0 | 0 | 0 | 0.365 | 0 | 0 | 143.4318
10 | 21 | 8 | 0 | 4.2546 | 4.2546 | 48 | 6.6246 | 2.9965 | 2.9965 | 442.1978 | 4.2546 | 0 | 1677.1472 | 0 | 0 | 0 | 4.2546 | 0 | 0 | 1677.1472
10 | 21 | 9 | 0 | 38.0595 | 38.0595 | 48 | 7.1924 | 33.1525 | 33.1525 | 440.7837 | 38.0595 | 0 | 14949.1665 | 0 | 0 | 0 | 38.0595 | 0 | 0 | 14949.1665
10 | 21 | 10 | 0 | 108.0182 | 108.0182 | 48 | 7.0398 | 88.464 | 88.464 | 439.0082 | 108.0182 | 0 | 42236.01 | 0 | 0 | 0 | 108.0182 | 0 | 0 | 42236.01
10 | 21 | 11 | 0.071667 | 198.9787 | 199.0504 | 47.9867 | 7.2093 | 174.6208 | 174.6208 | 441.4118 | 199.0504 | 0 | 78311.4221 | 0 | 0 | 0 | 199.0504 | 0 | 0 | 78311.4221
10 | 21 | 12 | 0.12667 | 113.3829 | 113.5095 | 47.9587 | 7.9296 | 142.7696 | 142.7696 | 442.2221 | 113.5095 | 0 | 44752.6462 | 0 | 0 | 0 | 113.5095 | 0 | 0 | 44752.6462
10 | 21 | 13 | 0 | 8.7747 | 8.7747 | 48 | 8.2601 | 13.7787 | 13.7787 | 443.4319 | 8.7747 | 0 | 3469.782 | 0 | 0 | 0 | 8.7747 | 0 | 0 | 3469.782
10 | 21 | 14 | 0 | 26.4632 | 26.4632 | 48 | 8.5313 | 52.1951 | 52.1951 | 441.9886 | 26.4632 | 0 | 10426.1951 | 0 | 0 | 0 | 26.4632 | 0 | 0 | 10426.1951
10 | 21 | 15 | 0 | 9.6439 | 9.6439 | 48 | 8.4041 | 16.9829 | 16.9829 | 439.2727 | 9.6439 | 0 | 3773.4006 | 0 | 0 | 0 | 9.6439 | 0 | 0 | 3773.4006
10 | 21 | 16 | 0 | 13.4703 | 13.4703 | 48 | 9.1753 | 67.8021 | 67.8021 | 445.2316 | 13.4703 | 0 | 5350.8391 | 0 | 0 | 0 | 13.4703 | 0 | 0 | 5350.8391
10 | 21 | 17 | 0 | 2.0183 | 2.0183 | 48 | 8.6753 | 4.6077 | 4.6077 | 439.8469 | 2.0183 | 0 | 790.8776 | 0 | 0 | 0 | 2.0183 | 0 | 0 | 790.8776
10 | 21 | 18 | 0 | 0.019167 | 0.019167 | 48 | 9.0397 | 0.072716 | 0.072716 | 434.1137 | 0.019167 | 0 | 7.4005 | 0 | 0 | 0 | 0.019167 | 0 | 0 | 7.4005
10 | 21 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 412.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 401.0175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 381.1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 369.4866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 21 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 360.942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 354.3885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 353.1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 363.3726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 370.7813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 381.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 385.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 388.9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 7 | 0 | 0.51917 | 0.51917 | 48 | 4.8705 | 0.22976 | 0.22976 | 390.0918 | 0.51917 | 0 | 177.6026 | 0 | 0 | 0 | 0.51917 | 0 | 0 | 177.6026
10 | 22 | 8 | 0 | 10.8707 | 10.8707 | 48 | 4.8451 | 4.785 | 4.785 | 399.6877 | 10.8707 | 0 | 3823.0792 | 0 | 0 | 0 | 10.8707 | 0 | 0 | 3823.0792
10 | 22 | 9 | 0.10833 | 281.4217 | 281.5301 | 47.9858 | 6.3789 | 183.1103 | 183.1103 | 404.2718 | 281.5301 | 0 | 100305.2357 | 0 | 0 | 0 | 281.5301 | 0 | 0 | 100305.2357
10 | 22 | 10 | 0 | 78.1115 | 78.1115 | 48 | 8.4804 | 147.0065 | 147.0065 | 408.2855 | 78.1115 | 0 | 28142.4312 | 0 | 0 | 0 | 78.1115 | 0 | 0 | 28142.4312
10 | 22 | 11 | 0 | 10.6606 | 10.6606 | 48 | 9.4549 | 164.5429 | 164.5429 | 413.147 | 10.6606 | 0 | 3892.6977 | 0 | 0 | 0 | 10.6606 | 0 | 0 | 3892.6977
10 | 22 | 12 | 0 | 9.829 | 9.829 | 48 | 9.8362 | 0 | 0 | 418.8457 | 0 | 9.829 | 0 | 1.0249 | 0 | 0 | 0 | 9.829 | 0 | 0
10 | 22 | 13 | 0 | 16.0269 | 16.0269 | 48 | 9.6159 | 0 | 0 | 423.5889 | 0 | 16.0269 | 0 | 1.6712 | 0 | 0 | 0 | 16.0269 | 0 | 0
10 | 22 | 14 | 0 | 11.493 | 11.493 | 48 | 9.5227 | 355.4552 | 288 | 445.4068 | 9.312 | 2.181 | 3700.6342 | 0.22742 | 0 | 0 | 9.312 | 2.181 | 0 | 3700.6342
10 | 22 | 15 | 0 | 10.1307 | 10.1307 | 48 | 10.7175 | 0 | 0 | 440.1239 | 0 | 10.1307 | 0 | 1.0564 | 0 | 0 | 0 | 10.1307 | 0 | 0
10 | 22 | 16 | 0 | 9.0681 | 9.0681 | 48 | 12.0564 | 0 | 0 | 445.7021 | 0 | 9.0681 | 0 | 0.94556 | 0 | 0 | 0 | 9.0681 | 0 | 0
10 | 22 | 17 | 0 | 2.815 | 2.815 | 48 | 11.8107 | 0 | 0 | 440.6595 | 0 | 2.815 | 0 | 0.29353 | 0 | 0 | 0 | 2.815 | 0 | 0
10 | 22 | 18 | 0 | 0.029167 | 0.029167 | 48 | 12.3445 | 0 | 0 | 451.425 | 0 | 0.029167 | 0 | 0.0030413 | 0 | 0 | 0 | 0.029167 | 0 | 0
10 | 22 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 437.8651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 411.5334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 392.0134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 375.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 22 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 374.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 366.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 370.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 387.6865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 426.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 444.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 457.9653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 449.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 7 | 0 | 0.6602 | 0.6602 | 48 | 4.8281 | 0.28957 | 0.28957 | 452.0217 | 0.6602 | 0 | 266.7363 | 0 | 0 | 0 | 0.6602 | 0 | 0 | 266.7363
10 | 23 | 8 | 0 | 46.8275 | 46.8275 | 48 | 5.4976 | 23.8987 | 23.8987 | 451.2033 | 46.8275 | 0 | 18881.0174 | 0 | 0 | 0 | 46.8275 | 0 | 0 | 18881.0174
10 | 23 | 9 | 0 | 131.2692 | 131.2692 | 48 | 6.4043 | 86.0602 | 86.0602 | 455.8166 | 131.2692 | 0 | 53533.7627 | 0 | 0 | 0 | 131.2692 | 0 | 0 | 53533.7627
10 | 23 | 10 | 0.0125 | 230.7926 | 230.8051 | 47.998 | 8.5991 | 486.3674 | 288 | 449.7891 | 136.6701 | 94.135 | 54912.8235 | 9.8157 | 0 | 0 | 136.6701 | 94.135 | 0 | 54912.8235
10 | 23 | 11 | 0 | 163.8446 | 163.8446 | 48 | 9.6413 | 0 | 0 | 452.1622 | 0 | 163.8446 | 0 | 17.0845 | 0 | 0 | 0 | 163.8446 | 0 | 0
10 | 23 | 12 | 0 | 28.1912 | 28.1912 | 48 | 9.7176 | 0 | 0 | 446.0174 | 0 | 28.1912 | 0 | 2.9396 | 0 | 0 | 0 | 28.1912 | 0 | 0
10 | 23 | 13 | 0 | 25.4003 | 25.4003 | 48 | 9.7939 | 0 | 0 | 445.6284 | 0 | 25.4003 | 0 | 2.6486 | 0 | 0 | 0 | 25.4003 | 0 | 0
10 | 23 | 14 | 0 | 20.5524 | 20.5524 | 48 | 9.4634 | 338.4094 | 288 | 444.6817 | 17.4909 | 3.0615 | 6938.3259 | 0.31923 | 0 | 0 | 17.4909 | 3.0615 | 0 | 6938.3259
10 | 23 | 15 | 0 | 6.8667 | 6.8667 | 48 | 10.5311 | 0 | 0 | 446.3599 | 0 | 6.8667 | 0 | 0.71601 | 0 | 0 | 0 | 6.8667 | 0 | 0
10 | 23 | 16 | 0 | 4.824 | 4.824 | 48 | 11.0904 | 0 | 0 | 447.2295 | 0 | 4.824 | 0 | 0.50301 | 0 | 0 | 0 | 4.824 | 0 | 0
10 | 23 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 443.5435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 442.7741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 434.8015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 418.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 401.4597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 385.1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 23 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 378.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 372.3287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 373.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 393.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 428.492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 445.2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 446.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 447.5244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 445.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 8 | 0 | 10.1006 | 10.1006 | 48 | 6.2094 | 6.2402 | 6.2402 | 445.5434 | 10.1006 | 0 | 4015.4378 | 0 | 0 | 0 | 10.1006 | 0 | 0 | 4015.4378
10 | 24 | 9 | 0 | 22.1781 | 22.1781 | 48 | 7.328 | 20.4765 | 20.4765 | 451.9044 | 22.1781 | 0 | 8957.8461 | 0 | 0 | 0 | 22.1781 | 0 | 0 | 8957.8461
10 | 24 | 10 | 0.0083333 | 23.8024 | 23.8107 | 47.9871 | 8.5482 | 47.7273 | 47.7273 | 444.448 | 23.8107 | 0 | 9440.0291 | 0 | 0 | 0 | 23.8107 | 0 | 0 | 9440.0291
10 | 24 | 11 | 0 | 6.0121 | 6.0121 | 48 | 9.1838 | 30.8924 | 30.8924 | 448.529 | 6.0121 | 0 | 2408.0213 | 0 | 0 | 0 | 6.0121 | 0 | 0 | 2408.0213
10 | 24 | 12 | 0 | 3.7035 | 3.7035 | 48 | 9.8701 | 0 | 0 | 447.415 | 0 | 3.7035 | 0 | 0.38617 | 0 | 0 | 0 | 3.7035 | 0 | 0
10 | 24 | 13 | 0 | 1.2244 | 1.2244 | 48 | 9.6668 | 0 | 0 | 450.9582 | 0 | 1.2244 | 0 | 0.12767 | 0 | 0 | 0 | 1.2244 | 0 | 0
10 | 24 | 14 | 0 | 0.9127 | 0.9127 | 48 | 10.2684 | 0 | 0 | 447.9474 | 0 | 0.9127 | 0 | 0.09517 | 0 | 0 | 0 | 0.9127 | 0 | 0
10 | 24 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 439.5986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 16 | 0 | 0.3125 | 0.3125 | 48 | 11.853 | 0 | 0 | 438.0873 | 0 | 0.3125 | 0 | 0.032585 | 0 | 0 | 0 | 0.3125 | 0 | 0
10 | 24 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 440.6758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 452.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 444.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 427.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 404.3085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 388.4856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 24 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 381.8248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 383.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 387.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 405.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 431.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 451.5444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 469.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 463.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 464.3949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 8 | 0 | 0.022065 | 0.022065 | 48 | 6.2094 | 0.013632 | 0.013632 | 470.6847 | 0.022065 | 0 | 9.3267 | 0 | 0 | 0 | 0.022065 | 0 | 0 | 9.3267
10 | 25 | 9 | 0 | 1.3131 | 1.3131 | 48 | 7.311 | 1.2034 | 1.2034 | 472.9437 | 1.3131 | 0 | 558.007 | 0 | 0 | 0 | 1.3131 | 0 | 0 | 558.007
10 | 25 | 10 | 0 | 32.3403 | 32.3403 | 48 | 8.0567 | 44.0485 | 44.0485 | 473.7065 | 32.3403 | 0 | 13767.4812 | 0 | 0 | 0 | 32.3403 | 0 | 0 | 13767.4812
10 | 25 | 11 | 0 | 22.3112 | 22.3112 | 48 | 9.3109 | 166.8015 | 166.8015 | 477.4912 | 22.3112 | 0 | 9582.4496 | 0 | 0 | 0 | 22.3112 | 0 | 0 | 9582.4496
10 | 25 | 12 | 0 | 3.5951 | 3.5951 | 48 | 9.0058 | 12.8481 | 12.8481 | 474.0269 | 3.5951 | 0 | 1531.5898 | 0 | 0 | 0 | 3.5951 | 0 | 0 | 1531.5898
10 | 25 | 13 | 0 | 5.6897 | 5.6897 | 48 | 8.4889 | 10.7905 | 10.7905 | 477.8303 | 5.6897 | 0 | 2445.6237 | 0 | 0 | 0 | 5.6897 | 0 | 0 | 2445.6237
10 | 25 | 14 | 0 | 2.7112 | 2.7112 | 48 | 8.938 | 8.6824 | 8.6824 | 473.6609 | 2.7112 | 0 | 1154.0602 | 0 | 0 | 0 | 2.7112 | 0 | 0 | 1154.0602
10 | 25 | 15 | 0 | 2.4172 | 2.4172 | 48 | 9.6075 | 0 | 0 | 459.4513 | 0 | 2.4172 | 0 | 0.25205 | 0 | 0 | 0 | 2.4172 | 0 | 0
10 | 25 | 16 | 0 | 0.075178 | 0.075178 | 48 | 10.9718 | 0 | 0 | 467.4167 | 0 | 0.075178 | 0 | 0.007839 | 0 | 0 | 0 | 0.075178 | 0 | 0
10 | 25 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 469.9216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 479.3392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 474.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 454.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 449.9108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 431.6745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 25 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 422.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 420.7899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 424.0559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 439.1678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 449.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 448.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 462.309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 465.1632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 7 | 0 | 0.36083 | 0.36083 | 48 | 4.6502 | 0.15256 | 0.15256 | 472.0615 | 0.36083 | 0 | 153.0155 | 0 | 0 | 0 | 0.36083 | 0 | 0 | 153.0155
10 | 26 | 8 | 0.21333 | 92.5425 | 92.7558 | 47.9149 | 5.1417 | 43.5511 | 43.5511 | 469.9035 | 92.7558 | 0 | 39141.8929 | 0 | 0 | 0 | 92.7558 | 0 | 0 | 39141.8929
10 | 26 | 9 | 0 | 95.2069 | 95.2069 | 48 | 6.6161 | 66.8638 | 66.8638 | 462.9525 | 95.2069 | 0 | 39506.3586 | 0 | 0 | 0 | 95.2069 | 0 | 0 | 39506.3586
10 | 26 | 10 | 0 | 144.2043 | 144.2043 | 48 | 6.9721 | 115.0415 | 115.0415 | 461.2679 | 144.2043 | 0 | 59594.994 | 0 | 0 | 0 | 144.2043 | 0 | 0 | 59594.994
10 | 26 | 11 | 0 | 336.7335 | 336.7335 | 48 | 8.5652 | 686.1233 | 288 | 453.0299 | 141.3438 | 195.3897 | 57248.4539 | 20.3738 | 0 | 0 | 141.3438 | 195.3897 | 0 | 57248.4539
10 | 26 | 12 | 1.8758 | 344.8841 | 346.7599 | 47.7998 | 7.8957 | 427.4222 | 288 | 445.9576 | 233.6492 | 113.1107 | 93029.2244 | 11.7944 | 0 | 0 | 233.6492 | 113.1107 | 0 | 93029.2244
10 | 26 | 13 | 0 | 326.3874 | 326.3874 | 48 | 7.4381 | 316.7699 | 288 | 442.4249 | 296.744 | 29.6434 | 117043.2381 | 3.091 | 0 | 0 | 296.744 | 29.6434 | 0 | 117043.2381
10 | 26 | 14 | 0 | 239.3956 | 239.3956 | 48 | 7.2771 | 216.1694 | 216.1694 | 440.27 | 239.3956 | 0 | 93907.7261 | 0 | 0 | 0 | 239.3956 | 0 | 0 | 93907.7261
10 | 26 | 15 | 0 | 105.6608 | 105.6608 | 48 | 7.3449 | 98.2902 | 98.2902 | 432.1886 | 105.6608 | 0 | 40593.6641 | 0 | 0 | 0 | 105.6608 | 0 | 0 | 40593.6641
10 | 26 | 16 | 0 | 25.2367 | 25.2367 | 48 | 6.9975 | 20.3304 | 20.3304 | 446.7752 | 25.2367 | 0 | 10063.755 | 0 | 0 | 0 | 25.2367 | 0 | 0 | 10063.755
10 | 26 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 454.9759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 458.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 448.0353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 437.5883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 410.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 399.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 26 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 400.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 398.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 400.8447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 402.5764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 415.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 438.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 448.4012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 455.5642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 7 | 0 | 15.659 | 15.659 | 48 | 6.1924 | 9.626 | 9.626 | 453.8806 | 15.659 | 0 | 6355.6916 | 0 | 0 | 0 | 15.659 | 0 | 0 | 6355.6916
10 | 27 | 8 | 0 | 14.0642 | 14.0642 | 48 | 6.8788 | 10.8342 | 10.8342 | 458.0018 | 14.0642 | 0 | 5766.3324 | 0 | 0 | 0 | 14.0642 | 0 | 0 | 5766.3324
10 | 27 | 9 | 0 | 13.5477 | 13.5477 | 48 | 7.3195 | 12.4615 | 12.4615 | 453.1702 | 13.5477 | 0 | 5489.1074 | 0 | 0 | 0 | 13.5477 | 0 | 0 | 5489.1074
10 | 27 | 10 | 0 | 7.3053 | 7.3053 | 48 | 7.4805 | 7.2325 | 7.2325 | 452.2104 | 7.3053 | 0 | 2952.8985 | 0 | 0 | 0 | 7.3053 | 0 | 0 | 2952.8985
10 | 27 | 11 | 0 | 47.0016 | 47.0016 | 48 | 7.2263 | 41.5287 | 41.5287 | 452.1303 | 47.0016 | 0 | 18994.7642 | 0 | 0 | 0 | 47.0016 | 0 | 0 | 18994.7642
10 | 27 | 12 | 0 | 46.9897 | 46.9897 | 48 | 7.8703 | 57.0643 | 57.0643 | 451.6 | 46.9897 | 0 | 18965.0588 | 0 | 0 | 0 | 46.9897 | 0 | 0 | 18965.0588
10 | 27 | 13 | 0 | 6.937 | 6.937 | 48 | 8.1754 | 10.2407 | 10.2407 | 449.8456 | 6.937 | 0 | 2787.6102 | 0 | 0 | 0 | 6.937 | 0 | 0 | 2787.6102
10 | 27 | 14 | 0 | 4.2837 | 4.2837 | 48 | 8.2431 | 6.642 | 6.642 | 451.1367 | 4.2837 | 0 | 1726.9364 | 0 | 0 | 0 | 4.2837 | 0 | 0 | 1726.9364
10 | 27 | 15 | 0 | 40.105 | 40.105 | 48 | 7.4212 | 38.6191 | 38.6191 | 450.6449 | 40.105 | 0 | 16148.0812 | 0 | 0 | 0 | 40.105 | 0 | 0 | 16148.0812
10 | 27 | 16 | 0 | 2.4143 | 2.4143 | 48 | 7.3195 | 2.2208 | 2.2208 | 456.8831 | 2.4143 | 0 | 987.1831 | 0 | 0 | 0 | 2.4143 | 0 | 0 | 987.1831
10 | 27 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 454.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 457.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 445.1986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 436.3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 418.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 410.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 27 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 403.9702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 401.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 402.6128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 409.9052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 429.238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 442.2367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 449.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 451.5577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 7 | 0 | 6.8229 | 6.8229 | 48 | 6.006 | 3.9761 | 3.9761 | 454.0781 | 6.8229 | 0 | 2770.629 | 0 | 0 | 0 | 6.8229 | 0 | 0 | 2770.629
10 | 28 | 8 | 0 | 29.3921 | 29.3921 | 48 | 6.6246 | 20.7011 | 20.7011 | 454.7192 | 29.3921 | 0 | 11954.3266 | 0 | 0 | 0 | 29.3921 | 0 | 0 | 11954.3266
10 | 28 | 9 | 0 | 6.1352 | 6.1352 | 48 | 7.1924 | 5.3442 | 5.3442 | 455.376 | 6.1352 | 0 | 2499.3482 | 0 | 0 | 0 | 6.1352 | 0 | 0 | 2499.3482
10 | 28 | 10 | 0 | 7.6397 | 7.6397 | 48 | 7.0398 | 6.2567 | 6.2567 | 456.5078 | 7.6397 | 0 | 3120.8735 | 0 | 0 | 0 | 7.6397 | 0 | 0 | 3120.8735
10 | 28 | 11 | 0 | 4.3726 | 4.3726 | 48 | 7.2093 | 3.8359 | 3.8359 | 448.4073 | 4.3726 | 0 | 1750.8118 | 0 | 0 | 0 | 4.3726 | 0 | 0 | 1750.8118
10 | 28 | 12 | 0 | 3.3574 | 3.3574 | 48 | 7.9296 | 4.2228 | 4.2228 | 450.4549 | 3.3574 | 0 | 1351.1831 | 0 | 0 | 0 | 3.3574 | 0 | 0 | 1351.1831
10 | 28 | 13 | 0 | 6.128 | 6.128 | 48 | 8.2601 | 9.6227 | 9.6227 | 451.0007 | 6.128 | 0 | 2469.6041 | 0 | 0 | 0 | 6.128 | 0 | 0 | 2469.6041
10 | 28 | 14 | 0 | 8.0421 | 8.0421 | 48 | 8.5313 | 15.862 | 15.862 | 454.9069 | 8.0421 | 0 | 3272.3819 | 0 | 0 | 0 | 8.0421 | 0 | 0 | 3272.3819
10 | 28 | 15 | 0 | 98.552 | 98.552 | 48 | 8.4041 | 173.5497 | 173.5497 | 450.5091 | 98.552 | 0 | 39668.0807 | 0 | 0 | 0 | 98.552 | 0 | 0 | 39668.0807
10 | 28 | 16 | 0 | 2.1826 | 2.1826 | 48 | 9.1753 | 10.986 | 10.986 | 454.7631 | 2.1826 | 0 | 887.8007 | 0 | 0 | 0 | 2.1826 | 0 | 0 | 887.8007
10 | 28 | 17 | 0 | 0.31583 | 0.31583 | 48 | 8.6753 | 0.72102 | 0.72102 | 464.9393 | 0.31583 | 0 | 131.6833 | 0 | 0 | 0 | 0.31583 | 0 | 0 | 131.6833
10 | 28 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 476.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 473.1732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 470.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 454.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 443.8636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 28 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 439.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 435.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 433.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 435.1288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 442.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 446.305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 461.3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 472.2334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 478.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 8 | 0 | 0.54078 | 0.54078 | 48 | 4.8451 | 0.23804 | 0.23804 | 478.6596 | 0.54078 | 0 | 232.8918 | 0 | 0 | 0 | 0.54078 | 0 | 0 | 232.8918
10 | 29 | 9 | 0.0225 | 253.4426 | 253.4651 | 47.9967 | 6.3789 | 164.8565 | 164.8565 | 478.1951 | 253.4651 | 0 | 109040.249 | 0 | 0 | 0 | 253.4651 | 0 | 0 | 109040.249
10 | 29 | 10 | 0 | 7.2043 | 7.2043 | 48 | 8.4804 | 13.5586 | 13.5586 | 477.7785 | 7.2043 | 0 | 3096.2652 | 0 | 0 | 0 | 7.2043 | 0 | 0 | 3096.2652
10 | 29 | 11 | 0 | 1.0793 | 1.0793 | 48 | 9.4549 | 16.6593 | 16.6593 | 474.5677 | 1.0793 | 0 | 460.4145 | 0 | 0 | 0 | 1.0793 | 0 | 0 | 460.4145
10 | 29 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 471.2982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 469.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 464.6699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 15 | 0 | 2.5567 | 2.5567 | 48 | 10.7175 | 0 | 0 | 456.8986 | 0 | 2.5567 | 0 | 0.26659 | 0 | 0 | 0 | 2.5567 | 0 | 0
10 | 29 | 16 | 0 | 0.11417 | 0.11417 | 48 | 12.0564 | 0 | 0 | 455.0275 | 0 | 0.11417 | 0 | 0.011904 | 0 | 0 | 0 | 0.11417 | 0 | 0
10 | 29 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 462.3613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 459.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 19 | 0.4325 | 0 | 0.4325 | 11 | 12.2767 | 0 | 0 | 446.7762 | 0 | 0.4325 | 0 | 0.045098 | 0 | 0 | 0 | 0.4325 | 0 | 0
10 | 29 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 437.5416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 421.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 416.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 29 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 412.6669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 413.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 425.859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 434.5254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 432.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 449.6945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 452.3921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 455.4657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 7 | 0 | 6.0275 | 6.0275 | 48 | 4.8281 | 2.6437 | 2.6437 | 458.2498 | 6.0275 | 0 | 2472.7976 | 0 | 0 | 0 | 6.0275 | 0 | 0 | 2472.7976
10 | 30 | 8 | 0 | 5.9217 | 5.9217 | 48 | 5.4976 | 3.0222 | 3.0222 | 459.0065 | 5.9217 | 0 | 2433.8448 | 0 | 0 | 0 | 5.9217 | 0 | 0 | 2433.8448
10 | 30 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 458.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 10 | 0 | 1.3947 | 1.3947 | 48 | 8.5991 | 2.939 | 2.939 | 454.0432 | 1.3947 | 0 | 566.3117 | 0 | 0 | 0 | 1.3947 | 0 | 0 | 566.3117
10 | 30 | 11 | 0.17 | 14.187 | 14.357 | 47.5619 | 9.6413 | 0 | 0 | 449.5136 | 0 | 14.357 | 0 | 1.497 | 0 | 0 | 0 | 14.357 | 0 | 0
10 | 30 | 12 | 0 | 69.1415 | 69.1415 | 48 | 9.7176 | 0 | 0 | 443.2369 | 0 | 69.1415 | 0 | 7.2096 | 0 | 0 | 0 | 69.1415 | 0 | 0
10 | 30 | 13 | 0 | 32.2599 | 32.2599 | 48 | 9.7939 | 0 | 0 | 443.7535 | 0 | 32.2599 | 0 | 3.3638 | 0 | 0 | 0 | 32.2599 | 0 | 0
10 | 30 | 14 | 0 | 83.5344 | 83.5344 | 48 | 9.4634 | 1375.4522 | 288 | 440.3057 | 17.4909 | 66.0435 | 6861.7866 | 6.8865 | 0 | 0 | 17.4909 | 66.0435 | 0 | 6861.7866
10 | 30 | 15 | 0 | 92.6133 | 92.6133 | 48 | 10.5311 | 0 | 0 | 430.1975 | 0 | 92.6133 | 0 | 9.657 | 0 | 0 | 0 | 92.6133 | 0 | 0
10 | 30 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 440.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 443.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 462.7231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 448.8479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 431.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 415.9705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 401.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 30 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 402.1469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 396.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 397.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 419.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 424.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 447.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 455.3671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 461.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 458.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 467.8564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 9 | 0 | 0.99072 | 0.99072 | 48 | 7.328 | 0.9147 | 0.9147 | 471.8969 | 0.99072 | 0 | 419.9621 | 0 | 0 | 0 | 0.99072 | 0 | 0 | 419.9621
10 | 31 | 10 | 0 | 48.579 | 48.579 | 48 | 8.5482 | 97.374 | 97.374 | 476.6396 | 48.579 | 0 | 20822.8811 | 0 | 0 | 0 | 48.579 | 0 | 0 | 20822.8811
10 | 31 | 11 | 0.3475 | 13.3421 | 13.6896 | 47.0608 | 9.1838 | 70.3421 | 70.3421 | 478.565 | 13.6896 | 0 | 5907.1092 | 0 | 0 | 0 | 13.6896 | 0 | 0 | 5907.1092
10 | 31 | 12 | 0 | 2.5403 | 2.5403 | 48 | 9.8701 | 0 | 0 | 479.4161 | 0 | 2.5403 | 0 | 0.26488 | 0 | 0 | 0 | 2.5403 | 0 | 0
10 | 31 | 13 | 0.6 | 63.4769 | 64.0769 | 47.6535 | 9.6668 | 0 | 0 | 483.0058 | 0 | 64.0769 | 0 | 6.6815 | 0 | 0 | 0 | 64.0769 | 0 | 0
10 | 31 | 14 | 0 | 4.9349 | 4.9349 | 48 | 10.2684 | 0 | 0 | 486.2894 | 0 | 4.9349 | 0 | 0.51457 | 0 | 0 | 0 | 4.9349 | 0 | 0
10 | 31 | 15 | 0 | 8.33 | 8.33 | 48 | 11.226 | 0 | 0 | 473.9532 | 0 | 8.33 | 0 | 0.86859 | 0 | 0 | 0 | 8.33 | 0 | 0
10 | 31 | 16 | 0 | 0.099999 | 0.099999 | 48 | 11.853 | 0 | 0 | 477.6478 | 0 | 0.099999 | 0 | 0.010427 | 0 | 0 | 0 | 0.099999 | 0 | 0
10 | 31 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 480.9353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 485.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 485.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 482.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 469.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 453.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 31 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 447.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 442.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 440.9148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 449.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 452.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 460.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 472.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 480.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 481.3827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 480.1607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 9 | 0 | 12.9025 | 12.9025 | 48 | 7.311 | 11.824 | 11.824 | 482.135 | 12.9025 | 0 | 5601.4267 | 0 | 0 | 0 | 12.9025 | 0 | 0 | 5601.4267
11 | 1 | 10 | 0.0575 | 22.1787 | 22.2362 | 47.9043 | 8.0567 | 30.2864 | 30.2864 | 483.7523 | 22.2362 | 0 | 9691.6032 | 0 | 0 | 0 | 22.2362 | 0 | 0 | 9691.6032
11 | 1 | 11 | 0.048333 | 10.8083 | 10.8567 | 47.8353 | 9.3109 | 81.166 | 81.166 | 483.2458 | 10.8567 | 0 | 4727.1065 | 0 | 0 | 0 | 10.8567 | 0 | 0 | 4727.1065
11 | 1 | 12 | 0.1425 | 59.2974 | 59.4399 | 47.9113 | 9.0058 | 212.4282 | 212.4282 | 481.5809 | 59.4399 | 0 | 25777.2717 | 0 | 0 | 0 | 59.4399 | 0 | 0 | 25777.2717
11 | 1 | 13 | 0 | 17.5627 | 17.5627 | 48 | 8.4889 | 33.3076 | 33.3076 | 484.7276 | 17.5627 | 0 | 7670.137 | 0 | 0 | 0 | 17.5627 | 0 | 0 | 7670.137
11 | 1 | 14 | 0 | 4.9325 | 4.9325 | 48 | 8.938 | 15.7957 | 15.7957 | 478.8625 | 4.9325 | 0 | 2125.2291 | 0 | 0 | 0 | 4.9325 | 0 | 0 | 2125.2291
11 | 1 | 15 | 0 | 7.9183 | 7.9183 | 48 | 9.6075 | 0 | 0 | 472.1671 | 0 | 7.9183 | 0 | 0.82567 | 0 | 0 | 0 | 7.9183 | 0 | 0
11 | 1 | 16 | 0 | 0.10417 | 0.10417 | 48 | 10.9718 | 0 | 0 | 474.4004 | 0 | 0.10417 | 0 | 0.010862 | 0 | 0 | 0 | 0.10417 | 0 | 0
11 | 1 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 470.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 474.9597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 461.2417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 446.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 422.8951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 397.5083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 391.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 386.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 396.1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 416.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 448.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 469.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 469.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 468.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 474.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 8 | 0 | 10.2229 | 10.2229 | 48 | 5.1417 | 4.7999 | 4.7999 | 474.272 | 10.2229 | 0 | 4357.7415 | 0 | 0 | 0 | 10.2229 | 0 | 0 | 4357.7415
11 | 2 | 9 | 0 | 147.7199 | 147.7199 | 48 | 6.6161 | 103.7437 | 103.7437 | 478.1048 | 147.7199 | 0 | 63535.0494 | 0 | 0 | 0 | 147.7199 | 0 | 0 | 63535.0494
11 | 2 | 10 | 0 | 188.5121 | 188.5121 | 48 | 6.9721 | 150.3888 | 150.3888 | 475.0709 | 188.5121 | 0 | 80508.0135 | 0 | 0 | 0 | 188.5121 | 0 | 0 | 80508.0135
11 | 2 | 11 | 0 | 66.2645 | 66.2645 | 48 | 8.5652 | 135.0197 | 135.0197 | 479.6409 | 66.2645 | 0 | 28602.4828 | 0 | 0 | 0 | 66.2645 | 0 | 0 | 28602.4828
11 | 2 | 12 | 0 | 6.6933 | 6.6933 | 48 | 7.8957 | 8.2503 | 8.2503 | 484.7439 | 6.6933 | 0 | 2923.2567 | 0 | 0 | 0 | 6.6933 | 0 | 0 | 2923.2567
11 | 2 | 13 | 0 | 94.3271 | 94.3271 | 48 | 7.4381 | 91.5476 | 91.5476 | 485.7231 | 94.3271 | 0 | 41289.1418 | 0 | 0 | 0 | 94.3271 | 0 | 0 | 41289.1418
11 | 2 | 14 | 0 | 246.2449 | 246.2449 | 48 | 7.2771 | 222.3541 | 222.3541 | 474.5257 | 246.2449 | 0 | 105029.7495 | 0 | 0 | 0 | 246.2449 | 0 | 0 | 105029.7495
11 | 2 | 15 | 0 | 267.6013 | 267.6013 | 48 | 7.3449 | 248.9341 | 248.9341 | 462.4874 | 267.6013 | 0 | 110917.3763 | 0 | 0 | 0 | 267.6013 | 0 | 0 | 110917.3763
11 | 2 | 16 | 0 | 35.7622 | 35.7622 | 48 | 6.9975 | 28.8097 | 28.8097 | 474.4968 | 35.7622 | 0 | 15252.4661 | 0 | 0 | 0 | 35.7622 | 0 | 0 | 15252.4661
11 | 2 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 476.3464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 474.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 454.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 430.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 418.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 402.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 400.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 394.2369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 393.5864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 404.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 426.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 447.9796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 460.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 451.8894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 455.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 455.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 461.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 10 | 0 | 34.9955 | 34.9955 | 48 | 7.4805 | 34.6464 | 34.6464 | 467.7034 | 34.9955 | 0 | 14687.7337 | 0 | 0 | 0 | 34.9955 | 0 | 0 | 14687.7337
11 | 3 | 11 | 0 | 59.1532 | 59.1532 | 48 | 7.2263 | 52.2654 | 52.2654 | 464.9708 | 59.1532 | 0 | 24665.1707 | 0 | 0 | 0 | 59.1532 | 0 | 0 | 24665.1707
11 | 3 | 12 | 0 | 63.1034 | 63.1034 | 48 | 7.8703 | 76.6327 | 76.6327 | 468.9885 | 63.1034 | 0 | 26565.7974 | 0 | 0 | 0 | 63.1034 | 0 | 0 | 26565.7974
11 | 3 | 13 | 0 | 4.3294 | 4.3294 | 48 | 8.1754 | 6.3912 | 6.3912 | 472.3549 | 4.3294 | 0 | 1837.1998 | 0 | 0 | 0 | 4.3294 | 0 | 0 | 1837.1998
11 | 3 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 468.3521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 15 | 0 | 0 | 0 | 0 | 7.4212 | 0 | 0 | 468.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 16 | 0 | 0.10917 | 0.10917 | 48 | 7.3195 | 0.10041 | 0.10041 | 460.9064 | 0.10917 | 0 | 45.0754 | 0 | 0 | 0 | 0.10917 | 0 | 0 | 45.0754
11 | 3 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 457.9537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 460.2086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 445.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 430.9271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 411.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 403.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 3 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 394.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 385.7692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 383.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 385.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 389.6075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 400.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 423.8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 439.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 449.7831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 460.4806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 457.7737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 10 | 0 | 0.41083 | 0.41083 | 48 | 7.0398 | 0.33646 | 0.33646 | 458.2059 | 0.41083 | 0 | 168.5263 | 0 | 0 | 0 | 0.41083 | 0 | 0 | 168.5263
11 | 4 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 458.153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 12 | 0 | 2.0289 | 2.0289 | 48 | 7.9296 | 2.5519 | 2.5519 | 460.3178 | 2.0289 | 0 | 836.5554 | 0 | 0 | 0 | 2.0289 | 0 | 0 | 836.5554
11 | 4 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 465.0355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 14 | 0.31667 | 60.7758 | 61.0924 | 47.8082 | 8.5313 | 120.4967 | 120.4967 | 468.3656 | 61.0924 | 0 | 25692.8718 | 0 | 0 | 0 | 61.0924 | 0 | 0 | 25692.8718
11 | 4 | 15 | 0 | 1.0858 | 1.0858 | 48 | 8.4041 | 1.9121 | 1.9121 | 448.2139 | 1.0858 | 0 | 434.5655 | 0 | 0 | 0 | 1.0858 | 0 | 0 | 434.5655
11 | 4 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 465.0799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 469.5339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 469.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 462.8912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 442.3253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 417.3416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 398.3724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 4 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 395.6489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 390.4202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 391.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 2 | 2.7992 | 0 | 2.7992 | 11 | 2.8791 | 0.87119 | 0.87119 | 396.0974 | 2.7992 | 0 | 1077.9517 | 0 | 0 | 0 | 2.7992 | 0 | 0 | 1077.9517
11 | 5 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 401.4577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 397.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 415.7352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 423.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 435.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 438.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 449.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 10 | 0 | 4.7058 | 4.7058 | 48 | 8.4804 | 8.8564 | 8.8564 | 453.4882 | 4.7058 | 0 | 1908.16 | 0 | 0 | 0 | 4.7058 | 0 | 0 | 1908.16
11 | 5 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 451.7126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 12 | 0 | 13.8934 | 13.8934 | 48 | 9.8362 | 0 | 0 | 450.3656 | 0 | 13.8934 | 0 | 1.4487 | 0 | 0 | 0 | 13.8934 | 0 | 0
11 | 5 | 13 | 0 | 20.7471 | 20.7471 | 48 | 9.6159 | 0 | 0 | 450.2814 | 0 | 20.7471 | 0 | 2.1634 | 0 | 0 | 0 | 20.7471 | 0 | 0
11 | 5 | 14 | 0 | 42.6259 | 42.6259 | 48 | 9.5227 | 1318.3339 | 288 | 464.5894 | 9.312 | 33.314 | 3879.2615 | 3.4737 | 0 | 0 | 9.312 | 33.314 | 0 | 3879.2615
11 | 5 | 15 | 0 | 3.6608 | 3.6608 | 48 | 10.7175 | 0 | 0 | 460.9188 | 0 | 3.6608 | 0 | 0.38172 | 0 | 0 | 0 | 3.6608 | 0 | 0
11 | 5 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 457.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 459.9534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 446.4674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 431.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 409.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 399.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 401.245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 5 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 392.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 392.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 397.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 412.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 444.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 476.3063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 473.4659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 473.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 476.614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 481.6508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 9 | 0 | 1.878 | 1.878 | 48 | 6.4043 | 1.2312 | 1.2312 | 480.9714 | 1.878 | 0 | 813.117 | 0 | 0 | 0 | 1.878 | 0 | 0 | 813.117
11 | 6 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 473.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 473.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 471.2561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 469.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 14 | 0 | 14.6489 | 14.6489 | 48 | 9.4634 | 241.2046 | 241.2046 | 465.761 | 14.6489 | 0 | 6119.7482 | 0 | 0 | 0 | 14.6489 | 0 | 0 | 6119.7482
11 | 6 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 471.7625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 471.9123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 469.9604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 479.2494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 467.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 454.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 435.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 416.7391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 6 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 412.9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 412.2787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 417.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 425.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 447.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 462.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 468.1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 474.112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 471.9353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 473.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 482.4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 10 | 0 | 0 | 0 | 0 | 8.5482 | 0 | 0 | 489.3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 11 | 0 | 0 | 0 | 0 | 9.1838 | 0 | 0 | 491.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 492.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 485.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 14 | 0 | 0.0049996 | 0.0049996 | 48 | 10.2684 | 0 | 0 | 483.015 | 0 | 0.0049996 | 0 | 0.00052132 | 0 | 0 | 0 | 0.0049996 | 0 | 0
11 | 7 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 481.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 480.8728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 488.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 491.0402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 493.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 493.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 488.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 480.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 470.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 468.117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 474.7356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 485.7794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 491.8616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 493.6986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 494.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 501.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 501.5378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 503.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 504.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 505.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 11 | 0 | 0 | 0 | 0 | 9.3109 | 0 | 0 | 504.4066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 12 | 0.0025 | 34.8671 | 34.8696 | 47.9973 | 9.0058 | 124.618 | 124.618 | 504.4018 | 34.8696 | 0 | 15914.6305 | 0 | 0 | 0 | 34.8696 | 0 | 0 | 15914.6305
11 | 8 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 498.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 14 | 0.0033333 | 1.1975 | 1.2008 | 47.8973 | 8.938 | 3.8455 | 3.8455 | 489.72 | 1.2008 | 0 | 530.5554 | 0 | 0 | 0 | 1.2008 | 0 | 0 | 530.5554
11 | 8 | 15 | 0 | 0.0058312 | 0.0058312 | 48 | 9.6075 | 0 | 0 | 494.5457 | 0 | 0.0058312 | 0 | 0.00060804 | 0 | 0 | 0 | 0.0058312 | 0 | 0
11 | 8 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 495.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 503.7741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 509.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 506.4736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 501.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 494.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 483.233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 8 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 471.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 469.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 468.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 476.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 470.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 473.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 471.0269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 483.3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 488.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 481.2604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 476.2546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 10 | 0.30833 | 100.8053 | 101.1136 | 47.8872 | 6.9721 | 80.6652 | 80.6652 | 481.335 | 101.1136 | 0 | 43827.4816 | 0 | 0 | 0 | 101.1136 | 0 | 0 | 43827.4816
11 | 9 | 11 | 0.67833 | 59.2471 | 59.9255 | 47.5812 | 8.5652 | 122.1033 | 122.1033 | 472.8123 | 59.9255 | 0 | 25482.1802 | 0 | 0 | 0 | 59.9255 | 0 | 0 | 25482.1802
11 | 9 | 12 | 0.9525 | 164.2679 | 165.2204 | 47.7867 | 7.8957 | 203.6535 | 203.6535 | 467.8652 | 165.2204 | 0 | 69405.5558 | 0 | 0 | 0 | 165.2204 | 0 | 0 | 69405.5558
11 | 9 | 13 | 0.5625 | 97.4897 | 98.0522 | 47.7877 | 7.4381 | 95.1629 | 95.1629 | 466.3194 | 98.0522 | 0 | 41037.9393 | 0 | 0 | 0 | 98.0522 | 0 | 0 | 41037.9393
11 | 9 | 14 | 0.785 | 155.1438 | 155.9288 | 47.8137 | 7.2771 | 140.8005 | 140.8005 | 459.5333 | 155.9288 | 0 | 64198.9275 | 0 | 0 | 0 | 155.9288 | 0 | 0 | 64198.9275
11 | 9 | 15 | 0 | 0.2025 | 0.2025 | 48 | 7.3449 | 0.18837 | 0.18837 | 474.5958 | 0.2025 | 0 | 86.3842 | 0 | 0 | 0 | 0.2025 | 0 | 0 | 86.3842
11 | 9 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 476.8869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 476.8492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 474.6393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 472.4403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 461.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 448.7916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 447.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 9 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 447.7937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 449.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 455.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 462.4267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 479.2798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 484.4911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 488.0935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 489.2545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 7 | 0 | 2.8333 | 2.8333 | 48 | 6.1924 | 1.7417 | 1.7417 | 492.4542 | 2.8333 | 0 | 1259.2871 | 0 | 0 | 0 | 2.8333 | 0 | 0 | 1259.2871
11 | 10 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 494.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 9 | 1.1208 | 182.3327 | 183.4535 | 47.7739 | 7.3195 | 168.7457 | 168.7457 | 496.5446 | 183.4535 | 0 | 82328.5565 | 0 | 0 | 0 | 183.4535 | 0 | 0 | 82328.5565
11 | 10 | 10 | 0.9325 | 115.806 | 116.7385 | 47.7044 | 7.4805 | 115.5739 | 115.5739 | 493.7018 | 116.7385 | 0 | 52065.0499 | 0 | 0 | 0 | 116.7385 | 0 | 0 | 52065.0499
11 | 10 | 11 | 0.32417 | 31.6129 | 31.9371 | 47.6244 | 7.2263 | 28.2183 | 28.2183 | 496.5599 | 31.9371 | 0 | 14337.6753 | 0 | 0 | 0 | 31.9371 | 0 | 0 | 14337.6753
11 | 10 | 12 | 1.4917 | 200.349 | 201.8406 | 47.7266 | 7.8703 | 245.115 | 245.115 | 496.0116 | 201.8406 | 0 | 90482.146 | 0 | 0 | 0 | 201.8406 | 0 | 0 | 90482.146
11 | 10 | 13 | 1.08 | 200.4683 | 201.5483 | 47.8017 | 8.1754 | 297.5321 | 288 | 491.102 | 195.0912 | 6.457 | 86483.9845 | 0.67329 | 0 | 0 | 195.0912 | 6.457 | 0 | 86483.9845
11 | 10 | 14 | 0.57667 | 25.5391 | 26.1158 | 47.183 | 8.2431 | 40.4931 | 40.4931 | 485.4641 | 26.1158 | 0 | 11446.051 | 0 | 0 | 0 | 26.1158 | 0 | 0 | 11446.051
11 | 10 | 15 | 0.14167 | 12.3272 | 12.4689 | 47.5796 | 7.4212 | 12.0069 | 12.0069 | 500.7347 | 12.4689 | 0 | 5650.3264 | 0 | 0 | 0 | 12.4689 | 0 | 0 | 5650.3264
11 | 10 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 490.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 17 | 0.18167 | 0 | 0.18167 | 11 | 7.2686 | 0.16344 | 0.16344 | 498.5393 | 0.18167 | 0 | 88.5696 | 0 | 0 | 0 | 0.18167 | 0 | 0 | 88.5696
11 | 10 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 508.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 508.7384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 514.0936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 509.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 504.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 10 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 498.1866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 494.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 495.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 501.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 498.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 495.4556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 492.6477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 495.9801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 7 | 0.029167 | 64.454 | 64.4832 | 47.9833 | 6.006 | 37.5776 | 37.5776 | 508.9706 | 64.4832 | 0 | 29725.9188 | 0 | 0 | 0 | 64.4832 | 0 | 0 | 29725.9188
11 | 11 | 8 | 0.0775 | 238.78 | 238.8575 | 47.988 | 6.6246 | 168.229 | 168.229 | 505.8038 | 238.8575 | 0 | 109352.7436 | 0 | 0 | 0 | 238.8575 | 0 | 0 | 109352.7436
11 | 11 | 9 | 0.044167 | 468.9244 | 468.9685 | 47.9965 | 7.1924 | 408.5039 | 288 | 507.6467 | 330.6283 | 138.3402 | 151973.3674 | 14.4251 | 0 | 0 | 330.6283 | 138.3402 | 0 | 151973.3674
11 | 11 | 10 | 0.086667 | 432.4321 | 432.5188 | 47.9926 | 7.0398 | 354.2212 | 288 | 506.7111 | 351.6599 | 80.8588 | 161312.9002 | 8.4314 | 0 | 0 | 351.6599 | 80.8588 | 0 | 161312.9002
11 | 11 | 11 | 0.3475 | 854.7334 | 855.0809 | 47.985 | 7.2093 | 750.1362 | 288 | 507.4606 | 328.2914 | 526.7894 | 150841.9119 | 54.9297 | 0 | 0 | 328.2914 | 526.7894 | 0 | 150841.9119
11 | 11 | 12 | 0.69 | 862.0661 | 862.7561 | 47.9704 | 7.9296 | 1085.1543 | 288 | 508.088 | 228.9755 | 633.7806 | 105355.6455 | 66.086 | 0 | 0 | 228.9755 | 633.7806 | 0 | 105355.6455
11 | 11 | 13 | 0 | 347.8643 | 347.8643 | 48 | 8.2601 | 546.2438 | 288 | 510.1003 | 183.407 | 164.4574 | 84752.417 | 17.1484 | 0 | 0 | 183.407 | 164.4574 | 0 | 84752.417
11 | 11 | 14 | 0 | 296.755 | 296.755 | 48 | 8.5313 | 585.3097 | 288 | 502.7667 | 146.0175 | 150.7375 | 66403.8714 | 15.7178 | 0 | 0 | 146.0175 | 150.7375 | 0 | 66403.8714
11 | 11 | 15 | 0 | 3.6889 | 3.6889 | 48 | 8.4041 | 6.4961 | 6.4961 | 507.4481 | 3.6889 | 0 | 1694.8377 | 0 | 0 | 0 | 3.6889 | 0 | 0 | 1694.8377
11 | 11 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 503.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 504.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 507.8996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 507.7163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 505.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 504.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 498.1539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 11 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 498.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 494.8126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 496.9326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 498.205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 501.4831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 499.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 502.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 501.9709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 7 | 0 | 3.8962 | 3.8962 | 48 | 4.8705 | 1.7243 | 1.7243 | 497.2402 | 3.8962 | 0 | 1750.3275 | 0 | 0 | 0 | 3.8962 | 0 | 0 | 1750.3275
11 | 12 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 499.5927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 497.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 494.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 493.4377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 12 | 0 | 0.32833 | 0.32833 | 48 | 9.8362 | 0 | 0 | 499.7401 | 0 | 0.32833 | 0 | 0.034236 | 0 | 0 | 0 | 0.32833 | 0 | 0
11 | 12 | 13 | 0 | 0.58083 | 0.58083 | 48 | 9.6159 | 0 | 0 | 497.712 | 0 | 0.58083 | 0 | 0.060565 | 0 | 0 | 0 | 0.58083 | 0 | 0
11 | 12 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 493.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 503.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 501.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 501.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 500.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 501.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 490.365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 479.146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 472.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 12 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 467.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 464.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 475.6554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 486.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 489.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 494.4428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 492.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 494.9141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 496.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 506.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 508.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 509.3212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 503.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 502.5975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 502.1161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 14 | 0 | 0.77128 | 0.77128 | 48 | 9.4634 | 12.6997 | 12.6997 | 492.1829 | 0.77128 | 0 | 342.5902 | 0 | 0 | 0 | 0.77128 | 0 | 0 | 342.5902
11 | 13 | 15 | 0 | 0.086666 | 0.086666 | 48 | 10.5311 | 0 | 0 | 491.1997 | 0 | 0.086666 | 0 | 0.0090369 | 0 | 0 | 0 | 0.086666 | 0 | 0
11 | 13 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 488.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 495.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 502.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 492.7264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 486.7069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 473.9439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 461.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 13 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 456.3098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 458.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 461.8625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 467.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 473.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 473.5641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 472.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 476.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 480.7676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 8 | 0.024167 | 19.9246 | 19.9488 | 47.9552 | 6.2094 | 12.3245 | 12.3245 | 475.3832 | 19.9488 | 0 | 8526.6601 | 0 | 0 | 0 | 19.9488 | 0 | 0 | 8526.6601
11 | 14 | 9 | 0.068333 | 32.9456 | 33.014 | 47.9234 | 7.328 | 30.4809 | 30.4809 | 474.9367 | 33.014 | 0 | 14097.3998 | 0 | 0 | 0 | 33.014 | 0 | 0 | 14097.3998
11 | 14 | 10 | 0 | 13.092 | 13.092 | 48 | 8.5482 | 26.2422 | 26.2422 | 477.3319 | 13.092 | 0 | 5620.8056 | 0 | 0 | 0 | 13.092 | 0 | 0 | 5620.8056
11 | 14 | 11 | 0 | 4.8117 | 4.8117 | 48 | 9.1838 | 24.7241 | 24.7241 | 478.3793 | 4.8117 | 0 | 2070.8411 | 0 | 0 | 0 | 4.8117 | 0 | 0 | 2070.8411
11 | 14 | 12 | 0.054167 | 30.565 | 30.6191 | 47.9345 | 9.8701 | 0 | 0 | 476.9191 | 0 | 30.6191 | 0 | 3.1927 | 0 | 0 | 0 | 30.6191 | 0 | 0
11 | 14 | 13 | 0.036667 | 18.7912 | 18.8279 | 47.9279 | 9.6668 | 0 | 0 | 473.3823 | 0 | 18.8279 | 0 | 1.9632 | 0 | 0 | 0 | 18.8279 | 0 | 0
11 | 14 | 14 | 0.13083 | 44.187 | 44.3179 | 47.8908 | 10.2684 | 0 | 0 | 467.5295 | 0 | 44.3179 | 0 | 4.6211 | 0 | 0 | 0 | 44.3179 | 0 | 0
11 | 14 | 15 | 0 | 0.57083 | 0.57083 | 48 | 11.226 | 0 | 0 | 476.6262 | 0 | 0.57083 | 0 | 0.059522 | 0 | 0 | 0 | 0.57083 | 0 | 0
11 | 14 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 477.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 478.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 474.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 469.8005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 465.0362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 461.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 455.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 453.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 458.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 461.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 462.2044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 454.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 459.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 467.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 468.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 460.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 8 | 0 | 8.6379 | 8.6379 | 48 | 6.2094 | 5.3365 | 5.3365 | 458.7373 | 8.6379 | 0 | 3547.9036 | 0 | 0 | 0 | 8.6379 | 0 | 0 | 3547.9036
11 | 15 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 460.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 463.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 11 | 0 | 1.1558 | 1.1558 | 48 | 9.3109 | 8.6412 | 8.6412 | 455.0508 | 1.1558 | 0 | 470.482 | 0 | 0 | 0 | 1.1558 | 0 | 0 | 470.482
11 | 15 | 12 | 0 | 77.8217 | 77.8217 | 48 | 9.0058 | 278.1216 | 278.1216 | 454.0558 | 77.8217 | 0 | 31599.9411 | 0 | 0 | 0 | 77.8217 | 0 | 0 | 31599.9411
11 | 15 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 454.1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 14 | 0 | 0.024997 | 0.024997 | 48 | 8.938 | 0.080049 | 0.080049 | 453.7859 | 0.024997 | 0 | 10.1433 | 0 | 0 | 0 | 0.024997 | 0 | 0 | 10.1433
11 | 15 | 15 | 0 | 1.2858 | 1.2858 | 48 | 9.6075 | 0 | 0 | 462.6733 | 0 | 1.2858 | 0 | 0.13408 | 0 | 0 | 0 | 1.2858 | 0 | 0
11 | 15 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 461.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 459.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 456.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 442.3568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 431.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 424.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 415.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 15 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 408.5331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 412.9547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 417.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 417.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 429.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 457.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 459.728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 471.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 7 | 0 | 9.4442 | 9.4442 | 48 | 4.6502 | 3.9931 | 3.9931 | 474.3338 | 9.4442 | 0 | 4026.3671 | 0 | 0 | 0 | 9.4442 | 0 | 0 | 4026.3671
11 | 16 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 478.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 9 | 0 | 5.9537 | 5.9537 | 48 | 6.6161 | 4.1813 | 4.1813 | 481.2747 | 5.9537 | 0 | 2579.5679 | 0 | 0 | 0 | 5.9537 | 0 | 0 | 2579.5679
11 | 16 | 10 | 0 | 19.9379 | 19.9379 | 48 | 6.9721 | 15.9058 | 15.9058 | 480.0563 | 19.9379 | 0 | 8614.2841 | 0 | 0 | 0 | 19.9379 | 0 | 0 | 8614.2841
11 | 16 | 11 | 0 | 50.0667 | 50.0667 | 48 | 8.5652 | 102.0151 | 102.0151 | 481.4084 | 50.0667 | 0 | 21699.3105 | 0 | 0 | 0 | 50.0667 | 0 | 0 | 21699.3105
11 | 16 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 479.6895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 13 | 0.013333 | 0.615 | 0.62833 | 47.2149 | 7.4381 | 0.60982 | 0.60982 | 475.468 | 0.62833 | 0 | 269.0857 | 0 | 0 | 0 | 0.62833 | 0 | 0 | 269.0857
11 | 16 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 471.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 15 | 0 | 4.4158 | 4.4158 | 48 | 7.3449 | 4.1077 | 4.1077 | 474.7598 | 4.4158 | 0 | 1884.4673 | 0 | 0 | 0 | 4.4158 | 0 | 0 | 1884.4673
11 | 16 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 478.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 482.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 486.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 486.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 471.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 461.4876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 450.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 16 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 443.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 441.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 440.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 444.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 443.6483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 448.7798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 460.6156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 459.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 7 | 0 | 9.8821 | 9.8821 | 48 | 6.1924 | 6.0748 | 6.0748 | 457.2042 | 9.8821 | 0 | 4043.7916 | 0 | 0 | 0 | 9.8821 | 0 | 0 | 4043.7916
11 | 17 | 8 | 0 | 0 | 0 | 0 | 6.8788 | 0 | 0 | 464.6137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 463.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 460.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 11 | 0 | 0 | 0 | 0 | 7.2263 | 0 | 0 | 460.6129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 459.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 459.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 451.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 15 | 0.18833 | 1.2383 | 1.4266 | 43.1156 | 7.4212 | 1.3738 | 1.3738 | 458.5019 | 1.4266 | 0 | 592.6065 | 0 | 0 | 0 | 1.4266 | 0 | 0 | 592.6065
11 | 17 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 457.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 464.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 460.9441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 453.3598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 456.3649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 453.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 449.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 17 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 457.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 462.9453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 463.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 455.9644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 454.9475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 466.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 467.7043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 461.6862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 453.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 8 | 0 | 67.6434 | 67.6434 | 48 | 6.6246 | 47.6417 | 47.6417 | 456.0811 | 67.6434 | 0 | 27603.984 | 0 | 0 | 0 | 67.6434 | 0 | 0 | 27603.984
11 | 18 | 9 | 0 | 264.7415 | 264.7415 | 48 | 7.1924 | 230.6081 | 230.6081 | 453.721 | 264.7415 | 0 | 107411.2032 | 0 | 0 | 0 | 264.7415 | 0 | 0 | 107411.2032
11 | 18 | 10 | 0 | 205.4494 | 205.4494 | 48 | 7.0398 | 168.2575 | 168.2575 | 447.0966 | 205.4494 | 0 | 81994.1517 | 0 | 0 | 0 | 205.4494 | 0 | 0 | 81994.1517
11 | 18 | 11 | 0 | 179.5786 | 179.5786 | 48 | 7.2093 | 157.5388 | 157.5388 | 445.8218 | 179.5786 | 0 | 71440.2603 | 0 | 0 | 0 | 179.5786 | 0 | 0 | 71440.2603
11 | 18 | 12 | 0 | 108.7114 | 108.7114 | 48 | 7.9296 | 136.7346 | 136.7346 | 439.8518 | 108.7114 | 0 | 42598.7519 | 0 | 0 | 0 | 108.7114 | 0 | 0 | 42598.7519
11 | 18 | 13 | 0 | 65.6912 | 65.6912 | 48 | 8.2601 | 103.1535 | 103.1535 | 433.7574 | 65.6912 | 0 | 25340.8842 | 0 | 0 | 0 | 65.6912 | 0 | 0 | 25340.8842
11 | 18 | 14 | 0 | 129.6576 | 129.6576 | 48 | 8.5313 | 255.7325 | 255.7325 | 440.2599 | 129.6576 | 0 | 50859.499 | 0 | 0 | 0 | 129.6576 | 0 | 0 | 50859.499
11 | 18 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 436.9648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 433.0436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 428.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 432.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 423.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 415.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 407.0553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 408.2896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 18 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 400.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 391.7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 388.3942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 387.1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 400.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 402.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 413.3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 423.7765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 420.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 8 | 0 | 24.4564 | 24.4564 | 48 | 4.8451 | 10.7652 | 10.7652 | 425.062 | 24.4564 | 0 | 9221.5748 | 0 | 0 | 0 | 24.4564 | 0 | 0 | 9221.5748
11 | 19 | 9 | 0 | 1.4042 | 1.4042 | 48 | 6.3789 | 0.91329 | 0.91329 | 418.8024 | 1.4042 | 0 | 520.6684 | 0 | 0 | 0 | 1.4042 | 0 | 0 | 520.6684
11 | 19 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 418.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 420.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 428.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 13 | 0 | 0.68056 | 0.68056 | 48 | 9.6159 | 0 | 0 | 435.7643 | 0 | 0.68056 | 0 | 0.070963 | 0 | 0 | 0 | 0.68056 | 0 | 0
11 | 19 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 439.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 15 | 0 | 0.33833 | 0.33833 | 48 | 10.7175 | 0 | 0 | 453.3429 | 0 | 0.33833 | 0 | 0.035279 | 0 | 0 | 0 | 0.33833 | 0 | 0
11 | 19 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 459.3116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 461.8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 460.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 456.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 447.2149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 433.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 427.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 19 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 426.5693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 427.7719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 431.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 428.8893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 438.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 447.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 445.8798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 443.7553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 7 | 0.0083333 | 74.976 | 74.9843 | 47.9959 | 4.8281 | 32.8889 | 32.8889 | 452.842 | 74.9843 | 0 | 30357.0948 | 0 | 0 | 0 | 74.9843 | 0 | 0 | 30357.0948
11 | 20 | 8 | 0 | 2.2408 | 2.2408 | 48 | 5.4976 | 1.1436 | 1.1436 | 449.0538 | 2.2408 | 0 | 898.6947 | 0 | 0 | 0 | 2.2408 | 0 | 0 | 898.6947
11 | 20 | 9 | 0 | 20.7106 | 20.7106 | 48 | 6.4043 | 13.5779 | 13.5779 | 445.7067 | 20.7106 | 0 | 8236.7508 | 0 | 0 | 0 | 20.7106 | 0 | 0 | 8236.7508
11 | 20 | 10 | 0 | 125.6919 | 125.6919 | 48 | 8.5991 | 264.8661 | 264.8661 | 444.7108 | 125.6919 | 0 | 49863.3351 | 0 | 0 | 0 | 125.6919 | 0 | 0 | 49863.3351
11 | 20 | 11 | 0 | 59.2372 | 59.2372 | 48 | 9.6413 | 0 | 0 | 439.7845 | 0 | 59.2372 | 0 | 6.1768 | 0 | 0 | 0 | 59.2372 | 0 | 0
11 | 20 | 12 | 0 | 22.4814 | 22.4814 | 48 | 9.7176 | 0 | 0 | 442.0798 | 0 | 22.4814 | 0 | 2.3442 | 0 | 0 | 0 | 22.4814 | 0 | 0
11 | 20 | 13 | 0 | 50.1492 | 50.1492 | 48 | 9.7939 | 0 | 0 | 442.4392 | 0 | 50.1492 | 0 | 5.2292 | 0 | 0 | 0 | 50.1492 | 0 | 0
11 | 20 | 14 | 0 | 3.0595 | 3.0595 | 48 | 9.4634 | 50.376 | 50.376 | 438.2264 | 3.0595 | 0 | 1193.8803 | 0 | 0 | 0 | 3.0595 | 0 | 0 | 1193.8803
11 | 20 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 446.2463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 453.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 450.4477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 458.0248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 450.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 440.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 428.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 424.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 20 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 417.7252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 420.9744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 424.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 427.2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 432.2684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 440.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 450.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 6 | 0 | 0.31667 | 0.31667 | 48 | 5.0061 | 0.14429 | 0.14429 | 452.8108 | 0.31667 | 0 | 128.1901 | 0 | 0 | 0 | 0.31667 | 0 | 0 | 128.1901
11 | 21 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 452.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 446.3752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 443.3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 10 | 0 | 0 | 0 | 0 | 8.5482 | 0 | 0 | 438.3296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 11 | 0 | 0.96417 | 0.96417 | 48 | 9.1838 | 4.9542 | 4.9542 | 440.9926 | 0.96417 | 0 | 378.9104 | 0 | 0 | 0 | 0.96417 | 0 | 0 | 378.9104
11 | 21 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 439.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 13 | 0 | 20.8866 | 20.8866 | 48 | 9.6668 | 0 | 0 | 445.35 | 0 | 20.8866 | 0 | 2.1779 | 0 | 0 | 0 | 20.8866 | 0 | 0
11 | 21 | 14 | 0 | 0 | 0 | 0 | 10.2684 | 0 | 0 | 460.6184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 15 | 0 | 0 | 0 | 0 | 11.226 | 0 | 0 | 470.2855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 468.0423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 468.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 458.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 452.9907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 439.591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 436.9245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 430.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 21 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 430.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 428.6034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 429.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 441.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.7674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 464.8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 483.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 492.7204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 489.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 8 | 0 | 12.1689 | 12.1689 | 48 | 6.2094 | 7.518 | 7.518 | 491.7354 | 12.1689 | 0 | 5399.7709 | 0 | 0 | 0 | 12.1689 | 0 | 0 | 5399.7709
11 | 22 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 488.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 10 | 0 | 0 | 0 | 0 | 8.0567 | 0 | 0 | 490.3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 11 | 0 | 221.0514 | 221.0514 | 48 | 9.3109 | 1652.6125 | 288 | 488.1063 | 38.5225 | 182.5289 | 16954.0094 | 19.0328 | 0 | 0 | 38.5225 | 182.5289 | 0 | 16954.0094
11 | 22 | 12 | 0 | 30.1937 | 30.1937 | 48 | 9.0058 | 107.9074 | 107.9074 | 481.4401 | 30.1937 | 0 | 13087.182 | 0 | 0 | 0 | 30.1937 | 0 | 0 | 13087.182
11 | 22 | 13 | 0 | 188.8858 | 188.8858 | 48 | 8.4889 | 358.2198 | 288 | 480.6769 | 151.8596 | 37.0262 | 65706.1209 | 3.8608 | 0 | 0 | 151.8596 | 37.0262 | 0 | 65706.1209
11 | 22 | 14 | 0.041667 | 245.5618 | 245.6035 | 47.9937 | 8.938 | 786.5154 | 288 | 469.1869 | 89.9331 | 155.6703 | 37879.2292 | 16.2322 | 0 | 0 | 89.9331 | 155.6703 | 0 | 37879.2292
11 | 22 | 15 | 0.019167 | 2.9369 | 2.956 | 47.7601 | 9.6075 | 0 | 0 | 473.6547 | 0 | 2.956 | 0 | 0.30823 | 0 | 0 | 0 | 2.956 | 0 | 0
11 | 22 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 473.0748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 475.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 488.5672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 486.0184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 475.8786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 463.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 458.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 22 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 453.6931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 452.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 453.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 453.3689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 464.7808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 472.9176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 477.8221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 482.1559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 480.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 479.0482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 472.5391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 461.8216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 450.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 12 | 0 | 91.2313 | 91.2313 | 48 | 7.8957 | 112.4533 | 112.4533 | 436.9491 | 91.2313 | 0 | 35484.3226 | 0 | 0 | 0 | 91.2313 | 0 | 0 | 35484.3226
11 | 23 | 13 | 0 | 43.672 | 43.672 | 48 | 7.4381 | 42.3851 | 42.3851 | 435.0915 | 43.672 | 0 | 16905.0608 | 0 | 0 | 0 | 43.672 | 0 | 0 | 16905.0608
11 | 23 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 443.4418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 15 | 0 | 7.4458 | 7.4458 | 48 | 7.3449 | 6.9264 | 6.9264 | 448.5106 | 7.4458 | 0 | 2982.1344 | 0 | 0 | 0 | 7.4458 | 0 | 0 | 2982.1344
11 | 23 | 16 | 0 | 0.70167 | 0.70167 | 48 | 6.9975 | 0.56526 | 0.56526 | 449.4169 | 0.70167 | 0 | 281.6609 | 0 | 0 | 0 | 0.70167 | 0 | 0 | 281.6609
11 | 23 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 452.7576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 452.2873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 448.2559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 446.2173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 440.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 444.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 23 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 440.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 439.4205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 448.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 458.2867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 460.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 464.9144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 460.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 452.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 7 | 4.0542 | 273.38 | 277.4342 | 47.4593 | 6.1924 | 170.5457 | 170.5457 | 441.1597 | 277.4342 | 0 | 109225.9396 | 0 | 0 | 0 | 277.4342 | 0 | 0 | 109225.9396
11 | 24 | 8 | 4.7033 | 311.2693 | 315.9726 | 47.4492 | 6.8788 | 243.407 | 243.407 | 433.9647 | 315.9726 | 0 | 122128.3101 | 0 | 0 | 0 | 315.9726 | 0 | 0 | 122128.3101
11 | 24 | 9 | 0 | 20.2767 | 20.2767 | 48 | 7.3195 | 18.6511 | 18.6511 | 413.0072 | 20.2767 | 0 | 7401.141 | 0 | 0 | 0 | 20.2767 | 0 | 0 | 7401.141
11 | 24 | 10 | 0 | 0 | 0 | 0 | 7.4805 | 0 | 0 | 400.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 11 | 0 | 63.7637 | 63.7637 | 48 | 7.2263 | 56.339 | 56.339 | 397.8325 | 63.7637 | 0 | 22306.6071 | 0 | 0 | 0 | 63.7637 | 0 | 0 | 22306.6071
11 | 24 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 396.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 398.6923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 410.3243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 15 | 0 | 24.1822 | 24.1822 | 48 | 7.4212 | 23.2863 | 23.2863 | 426.6026 | 24.1822 | 0 | 9155.4558 | 0 | 0 | 0 | 24.1822 | 0 | 0 | 9155.4558
11 | 24 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 423.4493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 419.7902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 419.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 410.1991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 399.7231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 390.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 385.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 24 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 388.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 381.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 383.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 393.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 412.4412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 420.7889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 424.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 425.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 7 | 0 | 0.39542 | 0.39542 | 48 | 6.006 | 0.23043 | 0.23043 | 417.3384 | 0.39542 | 0 | 146.0424 | 0 | 0 | 0 | 0.39542 | 0 | 0 | 146.0424
11 | 25 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 408.9428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 402.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 402.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 398.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 395.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 402.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 418.9126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 15 | 0 | 0.11917 | 0.11917 | 48 | 8.4041 | 0.20985 | 0.20985 | 442.7673 | 0.11917 | 0 | 47.0429 | 0 | 0 | 0 | 0.11917 | 0 | 0 | 47.0429
11 | 25 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 438.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 437.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 434.3504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 429.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 419.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 421.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 416.6517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 25 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 419.7741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 420.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 423.4165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 426.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 434.9263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 445.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 456.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 455.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 450.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 8 | 0 | 0.68667 | 0.68667 | 48 | 4.8451 | 0.30226 | 0.30226 | 441.2328 | 0.68667 | 0 | 270.0199 | 0 | 0 | 0 | 0.68667 | 0 | 0 | 270.0199
11 | 26 | 9 | 0.005 | 39.305 | 39.31 | 47.9953 | 6.3789 | 25.5676 | 25.5676 | 427.7823 | 39.31 | 0 | 14929.414 | 0 | 0 | 0 | 39.31 | 0 | 0 | 14929.414
11 | 26 | 10 | 0 | 0.68615 | 0.68615 | 48 | 8.4804 | 1.2913 | 1.2913 | 426.9066 | 0.68615 | 0 | 259.9862 | 0 | 0 | 0 | 0.68615 | 0 | 0 | 259.9862
11 | 26 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 423.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 420.3943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 431.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 446.2362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 15 | 0 | 0.047916 | 0.047916 | 48 | 10.7175 | 0 | 0 | 454.9236 | 0 | 0.047916 | 0 | 0.0049963 | 0 | 0 | 0 | 0.047916 | 0 | 0
11 | 26 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 457.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 454.5276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 452.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 437.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 424.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 415.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 412.2093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 26 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 411.1884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 415.4587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 425.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 437.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 3 | 3.5154 | 0 | 3.5154 | 11 | 3.1249 | 1.1357 | 1.1357 | 446.2889 | 3.5154 | 0 | 1530.2268 | 0 | 0 | 0 | 3.5154 | 0 | 0 | 1530.2268
11 | 27 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 461.9438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 462.9749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 473.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 7 | 1.1775 | 0.39833 | 1.5758 | 20.3527 | 4.8281 | 0.69118 | 0.69118 | 474.363 | 1.5758 | 0 | 715.4445 | 0 | 0 | 0 | 1.5758 | 0 | 0 | 715.4445
11 | 27 | 8 | 1.2133 | 2.1516 | 3.3649 | 34.6584 | 5.4976 | 1.7173 | 1.7173 | 476.992 | 3.3649 | 0 | 1488.4176 | 0 | 0 | 0 | 3.3649 | 0 | 0 | 1488.4176
11 | 27 | 9 | 0.41333 | 31.8685 | 32.2819 | 47.5263 | 6.4043 | 21.164 | 21.164 | 472.3237 | 32.2819 | 0 | 13713.2527 | 0 | 0 | 0 | 32.2819 | 0 | 0 | 13713.2527
11 | 27 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 458.9928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 453.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 447.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 13 | 0 | 0 | 0 | 0 | 9.7939 | 0 | 0 | 451.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 14 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 445.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 15 | 0 | 0 | 0 | 0 | 10.5311 | 0 | 0 | 459.6264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 459.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 462.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 459.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 446.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 430.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 419.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 415.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 27 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 415.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 415.2499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 414.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 430.3859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 440.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 456.799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 461.1743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 459.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 7 | 0.036667 | 58.8527 | 58.8894 | 47.977 | 5.2518 | 28.3521 | 28.3521 | 445.497 | 58.8894 | 0 | 23409.6987 | 0 | 0 | 0 | 58.8894 | 0 | 0 | 23409.6987
11 | 28 | 8 | 0 | 180.9136 | 180.9136 | 48 | 6.2094 | 111.7696 | 111.7696 | 436.0432 | 180.9136 | 0 | 70202.288 | 0 | 0 | 0 | 180.9136 | 0 | 0 | 70202.288
11 | 28 | 9 | 0 | 180.1271 | 180.1271 | 48 | 7.328 | 166.3066 | 166.3066 | 430.0855 | 180.1271 | 0 | 68823.9554 | 0 | 0 | 0 | 180.1271 | 0 | 0 | 68823.9554
11 | 28 | 10 | 0.10667 | 262.7672 | 262.8739 | 47.985 | 8.5482 | 526.9165 | 288 | 428.5404 | 143.6806 | 119.1933 | 54678.4361 | 12.4286 | 0 | 0 | 143.6806 | 119.1933 | 0 | 54678.4361
11 | 28 | 11 | 0.069167 | 294.9748 | 295.0439 | 47.9913 | 9.1838 | 1516.0456 | 288 | 427.4546 | 56.0489 | 238.9951 | 21268.4907 | 24.9206 | 0 | 0 | 56.0489 | 238.9951 | 0 | 21268.4907
11 | 28 | 12 | 0 | 301.4509 | 301.4509 | 48 | 9.8701 | 0 | 0 | 432.0692 | 0 | 301.4509 | 0 | 31.4331 | 0 | 0 | 0 | 301.4509 | 0 | 0
11 | 28 | 13 | 0 | 160.3004 | 160.3004 | 48 | 9.6668 | 0 | 0 | 442.1899 | 0 | 160.3004 | 0 | 16.7149 | 0 | 0 | 0 | 160.3004 | 0 | 0
11 | 28 | 14 | 0 | 6.6167 | 6.6167 | 48 | 10.2684 | 0 | 0 | 450.0278 | 0 | 6.6167 | 0 | 0.68994 | 0 | 0 | 0 | 6.6167 | 0 | 0
11 | 28 | 15 | 0 | 12.8231 | 12.8231 | 48 | 11.226 | 0 | 0 | 466.1883 | 0 | 12.8231 | 0 | 1.3371 | 0 | 0 | 0 | 12.8231 | 0 | 0
11 | 28 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 465.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 468.8957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 455.5934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 439.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 413.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 405.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 409.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 28 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 404.4374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 407.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 418.4582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 434.1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 452.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 465.0907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 477.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 468.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 7 | 0 | 3.4938 | 3.4938 | 48 | 5.0146 | 1.5948 | 1.5948 | 463.0421 | 3.4938 | 0 | 1450.0537 | 0 | 0 | 0 | 3.4938 | 0 | 0 | 1450.0537
11 | 29 | 8 | 0 | 1.3583 | 1.3583 | 48 | 6.2094 | 0.83919 | 0.83919 | 455.8389 | 1.3583 | 0 | 553.9828 | 0 | 0 | 0 | 1.3583 | 0 | 0 | 553.9828
11 | 29 | 9 | 0 | 0 | 0 | 0 | 7.311 | 0 | 0 | 457.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 10 | 0 | 8.6445 | 8.6445 | 48 | 8.0567 | 11.7741 | 11.7741 | 460.2023 | 8.6445 | 0 | 3563.285 | 0 | 0 | 0 | 8.6445 | 0 | 0 | 3563.285
11 | 29 | 11 | 0 | 30.1156 | 30.1156 | 48 | 9.3109 | 225.1482 | 225.1482 | 462.9839 | 30.1156 | 0 | 12497.4685 | 0 | 0 | 0 | 30.1156 | 0 | 0 | 12497.4685
11 | 29 | 12 | 0 | 0.92349 | 0.92349 | 48 | 9.0058 | 3.3004 | 3.3004 | 465.6098 | 0.92349 | 0 | 385.6566 | 0 | 0 | 0 | 0.92349 | 0 | 0 | 385.6566
11 | 29 | 13 | 0 | 7.9137 | 7.9137 | 48 | 8.4889 | 15.0082 | 15.0082 | 468.7348 | 7.9137 | 0 | 3329.5585 | 0 | 0 | 0 | 7.9137 | 0 | 0 | 3329.5585
11 | 29 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 469.2658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 15 | 0 | 1.1867 | 1.1867 | 48 | 9.6075 | 0 | 0 | 480.6591 | 0 | 1.1867 | 0 | 0.12374 | 0 | 0 | 0 | 1.1867 | 0 | 0
11 | 29 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 478.4819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 481.4342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 483.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 474.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 459.1147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 446.7277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 441.8389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 29 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 434.1384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 428.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 432.2911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 438.0195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 447.1669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 461.3021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 466.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 475.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 468.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 8 | 0 | 0 | 0 | 0 | 5.1417 | 0 | 0 | 466.9302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 9 | 0 | 0 | 0 | 0 | 6.6161 | 0 | 0 | 464.0959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 462.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 455.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 12 | 0 | 0 | 0 | 0 | 7.8957 | 0 | 0 | 449.9474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 13 | 0 | 0 | 0 | 0 | 7.4381 | 0 | 0 | 460.6348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 14 | 0 | 0 | 0 | 0 | 7.2771 | 0 | 0 | 458.5023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 15 | 0 | 0 | 0 | 0 | 7.3449 | 0 | 0 | 467.5834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 471.2661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 469.3366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 468.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 454.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 433.5488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 433.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 436.5617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 30 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 438.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 441.8905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 446.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 448.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 461.9002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 474.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 478.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 477.247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 7 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 484.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 8 | 0 | 97.8433 | 97.8433 | 48 | 6.8788 | 75.3728 | 75.3728 | 481.0264 | 97.8433 | 0 | 42368.7561 | 0 | 0 | 0 | 97.8433 | 0 | 0 | 42368.7561
12 | 1 | 9 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 469.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 10 | 0 | 22.9572 | 22.9572 | 48 | 7.4805 | 22.7282 | 22.7282 | 472.8605 | 22.9572 | 0 | 9753.5968 | 0 | 0 | 0 | 22.9572 | 0 | 0 | 9753.5968
12 | 1 | 11 | 0 | 61.6596 | 61.6596 | 48 | 7.2263 | 54.4799 | 54.4799 | 466.9168 | 61.6596 | 0 | 25830.2605 | 0 | 0 | 0 | 61.6596 | 0 | 0 | 25830.2605
12 | 1 | 12 | 0 | 192.3299 | 192.3299 | 48 | 7.8703 | 233.5651 | 233.5651 | 464.0653 | 192.3299 | 0 | 80021.7859 | 0 | 0 | 0 | 192.3299 | 0 | 0 | 80021.7859
12 | 1 | 13 | 0.040833 | 78.9024 | 78.9432 | 47.9809 | 8.1754 | 116.5385 | 116.5385 | 470.1232 | 78.9432 | 0 | 33325.2708 | 0 | 0 | 0 | 78.9432 | 0 | 0 | 33325.2708
12 | 1 | 14 | 0.2325 | 0 | 0.2325 | 11 | 8.2431 | 0.3605 | 0.3605 | 469.8224 | 0.2325 | 0 | 106.6762 | 0 | 0 | 0 | 0.2325 | 0 | 0 | 106.6762
12 | 1 | 15 | 0 | 0.14541 | 0.14541 | 48 | 7.4212 | 0.14003 | 0.14003 | 479.0629 | 0.14541 | 0 | 62.6828 | 0 | 0 | 0 | 0.14541 | 0 | 0 | 62.6828
12 | 1 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 472.4246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 481.9879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 490.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 480.1687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 472.1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 458.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 457.1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 456.7135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 459.1999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 462.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 457.4239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 459.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 468.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 465.6087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 474.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 7 | 0 | 0.47458 | 0.47458 | 48 | 6.006 | 0.27656 | 0.27656 | 483.8979 | 0.47458 | 0 | 206.8697 | 0 | 0 | 0 | 0.47458 | 0 | 0 | 206.8697
12 | 2 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 482.2357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 9 | 0.0041667 | 58.195 | 58.1992 | 47.9974 | 7.1924 | 50.6955 | 50.6955 | 473.6937 | 58.1992 | 0 | 24775.1922 | 0 | 0 | 0 | 58.1992 | 0 | 0 | 24775.1922
12 | 2 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 471.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 467.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 467.1567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 464.9161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 474.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 15 | 0 | 0 | 0 | 0 | 8.4041 | 0 | 0 | 482.4899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 483.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 485.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 486.9427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 477.9619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 466.8946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 461.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 449.7156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 445.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 446.9146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 454.417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 445.6376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 447.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 466.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 473.7196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 476.1696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 7 | 0 | 0.39208 | 0.39208 | 48 | 4.8705 | 0.17352 | 0.17352 | 467.9474 | 0.39208 | 0 | 164.6542 | 0 | 0 | 0 | 0.39208 | 0 | 0 | 164.6542
12 | 3 | 8 | 0 | 21.4417 | 21.4417 | 48 | 4.8451 | 9.4382 | 9.4382 | 458.5057 | 21.4417 | 0 | 8801.9543 | 0 | 0 | 0 | 21.4417 | 0 | 0 | 8801.9543
12 | 3 | 9 | 0.13667 | 144.3241 | 144.4608 | 47.965 | 6.3789 | 93.9589 | 93.9589 | 449.5673 | 144.4608 | 0 | 58015.7839 | 0 | 0 | 0 | 144.4608 | 0 | 0 | 58015.7839
12 | 3 | 10 | 0 | 84.7496 | 84.7496 | 48 | 8.4804 | 159.4995 | 159.4995 | 446.4816 | 84.7496 | 0 | 33771.1711 | 0 | 0 | 0 | 84.7496 | 0 | 0 | 33771.1711
12 | 3 | 11 | 1.5075 | 141.5017 | 143.0092 | 47.61 | 9.4549 | 2207.2948 | 288 | 441.927 | 18.6593 | 124.3499 | 7357.6957 | 12.9663 | 0 | 0 | 18.6593 | 124.3499 | 0 | 7357.6957
12 | 3 | 12 | 0 | 10.0725 | 10.0725 | 48 | 9.8362 | 0 | 0 | 437.5297 | 0 | 10.0725 | 0 | 1.0503 | 0 | 0 | 0 | 10.0725 | 0 | 0
12 | 3 | 13 | 0 | 15.5194 | 15.5194 | 48 | 9.6159 | 0 | 0 | 445.7111 | 0 | 15.5194 | 0 | 1.6182 | 0 | 0 | 0 | 15.5194 | 0 | 0
12 | 3 | 14 | 0 | 6.54 | 6.54 | 48 | 9.5227 | 202.269 | 202.269 | 459.9046 | 6.54 | 0 | 2693.856 | 0 | 0 | 0 | 6.54 | 0 | 0 | 2693.856
12 | 3 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 468.9475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 460.8848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 458.5769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 449.4859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 436.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 428.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 421.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 415.6564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 3 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 411.1101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 413.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 429.6563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 427.9808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 443.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 459.7787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 456.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 455.8243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 451.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 8 | 0 | 1.8331 | 1.8331 | 48 | 5.4976 | 0.93551 | 0.93551 | 451.1192 | 1.8331 | 0 | 738.9419 | 0 | 0 | 0 | 1.8331 | 0 | 0 | 738.9419
12 | 4 | 9 | 0.63255 | 0 | 0.63255 | 11 | 6.4043 | 0.4147 | 0.4147 | 445.5994 | 0.63255 | 0 | 274.9055 | 0 | 0 | 0 | 0.63255 | 0 | 0 | 274.9055
12 | 4 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 434.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 4 | 11 | 2.2158 | 0.70833 | 2.9242 | 19.9627 | 9.6413 | 0 | 0 | 432.1012 | 0 | 2.9242 | 0 | 0.30491 | 0 | 0 | 0 | 2.9242 | 0 | 0
12 | 4 | 12 | 57.4508 | 0 | 57.4508 | 11 | 9.7176 | 0 | 0 | 429.4471 | 0 | 57.4508 | 0 | 5.9905 | 0 | 0 | 0 | 57.4508 | 0 | 0
12 | 4 | 13 | 96.5083 | 0 | 96.5083 | 11 | 9.7939 | 0 | 0 | 427.8142 | 0 | 96.5083 | 0 | 10.0632 | 0 | 0 | 0 | 96.5083 | 0 | 0
12 | 4 | 14 | 149.43 | 0 | 149.43 | 11 | 9.4634 | 2460.4681 | 288 | 437.6315 | 17.4909 | 131.9391 | 7462.1758 | 13.7576 | 0 | 0 | 17.4909 | 131.9391 | 0 | 7462.1758
12 | 4 | 15 | 2.5099 | 0.66417 | 3.1741 | 18.7421 | 10.5311 | 0 | 0 | 447.664 | 0 | 3.1741 | 0 | 0.33097 | 0 | 0 | 0 | 3.1741 | 0 | 0
12 | 4 | 16 | 30.3459 | 0 | 30.3459 | 11 | 11.0904 | 0 | 0 | 449.4856 | 0 | 30.3459 | 0 | 3.1643 | 0 | 0 | 0 | 30.3459 | 0 | 0
12 | 4 | 17 | 98.5052 | 0 | 98.5052 | 11 | 11.1073 | 0 | 0 | 453.0717 | 0 | 98.5052 | 0 | 10.2714 | 0 | 0 | 0 | 98.5052 | 0 | 0
12 | 4 | 18 | 94.37 | 0 | 94.37 | 11 | 11.4802 | 0 | 0 | 448.1527 | 0 | 94.37 | 0 | 9.8402 | 0 | 0 | 0 | 94.37 | 0 | 0
12 | 4 | 19 | 141.3734 | 0 | 141.3734 | 11 | 12.6496 | 0 | 0 | 429.1073 | 0 | 141.3734 | 0 | 14.7414 | 0 | 0 | 0 | 141.3734 | 0 | 0
12 | 4 | 20 | 126.3825 | 0 | 126.3825 | 11 | 12.2428 | 0 | 0 | 414.7282 | 0 | 126.3825 | 0 | 13.1782 | 0 | 0 | 0 | 126.3825 | 0 | 0
12 | 4 | 21 | 90.8104 | 0 | 90.8104 | 11 | 9.4634 | 1495.2553 | 288 | 395.2511 | 17.4909 | 73.3194 | 6720.9042 | 7.6452 | 0 | 0 | 17.4909 | 73.3194 | 0 | 6720.9042
12 | 4 | 22 | 119.9703 | 0 | 119.9703 | 11 | 5.8196 | 66.4562 | 66.4562 | 391.6151 | 119.9703 | 0 | 45662.511 | 0 | 0 | 0 | 119.9703 | 0 | 0 | 45662.511
12 | 4 | 23 | 161.9789 | 0 | 161.9789 | 11 | 4.3028 | 63.9863 | 63.9863 | 382.7315 | 161.9789 | 0 | 60212.6513 | 0 | 0 | 0 | 161.9789 | 0 | 0 | 60212.6513
12 | 5 | 0 | 96.309 | 0 | 96.309 | 11 | 3.6333 | 33.7693 | 33.7693 | 378.8041 | 96.309 | 0 | 35422.8305 | 0 | 0 | 0 | 96.309 | 0 | 0 | 35422.8305
12 | 5 | 1 | 106.292 | 0 | 106.292 | 11 | 3.3198 | 35.4062 | 35.4062 | 380.06 | 106.292 | 0 | 39228.1342 | 0 | 0 | 0 | 106.292 | 0 | 0 | 39228.1342
12 | 5 | 2 | 137.3806 | 0 | 137.3806 | 11 | 3.2096 | 44.9718 | 44.9718 | 382.9529 | 137.3806 | 0 | 51099.105 | 0 | 0 | 0 | 137.3806 | 0 | 0 | 51099.105
12 | 5 | 3 | 101.5813 | 0 | 101.5813 | 11 | 3.2435 | 33.4304 | 33.4304 | 406.6257 | 101.5813 | 0 | 40188.1563 | 0 | 0 | 0 | 101.5813 | 0 | 0 | 40188.1563
12 | 5 | 4 | 139.4012 | 0 | 139.4012 | 11 | 3.2689 | 46.0615 | 46.0615 | 430.0423 | 139.4012 | 0 | 58414.9928 | 0 | 0 | 0 | 139.4012 | 0 | 0 | 58414.9928
12 | 5 | 5 | 172.4312 | 0 | 172.4312 | 11 | 3.8536 | 62.7826 | 62.7826 | 445.2765 | 172.4312 | 0 | 74882.8083 | 0 | 0 | 0 | 172.4312 | 0 | 0 | 74882.8083
12 | 5 | 6 | 158.183 | 0 | 158.183 | 11 | 5.0061 | 72.0741 | 72.0741 | 446.3165 | 158.183 | 0 | 68859.6882 | 0 | 0 | 0 | 158.183 | 0 | 0 | 68859.6882
12 | 5 | 7 | 35.3682 | 0 | 35.3682 | 11 | 5.2518 | 17.0279 | 17.0279 | 446.9179 | 35.3682 | 0 | 15417.6188 | 0 | 0 | 0 | 35.3682 | 0 | 0 | 15417.6188
12 | 5 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 447.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 9 | 0 | 0 | 0 | 0 | 7.328 | 0 | 0 | 444.4605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 10 | 0 | 0 | 0 | 0 | 8.5482 | 0 | 0 | 448.8112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 11 | 0 | 0 | 0 | 0 | 9.1838 | 0 | 0 | 444.5339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 12 | 0 | 0 | 0 | 0 | 9.8701 | 0 | 0 | 441.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 13 | 0 | 0 | 0 | 0 | 9.6668 | 0 | 0 | 440.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 14 | 0 | 0.61416 | 0.61416 | 48 | 10.2684 | 0 | 0 | 434.5071 | 0 | 0.61416 | 0 | 0.06404 | 0 | 0 | 0 | 0.61416 | 0 | 0
12 | 5 | 15 | 0 | 1.5042 | 1.5042 | 48 | 11.226 | 0 | 0 | 447.9461 | 0 | 1.5042 | 0 | 0.15684 | 0 | 0 | 0 | 1.5042 | 0 | 0
12 | 5 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 458.7776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 465.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 467.7244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 449.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 429.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 414.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 409.9751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 5 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 409.9365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 413.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 426.6677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 441.6535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 451.9525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 457.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 460.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 470.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 7 | 0 | 5.6393 | 5.6393 | 48 | 5.0146 | 2.5742 | 2.5742 | 464.8353 | 5.6393 | 0 | 2350.6462 | 0 | 0 | 0 | 5.6393 | 0 | 0 | 2350.6462
12 | 6 | 8 | 0 | 121.4764 | 121.4764 | 48 | 6.2094 | 75.0489 | 75.0489 | 458.9054 | 121.4764 | 0 | 49915.3102 | 0 | 0 | 0 | 121.4764 | 0 | 0 | 49915.3102
12 | 6 | 9 | 0.67 | 380.2194 | 380.8894 | 47.9349 | 7.311 | 349.0502 | 288 | 456.8722 | 314.2704 | 66.619 | 128516.8791 | 6.9465 | 0 | 0 | 314.2704 | 66.619 | 0 | 128516.8791
12 | 6 | 10 | 0 | 81.8818 | 81.8818 | 48 | 8.0567 | 111.5254 | 111.5254 | 457.8482 | 81.8818 | 0 | 33559.0932 | 0 | 0 | 0 | 81.8818 | 0 | 0 | 33559.0932
12 | 6 | 11 | 0 | 1.1775 | 1.1775 | 48 | 9.3109 | 8.8032 | 8.8032 | 456.9741 | 1.1775 | 0 | 481.567 | 0 | 0 | 0 | 1.1775 | 0 | 0 | 481.567
12 | 6 | 12 | 0 | 0 | 0 | 0 | 9.0058 | 0 | 0 | 458.2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 13 | 0 | 0 | 0 | 0 | 8.4889 | 0 | 0 | 458.9037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 456.3587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 15 | 0 | 1.8483 | 1.8483 | 48 | 9.6075 | 0 | 0 | 459.101 | 0 | 1.8483 | 0 | 0.19273 | 0 | 0 | 0 | 1.8483 | 0 | 0
12 | 6 | 16 | 0 | 0.065833 | 0.065833 | 48 | 10.9718 | 0 | 0 | 461.1771 | 0 | 0.065833 | 0 | 0.0068646 | 0 | 0 | 0 | 0.065833 | 0 | 0
12 | 6 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 464.7893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 466.5924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 463.7915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 456.4629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 449.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 433.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 6 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 427.7735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 429.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 436.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 440.3247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 452.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 463.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 480.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 479.0982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 479.5162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 8 | 0 | 91.4783 | 91.4783 | 48 | 5.1417 | 42.9513 | 42.9513 | 486.3575 | 91.4783 | 0 | 40100.1795 | 0 | 0 | 0 | 91.4783 | 0 | 0 | 40100.1795
12 | 7 | 9 | 0 | 8.4542 | 8.4542 | 48 | 6.6161 | 5.9374 | 5.9374 | 485.8375 | 8.4542 | 0 | 3701.5516 | 0 | 0 | 0 | 8.4542 | 0 | 0 | 3701.5516
12 | 7 | 10 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 487.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 11 | 0 | 0 | 0 | 0 | 8.5652 | 0 | 0 | 483.8811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 12 | 0 | 2.9775 | 2.9775 | 48 | 7.8957 | 3.6701 | 3.6701 | 489.787 | 2.9775 | 0 | 1315.4209 | 0 | 0 | 0 | 2.9775 | 0 | 0 | 1315.4209
12 | 7 | 13 | 0 | 26.2865 | 26.2865 | 48 | 7.4381 | 25.5119 | 25.5119 | 487.1804 | 26.2865 | 0 | 11544.5146 | 0 | 0 | 0 | 26.2865 | 0 | 0 | 11544.5146
12 | 7 | 14 | 0 | 0.62395 | 0.62395 | 48 | 7.2771 | 0.56341 | 0.56341 | 481.6148 | 0.62395 | 0 | 270.5526 | 0 | 0 | 0 | 0.62395 | 0 | 0 | 270.5526
12 | 7 | 15 | 0 | 1.6825 | 1.6825 | 48 | 7.3449 | 1.5651 | 1.5651 | 481.9673 | 1.6825 | 0 | 730.1454 | 0 | 0 | 0 | 1.6825 | 0 | 0 | 730.1454
12 | 7 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 481.1909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 487.1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 503.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 499.9942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 491.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 485.6413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 475.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 7 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 470.759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 473.3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 474.2634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 477.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 473.8659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 481.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 488.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 505.1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 7 | 0 | 3.4898 | 3.4898 | 48 | 6.1924 | 2.1452 | 2.1452 | 511.0857 | 3.4898 | 0 | 1616.0628 | 0 | 0 | 0 | 3.4898 | 0 | 0 | 1616.0628
12 | 8 | 8 | 0 | 167.0128 | 167.0128 | 48 | 6.8788 | 128.657 | 128.657 | 513.0643 | 167.0128 | 0 | 77671.7174 | 0 | 0 | 0 | 167.0128 | 0 | 0 | 77671.7174
12 | 8 | 9 | 0 | 17.7275 | 17.7275 | 48 | 7.3195 | 16.3063 | 16.3063 | 514.9208 | 17.7275 | 0 | 8277.3576 | 0 | 0 | 0 | 17.7275 | 0 | 0 | 8277.3576
12 | 8 | 10 | 0 | 6.195 | 6.195 | 48 | 7.4805 | 6.1332 | 6.1332 | 508.402 | 6.195 | 0 | 2852.1903 | 0 | 0 | 0 | 6.195 | 0 | 0 | 2852.1903
12 | 8 | 11 | 0 | 0.83917 | 0.83917 | 48 | 7.2263 | 0.74145 | 0.74145 | 511.0111 | 0.83917 | 0 | 388.5435 | 0 | 0 | 0 | 0.83917 | 0 | 0 | 388.5435
12 | 8 | 12 | 0 | 0 | 0 | 0 | 7.8703 | 0 | 0 | 512.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 13 | 0 | 0 | 0 | 0 | 8.1754 | 0 | 0 | 510.9991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 14 | 0 | 0 | 0 | 0 | 8.2431 | 0 | 0 | 502.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 15 | 0 | 1.5042 | 1.5042 | 48 | 7.4212 | 1.4484 | 1.4484 | 501.8052 | 1.5042 | 0 | 682.5939 | 0 | 0 | 0 | 1.5042 | 0 | 0 | 682.5939
12 | 8 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 505.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 508.7364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 504.7744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 498.0186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 497.1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 497.1468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 487.5782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 8 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 484.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 487.2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 488.2076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 492.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 494.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 496.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 5 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 496.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 6 | 0 | 0 | 0 | 0 | 4.4638 | 0 | 0 | 497.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 7 | 0 | 0 | 0 | 0 | 6.006 | 0 | 0 | 501.3152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 8 | 0 | 0 | 0 | 0 | 6.6246 | 0 | 0 | 503.2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 9 | 0 | 0 | 0 | 0 | 7.1924 | 0 | 0 | 507.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 10 | 0 | 0 | 0 | 0 | 7.0398 | 0 | 0 | 501.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 11 | 0 | 0 | 0 | 0 | 7.2093 | 0 | 0 | 495.8389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 12 | 0 | 0 | 0 | 0 | 7.9296 | 0 | 0 | 491.4595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 13 | 0 | 0 | 0 | 0 | 8.2601 | 0 | 0 | 483.8411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 14 | 0 | 0 | 0 | 0 | 8.5313 | 0 | 0 | 489.3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 15 | 0 | 1.6883 | 1.6883 | 48 | 8.4041 | 2.9731 | 2.9731 | 494.5241 | 1.6883 | 0 | 753.8772 | 0 | 0 | 0 | 1.6883 | 0 | 0 | 753.8772
12 | 9 | 16 | 0 | 0 | 0 | 0 | 9.1753 | 0 | 0 | 495.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 17 | 0 | 0 | 0 | 0 | 8.6753 | 0 | 0 | 494.4156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 18 | 0 | 0 | 0 | 0 | 9.0397 | 0 | 0 | 508.5391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 19 | 0 | 0 | 0 | 0 | 7.6754 | 0 | 0 | 511.2337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 20 | 0 | 0 | 0 | 0 | 10.8362 | 0 | 0 | 510.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 21 | 0 | 0 | 0 | 0 | 8.7685 | 0 | 0 | 507.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 22 | 0 | 0 | 0 | 0 | 5.1247 | 0 | 0 | 500.4598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 9 | 23 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 492.5856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 0 | 0 | 0 | 0 | 0 | 2.9978 | 0 | 0 | 488.4722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 1 | 0 | 0 | 0 | 0 | 2.8876 | 0 | 0 | 484.9875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 2 | 0 | 0 | 0 | 0 | 2.8791 | 0 | 0 | 486.2194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 3 | 0 | 0 | 0 | 0 | 3.0147 | 0 | 0 | 486.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 4 | 0 | 0 | 0 | 0 | 3.0317 | 0 | 0 | 489.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 5 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 488.5739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 6 | 0 | 0 | 0 | 0 | 4.1926 | 0 | 0 | 488.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 7 | 0 | 0 | 0 | 0 | 4.8705 | 0 | 0 | 491.7535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 490.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 498.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 500.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 499.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 498.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 500.2844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 512.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 515.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 16 | 0 | 0 | 0 | 0 | 12.0564 | 0 | 0 | 522.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 524.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 526.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 522.6774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 510.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 508.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 506.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 10 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 507.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 504.9364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 504.6073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 504.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 507.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 516.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 515.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 517.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 523.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 8 | 0 | 8.8872 | 8.8872 | 48 | 5.4976 | 4.5356 | 4.5356 | 528.0514 | 8.8872 | 0 | 4266.3117 | 0 | 0 | 0 | 8.8872 | 0 | 0 | 4266.3117
12 | 11 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 527.9678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 10 | 0 | 0 | 0 | 0 | 8.5991 | 0 | 0 | 522.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 11 | 0 | 196.9399 | 196.9399 | 48 | 9.6413 | 0 | 0 | 524.4496 | 0 | 196.9399 | 0 | 20.5354 | 0 | 0 | 0 | 196.9399 | 0 | 0
12 | 11 | 12 | 0 | 201.074 | 201.074 | 48 | 9.7176 | 0 | 0 | 529.9764 | 0 | 201.074 | 0 | 20.9665 | 0 | 0 | 0 | 201.074 | 0 | 0
12 | 11 | 13 | 0 | 70.2217 | 70.2217 | 48 | 9.7939 | 0 | 0 | 521.9663 | 0 | 70.2217 | 0 | 7.3222 | 0 | 0 | 0 | 70.2217 | 0 | 0
12 | 11 | 14 | 0 | 7.7321 | 7.7321 | 48 | 9.4634 | 127.314 | 127.314 | 521.6507 | 7.7321 | 0 | 3662.3037 | 0 | 0 | 0 | 7.7321 | 0 | 0 | 3662.3037
12 | 11 | 15 | 0 | 0.58749 | 0.58749 | 48 | 10.5311 | 0 | 0 | 523.776 | 0 | 0.58749 | 0 | 0.06126 | 0 | 0 | 0 | 0.58749 | 0 | 0
12 | 11 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 519.9706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 530.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 522.7069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 510.0677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 485.692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 471.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 457.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 11 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 447.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 447.7169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 454.8246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 465.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 489.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 516.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 522.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 526.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 7 | 0 | 27.9223 | 27.9223 | 48 | 5.2518 | 13.4431 | 13.4431 | 525.4396 | 27.9223 | 0 | 13331.2298 | 0 | 0 | 0 | 27.9223 | 0 | 0 | 13331.2298
12 | 12 | 8 | 0 | 93.0949 | 93.0949 | 48 | 6.2094 | 57.5146 | 57.5146 | 523.8596 | 93.0949 | 0 | 44300.0834 | 0 | 0 | 0 | 93.0949 | 0 | 0 | 44300.0834
12 | 12 | 9 | 0.015 | 329.3516 | 329.3666 | 47.9983 | 7.328 | 304.0955 | 288 | 524.9593 | 311.9335 | 17.4331 | 148780.1286 | 1.8178 | 0 | 0 | 311.9335 | 17.4331 | 0 | 148780.1286
12 | 12 | 10 | 0 | 300.8109 | 300.8109 | 48 | 8.5482 | 602.9592 | 288 | 523.9697 | 143.6806 | 157.1303 | 68387.6172 | 16.3844 | 0 | 0 | 143.6806 | 157.1303 | 0 | 68387.6172
12 | 12 | 11 | 0 | 308.8051 | 308.8051 | 48 | 9.1838 | 1586.7558 | 288 | 519.9121 | 56.0489 | 252.7563 | 26450.1435 | 26.3556 | 0 | 0 | 56.0489 | 252.7563 | 0 | 26450.1435
12 | 12 | 12 | 0 | 293.9597 | 293.9597 | 48 | 9.8701 | 0 | 0 | 518.1898 | 0 | 293.9597 | 0 | 30.6519 | 0 | 0 | 0 | 293.9597 | 0 | 0
12 | 12 | 13 | 0.030833 | 381.3297 | 381.3605 | 47.997 | 9.6668 | 0 | 0 | 516.331 | 0 | 381.3605 | 0 | 39.7655 | 0 | 0 | 0 | 381.3605 | 0 | 0
12 | 12 | 14 | 0 | 284.0994 | 284.0994 | 48 | 10.2684 | 0 | 0 | 515.2676 | 0 | 284.0994 | 0 | 29.6238 | 0 | 0 | 0 | 284.0994 | 0 | 0
12 | 12 | 15 | 0 | 9.8441 | 9.8441 | 48 | 11.226 | 0 | 0 | 528.5534 | 0 | 9.8441 | 0 | 1.0265 | 0 | 0 | 0 | 9.8441 | 0 | 0
12 | 12 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 532.7502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 535.9682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 542.8481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 546.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 545.8745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 538.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 533.0135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 12 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 531.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 532.825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 527.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 518.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 510.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 516.1656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 518.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 522.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 523.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 8 | 0.10917 | 22.2738 | 22.3829 | 47.8195 | 6.2094 | 13.8283 | 13.8283 | 523.2433 | 22.3829 | 0 | 10641.3777 | 0 | 0 | 0 | 22.3829 | 0 | 0 | 10641.3777
12 | 13 | 9 | 0.051667 | 20.9045 | 20.9561 | 47.9088 | 7.311 | 19.2044 | 19.2044 | 522.96 | 20.9561 | 0 | 9955.2415 | 0 | 0 | 0 | 20.9561 | 0 | 0 | 9955.2415
12 | 13 | 10 | 0 | 22.8689 | 22.8689 | 48 | 8.0567 | 31.1481 | 31.1481 | 523.483 | 22.8689 | 0 | 10873.7714 | 0 | 0 | 0 | 22.8689 | 0 | 0 | 10873.7714
12 | 13 | 11 | 0 | 11.7294 | 11.7294 | 48 | 9.3109 | 87.6909 | 87.6909 | 527.2105 | 11.7294 | 0 | 5620.8644 | 0 | 0 | 0 | 11.7294 | 0 | 0 | 5620.8644
12 | 13 | 12 | 0 | 191.0695 | 191.0695 | 48 | 9.0058 | 682.8503 | 288 | 529.0908 | 80.5858 | 110.4837 | 38769.0711 | 11.5204 | 0 | 0 | 80.5858 | 110.4837 | 0 | 38769.0711
12 | 13 | 13 | 0 | 115.0487 | 115.0487 | 48 | 8.4889 | 218.1886 | 218.1886 | 529.5027 | 115.0487 | 0 | 55396.2545 | 0 | 0 | 0 | 115.0487 | 0 | 0 | 55396.2545
12 | 13 | 14 | 0 | 0 | 0 | 0 | 8.938 | 0 | 0 | 522.2531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 15 | 0 | 1.2825 | 1.2825 | 48 | 9.6075 | 0 | 0 | 522.4484 | 0 | 1.2825 | 0 | 0.13373 | 0 | 0 | 0 | 1.2825 | 0 | 0
12 | 13 | 16 | 0 | 0 | 0 | 0 | 10.9718 | 0 | 0 | 520.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 17 | 0 | 0 | 0 | 0 | 10.3786 | 0 | 0 | 520.6405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 18 | 0 | 0 | 0 | 0 | 11.0734 | 0 | 0 | 526.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 19 | 0 | 0 | 0 | 0 | 10.4633 | 0 | 0 | 520.6395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 20 | 0 | 0 | 0 | 0 | 8.0228 | 0 | 0 | 513.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 21 | 0 | 0 | 0 | 0 | 7.1076 | 0 | 0 | 502.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 22 | 0 | 0 | 0 | 0 | 5.2264 | 0 | 0 | 505.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 13 | 23 | 0 | 0 | 0 | 0 | 4.2265 | 0 | 0 | 502.2183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 0 | 0 | 0 | 0 | 0 | 4.1757 | 0 | 0 | 503.9003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 1 | 0 | 0 | 0 | 0 | 3.8791 | 0 | 0 | 516.8429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 2 | 0 | 0 | 0 | 0 | 3.8197 | 0 | 0 | 527.3569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 3 | 0 | 0 | 0 | 0 | 3.4638 | 0 | 0 | 529.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 4 | 0 | 0 | 0 | 0 | 3.4045 | 0 | 0 | 535.887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 5 | 0 | 0 | 0 | 0 | 3.6418 | 0 | 0 | 543.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 6 | 0 | 0 | 0 | 0 | 4.396 | 0 | 0 | 546.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 7 | 0 | 0 | 0 | 0 | 4.6502 | 0 | 0 | 545.5552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 8 | 0.29583 | 26.3027 | 26.5986 | 47.5885 | 5.1417 | 12.4887 | 12.4887 | 546.9836 | 26.5986 | 0 | 13283.1954 | 0 | 0 | 0 | 26.5986 | 0 | 0 | 13283.1954
12 | 14 | 9 | 0 | 65.0954 | 65.0954 | 48 | 6.6161 | 45.7165 | 45.7165 | 545.1522 | 65.0954 | 0 | 32362.3204 | 0 | 0 | 0 | 65.0954 | 0 | 0 | 32362.3204
12 | 14 | 10 | 0 | 8.5293 | 8.5293 | 48 | 6.9721 | 6.8044 | 6.8044 | 545.6058 | 8.5293 | 0 | 4244.247 | 0 | 0 | 0 | 8.5293 | 0 | 0 | 4244.247
12 | 14 | 11 | 0 | 100.4463 | 100.4463 | 48 | 8.5652 | 204.6679 | 204.6679 | 545.611 | 100.4463 | 0 | 49983.1806 | 0 | 0 | 0 | 100.4463 | 0 | 0 | 49983.1806
12 | 14 | 12 | 0 | 294.7009 | 294.7009 | 48 | 7.8957 | 363.2534 | 288 | 547.231 | 233.6492 | 61.0517 | 116644.9171 | 6.366 | 0 | 0 | 233.6492 | 61.0517 | 0 | 116644.9171
12 | 14 | 13 | 24.2242 | 439.773 | 463.9971 | 46.0683 | 7.4381 | 450.3248 | 288 | 551.0308 | 296.744 | 167.2531 | 149844.585 | 17.4399 | 0 | 0 | 296.744 | 167.2531 | 0 | 149844.585
12 | 14 | 14 | 23.9655 | 400.2404 | 424.206 | 45.9097 | 7.2771 | 383.0494 | 288 | 543.5316 | 318.9441 | 105.2619 | 158713.5548 | 10.9759 | 0 | 0 | 318.9441 | 105.2619 | 0 | 158713.5548
12 | 14 | 15 | 0 | 1.555 | 1.555 | 48 | 7.3449 | 1.4465 | 1.4465 | 545.7243 | 1.555 | 0 | 773.9565 | 0 | 0 | 0 | 1.555 | 0 | 0 | 773.9565
12 | 14 | 16 | 0 | 0 | 0 | 0 | 6.9975 | 0 | 0 | 545.2519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 17 | 0 | 0 | 0 | 0 | 7.167 | 0 | 0 | 549.1822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 18 | 0 | 0 | 0 | 0 | 6.7094 | 0 | 0 | 559.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 19 | 0 | 0 | 0 | 0 | 7.3958 | 0 | 0 | 557.9083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 20 | 0 | 0 | 0 | 0 | 6.9721 | 0 | 0 | 553.3865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 21 | 0 | 0 | 0 | 0 | 6.1924 | 0 | 0 | 539.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 22 | 0 | 0 | 0 | 0 | 4.5824 | 0 | 0 | 532.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 14 | 23 | 0 | 0 | 0 | 0 | 4.2615 | 0 | 0 | 527.3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 0 | 0 | 0 | 0 | 0 | 3.5232 | 0 | 0 | 527.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 1 | 0 | 0 | 0 | 0 | 3.1079 | 0 | 0 | 524.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 2 | 0 | 0 | 0 | 0 | 3.0232 | 0 | 0 | 527.9798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 3 | 0 | 0 | 0 | 0 | 2.9893 | 0 | 0 | 514.6201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 4 | 0 | 0 | 0 | 0 | 2.9469 | 0 | 0 | 519.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 5 | 0 | 0 | 0 | 0 | 3.091 | 0 | 0 | 514.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 6 | 0 | 0 | 0 | 0 | 4.6163 | 0 | 0 | 524.2777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 7 | 0 | 4.9923 | 4.9923 | 48 | 6.1924 | 3.0689 | 3.0689 | 531.0917 | 4.9923 | 0 | 2411.7199 | 0 | 0 | 0 | 4.9923 | 0 | 0 | 2411.7199
12 | 15 | 8 | 0 | 68.2935 | 68.2935 | 48 | 6.8788 | 52.6094 | 52.6094 | 530.2092 | 68.2935 | 0 | 32931.7701 | 0 | 0 | 0 | 68.2935 | 0 | 0 | 32931.7701
12 | 15 | 9 | 0 | 201.4039 | 201.4039 | 48 | 7.3195 | 185.257 | 185.257 | 526.0487 | 201.4039 | 0 | 96280.8563 | 0 | 0 | 0 | 201.4039 | 0 | 0 | 96280.8563
12 | 15 | 10 | 0 | 268.1654 | 268.1654 | 48 | 7.4805 | 265.4903 | 265.4903 | 523.5537 | 268.1654 | 0 | 127527.0597 | 0 | 0 | 0 | 268.1654 | 0 | 0 | 127527.0597
12 | 15 | 11 | 0 | 118.6404 | 118.6404 | 48 | 7.2263 | 104.8257 | 104.8257 | 525.366 | 118.6404 | 0 | 56634.897 | 0 | 0 | 0 | 118.6404 | 0 | 0 | 56634.897
12 | 15 | 12 | 0 | 195.8903 | 195.8903 | 48 | 7.8703 | 237.8889 | 237.8889 | 522.2371 | 195.8903 | 0 | 92898.4644 | 0 | 0 | 0 | 195.8903 | 0 | 0 | 92898.4644
12 | 15 | 13 | 0 | 190.4732 | 190.4732 | 48 | 8.1754 | 281.1827 | 281.1827 | 521.3378 | 190.4732 | 0 | 90158.1405 | 0 | 0 | 0 | 190.4732 | 0 | 0 | 90158.1405
12 | 15 | 14 | 0 | 181.9128 | 181.9128 | 48 | 8.2431 | 282.0599 | 282.0599 | 524.145 | 181.9128 | 0 | 86616.8641 | 0 | 0 | 0 | 181.9128 | 0 | 0 | 86616.8641
12 | 15 | 15 | 0 | 0.0033313 | 0.0033313 | 48 | 7.4212 | 0.0032078 | 0.0032078 | 530.6521 | 0.0033313 | 0 | 1.6078 | 0 | 0 | 0 | 0.0033313 | 0 | 0 | 1.6078
12 | 15 | 16 | 0 | 0 | 0 | 0 | 7.3195 | 0 | 0 | 526.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 17 | 0 | 0 | 0 | 0 | 7.2686 | 0 | 0 | 520.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 18 | 0 | 0 | 0 | 0 | 6.9297 | 0 | 0 | 522.4028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 19 | 0 | 0 | 0 | 0 | 6.9382 | 0 | 0 | 516.8549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 20 | 0 | 0 | 0 | 0 | 6.2772 | 0 | 0 | 512.4423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 21 | 0 | 0 | 0 | 0 | 5.6332 | 0 | 0 | 501.6124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 22 | 0 | 0 | 0 | 0 | 4.7434 | 0 | 0 | 488.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 15 | 23 | 0 | 0 | 0 | 0 | 4.1248 | 0 | 0 | 482.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 0 | 0 | 0 | 0 | 0 | 3.6503 | 0 | 0 | 481.4703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 1 | 0 | 0 | 0 | 0 | 3.4384 | 0 | 0 | 486.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 2 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 489.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 3 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 487.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 4 | 0 | 0 | 0 | 0 | 3.3622 | 0 | 0 | 493.7554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 16 | 5 | 74.0546 | 0 | 74.0546 | 11 | 3.3706 | 24.8695 | 24.8695 | 492.2179 | 74.0546 | 0 | 35636.4183 | 0 | 0 | 0 | 74.0546 | 0 | 0 | 35636.4183
12 | 16 | 6 | 142.1102 | 0 | 142.1102 | 11 | 4.4638 | 57.9007 | 57.9007 | 494.4515 | 142.1102 | 0 | 68703.3808 | 0 | 0 | 0 | 142.1102 | 0 | 0 | 68703.3808
12 | 16 | 7 | 148.6573 | 0.01325 | 148.6706 | 11.0033 | 6.006 | 86.638 | 86.638 | 499.236 | 148.6706 | 0 | 72585.8471 | 0 | 0 | 0 | 148.6706 | 0 | 0 | 72585.8471
12 | 16 | 8 | 114.1113 | 0 | 114.1113 | 11 | 6.6246 | 80.3694 | 80.3694 | 495.2763 | 114.1113 | 0 | 55261.3855 | 0 | 0 | 0 | 114.1113 | 0 | 0 | 55261.3855
12 | 16 | 9 | 138.9093 | 0.059078 | 138.9684 | 11.0157 | 7.1924 | 121.051 | 121.051 | 486.3076 | 138.9684 | 0 | 66050.5412 | 0 | 0 | 0 | 138.9684 | 0 | 0 | 66050.5412
12 | 16 | 10 | 100.6212 | 0.335 | 100.9562 | 11.1228 | 7.0398 | 82.6804 | 82.6804 | 488.1016 | 100.9562 | 0 | 48153.985 | 0 | 0 | 0 | 100.9562 | 0 | 0 | 48153.985
12 | 16 | 11 | 110.2499 | 0.81083 | 111.0608 | 11.2701 | 7.2093 | 97.4302 | 97.4302 | 487.0031 | 111.0608 | 0 | 52835.2634 | 0 | 0 | 0 | 111.0608 | 0 | 0 | 52835.2634
12 | 16 | 12 | 118.8192 | 8.9425 | 127.7617 | 13.5898 | 7.9296 | 160.6957 | 160.6957 | 486.872 | 127.7617 | 0 | 60467.344 | 0 | 0 | 0 | 127.7617 | 0 | 0 | 60467.344
12 | 16 | 13 | 116.5574 | 0 | 116.5574 | 11 | 8.2601 | 183.0275 | 183.0275 | 495.9821 | 116.5574 | 0 | 56528.2569 | 0 | 0 | 0 | 116.5574 | 0 | 0 | 56528.2569
12 | 16 | 14 | 108.3697 | 0 | 108.3697 | 11 | 8.5313 | 213.7449 | 213.7449 | 504.1701 | 108.3697 | 0 | 53444.711 | 0 | 0 | 0 | 108.3697 | 0 | 0 | 53444.711
12 | 16 | 15 | 112.3649 | 0 | 112.3649 | 11 | 8.4041 | 197.8742 | 197.8742 | 516.0786 | 112.3649 | 0 | 56753.1287 | 0 | 0 | 0 | 112.3649 | 0 | 0 | 56753.1287
12 | 16 | 16 | 142.2953 | 0 | 142.2953 | 11 | 9.1753 | 716.2354 | 288 | 512.6784 | 57.2173 | 85.078 | 28704.6827 | 8.8713 | 0 | 0 | 57.2173 | 85.078 | 0 | 28704.6827
12 | 16 | 17 | 128.5397 | 0 | 128.5397 | 11 | 8.6753 | 293.4458 | 288 | 515.3638 | 126.1543 | 2.3854 | 63627.6461 | 0.24874 | 0 | 0 | 126.1543 | 2.3854 | 0 | 63627.6461
12 | 16 | 18 | 107.613 | 0 | 107.613 | 11 | 9.0397 | 408.2691 | 288 | 514.404 | 75.9121 | 31.701 | 38214.4399 | 3.3055 | 0 | 0 | 75.9121 | 31.701 | 0 | 38214.4399
12 | 16 | 19 | 104.6849 | 0 | 104.6849 | 11 | 7.6754 | 114.1895 | 114.1895 | 506.9275 | 104.6849 | 0 | 51916.132 | 0 | 0 | 0 | 104.6849 | 0 | 0 | 51916.132
12 | 16 | 20 | 103.8259 | 0 | 103.8259 | 11 | 10.8362 | 0 | 0 | 500.8077 | 0 | 103.8259 | 0 | 10.8262 | 0 | 0 | 0 | 103.8259 | 0 | 0
12 | 16 | 21 | 76.7613 | 0 | 76.7613 | 11 | 8.7685 | 195.1186 | 195.1186 | 492.1047 | 76.7613 | 0 | 36930.2185 | 0 | 0 | 0 | 76.7613 | 0 | 0 | 36930.2185
12 | 16 | 22 | 96.0002 | 0 | 96.0002 | 11 | 5.1247 | 44.9034 | 44.9034 | 483.2378 | 96.0002 | 0 | 45334.9145 | 0 | 0 | 0 | 96.0002 | 0 | 0 | 45334.9145
12 | 16 | 23 | 204.2482 | 0 | 204.2482 | 11 | 4.4722 | 83.3557 | 83.3557 | 477.9185 | 204.2482 | 0 | 95367.2613 | 0 | 0 | 0 | 204.2482 | 0 | 0 | 95367.2613
12 | 17 | 0 | 154.8895 | 0 | 154.8895 | 11 | 2.9978 | 49.074 | 49.074 | 480.9314 | 154.8895 | 0 | 72787.4277 | 0 | 0 | 0 | 154.8895 | 0 | 0 | 72787.4277
12 | 17 | 1 | 142.7066 | 0 | 142.7066 | 11 | 2.8876 | 44.471 | 44.471 | 482.3266 | 142.7066 | 0 | 67261.4183 | 0 | 0 | 0 | 142.7066 | 0 | 0 | 67261.4183
12 | 17 | 2 | 110.0178 | 0 | 110.0178 | 11 | 2.8791 | 34.241 | 34.241 | 488.2773 | 110.0178 | 0 | 52508.9738 | 0 | 0 | 0 | 110.0178 | 0 | 0 | 52508.9738
12 | 17 | 3 | 155.1338 | 0 | 155.1338 | 11 | 3.0147 | 49.2781 | 49.2781 | 493.1638 | 155.1338 | 0 | 74799.883 | 0 | 0 | 0 | 155.1338 | 0 | 0 | 74799.883
12 | 17 | 4 | 118.8771 | 0 | 118.8771 | 11 | 3.0317 | 37.8588 | 37.8588 | 496.8963 | 118.8771 | 0 | 57761.9557 | 0 | 0 | 0 | 118.8771 | 0 | 0 | 57761.9557
12 | 17 | 5 | 162.9934 | 0 | 162.9934 | 11 | 3.4638 | 55.5702 | 55.5702 | 506.4703 | 162.9934 | 0 | 80758.3694 | 0 | 0 | 0 | 162.9934 | 0 | 0 | 80758.3694
12 | 17 | 6 | 96.396 | 0 | 96.396 | 11 | 4.1926 | 37.3021 | 37.3021 | 509.346 | 96.396 | 0 | 48038.5782 | 0 | 0 | 0 | 96.396 | 0 | 0 | 48038.5782
12 | 17 | 7 | 41.5813 | 0.11079 | 41.6921 | 11.0983 | 4.8705 | 18.4508 | 18.4508 | 497.8631 | 41.6921 | 0 | 20294.2267 | 0 | 0 | 0 | 41.6921 | 0 | 0 | 20294.2267
12 | 17 | 8 | 0 | 0 | 0 | 0 | 4.8451 | 0 | 0 | 499.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 9 | 0 | 0 | 0 | 0 | 6.3789 | 0 | 0 | 499.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 10 | 0 | 0 | 0 | 0 | 8.4804 | 0 | 0 | 501.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 11 | 0 | 0 | 0 | 0 | 9.4549 | 0 | 0 | 503.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 12 | 0 | 0 | 0 | 0 | 9.8362 | 0 | 0 | 500.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 13 | 0 | 0 | 0 | 0 | 9.6159 | 0 | 0 | 494.7516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 14 | 0 | 0 | 0 | 0 | 9.5227 | 0 | 0 | 494.3165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 15 | 0 | 0 | 0 | 0 | 10.7175 | 0 | 0 | 499.2717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 16 | 0 | 0.21333 | 0.21333 | 48 | 12.0564 | 0 | 0 | 502.5244 | 0 | 0.21333 | 0 | 0.022245 | 0 | 0 | 0 | 0.21333 | 0 | 0
12 | 17 | 17 | 0 | 0 | 0 | 0 | 11.8107 | 0 | 0 | 503.5758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 18 | 0 | 0 | 0 | 0 | 12.3445 | 0 | 0 | 496.8127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 19 | 0 | 0 | 0 | 0 | 12.2767 | 0 | 0 | 484.3784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 20 | 0 | 0 | 0 | 0 | 12.853 | 0 | 0 | 468.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 21 | 0 | 0 | 0 | 0 | 8.8533 | 0 | 0 | 460.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 22 | 0 | 0 | 0 | 0 | 5.04 | 0 | 0 | 453.1897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 17 | 23 | 0 | 0 | 0 | 0 | 3.3504 | 0 | 0 | 444.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 0 | 0 | 0 | 0 | 0 | 3.252 | 0 | 0 | 442.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 1 | 0 | 0 | 0 | 0 | 3.1418 | 0 | 0 | 447.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 2 | 0 | 0 | 0 | 0 | 3.0401 | 0 | 0 | 454.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 466.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 4 | 0 | 0 | 0 | 0 | 3.3706 | 0 | 0 | 479.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 5 | 0 | 0 | 0 | 0 | 3.6164 | 0 | 0 | 481.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 6 | 0 | 0 | 0 | 0 | 4.4722 | 0 | 0 | 475.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 7 | 0 | 0 | 0 | 0 | 4.8281 | 0 | 0 | 475.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 8 | 0 | 0 | 0 | 0 | 5.4976 | 0 | 0 | 485.671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 9 | 0 | 0 | 0 | 0 | 6.4043 | 0 | 0 | 478.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 10 | 0 | 7.8917 | 7.8917 | 48 | 8.5991 | 16.6298 | 16.6298 | 472.662 | 7.8917 | 0 | 3351.2952 | 0 | 0 | 0 | 7.8917 | 0 | 0 | 3351.2952
12 | 18 | 11 | 0 | 0 | 0 | 0 | 9.6413 | 0 | 0 | 466.373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 12 | 0 | 0 | 0 | 0 | 9.7176 | 0 | 0 | 464.7797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 13 | 0 | 37.7629 | 37.7629 | 48 | 9.7939 | 0 | 0 | 459.0049 | 0 | 37.7629 | 0 | 3.9376 | 0 | 0 | 0 | 37.7629 | 0 | 0
12 | 18 | 14 | 0 | 29.8206 | 29.8206 | 48 | 9.4634 | 491.0162 | 288 | 462.9938 | 17.4909 | 12.3297 | 7258.6206 | 1.2856 | 0 | 0 | 17.4909 | 12.3297 | 0 | 7258.6206
12 | 18 | 15 | 0 | 0.0016658 | 0.0016658 | 48 | 10.5311 | 0 | 0 | 463.9591 | 0 | 0.0016658 | 0 | 0.0001737 | 0 | 0 | 0 | 0.0016658 | 0 | 0
12 | 18 | 16 | 0 | 0 | 0 | 0 | 11.0904 | 0 | 0 | 465.7452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 17 | 0 | 0 | 0 | 0 | 11.1073 | 0 | 0 | 480.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 18 | 0 | 0 | 0 | 0 | 11.4802 | 0 | 0 | 472.1116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 19 | 0 | 0 | 0 | 0 | 12.6496 | 0 | 0 | 453.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 20 | 0 | 0 | 0 | 0 | 12.2428 | 0 | 0 | 434.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 21 | 0 | 0 | 0 | 0 | 9.4634 | 0 | 0 | 418.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 22 | 0 | 0 | 0 | 0 | 5.8196 | 0 | 0 | 410.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 18 | 23 | 0 | 0 | 0 | 0 | 4.3028 | 0 | 0 | 402.283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 0 | 0 | 0 | 0 | 0 | 3.6333 | 0 | 0 | 398.6308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 1 | 0 | 0 | 0 | 0 | 3.3198 | 0 | 0 | 406.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 2 | 0 | 0 | 0 | 0 | 3.2096 | 0 | 0 | 418.9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 3 | 0 | 0 | 0 | 0 | 3.2435 | 0 | 0 | 443.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 4 | 0 | 0 | 0 | 0 | 3.2689 | 0 | 0 | 465.1473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 5 | 0 | 0 | 0 | 0 | 3.8536 | 0 | 0 | 471.1635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 6 | 0 | 0 | 0 | 0 | 5.0061 | 0 | 0 | 470.0572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 7 | 0 | 0 | 0 | 0 | 5.2518 | 0 | 0 | 468.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 8 | 0 | 1.6503 | 1.6503 | 48 | 6.2094 | 1.0196 | 1.0196 | 467.0318 | 1.6503 | 0 | 691.5224 | 0 | 0 | 0 | 1.6503 | 0 | 0 | 691.5224
12 | 19 | 9 | 0 | 35.8983 | 35.8983 | 48 | 7.328 | 33.144 | 33.144 | 462.2293 | 35.8983 | 0 | 14870.1413 | 0 | 0 | 0 | 35.8983 | 0 | 0 | 14870.1413
12 | 19 | 10 | 0 | 270.6108 | 270.6108 | 48 | 8.5482 | 542.4247 | 288 | 462.4297 | 143.6806 | 126.9302 | 59545.5048 | 13.2353 | 0 | 0 | 143.6806 | 126.9302 | 0 | 59545.5048
12 | 19 | 11 | 0 | 23.52 | 23.52 | 48 | 9.1838 | 120.8547 | 120.8547 | 459.4817 | 23.52 | 0 | 9678.0665 | 0 | 0 | 0 | 23.52 | 0 | 0 | 9678.0665
12 | 19 | 12 | 0 | 15.3309 | 15.3309 | 48 | 9.8701 | 0 | 0 | 461.9271 | 0 | 15.3309 | 0 | 1.5986 | 0 | 0 | 0 | 15.3309 | 0 | 0
12 | 19 | 13 | 0 | 17.5803 | 17.5803 | 48 | 9.6668 | 0 | 0 | 466.4862 | 0 | 17.5803 | 0 | 1.8331 | 0 | 0 | 0 | 17.5803 | 0 | 0
12 | 19 | 14 | 0 | 34.1349 | 34.1349 | 48 | 10.2684 | 0 | 0 | 469.2543 | 0 | 34.1349 | 0 | 3.5593 | 0 | 0 | 0 | 34.1349 | 0 | 0
12 | 19 | 15 | 0 | 1.0267 | 1.0267 | 48 | 11.226 | 0 | 0 | 481.6295 | 0 | 1.0267 | 0 | 0.10706 | 0 | 0 | 0 | 1.0267 | 0 | 0
12 | 19 | 16 | 0 | 0 | 0 | 0 | 11.853 | 0 | 0 | 481.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 17 | 0 | 0 | 0 | 0 | 11.7514 | 0 | 0 | 486.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 18 | 0 | 0 | 0 | 0 | 12.4971 | 0 | 0 | 481.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 19 | 0 | 0 | 0 | 0 | 12.7428 | 0 | 0 | 456.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 20 | 0 | 0 | 0 | 0 | 12.2259 | 0 | 0 | 430.2992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 21 | 0 | 0 | 0 | 0 | 9.904 | 0 | 0 | 420.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 22 | 0 | 0 | 0 | 0 | 5.3366 | 0 | 0 | 418.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 19 | 23 | 0 | 0 | 0 | 0 | 4.2398 | 0 | 0 | 419.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 0 | 0 | 0 | 0 | 0 | 3.5147 | 0 | 0 | 418.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 1 | 0 | 0 | 0 | 0 | 3.2859 | 0 | 0 | 427.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 2 | 0 | 0 | 0 | 0 | 3.1842 | 0 | 0 | 440.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 3 | 0 | 0 | 0 | 0 | 3.1249 | 0 | 0 | 455.5185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 4 | 0 | 0 | 0 | 0 | 3.3028 | 0 | 0 | 483.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 5 | 0 | 0 | 0 | 0 | 3.7096 | 0 | 0 | 492.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 6 | 0 | 0 | 0 | 0 | 4.8366 | 0 | 0 | 494.6775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 7 | 0 | 0 | 0 | 0 | 5.0146 | 0 | 0 | 503.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 8 | 0 | 0 | 0 | 0 | 6.2094 | 0 | 0 | 506.9403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 20 | 9 | 0 | 25.1664 | 25.1664 | 48 | 7.311 | 23.0627 | 23.0627 | 505.8358 | 25.1664 | 0 | 11522.0648 | 0 | 0 | 0 | 25.1664 | 0 | 0 | 11522.0648
12 | 20 | 10 | 0 | 73.9339 | 73.9339 | 48 | 8.0567 | 100.7001 | 100.7001 | 502.137 | 73.9339 | 0 | 33576.0978 | 0 | 0 | 0 | 73.9339 | 0 | 0 | 33576.0978
12 | 20 | 11 | 0 | 63.7176 | 63.7176 | 48 | 9.3109 | 476.3618 | 288 | 495.84 | 38.5225 | 25.195 | 17251.9309 | 2.6272 | 0 | 0 | 38.5225 | 25.195 | 0 | 17251.9309
12 | 20 | 12 | 0 | 22.9724 | 22.9724 | 48 | 9.0058 | 82.0995 | 82.0995 | 498.4837 | 22.9724 | 0 | 10348.691 | 0 | 0 | 0 | 22.9724 | 0 | 0 | 10348.691